## Winter Forecast
Transformer Station | Net Extreme Winter Weather Station Peak Demand Forecast, Coincident to NE of Sudbury Region (MW)
| 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040
Calstock DS | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.5 | 5.5 | 5.5 | 5.6
Cochrane DS | 11.6 | 11.6 | 11.5 | 11.4 | 11.3 | 11.3 | 11.2 | 11.2 | 11.1 | 11.1 | 11 | 10.9 | 10.9 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8
Cochrane West DS | 3.5 | 3.5 | 3.5 | 3.5 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.7 | 3.7 | 3.7 | 3.7 | 3.8
Crystal Falls TS | 19.9 | 20.2 | 19.9 | 20.2 | 20.2 | 20.3 | 20.3 | 20.4 | 20.4 | 23.7 | 25.2 | 25.3 | 25.5 | 25.7 | 25.8 | 26.2 | 26.4 | 26.7 | 27 | 27.2
Dymond TS | 30.8 | 30.8 | 30.8 | 30.8 | 30.8 | 30.8 | 30.9 | 30.9 | 31 | 31 | 31 | 31 | 33.9 | 33.9 | 34 | 34.1 | 34.2 | 34.4 | 34.6 | 34.7
Fauquier DS | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.3 | 2.3 | 2.3
Hearst TS | 24.3 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.3 | 18.3 | 18.4 | 18.4 | 18.4 | 18.5 | 18.6 | 18.7 | 18.8
Herridge Lake DS | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.6 | 3.6 | 3.6 | 3.6 | 3.7 | 3.7
Hoyle DS | 7 | 7 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.3 | 7.3 | 7.4 | 7.4
Iroquois Falls DS | 5.2 | 5.2 | 5.2 | 5.2 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Kapuskasing TS | 6 | 5.9 | 5.9 | 5.8 | 5.8 | 5.8 | 5.8 | 5.7 | 5.7 | 5.7 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6
Kirkland Lake TS | 31.4 | 31.4 | 31.3 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.1 | 31.1 | 31.1 | 31.1 | 31.2 | 31.3 | 31.4 | 31.5 | 31.6
Laforest Road DS | 12.7 | 12.8 | 12.8 | 12.8 | 12.8 | 12.9 | 12.9 | 13 | 13 | 13 | 13.1 | 13.1 | 13.1 | 13.2 | 13.2 | 13.3 | 13.4 | 13.4 | 13.5 | 13.6
Mattawa DS | 5 | 5 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.3 | 5.3 | 5.3 | 5.4 | 5.4 | 5.4 | 5.5
Monteith DS | 2.9 | 2.9 | 2.9 | 2.9 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.2 | 3.2 | 3.2
Moosonee DS | 14.2 | 14.3 | 14.3 | 14.3 | 14.3 | 14.4 | 14.4 | 14.4 | 14.5 | 14.5 | 14.5 | 14.6 | 14.6 | 14.6 | 14.7 | 14.7 | 14.8 | 14.9 | 15 | 15.1
North Bay TS | 27.4 | 26.3 | 25.2 | 24 | 22.9 | 23.3 | 23.7 | 24.1 | 24.6 | 25 | 25.4 | 25.8 | 26.3 | 26.7 | 27.2 | 27.6 | 28.1 | 28.6 | 29.1 | 29.6
Otto Holden TS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ramore TS | 12.1 | 12.2 | 12.4 | 12.4 | 12.5 | 12.6 | 12.7 | 12.8 | 12.9 | 13.3 | 13.4 | 13.5 | 13.6 | 13.7 | 13.8 | 14 | 14.1 | 14.3 | 14.4 | 14.6
Shiningtree DS | 4 | 4 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 4 | 4 | 4
Smooth Rock Falls DS | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.9 | 1.9
Temagami DS 2 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.6 | 1.6
Timmins TS | 52.6 | 52.7 | 52.8 | 52.8 | 52.9 | 53.1 | 53.2 | 53.4 | 53.6 | 53.8 | 53.9 | 53.9 | 54.1 | 54.3 | 54.5 | 54.7 | 55 | 55.4 | 55.8 | 56.2
Trout Lake TS | 100.4 | 100.3 | 98.9 | 97.9 | 97 | 100.2 | 100.8 | 101.5 | 102 | 102.6 | 103.3 | 103.8 | 104.8 | 105.6 | 106.4 | 107.4 | 108.5 | 109.7 | 110.9 | 113.1
Verner DS | 5.9 | 5.9 | 5.9 | 5.9 | 5.9 | 5.9 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6.1 | 6.1 | 6.1 | 6.2
Warren DS | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.2 | 7.2 | 7.2 | 7.3
The IRRP planning forecast accounts for the median weather gross forecast provided by the local distributors, savings from distributed generation and conservation and demand management, as well as extreme weather adjustments. Full details on the overall IRRP forecast methodology will be provided in the IRRP report, once finalized.
This document and the information contained herein is provided for informational purposes only. The IESO has prepared this document based on information currently available to the IESO and reasonable assumptions associated therewith, including relating to electricity supply and demand. The information, statements and conclusions contained herein are subject to risks, uncertainties and other factors, and actual results or circumstances may differ materially. The IESO provides no guarantee, representation, or warranty, express or implied, with respect to any statement or information contained herein and disclaims any liability in connection therewith. Readers are cautioned not to place undue reliance on forward-looking information contained in this document as actual results could differ materially from the plans, expectations, estimates, intentions and statements expressed herein. The IESO undertakes no obligation to revise or update any information contained in this document as a result of new information, future events or otherwise. In the event there is any conflict or inconsistency between this document and the IESO market rules, any IESO contract, any legislation or regulation, or any request for proposals or other procurement document, the terms in the market rules, or the subject contract, legislation, regulation, or procurement document, as applicable, govern.
DRAFT

## Summer Forecast
Transformer Station | Net Extreme Summer Weather Station Peak Demand Forecast, Coincident to NE of Sudbury Region (MW)
| 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040
Calstock DS | 3.8 | 3.8 | 3.8 | 3.7 | 3.7 | 3.8 | 3.7 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.9 | 3.9
Cochrane DS | 10.2 | 10.1 | 10 | 9.9 | 9.8 | 9.8 | 9.7 | 9.6 | 9.5 | 9.5 | 9.4 | 9.3 | 9.3 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2
Cochrane West DS | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.7 | 2.7
Crystal Falls TS | 14.4 | 14.9 | 14.8 | 15.2 | 15.3 | 15.5 | 15.6 | 15.8 | 15.9 | 18.5 | 18.7 | 18.8 | 19 | 19.2 | 19.4 | 19.7 | 20 | 20.3 | 20.6 | 20.8
Dymond TS | 25.9 | 26 | 25.9 | 25.8 | 25.8 | 25.8 | 25.7 | 25.7 | 25.7 | 25.6 | 25.6 | 25.5 | 26.8 | 26.8 | 26.8 | 26.9 | 27 | 27.1 | 27.3 | 27.4
Fauquier DS | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2.1
Hearst TS | 12.7 | 12.6 | 12.5 | 12.6 | 12.6 | 12.6 | 12.5 | 12.5 | 12.4 | 12.4 | 12.3 | 12.3 | 12.3 | 12.2 | 12.2 | 12.3 | 12.3 | 12.4 | 12.4 | 12.5
Herridge Lake DS | 1.6 | 1.6 | 1.7 | 1.6 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7
Hoyle DS | 4.4 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.6 | 4.6
Iroquois Falls DS | 5 | 5 | 5 | 4.9 | 4.9 | 4.9 | 4.8 | 4.8 | 4.8 | 4.7 | 4.7 | 4.7 | 4.7 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.7 | 4.7
Kapuskasing TS | 36.1 | 36.2 | 36.2 | 36 | 35.9 | 35.9 | 35.8 | 35.8 | 35.7 | 35.6 | 35.5 | 35.4 | 35.4 | 35.4 | 35.4 | 35.5 | 35.7 | 36 | 36.2 | 36.4
Kirkland Lake TS | 17.1 | 17.1 | 17 | 16.9 | 16.9 | 16.8 | 16.8 | 16.7 | 16.7 | 16.7 | 16.7 | 16.6 | 16.6 | 16.5 | 16.5 | 16.5 | 16.6 | 16.6 | 16.7 | 16.8
Laforest Road DS | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11.1 | 11.1 | 11.1 | 11.2 | 11.3 | 11.4 | 11.5
Mattawa DS | 4.3 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.5 | 4.5 | 4.5 | 4.6 | 4.6
Monteith DS | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 2 | 2 | 2 | 2 | 2 | 2 | 2
Moosonee DS | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5.1 | 5.1 | 5.1
North Bay TS | 17.2 | 16.1 | 15 | 13.9 | 12.8 | 13.2 | 13.7 | 14.1 | 14.5 | 15 | 15.4 | 15.8 | 16.2 | 16.7 | 17.1 | 17.6 | 18.1 | 18.6 | 19.1 | 19.6
Otto Holden TS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ramore TS | 4.8 | 4.9 | 5 | 5 | 5 | 5 | 5.1 | 5.1 | 5.2 | 5.3 | 5.4 | 5.4 | 5.4 | 5.5 | 5.5 | 5.6 | 5.7 | 5.7 | 5.8 | 5.8
Shiningtree DS | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4
Smooth Rock Falls DS | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.7
Temagami DS 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.1 | 1.1 | 1.1
Timmins TS | 33.3 | 33.4 | 33.5 | 33.4 | 33.4 | 33.4 | 33.4 | 33.5 | 33.5 | 33.5 | 33.5 | 33.5 | 33.5 | 33.6 | 33.7 | 33.8 | 34 | 34.3 | 34.5 | 34.7
Trout Lake TS | 68.4 | 67.4 | 66.1 | 64.9 | 63.8 | 66.8 | 67.1 | 67.6 | 67.8 | 68.1 | 68.5 | 68.8 | 69.3 | 69.8 | 70.4 | 71.2 | 72.1 | 73 | 74 | 75.3
Verner DS | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4.1 | 4.1
Warren DS | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 5 | 5 | 5
The IRRP planning forecast accounts for the median weather gross forecast provided by the local distributors, savings from distributed generation and conservation and demand management, as well as extreme weather adjustments. Full details on the overall IRRP forecast methodology will be provided in the IRRP report, once finalized.
This document and the information contained herein is provided for informational purposes only. The IESO has prepared this document based on information currently available to the IESO and reasonable assumptions associated therewith, including relating to electricity supply and demand. The information, statements and conclusions contained herein are subject to risks, uncertainties and other factors, and actual results or circumstances may differ materially. The IESO provides no guarantee, representation, or warranty, express or implied, with respect to any statement or information contained herein and disclaims any liability in connection therewith. Readers are cautioned not to place undue reliance on forward-looking information contained in this document as actual results could differ materially from the plans, expectations, estimates, intentions and statements expressed herein. The IESO undertakes no obligation to revise or update any information contained in this document as a result of new information, future events or otherwise. In the event there is any conflict or inconsistency between this document and the IESO market rules, any IESO contract, any legislation or regulation, or any request for proposals or other procurement document, the terms in the market rules, or the subject contract, legislation, regulation, or procurement document, as applicable, govern.
DRAFT

## Winter CDM
Transformer Station | Winter Weather Station CDM Forecast (MW)
| 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040
Calstock DS | 0.09 | 0.14 | 0.22 | 0.26 | 0.29 | 0.32 | 0.36 | 0.4 | 0.42 | 0.43 | 0.47 | 0.51 | 0.53 | 0.56 | 0.58 | 0.62 | 0.63 | 0.63 | 0.64 | 0.64
Cochrane MTS | 0.1 | 0.16 | 0.26 | 0.33 | 0.39 | 0.44 | 0.51 | 0.56 | 0.62 | 0.67 | 0.74 | 0.8 | 0.84 | 0.88 | 0.91 | 0.94 | 0.94 | 0.93 | 0.93 | 0.93
Cochrane West DS | 0.02 | 0.04 | 0.07 | 0.09 | 0.11 | 0.12 | 0.14 | 0.16 | 0.18 | 0.2 | 0.23 | 0.25 | 0.26 | 0.28 | 0.29 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Crystal Falls TS | 0.14 | 0.24 | 0.42 | 0.56 | 0.67 | 0.78 | 0.92 | 1.03 | 1.18 | 1.3 | 1.53 | 1.68 | 1.8 | 1.9 | 1.99 | 2.05 | 2.07 | 2.08 | 2.09 | 2.1
Dymond TS | 0.32 | 0.53 | 0.85 | 1.07 | 1.24 | 1.41 | 1.62 | 1.79 | 1.98 | 2.13 | 2.33 | 2.54 | 2.69 | 2.83 | 2.94 | 3.04 | 3.07 | 3.08 | 3.08 | 3.1
Fauquier DS | 0.01 | 0.02 | 0.03 | 0.04 | 0.05 | 0.06 | 0.08 | 0.09 | 0.1 | 0.11 | 0.13 | 0.14 | 0.15 | 0.16 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17
Hearst TS | 0.18 | 0.24 | 0.4 | 0.51 | 0.6 | 0.69 | 0.8 | 0.89 | 1.01 | 1.1 | 1.2 | 1.32 | 1.4 | 1.47 | 1.53 | 1.57 | 1.58 | 1.58 | 1.58 | 1.58
Herridge Lake DS | 0.03 | 0.05 | 0.08 | 0.1 | 0.12 | 0.13 | 0.16 | 0.17 | 0.2 | 0.21 | 0.24 | 0.26 | 0.27 | 0.29 | 0.3 | 0.31 | 0.31 | 0.32 | 0.32 | 0.32
Hoyle DS | 0.06 | 0.1 | 0.16 | 0.2 | 0.24 | 0.27 | 0.32 | 0.35 | 0.39 | 0.42 | 0.46 | 0.5 | 0.53 | 0.56 | 0.58 | 0.6 | 0.6 | 0.61 | 0.61 | 0.61
Iroquois Falls DS | 0.04 | 0.07 | 0.12 | 0.15 | 0.17 | 0.2 | 0.23 | 0.25 | 0.28 | 0.31 | 0.33 | 0.36 | 0.39 | 0.4 | 0.42 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43
Kapuskasing TS | 0.08 | 0.14 | 0.23 | 0.29 | 0.34 | 0.39 | 0.45 | 0.49 | 0.55 | 0.59 | 0.65 | 0.71 | 0.75 | 0.78 | 0.81 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84
Kirkland Lake TS | 0.37 | 0.61 | 0.95 | 1.17 | 1.34 | 1.49 | 1.72 | 1.88 | 2.04 | 2.16 | 2.35 | 2.56 | 2.7 | 2.82 | 2.94 | 3.05 | 3.08 | 3.1 | 3.11 | 3.12
Laforest Road DS | 0.12 | 0.21 | 0.33 | 0.42 | 0.48 | 0.55 | 0.64 | 0.7 | 0.78 | 0.84 | 0.92 | 1 | 1.07 | 1.12 | 1.17 | 1.21 | 1.23 | 1.23 | 1.24 | 1.24
Mattawa DS | 0.04 | 0.07 | 0.12 | 0.15 | 0.18 | 0.21 | 0.24 | 0.27 | 0.3 | 0.32 | 0.36 | 0.39 | 0.41 | 0.44 | 0.46 | 0.47 | 0.48 | 0.48 | 0.48 | 0.48
Monteith DS | 0.02 | 0.03 | 0.06 | 0.07 | 0.09 | 0.1 | 0.12 | 0.14 | 0.16 | 0.17 | 0.19 | 0.21 | 0.22 | 0.24 | 0.25 | 0.25 | 0.26 | 0.26 | 0.26 | 0.26
Moosonee DS | 0.14 | 0.23 | 0.37 | 0.47 | 0.54 | 0.61 | 0.71 | 0.78 | 0.86 | 0.92 | 1 | 1.1 | 1.16 | 1.22 | 1.27 | 1.32 | 1.33 | 1.34 | 1.34 | 1.35
North Bay TS | 0.11 | 0.18 | 0.28 | 0.39 | 0.49 | 0.61 | 0.7 | 0.78 | 0.88 | 0.95 | 1.05 | 1.18 | 1.27 | 1.35 | 1.4 | 1.43 | 1.46 | 1.49 | 1.51 | 1.53
Otto Holden TS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ramore TS | 0.04 | 0.06 | 0.1 | 0.16 | 0.22 | 0.29 | 0.32 | 0.35 | 0.39 | 0.42 | 0.46 | 0.51 | 0.55 | 0.58 | 0.59 | 0.59 | 0.6 | 0.61 | 0.61 | 0.62
Shiningtree DS | 0.04 | 0.07 | 0.11 | 0.14 | 0.16 | 0.18 | 0.21 | 0.22 | 0.24 | 0.26 | 0.28 | 0.3 | 0.32 | 0.34 | 0.35 | 0.36 | 0.37 | 0.37 | 0.37 | 0.37
Smooth Rock Falls DS | 0.02 | 0.03 | 0.05 | 0.06 | 0.07 | 0.08 | 0.09 | 0.1 | 0.11 | 0.12 | 0.13 | 0.14 | 0.15 | 0.16 | 0.17 | 0.17 | 0.17 | 0.17 | 0.18 | 0.18
Temagami DS 2 | 0.01 | 0.02 | 0.04 | 0.05 | 0.05 | 0.06 | 0.07 | 0.08 | 0.09 | 0.09 | 0.1 | 0.11 | 0.12 | 0.13 | 0.13 | 0.14 | 0.14 | 0.14 | 0.14 | 0.15
Timmins TS | 0.57 | 0.94 | 1.49 | 1.86 | 2.14 | 2.41 | 2.79 | 3.07 | 3.37 | 3.6 | 3.93 | 4.29 | 4.55 | 4.78 | 4.99 | 5.18 | 5.25 | 5.28 | 5.31 | 5.34
Trout Lake TS | 0.58 | 1.03 | 1.81 | 2.39 | 2.86 | 3.43 | 4.06 | 4.59 | 5.31 | 5.92 | 6.6 | 7.28 | 7.8 | 8.24 | 8.63 | 8.84 | 8.91 | 8.94 | 8.98 | 9.04
Verner DS | 0.03 | 0.06 | 0.1 | 0.13 | 0.16 | 0.19 | 0.22 | 0.25 | 0.29 | 0.33 | 0.36 | 0.4 | 0.42 | 0.44 | 0.46 | 0.47 | 0.47 | 0.47 | 0.47 | 0.47
Warren DS | 0.04 | 0.08 | 0.13 | 0.18 | 0.21 | 0.24 | 0.28 | 0.32 | 0.36 | 0.4 | 0.44 | 0.49 | 0.52 | 0.54 | 0.57 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58
Peak demand savings from codes and standards, as well as the delivery of conservation programs, were estimated for each sector and totalled for each station in the region. The analyses were conducted under normal weather conditions and can be adjusted to reflect extreme weather conditions. The resulting forecast savings were applied to gross demand to help determine the net peak demand for the IRRP planning forecast. Additional details on the overall IRRP forecast methodology will be provided in the final report.
DRAFT

## Summer CDM
Transformer Station | Summer Weather Station CDM Forecast (MW)
| 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040
Calstock DS | 0.07 | 0.11 | 0.17 | 0.21 | 0.24 | 0.27 | 0.31 | 0.34 | 0.36 | 0.37 | 0.4 | 0.44 | 0.46 | 0.49 | 0.51 | 0.54 | 0.55 | 0.55 | 0.55 | 0.56
Cochrane MTS | 0.09 | 0.17 | 0.29 | 0.37 | 0.45 | 0.51 | 0.59 | 0.66 | 0.75 | 0.81 | 0.89 | 0.97 | 1.02 | 1.07 | 1.1 | 1.12 | 1.12 | 1.11 | 1.11 | 1.1
Cochrane West DS | 0.02 | 0.03 | 0.06 | 0.09 | 0.11 | 0.12 | 0.15 | 0.16 | 0.19 | 0.21 | 0.24 | 0.26 | 0.28 | 0.29 | 0.3 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31
Crystal Falls TS | 0.14 | 0.26 | 0.46 | 0.62 | 0.76 | 0.89 | 1.05 | 1.19 | 1.37 | 1.53 | 1.71 | 1.89 | 2.03 | 2.14 | 2.25 | 2.32 | 2.35 | 2.36 | 2.38 | 2.4
Dymond TS | 0.29 | 0.5 | 0.84 | 1.09 | 1.29 | 1.48 | 1.72 | 1.92 | 2.15 | 2.33 | 2.56 | 2.79 | 2.96 | 3.11 | 3.23 | 3.32 | 3.34 | 3.34 | 3.34 | 3.35
Fauquier DS | 0.02 | 0.03 | 0.05 | 0.07 | 0.09 | 0.1 | 0.12 | 0.13 | 0.15 | 0.17 | 0.19 | 0.2 | 0.22 | 0.23 | 0.24 | 0.24 | 0.25 | 0.25 | 0.25 | 0.25
Hearst TS | 0.12 | 0.22 | 0.37 | 0.49 | 0.58 | 0.67 | 0.78 | 0.87 | 0.99 | 1.08 | 1.18 | 1.29 | 1.37 | 1.43 | 1.49 | 1.52 | 1.53 | 1.52 | 1.52 | 1.52
Herridge Lake DS | 0.02 | 0.03 | 0.05 | 0.06 | 0.08 | 0.09 | 0.1 | 0.12 | 0.13 | 0.14 | 0.16 | 0.17 | 0.19 | 0.2 | 0.2 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21
Hoyle DS | 0.04 | 0.07 | 0.12 | 0.16 | 0.19 | 0.22 | 0.26 | 0.29 | 0.32 | 0.35 | 0.39 | 0.42 | 0.45 | 0.47 | 0.49 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51
Iroquois Falls DS | 0.04 | 0.08 | 0.14 | 0.18 | 0.22 | 0.25 | 0.29 | 0.33 | 0.37 | 0.41 | 0.45 | 0.48 | 0.51 | 0.54 | 0.56 | 0.57 | 0.56 | 0.56 | 0.56 | 0.56
Kapuskasing TS | 0.38 | 0.67 | 1.17 | 1.54 | 1.84 | 2.11 | 2.47 | 2.77 | 3.15 | 3.45 | 3.8 | 4.15 | 4.41 | 4.63 | 4.81 | 4.93 | 4.94 | 4.93 | 4.92 | 4.93
Kirkland Lake TS | 0.26 | 0.42 | 0.67 | 0.84 | 0.97 | 1.09 | 1.25 | 1.38 | 1.5 | 1.58 | 1.71 | 1.86 | 1.97 | 2.06 | 2.15 | 2.24 | 2.26 | 2.27 | 2.27 | 2.28
Laforest Road DS | 0.11 | 0.2 | 0.34 | 0.44 | 0.53 | 0.6 | 0.7 | 0.79 | 0.89 | 0.97 | 1.07 | 1.17 | 1.24 | 1.3 | 1.36 | 1.4 | 1.41 | 1.41 | 1.41 | 1.42
Mattawa DS | 0.04 | 0.08 | 0.13 | 0.17 | 0.21 | 0.24 | 0.28 | 0.31 | 0.35 | 0.38 | 0.42 | 0.46 | 0.49 | 0.52 | 0.54 | 0.56 | 0.56 | 0.56 | 0.56 | 0.57
Monteith DS | 0.02 | 0.03 | 0.05 | 0.07 | 0.08 | 0.1 | 0.11 | 0.13 | 0.15 | 0.16 | 0.18 | 0.2 | 0.21 | 0.22 | 0.23 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24
Moosonee DS | 0.06 | 0.11 | 0.17 | 0.22 | 0.26 | 0.29 | 0.34 | 0.38 | 0.41 | 0.44 | 0.48 | 0.52 | 0.56 | 0.58 | 0.61 | 0.63 | 0.64 | 0.64 | 0.64 | 0.65
North Bay TS | 0.08 | 0.13 | 0.21 | 0.28 | 0.35 | 0.44 | 0.51 | 0.58 | 0.66 | 0.74 | 0.83 | 0.93 | 1.02 | 1.1 | 1.15 | 1.19 | 1.23 | 1.25 | 1.28 | 1.31
Otto Holden TS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ramore TS | 0.01 | 0.02 | 0.04 | 0.07 | 0.1 | 0.13 | 0.14 | 0.16 | 0.18 | 0.19 | 0.21 | 0.24 | 0.25 | 0.27 | 0.27 | 0.27 | 0.27 | 0.28 | 0.28 | 0.28
Shiningtree DS | 0.04 | 0.06 | 0.09 | 0.12 | 0.14 | 0.15 | 0.17 | 0.19 | 0.21 | 0.22 | 0.24 | 0.26 | 0.27 | 0.28 | 0.3 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31
Smooth Rock Falls DS | 0.02 | 0.03 | 0.05 | 0.07 | 0.08 | 0.09 | 0.11 | 0.12 | 0.13 | 0.14 | 0.16 | 0.17 | 0.18 | 0.19 | 0.2 | 0.2 | 0.21 | 0.21 | 0.21 | 0.21
Temagami DS 2 | 0.01 | 0.02 | 0.03 | 0.04 | 0.05 | 0.06 | 0.07 | 0.07 | 0.08 | 0.09 | 0.1 | 0.11 | 0.12 | 0.12 | 0.13 | 0.13 | 0.13 | 0.13 | 0.14 | 0.14
Timmins TS | 0.4 | 0.69 | 1.13 | 1.46 | 1.71 | 1.94 | 2.26 | 2.52 | 2.8 | 3.02 | 3.31 | 3.62 | 3.84 | 4.04 | 4.21 | 4.36 | 4.4 | 4.41 | 4.42 | 4.44
Trout Lake TS | 0.5 | 0.92 | 1.68 | 2.24 | 2.69 | 3.29 | 3.9 | 4.44 | 5.19 | 5.83 | 6.51 | 7.17 | 7.69 | 8.11 | 8.48 | 8.68 | 8.73 | 8.74 | 8.77 | 8.83
Verner DS | 0.03 | 0.05 | 0.1 | 0.13 | 0.16 | 0.19 | 0.23 | 0.26 | 0.3 | 0.33 | 0.37 | 0.4 | 0.43 | 0.45 | 0.46 | 0.47 | 0.47 | 0.47 | 0.47 | 0.47
Warren DS | 0.04 | 0.07 | 0.13 | 0.17 | 0.21 | 0.24 | 0.28 | 0.32 | 0.37 | 0.41 | 0.46 | 0.5 | 0.53 | 0.55 | 0.58 | 0.59 | 0.59 | 0.58 | 0.58 | 0.58
Peak demand savings from codes and standards, as well as the delivery of conservation programs, were estimated for each sector and totalled for each station in the region. The analyses were conducted under normal weather conditions and can be adjusted to reflect extreme weather conditions. The resulting forecast savings were applied to gross demand to help determine the net peak demand for the IRRP planning forecast. Additional details on the overall IRRP forecast methodology will be provided in the final report.
DRAFT

## Winter Effective DG
Transformer Station | Winter Weather Effective DG Contribution to Peak (MW)
| 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040
Calstock DS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cochrane MTS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cochrane West DS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Crystal Falls TS | 3.28 | 3.28 | 3.28 | 3.28 | 3.28 | 3.28 | 3.28 | 3.28 | 3.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Dymond TS | 2.86 | 2.86 | 2.86 | 2.86 | 2.86 | 2.86 | 2.86 | 2.86 | 2.86 | 2.86 | 2.86 | 2.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fauquier DS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hearst TS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Herridge Lake DS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hoyle DS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iroquois Falls DS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kapuskasing TS | 4.07 | 4.07 | 4.07 | 4.07 | 4.07 | 4.07 | 4.07 | 4.07 | 4.07 | 4.07 | 4.07 | 4.07 | 4.07 | 4.07 | 4.07 | 4.07 | 4.07 | 4.07 | 4.07 | 4.07
Kirkland Lake TS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Laforest Road DS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mattawa DS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Monteith DS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Moosonee DS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Bay TS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Otto Holden TS | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ramore TS | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Shiningtree DS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Smooth Rock Falls DS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Temagami DS 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Timmins TS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Trout Lake TS | 5.49 | 5.49 | 5.49 | 5.49 | 5.49 | 5.49 | 5.49 | 5.49 | 5.49 | 5.49 | 5.27 | 5.27 | 5.01 | 5.01 | 5.01 | 5.01 | 5.01 | 5.01 | 5.01 | 3.95
Verner DS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Warren DS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Peak demand contribution from contracted, existing distributed generation was estimated based on technology type and totalled for each station in the region. The resulting forecast savings were applied to gross demand to help determine the net peak demand for the IRRP planning forecast. Additional details on the overall IRRP forecast methodology will be provided in the final report.
DRAFT

## Summer Effective DG
Transformer Station | Summer Weather Effective DG Contribution to Peak (MW)
| 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040
Calstock DS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cochrane MTS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cochrane West DS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Crystal Falls TS | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 0.74 | 0.74 | 0.74 | 0.74 | 0.72 | 0.71 | 0.24 | 0 | 0 | 0 | 0
Dymond TS | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.6 | 2.6 | 1.28 | 1.26 | 0.53 | 0 | 0 | 0 | 0 | 0
Fauquier DS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hearst TS | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Herridge Lake DS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hoyle DS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iroquois Falls DS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kapuskasing TS | 5.68 | 5.68 | 5.68 | 5.68 | 5.68 | 5.68 | 5.68 | 5.68 | 5.68 | 5.68 | 5.68 | 5.68 | 5.68 | 4.64 | 4.58 | 4.58 | 4.58 | 4.58 | 4.58 | 4.58
Kirkland Lake TS | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 0.97 | 0.9 | 0.07 | 0 | 0 | 0
Laforest Road DS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mattawa DS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Monteith DS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Moosonee DS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Bay TS | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0
Otto Holden TS | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ramore TS | 1.21 | 1.21 | 1.21 | 1.21 | 1.21 | 1.21 | 1.21 | 1.21 | 1.21 | 1.1 | 1.1 | 1.1 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Shiningtree DS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Smooth Rock Falls DS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Temagami DS 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Timmins TS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Trout Lake TS | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.24 | 2.23 | 2.12 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 1.64
Verner DS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Warren DS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Peak demand contribution from contracted, existing distributed generation was estimated based on technology type and totalled for each station in the region. The resulting forecast savings were applied to gross demand to help determine the net peak demand for the IRRP planning forecast. Additional details on the overall IRRP forecast methodology will be provided in the final report.
DRAFT