## Menu
Reliability Outlook - Tables
2024-03-20
2024 Q1 Outlook
3.0 Demand Forecast: First 18 Months
Table 3.1: Historical and Forecast Energy Summary
Table 3.1.1: Monthly Peak and Energy Demand
Table 3.1.2: Weekly Coincident Peak Demand by Zone
Table 3.1.3: Weekly Energy Demand by Zone
Table 3.2: Forecasted Seasonal Peaks
Table 3.3: Weekly Energy and Peak Demand Forecast
Table 3.3.1: Weekly Weather and Demand History
Table 3.3.2: Monthly Weather and Demand History
Table 3.3.3: Monthly Consumption by Market Participant Type
Table 3.3.4: Economic Assumptions
Table 3.3.5: Weather Scenarios
Table 3.3.6: Contracted Embedded Capacity
4.0 Resource Adequacy Assessment: First 18 Months
Table 4.1: Existing Grid-Connected Resource Capacity
Table 4.2: Committed Generation Resources Status
Table 4.3: Monthly Historical Hydroelectric Median Values for Normal Weather Conditions
Figure 4.1: Monthly Wind Capacity Contribution Values
Figure 4.2: Monthly Solar Capacity Contribution Values
Table 4.4: Summary of Available Resources under Normal Weather
Table 4.5: Summary of Zonal Energy for Firm Scenario Normal Weather
Table 4.6: Ontario Energy Production by Fuel Type for the Firm Scenario Normal Weather
6.0 Operability Assessment: First 18 Months
Figure 6.3: Monthly Off-Peak Wind Capacity Contribution Values
Appendix A Resource Adequacy Assessment Details: First 18 Months
Table A1: Assessment of Resource Adequacy: Normal Weather, Firm Scenario
Table A2: Assessment of Resource Adequacy: Normal Weather, Planned Scenario
Table A3: Zonal Bottled Generation: Normal Weather, Both Scenarios
Table A4: Assessment of Resource Adequacy: Extreme Weather, Firm Scenario
Table A5: Assessment of Resource Adequacy: Extreme Weather, Planned Scenario
Table A6: Zonal Bottled Generation: Extreme Weather, Both Scenarios
Table A7: Energy Production Capability Forecast
Table A8: Reductions by Fuel Type: Normal Weather, Firm Scenario
Table A9: Firm Scenario - Normal Weather: Ontario Monthly Energy Production by Fuel Type
Appendix B Transmission Projects
Table B1: Transmission Projects
Table B2: Interface Limits with All Elements in Service
Table B3: Interconnection Flow Limits
Appendix C Transmission Outages
Table C1: Bruce Zone
Table C2: East Zone
Table C3: Essa Zone
Table C4: Niagara Zone
Table C5: Northeast Zone
Table C6: Northwest Zone
Table C7: Ottawa Zone
Table C8: Southwest Zone
Table C9: Toronto Zone
Table C10: West Zone
Table C11: External Interties

## Table 3.1
Back to main menu
Table 3.1 Historical and Forecast Energy Summary
Year | Normal Weather Energy (TWh) | % Growth in Energy
2006 | 152.349 | -1.858%
2007 | 151.6029 | -0.4897%
2008 | 148.9203 | -1.769%
2009 | 140.59 | -5.594%
2010 | 141.7415 | 0.819%
2011 | 141.0103 | -0.5158%
2012 | 140.7232 | -0.2036%
2013 | 140.4483 | -0.1954%
2014 | 139.4864 | -0.6848%
2015 | 136.3504 | -2.248%
2016 | 135.9259 | -0.3113%
2017 | 132.1965 | -2.744%
2018 | 135.5109 | 2.507%
2019 | 134.6666 | -0.6231%
2020 | 131.9143 | -2.044%
2021 | 133.7042 | 1.357%
2022 | 136.6504 | 2.204%
2023 | 138.0378 | 1.015%
2024 (Forecast) | 139.4996 | 1.059%
2025 (Forecast) | 141.5107 | 1.442%
Back to main menu

## Table 3.1.1
Back to main menu
Table 3.1.1: Monthly Peak and Energy Demand
Forecasted Peak and Energy Demand
| Peak Demand (MW) |  |  | Energy Demand (GWh)
Month | Current Forecast | Previous Forecast | Weather Corrected Actual | Current Forecast | Previous Forecast | Weather Corrected Actual
2012-01-01 | 22160.0997 | 22311.4705 | 22084.7322 | 13280.0235 | 13426.3128 | 12932.2873
2012-02-01 | 21813.8691 | 21969.9045 | 20756.8677 | 12202.5791 | 12342.1767 | 11380.2015
2012-03-01 | 20708.9072 | 20812.9741 | 20595.0545 | 12264.8125 | 12376.1481 | 11726.1779
2012-04-01 | 18745.092 | 18839.2949 | 19830.1533 | 10866.5786 | 10965.2216 | 10883.4994
2012-05-01 | 19038.2309 | 19133.9054 | 19736.9901 | 10943.6824 | 11043.0252 | 10838.5019
2012-06-01 | 22569.1521 | 22769.3781 | 22832.4909 | 11398.2442 | 11438.9546 | 11511.081
2012-07-01 | 23298.1422 | 23409.2742 | 23630.2664 | 12319.3311 | 12345.1403 | 13057.6199
2012-08-01 | 22956.5741 | 23120.2317 | 22726.501 | 12419.0386 | 12441.2801 | 12373.2613
2012-09-01 | 20506.0631 | 20801.4263 | 20370.1157 | 10811.3017 | 10908.5955 | 10900.4102
2012-10-01 | 18345.9037 | 18470.789 | 18684.153 | 11199.8353 | 11249.1624 | 11149.8822
2012-11-01 | 20571.5606 | 20719.6649 | 20258.2258 | 11629.6439 | 11647.1911 | 11663.449
2012-12-01 | 21693.287 | 21693.287 | 20910.8981 | 12612.0073 | 12612.0073 | 12306.8289
2012 | 23298.1422 | 23409.2742 | 23630.2664 | 141947.0782 | 142795.2156 | 140723.2004
2013-01-31 | 22013.997 | 22087.1815 | 22610 | 13314.3055 | 13414.0579 | 13061.0693
2013-02-28 | 21773.6201 | 21812.6402 | 21333.0082 | 11819.7381 | 11848.0211 | 11668.8474
2013-03-31 | 20634.9497 | 20655.2636 | 20784.4526 | 12283.0437 | 12234.9583 | 11869.9986
2013-04-30 | 18492.3312 | 18511.2916 | 19284.8182 | 11018.1303 | 10974.2592 | 11090.2932
2013-05-31 | 19100.9692 | 19112.1279 | 18341.9804 | 10932.3105 | 10888.1497 | 10533.5712
2013-06-30 | 22499.2459 | 22558.9581 | 22719.4401 | 11406.4319 | 11302.8302 | 11283.4325
2013-07-31 | 23212.9348 | 23274.7748 | 24352.1456 | 12479.5529 | 12365.1981 | 12736.3503
2013-08-31 | 22359.7987 | 22418.3572 | 23255.371 | 12227.7513 | 12114.2235 | 12084.9413
2013-09-30 | 20513.3592 | 20405.2189 | 20422.3176 | 11015.3041 | 10949.6326 | 10767.0057
2013-10-31 | 18388.3002 | 18346.8765 | 18981.007 | 11279.1846 | 11259.8117 | 11114.0467
2013-11-30 | 20326.4941 | 20278.2514 | 20034.8189 | 11686.9287 | 11540.2619 | 11709.7788
2013-12-31 | 21395.0558 | 21395.0558 | 21184.5386 | 12699.9803 | 12699.9803 | 12528.9266
2013 | 23212.9348 | 23274.7748 | 24352.1456 | 142162.6617 | 141591.3843 | 140448.2614
2014-01-31 | 22319.8106 | 22281.5654 | 22043.8439 | 13356.427 | 13460.4545 | 13409.7767
2014-02-28 | 20964.0592 | 21036.432 | 21218.2216 | 11748.3799 | 11801.9939 | 11812.9441
2014-03-31 | 19906 | 19976.2561 | 20728.4579 | 12054.5719 | 12104.2826 | 12242.1563
2014-04-30 | 17649 | 17587.1303 | 19249.9632 | 10731.1367 | 10788.8672 | 11038.5265
2014-05-31 | 18964 | 19048.9658 | 18750.4605 | 10790.2174 | 10851.4531 | 10546.4252
2014-06-30 | 22469.55 | 22435 | 20705.1957 | 11346.2756 | 11485.0325 | 11140.5499
2014-07-31 | 22948.69 | 23025 | 22294.8035 | 12360.0815 | 12350.9003 | 12324.9268
2014-08-31 | 21403.44 | 21483 | 21644.3547 | 11992.5131 | 11900.7025 | 11819.2371
2014-09-30 | 19023.2704 | 18933.24 | 19449.0766 | 10579.5258 | 10661.5775 | 10671.4853
2014-10-31 | 18638.7361 | 18588.6 | 18447.2196 | 11126.7565 | 11340.0968 | 10814.1957
2014-11-30 | 20302.34 | 20335.99 | 19923.2587 | 11497.4835 | 11729.6029 | 11410.1121
2014-12-31 | 21237.74 | 21117.85 | 21582.6701 | 12769.4956 | 12721.7996 | 12256.0958
2014 | 22948.69 | 23025 | 22294.8035 | 140352.8643 | 141196.7633 | 139486.4317
2015-01-31 | 22293.59 | 22148.5086 | 21503.4489 | 13068.9431 | 13008.638 | 12937.1182
2015-02-28 | 21016.81 | 20895.8261 | 19709.6284 | 11528.5197 | 11523.9679 | 11740.7311
2015-03-31 | 19840.93 | 19916.86 | 20109.8817 | 11856.8161 | 11909.1231 | 11748.227
2015-04-30 | 18121.2 | 18197.12 | 19362.8308 | 10542.0267 | 10616.7981 | 10624.618
2015-05-31 | 19370.33 | 19451.06 | 17881.7583 | 10635.9243 | 10710.0762 | 10231.5964
2015-06-30 | 22276.64 | 22318.29 | 20554.6293 | 11410.2692 | 11467.269 | 10908.724
2015-07-31 | 22888.49 | 22990.85 | 22638.5319 | 12174.2184 | 12268.7948 | 12273.6405
2015-08-31 | 21463.69 | 21573.24 | 22383 | 11821.2763 | 11926.0907 | 11782.7212
2015-09-30 | 18485 | 18470.35 | 19299.6325 | 10512.648 | 10527.7842 | 10718.9879
2015-10-31 | 18339 | 18288.43 | 18444.3181 | 11150.1256 | 11108.4988 | 10731.7474
2015-11-30 | 20306 | 20289.75 | 19631.9089 | 11595.0899 | 11611.8869 | 10867.5486
2015-12-31 | 21160.04 | 21041 | 20418.0801 | 12611.2501 | 12716.5842 | 11784.7123
2015 | 22888.49 | 22990.85 | 22638.5319 | 138907.1073 | 139395.512 | 136350.3725
2016-01-31 | 22360.24 | 22389 | 21249.7402 | 12982.1466 | 13133.9036 | 12523.599
2016-02-28 | 20985.25 | 20976 | 20194.6163 | 11806.8997 | 11905.4275 | 11502.97
2016-03-31 | 20075.21 | 20075.21 | 20324.618 | 11758.7447 | 11764.9017 | 11445.7227
2016-04-30 | 17405.08 | 17405.08 | 18912.1728 | 10309.6515 | 10355.9315 | 10578.9099
2016-05-31 | 19235.65 | 19235.65 | 19707.6447 | 10530.0143 | 10686.8299 | 10115.8584
2016-06-30 | 22315.7305 | 22310.79 | 21568.912 | 11378.6081 | 11376.3742 | 11141.3797
2016-07-31 | 22599.9414 | 22586.86 | 22288.7672 | 11896.1402 | 11847.0197 | 12345.0421
2016-08-31 | 21440.3166 | 21368.76 | 22375.997 | 11771.834 | 11711.8709 | 12295.9028
2016-09-30 | 18289 | 18302.4926 | 19712.7154 | 10401.8861 | 10424.2936 | 10659.2295
2016-10-31 | 18079 | 18165.7614 | 18394.9922 | 10947.5325 | 10932.0243 | 10453.1463
2016-11-30 | 20296 | 20406.3475 | 19544.7667 | 11524.026 | 11489.2943 | 10913.6011
2016-12-31 | 20888 | 20888 | 20286.7849 | 12430.7427 | 12430.7427 | 11950.5536
2016 | 22599.9414 | 22586.86 | 22375.997 | 137738.2263 | 138058.614 | 135925.9151
2017-01-31 | 21913.73 | 21981 | 20965.9674 | 12818.8508 | 12859.1363 | 12369.7298
2017-02-28 | 20966.2287 | 21043 | 20379.4501 | 11294.713 | 11332.858 | 10787.4931
2017-03-31 | 20137.3 | 20125.57 | 18692.3503 | 11824.0632 | 11820.8363 | 11413.3465
2017-04-30 | 17969.79 | 17999.63 | 18482.7844 | 10366.7129 | 10383.899 | 10105.7565
2017-05-31 | 19193.19 | 19223.9 | 18260.3078 | 10576.9018 | 10599.4394 | 10012.8427
2017-06-30 | 22454.87 | 22374.02 | 21144.8187 | 11159.3312 | 11176.8995 | 10682.999
2017-07-31 | 22492.73 | 22614.36 | 22152.8524 | 11984.7355 | 11995.2502 | 11851.6211
2017-08-31 | 22376.43 | 22378.02 | 21323.3584 | 12105.5471 | 12111.7263 | 11513.597
2017-09-30 | 19490.21 | 19328.32 | 17821.4732 | 10494.2948 | 10498.419 | 10155.927
2017-10-31 | 18030.62 | 17984.95 | 17407.7858 | 10942.7953 | 10911.8652 | 10260.3837
2017-11-30 | 20230.97 | 20247.95 | 19195.4397 | 11371.7451 | 11383.4887 | 10946.7668
2017-12-31 | 20901.44 | 20901.44 | 21439.6493 | 12303.6865 | 12303.6865 | 12096.0133
2017 | 22492.73 | 22614.36 | 22152.8524 | 137243.3774 | 137377.5044 | 132196.4765
2018-01-31 | 21618.93 | 21761.48 | 20177.5339 | 12685.9178 | 12739.2507 | 12679.8037
2018-02-28 | 20242.21 | 20303.37 | 20042.2165 | 11074.1738 | 11102.3023 | 11081.1365
2018-03-31 | 19551.97 | 19623.4 | 19330.8728 | 11423.555 | 11462.0987 | 11267.3415
2018-04-30 | 17669.81 | 17797.45 | 18107.9593 | 10157.8502 | 10189.0993 | 10586.2978
2018-05-31 | 18817.47 | 18914.03 | 19262.1307 | 10289.6502 | 10319.2302 | 10081.137
2018-06-30 | 21890.0001 | 21874.44 | 20626.9619 | 10863.4062 | 10862.0067 | 10980.4534
2018-07-31 | 22076.0001 | 22002.38 | 22409.0792 | 11652.7714 | 11637.8996 | 12483.776
2018-08-31 | 21946.0001 | 21936.42 | 21385.6483 | 11685.5744 | 11688.5067 | 12040.5393
2018-09-30 | 19019 | 19013.0001 | 19505.5646 | 10189.9802 | 10125.5779 | 10579.1906
2018-10-31 | 17788 | 17799.0001 | 17751.4152 | 10750.0648 | 10677.4838 | 10526.7735
2018-11-30 | 19828 | 19752.0001 | 19266.3918 | 11170.7506 | 11077.6035 | 11184.9393
2018-12-31 | 20503 | 20450.0001 | 20375.1864 | 12007.3958 | 11796.5086 | 12019.553
2018 | 22076.0001 | 22002.38 | 22409.0792 | 133951.0905 | 133677.568 | 135510.9416
2019-01-31 | 21506 | 21334 | 21058.2817 | 12973.2132 | 12767.5977 | 12688.8389
2019-02-28 | 20008 | 20016 | 20420.3692 | 11162.2057 | 11115.2732 | 11212.4836
2019-03-31 | 19457 | 19474 | 19573.6921 | 11522.1982 | 11474.3257 | 11458.0531
2019-04-30 | 17548 | 17605 | 18796.3299 | 10252.9314 | 10251.5353 | 10432.2785
2019-05-31 | 18663 | 18660 | 17977.0308 | 10412.0446 | 10413.1286 | 10218.7126
2019-06-30 | 21623 | 21570 | 21239.1838 | 10939.3571 | 10939.6692 | 10608.5215
2019-07-31 | 22061 | 22105 | 21120.5208 | 11763.9974 | 11911.1182 | 12446.1887
2019-08-31 | 21200 | 21550 | 22490.4547 | 11598.2109 | 11669.5054 | 11798.5843
2019-09-30 | 19469.84 | 18920 | 18958.9757 | 10564.4926 | 10160.875 | 10167.6302
2019-10-31 | 17559 | 17535 | 18814.592 | 10788.0047 | 10681.7179 | 10446.8836
2019-11-30 | 19597 | 19734 | 19001.8635 | 11194.6524 | 11149.8828 | 11094.2081
2019-12-31 | 20307 | 20437 | 20974 | 12086.6766 | 12159.4719 | 12094.1802
2019 | 22061 | 22105 | 22490.4547 | 135257.9849 | 134694.1009 | 134666.5633
2020-01-31 | 21185.0004 | 21115 | 21137.8728 | 12859.4588 | 12814.6236 | 12460.9405
2020-02-28 | 19917.0004 | 19853 | 19776.0281 | 11586.6754 | 11545.2458 | 11253.1814
2020-03-31 | 19377.0004 | 19318 | 19680.948 | 11522.322 | 11491.168 | 11058.3098
2020-04-30 | 17302.0004 | 17323.0004 | 16515.7848 | 10229.1483 | 10269.9312 | 9383.3554
2020-05-31 | 17426 | 18560.0004 | 18761.2836 | 9434.378 | 10330.8315 | 9306.4436
2020-06-30 | 20034 | 21540.0004 | 20741.8718 | 10274.389 | 11220.2712 | 10596.6512
2020-07-31 | 22364.4404 | 22195.0004 | 24057.7367 | 11731.6936 | 12010.2547 | 12529.7172
2020-08-31 | 21631.4406 | 21362.0004 | 25317.7535 | 11441.5908 | 11604.6804 | 12338.1938
2020-09-30 | 20312.4408 | 18817.0004 | 19254.2062 | 10356.1124 | 10324.3729 | 10011.2355
2020-10-31 | 17039.9727 | 16560.4413 | 17587.3164 | 10040.7873 | 10056.3893 | 10349.5982
2020-11-30 | 18891.9134 | 18730.4416 | 19416.1975 | 10531.6058 | 10535.5719 | 10693.8532
2020-12-31 | 19805.1651 | 19574.4417 | 20975.3455 | 11815.0887 | 11796.3797 | 11932.8039
2020 | 22364.4404 | 22195.0004 | 25317.7535 | 131823.25 | 133999.7201 | 131914.2838
2021-01-31 | 21176.0005 | 20837.4605 | 20951.6431 | 12539.1611 | 12334.6588 | 12307.6071
2021-02-28 | 20760.0005 | 20423.6173 | 20175.4672 | 11073.4765 | 10834.2847 | 11144.3783
2021-03-31 | 19384.0005 | 18914.3515 | 19868.2566 | 11497.7125 | 11108.3487 | 11249.5616
2021-04-30 | 17070.0009 | 16953.0005 | 17618.7846 | 10244.8035 | 10129.1803 | 10097.7166
2021-05-31 | 18055.3342 | 17941.0005 | 18021.5172 | 10152.0681 | 10150.0117 | 9986.9371
2021-06-30 | 22162.0009 | 22212.5105 | 21528.4908 | 10747.5852 | 10755.5082 | 10840.8856
2021-07-31 | 22413.0005 | 22500.0009 | 22251.4821 | 11806.5074 | 11818.4696 | 11970.9832
2021-08-31 | 22235.0005 | 22332.0009 | 21854.4728 | 11706.2663 | 11708.3351 | 12072.0791
2021-09-30 | 21212.0005 | 21307.0009 | 18979.8917 | 10472.6839 | 10482.8995 | 10401.3058
2021-10-31 | 17270.7147 | 17261.0005 | 17606.8602 | 10365.0376 | 10433.28 | 10429.4829
2021-11-30 | 19227.38 | 19228.3338 | 19684.7166 | 10886.7659 | 10903.2144 | 11017.3258
2021-12-31 | 20088.8968 | 20071.3338 | 21331.5579 | 11984.4925 | 11986.8857 | 12185.9418
2021 | 22413.0005 | 22500.0009 | 22251.4821 | 133476.5604 | 132645.0766 | 133704.2048
2022-01-31 | 20983.6671 | 20940.1258 | 21334.1018 | 12536.9576 | 12489.7994 | 12928.5532
2022-02-28 | 20446.0004 | 20331.4888 | 20782.3287 | 11208.712 | 11171.9517 | 11400.5165
2022-03-31 | 19401.3338 | 19482.5828 | 19941.2707 | 11617.5125 | 11591.1551 | 11793.6956
2022-04-30 | 17251.0005 | 17264.0004 | 17752.3935 | 10239.112 | 10244.1893 | 10311.1592
2022-05-31 | 18269.0005 | 18273.6671 | 20136.0014 | 10372.2878 | 10375.4674 | 10137.6947
2022-06-30 | 22161.0005 | 22173.0004 | 22101.7092 | 10967.9836 | 10969.0566 | 11002.2267
2022-07-31 | 22542.0005 | 22546.0005 | 22484.9516 | 11893.9057 | 11889.6983 | 12411.016
2022-08-31 | 22430.0005 | 22399.0005 | 23477.9346 | 12028.3221 | 12019.7286 | 11998.9314
2022-09-30 | 21489.0005 | 21346.0005 | 20446.2276 | 10551.0851 | 10488.1448 | 10678.4907
2022-10-31 | 17559.0005 | 17550.0005 | 17724.6236 | 10603.0084 | 10584.0232 | 10447.0825
2022-11-30 | 19812.0005 | 19791.0005 | 19389.6575 | 11151.0711 | 11134.34 | 11128.3255
2022-12-31 | 20241.0005 | 20225.0005 | 20584.5241 | 12191.9609 | 12176.1081 | 12412.7534
2022 | 22542.0005 | 22546.0005 | 23477.9346 | 135361.9188 | 135133.6625 | 136650.4453
2023-01-31 | 21170.3338 | 21255.0005 | 21435.1399 | 12663.6554 | 12762.2603 | 13052.768
2023-02-28 | 20892.3338 | 20984.0005 | 20433.0112 | 11375.0622 | 11461.3076 | 11325.8235
2023-03-31 | 19701.0485 | 19818.0005 | 19000.8853 | 11846.6528 | 11951.1697 | 11814.7494
2023-04-30 | 17785.9996 | 17831.0005 | 19103.3719 | 10349.2653 | 10370.0521 | 10374.8437
2023-05-31 | 18869.9996 | 18912.0005 | 18001.5877 | 10418.8057 | 10440.3611 | 10473.6584
2023-06-30 | 21884.9996 | 21931.0005 | 22417.4764 | 10652.496 | 10672.7289 | 11230.6805
2023-07-31 | 22445.9996 | 22438.9996 | 23368.3724 | 11858.9002 | 11846.9233 | 12455.0186
2023-08-31 | 22396.9996 | 22393.9996 | 21865.1956 | 12249.9171 | 12236.9698 | 12005.3253
2023-09-30 | 21479.9996 | 21517.9996 | 21317.3942 | 10718.9739 | 10702.4917 | 10685.1004
2023-10-31 | 17668.0452 | 17669.3329 | 19208.5675 | 10593.967 | 10600.3454 | 10757.1302
2023-11-30 | 19742.0453 | 19755.3329 | 20453.2108 | 11007.299 | 11013.2596 | 11478.5016
2023-12-31 | 20346.0453 | 20354.6663 | 21211.1571 | 12018.94 | 12023.4944 | 12384.2261
2023 | 22445.9996 | 22438.9996 | 23368 | 135753.9345 | 136081.364 | 138037.826
2024-01-31 | 21418.2553 | 21402.0453 | 21204.4347 | 12929.406 | 12921.66 | 13105.3696
2024-02-28 | 20987.7553 | 20977.0453 | 20151.4548 | 11956.6273 | 11946.748 | 11650.3599
2024-03-31 | 19639.8954 | 19645.2454 |  | 11798.7099 | 11836.2413
2024-04-30 | 17839.6154 | 17854.0654 |  | 10616.6408 | 10655.7906
2024-05-31 | 19148.7554 | 19124.2354 |  | 10660.6544 | 10683.7118
2024-06-30 | 22502.1655 | 22372.1055 |  | 10892.6773 | 10881.7852
2024-07-31 | 22753.1555 | 22602.4655 |  | 12346.4602 | 12304.5612
2024-08-31 | 22582.3655 | 22404.9255 |  | 12391.7927 | 12330.6424
2024-09-30 | 21956.7255 | 21783.5255 |  | 10997.8597 | 10946.6681
2024-10-31 | 17986.2756 | 17914.7556 |  | 11069.4251 | 11022.2349
2024-11-30 | 20150.1856 | 19982.4556 |  | 11444.03 | 11363.1197
2024-12-31 | 20893.9156 | 20686.6556 |  | 12525.6486 | 12402.5163
2024 | 22753.1555 | 22602.4655 |  | 139629.9319 | 139295.6794
Note: Last Forecast is the most recent or last forecast made for the month. Previous Forecast is the second last forecast for the month.
Back to main menu

## Table 3.1.2
Back to main menu
Table 3.1.2: Weekly Coincident Peak Demand by Zone
Hourly Coincident Peak Demand (MW)
Week Ending | Bruce | East | Essa | Niagara | Northeast | Northwest | Ottawa | Southwest | Toronto | West | Ontario | Load Forecast Uncertainty
2024-04-07 23:00 | 80.1474 | 1237.475 | 1335.838 | 522.8547 | 1314.967 | 458.2136 | 1146.325 | 3717.502 | 6202.521 | 1823.728 | 17839.6154 | 566.6881
2024-04-14 23:00 | 94.6501 | 1268.83 | 1356.536 | 513.1324 | 1313.153 | 437.604 | 1145.781 | 3557.349 | 6289.437 | 1754.668 | 17731.1854 | 471.407
2024-04-21 23:00 | 93.3179 | 1273.443 | 1352.002 | 527.5502 | 1311.351 | 433.7496 | 1128.408 | 3556.13 | 6297.272 | 1716.092 | 17689.3654 | 496.4143
2024-04-28 23:00 | 78.7236 | 1273.995 | 1363.125 | 491.2622 | 1303.656 | 407.8397 | 1167.723 | 3364.426 | 6336.51 | 1608.533 | 17395.8354 | 531.1471
2024-05-05 23:00 | 76.8989 | 1167.514 | 1305.557 | 499.5931 | 1213.169 | 407.9733 | 1100.722 | 3615.997 | 6172.71 | 1803.72 | 17363.8954 | 721.2879
2024-05-12 23:00 | 69.671 | 1037.42 | 1222.991 | 519.9787 | 1029.34 | 302.9264 | 1197.145 | 3409.631 | 6687.208 | 1797.843 | 17274.1954 | 848.5104
2024-05-19 23:00 | 86.8499 | 1115.961 | 1298.518 | 465.13 | 1254.648 | 367.6448 | 1148.425 | 3604.606 | 6405.844 | 1727.167 | 17474.8454 | 845.4734
2024-05-26 23:00 | 69.8875 | 1005.743 | 1225.501 | 528.6832 | 974.689 | 346.048 | 1171.382 | 3552.727 | 6759.115 | 1909.393 | 17543.2154 | 1174.6271
2024-06-02 23:00 | 81.8702 | 1091.05 | 1310.864 | 596.3182 | 990.045 | 350.3006 | 1088.865 | 3867.724 | 7636.385 | 2135.282 | 19148.7554 | 1330.3168
2024-06-09 23:00 | 65.8527 | 1047.268 | 1355.74 | 618.7963 | 1116.855 | 384.8041 | 1366.107 | 4102.438 | 7265.156 | 2230.965 | 19554.0254 | 1291.8347
2024-06-16 23:00 | 87.4101 | 1285.378 | 1537.846 | 648.4833 | 1157.748 | 428.8218 | 1477.75 | 4213.786 | 8034.816 | 2344.897 | 21216.9855 | 1054.9133
2024-06-23 23:00 | 73.2151 | 1291.156 | 1644.908 | 682.8282 | 1111.288 | 415.433 | 1333.161 | 4323.476 | 8598.495 | 2406.011 | 21880.0155 | 834.5212
2024-06-30 23:00 | 83.2132 | 1292.922 | 1632.251 | 725.8697 | 1087.196 | 379.9753 | 1551.856 | 4543.853 | 8686.554 | 2518.432 | 22502.1655 | 753.9586
2024-07-07 23:00 | 55.6209 | 1434.578 | 1681.141 | 714.9454 | 966.1876 | 382.9751 | 1648.355 | 4447.937 | 8776.658 | 2340.648 | 22449.0955 | 1015.7813
2024-07-14 23:00 | 65.2041 | 1368.049 | 1658.966 | 724.9385 | 950.1872 | 428.9352 | 1613.212 | 4581.98 | 8809.551 | 2483.686 | 22684.7555 | 813.8859
2024-07-21 23:00 | 73.7922 | 1410.528 | 1723.656 | 740.6743 | 943.2512 | 419.4933 | 1591.86 | 4732.649 | 8483.589 | 2633.614 | 22753.1555 | 838.2996
2024-07-28 23:00 | 74.9383 | 1345.465 | 1656.997 | 729.8926 | 1016.081 | 401.6749 | 1608.008 | 4753.835 | 8447.984 | 2664.519 | 22699.4355 | 1035.1434
2024-08-04 23:00 | 80.0744 | 1391.375 | 1645.814 | 745.257 | 913.428 | 409.112 | 1491.509 | 4610.094 | 8728.124 | 2609.929 | 22624.7655 | 840.7763
2024-08-11 23:00 | 80.6528 | 1351.329 | 1627.18 | 728.4621 | 1144.179 | 438.175 | 1546.313 | 4597.755 | 8578.687 | 2489.59 | 22582.3655 | 958.4901
2024-08-18 23:00 | 83.8182 | 1395.52 | 1726.654 | 720.8712 | 1110.267 | 410.0339 | 1543.473 | 4434.654 | 8677.487 | 2465.789 | 22568.6155 | 984.73
2024-08-25 23:00 | 80.7846 | 1365.201 | 1679.704 | 735.9293 | 1143.371 | 427.2808 | 1480.498 | 4615.851 | 8515.312 | 2494.833 | 22538.8055 | 1361.9286
2024-09-01 23:00 | 91.9694 | 1387.716 | 1645.581 | 712.1713 | 1208.119 | 427.5302 | 1624.351 | 4432.9 | 8508.256 | 2423.386 | 22462.0255 | 1412.797
2024-09-08 23:00 | 87.668 | 1327.76 | 1527.133 | 701.5826 | 1097.119 | 376.5653 | 1483.81 | 4420.237 | 8446.007 | 2447.108 | 21915.0355 | 1369.9914
2024-09-15 23:00 | 88.4955 | 1323.163 | 1531.969 | 707.1956 | 1173.205 | 404.8484 | 1503.566 | 4590.006 | 8086.053 | 2548.177 | 21956.7255 | 680.0262
2024-09-22 23:00 | 89.4181 | 1326.716 | 1547.649 | 635.5765 | 1176.16 | 381.1124 | 1282.919 | 4070.937 | 7709.741 | 2260.61 | 20480.8856 | 780.6026
2024-09-29 23:00 | 75.75 | 1278.732 | 1414.408 | 586.5704 | 1180.434 | 383.984 | 1097.788 | 3881.221 | 6877.81 | 2107.332 | 18884.0756 | 419.5083
2024-10-06 23:00 | 64.8341 | 1201.998 | 1289.336 | 581.9535 | 1190.823 | 374.645 | 1117.442 | 3799.635 | 6361.417 | 1996.171 | 17978.2956 | 553.8457
2024-10-13 23:00 | 85.1221 | 1268.367 | 1379.475 | 528.7753 | 1258.914 | 416.7885 | 1121.239 | 3515.801 | 6320.919 | 1794.163 | 17689.6056 | 786.4353
2024-10-20 23:00 | 73.4515 | 1262.735 | 1366.281 | 539.9802 | 1242.063 | 378.4672 | 1136.503 | 3559.695 | 6232.666 | 1818.885 | 17610.7756 | 507.0646
2024-10-27 23:00 | 73.9932 | 1268.984 | 1376.228 | 531.2179 | 1250.516 | 434.2446 | 1134.016 | 3671.297 | 6203.316 | 1890.017 | 17833.8756 | 391.8319
2024-11-03 23:00 | 79.3054 | 1298.431 | 1383.44 | 534.3386 | 1248.159 | 440.6912 | 1140.568 | 3630.98 | 6351.246 | 1879.068 | 17986.2756 | 318.0498
2024-11-10 23:00 | 80.489 | 1326.851 | 1455.358 | 542.8987 | 1303.479 | 470.9964 | 1207.44 | 3744.094 | 6449.03 | 2001.211 | 18581.8956 | 416.0919
2024-11-17 23:00 | 93.0807 | 1396.569 | 1509.652 | 575.3851 | 1344.369 | 491.464 | 1253.805 | 3865.749 | 6657.745 | 2052.461 | 19240.3256 | 601.0757
2024-11-24 23:00 | 96.5357 | 1443.897 | 1572.465 | 588.0583 | 1349.138 | 514.9811 | 1292.047 | 3975.3 | 6983.819 | 2105.504 | 19921.7856 | 342.1019
2024-12-01 23:00 | 99.225 | 1504.471 | 1657.163 | 585.3036 | 1438.309 | 511.8566 | 1381.305 | 3881.168 | 7025.965 | 2065.376 | 20150.1856 | 606.7352
2024-12-08 23:00 | 112.6978 | 1497.727 | 1755.76 | 603.6982 | 1463.419 | 522.301 | 1380.242 | 4046.586 | 7126.258 | 2121.102 | 20629.8356 | 409.0047
2024-12-15 23:00 | 114.4672 | 1536.002 | 1779.422 | 623.9119 | 1452.178 | 529.3568 | 1419.928 | 4163.941 | 7015.342 | 2183.028 | 20817.6256 | 554.776
2024-12-22 23:00 | 111.7601 | 1552.006 | 1819.323 | 609.0366 | 1502.907 | 544.9188 | 1506.164 | 4025.821 | 7119.022 | 2102.906 | 20893.9156 | 690.1656
2024-12-29 23:00 | 99.1422 | 1361.811 | 1659.371 | 533.3661 | 1359.39 | 523.3912 | 1294.621 | 3739.631 | 6258.037 | 1938.597 | 18767.4056 | 361.8553
2025-01-05 23:00 | 109.6174 | 1568.321 | 1752.825 | 592.4261 | 1470.462 | 490.1096 | 1390.102 | 4009.041 | 6729.94 | 2035.545 | 20148.4357 | 528.3376
2025-01-12 23:00 | 119.3627 | 1621.031 | 1816.202 | 616.9462 | 1501.312 | 531.5974 | 1496.752 | 4259.908 | 7271.406 | 2199.5 | 21434.0657 | 570.1898
2025-01-19 23:00 | 111.8532 | 1667.124 | 1876.14 | 622.867 | 1508.052 | 562.1192 | 1497.1 | 4246.911 | 7211.543 | 2152.145 | 21455.8957 | 546.9287
2025-01-26 23:00 | 125.1779 | 1687.167 | 1916.789 | 628.709 | 1551.932 | 568.1324 | 1500.163 | 4226.34 | 7356.047 | 2157.839 | 21718.3357 | 483.2935
2025-02-02 23:00 | 125.5483 | 1684.392 | 1910.735 | 638.9494 | 1526.124 | 571.5594 | 1483.78 | 4262.596 | 7341.427 | 2143.144 | 21688.3057 | 404.3657
2025-02-09 23:00 | 98.2017 | 1602.884 | 1811.403 | 609.5958 | 1546.809 | 550.4374 | 1468.228 | 4204.21 | 7239.765 | 2155.141 | 21286.7257 | 734.0046
2025-02-16 23:00 | 102.9656 | 1568.675 | 1771.003 | 597.3094 | 1516.46 | 530.6592 | 1452.697 | 4009.989 | 7251.922 | 2018.385 | 20820.1057 | 634.9437
2025-02-23 23:00 | 99.7845 | 1522.288 | 1747.351 | 583.143 | 1511.495 | 513.5042 | 1404.273 | 4089.367 | 7064.67 | 2105.351 | 20641.2757 | 581.2763
2025-03-02 23:00 | 102.0841 | 1514.601 | 1723.803 | 587.5745 | 1554.972 | 518.7258 | 1405.186 | 4030.979 | 7056.66 | 2045.176 | 20539.8057 | 501.4677
2025-03-09 23:00 | 100.9883 | 1488.951 | 1653.198 | 570.0826 | 1512.231 | 540.4682 | 1379.887 | 3839.811 | 6989.472 | 1887.905 | 19963.0357 | 531.477
2025-03-16 23:00 | 103.4433 | 1405.223 | 1600.715 | 544.5864 | 1499.567 | 538.8735 | 1261.847 | 3809.238 | 6767.359 | 1905.641 | 19436.5357 | 648.7024
2025-03-23 23:00 | 94.7744 | 1350.763 | 1522.064 | 531.4564 | 1454.745 | 476.7682 | 1262.468 | 3725.624 | 6590.393 | 1872.086 | 18881.1857 | 610.8327
2025-03-30 23:00 | 87.4351 | 1304.46 | 1450.49 | 543.8643 | 1390.951 | 456.2298 | 1230.427 | 3748.993 | 6352.698 | 1841.756 | 18407.3457 | 568.5487
2025-04-06 23:00 | 78.8553 | 1251.69 | 1364.01 | 530.027 | 1335.22 | 466.3786 | 1159.059 | 3804.179 | 6294.349 | 1855.514 | 18139.3257 | 566.6881
2025-04-13 23:00 | 93.3992 | 1282.579 | 1384.216 | 519.5701 | 1338.837 | 443.4493 | 1157.902 | 3641.584 | 6378.527 | 1787.551 | 18027.6658 | 471.407
2025-04-20 23:00 | 92.8744 | 1287.314 | 1378.546 | 533.9573 | 1336.647 | 439.925 | 1140.033 | 3639.317 | 6386.008 | 1749.637 | 17984.3058 | 496.4143
2025-04-27 23:00 | 78.219 | 1288.776 | 1391.18 | 497.7187 | 1331.963 | 411.7157 | 1180.593 | 3449.459 | 6431.234 | 1634.427 | 17695.3358 | 531.1471
2025-05-04 23:00 | 66.6828 | 1201.199 | 1293.508 | 524.3577 | 1279.538 | 404.8591 | 1123.968 | 3694.737 | 6299.833 | 1785.088 | 17673.8158 | 721.2879
2025-05-11 23:00 | 69.4612 | 1048.164 | 1248.551 | 524.8669 | 1061.911 | 305.4832 | 1205.882 | 3478.277 | 6755.69 | 1824.939 | 17523.2658 | 848.5104
2025-05-18 23:00 | 86.7119 | 1132.745 | 1331.288 | 472.6443 | 1294.938 | 373.7054 | 1159.086 | 3699.749 | 6486.853 | 1775.942 | 17813.7058 | 845.4734
2025-05-25 23:00 | 69.7563 | 1022.069 | 1256.638 | 534.156 | 978.5913 | 350.3279 | 1183.505 | 3631.578 | 6846.018 | 1943.491 | 17816.1758 | 1174.6271
2025-06-01 23:00 | 81.8219 | 1107.512 | 1343.449 | 603.2964 | 992.2135 | 355.493 | 1100.638 | 3943.454 | 7733.86 | 2167.992 | 19429.7758 | 1330.3168
2025-06-08 23:00 | 65.3953 | 1060.28 | 1384.933 | 623.1464 | 1168.268 | 387.4031 | 1374.452 | 4163.173 | 7325.722 | 2260.469 | 19813.2858 | 1291.8347
2025-06-15 23:00 | 87.1934 | 1297.314 | 1567.489 | 654.4406 | 1187.099 | 432.6208 | 1489.323 | 4289.52 | 8110.438 | 2377.084 | 21492.5658 | 1054.9133
2025-06-22 23:00 | 72.9142 | 1301.543 | 1671.043 | 687.7756 | 1147.854 | 417.6545 | 1341.416 | 4390.619 | 8666.712 | 2434.511 | 22132.0858 | 834.5212
2025-06-29 23:00 | 82.2383 | 1295.638 | 1648.865 | 726.4057 | 1112.737 | 380.0729 | 1551.587 | 4585.92 | 8703.246 | 2534.897 | 22621.6558 | 753.9586
2025-07-06 23:00 | 54.2831 | 1448.905 | 1703.836 | 718.9655 | 951.4484 | 387.5063 | 1655.388 | 4510.692 | 8827.204 | 2360.707 | 22618.9858 | 1015.7813
2025-07-13 23:00 | 63.6144 | 1377.612 | 1680.39 | 727.4639 | 931.9911 | 429.2708 | 1617.595 | 4634.209 | 8858.822 | 2500.439 | 22821.4558 | 813.8859
2025-07-20 23:00 | 72.5726 | 1417.184 | 1744.723 | 742.0985 | 925.1509 | 419.9435 | 1595.592 | 4782.631 | 8522.826 | 2649.315 | 22872.0859 | 838.2996
2025-07-27 23:00 | 73.6197 | 1350.404 | 1676.102 | 731.6493 | 1016.633 | 402.214 | 1611.053 | 4800.213 | 8484.083 | 2679.28 | 22825.2959 | 1035.1434
2025-08-03 23:00 | 79.0776 | 1396.971 | 1665.658 | 747.5187 | 886.2484 | 410.4773 | 1495.236 | 4660.728 | 8763.458 | 2628.859 | 22734.2759 | 840.7763
2025-08-10 23:00 | 79.1238 | 1355.09 | 1643.633 | 729.3087 | 1159.204 | 437.9945 | 1547.138 | 4641.661 | 8598.448 | 2503.404 | 22695.0459 | 958.4901
2025-08-17 23:00 | 82.2776 | 1397.857 | 1741.715 | 721.3088 | 1129.472 | 410.3021 | 1543.428 | 4475.162 | 8692.776 | 2479.332 | 22673.6759 | 984.73
2025-08-24 23:00 | 79.1901 | 1366.106 | 1694.474 | 735.9755 | 1158.716 | 427.658 | 1479.327 | 4656.748 | 8529.16 | 2509.875 | 22637.2759 | 1361.9286
2025-08-31 23:00 | 90.968 | 1399 | 1672.712 | 717.1389 | 1235.429 | 430.3801 | 1632.746 | 4507.784 | 8580.061 | 2455.421 | 22721.6859 | 1412.797
2025-09-07 23:00 | 86.7064 | 1328.741 | 1540.752 | 701.6398 | 1112.84 | 376.5962 | 1480.571 | 4463.639 | 8457.413 | 2463.267 | 22012.2159 | 1369.9914
2025-09-14 23:00 | 87.6644 | 1327.072 | 1552.849 | 706.9512 | 1200.53 | 404.6814 | 1500.222 | 4627.475 | 8098.269 | 2560.134 | 22065.8959 | 680.0262
2025-09-21 23:00 | 89.1928 | 1338.825 | 1579.973 | 640.764 | 1207.096 | 383.7354 | 1291.008 | 4141.281 | 7780.975 | 2291.348 | 20744.2459 | 780.6026
2025-09-28 23:00 | 78.5832 | 1217.718 | 1402.707 | 592.3502 | 1129.186 | 372.4766 | 1133.797 | 3973.062 | 7065.319 | 2182.271 | 19147.5159 | 419.5083
2025-10-05 23:00 | 64.442 | 1212.826 | 1314.528 | 587.5355 | 1219.598 | 375.7103 | 1125.344 | 3864.587 | 6422.861 | 2025.546 | 18213.0259 | 553.8457
Back to main menu

## Table 3.1.3
Back to main menu
Table 3.1.3: Weekly Energy Demand by Zone
Weeky Normal Energy (GWh)
Week Ending | Bruce | East | Essa | Niagara | Northeast | Northwest | Ottawa | Southwest | Toronto | West | Ontario
2024-04-07 23:00 | 13.1458 | 159.8827 | 177.7125 | 73.9508 | 200.4974 | 68.2316 | 159.4053 | 518.693 | 893.3884 | 259.0277 | 2523.9351
2024-04-14 23:00 | 13.0799 | 157.7067 | 175.2185 | 73.0752 | 196.8318 | 66.267 | 159.5799 | 518.0146 | 887.26 | 260.3843 | 2507.4179
2024-04-21 23:00 | 13.2328 | 158.1153 | 175.433 | 70.9648 | 198.3289 | 66.7666 | 154.9041 | 501.3717 | 882.7536 | 251.7843 | 2473.6551
2024-04-28 23:00 | 11.5758 | 147.8393 | 165.2084 | 69.2617 | 191.4709 | 63.8576 | 152.1628 | 492.8177 | 871.3215 | 244.1997 | 2409.7153
2024-05-05 23:00 | 12.6469 | 144.5708 | 166.6783 | 69.3798 | 184.9546 | 61.7956 | 149.6902 | 495.3464 | 866.8775 | 252.6735 | 2404.6137
2024-05-12 23:00 | 11.7013 | 138.8768 | 162.4867 | 70.2956 | 172.9596 | 58.9865 | 151.8275 | 488.107 | 878.3417 | 251.3122 | 2384.8949
2024-05-19 23:00 | 12.6581 | 144.557 | 169.5189 | 68.9894 | 180.7113 | 62.5398 | 149.6882 | 491.8486 | 875.6581 | 253.7202 | 2409.8896
2024-05-26 23:00 | 9.9292 | 134.5936 | 159.186 | 70.1413 | 170.687 | 57.7902 | 146.1307 | 491.5359 | 854.5943 | 254.8207 | 2349.4088
2024-06-02 23:00 | 11.3252 | 142.6298 | 168.9223 | 72.1215 | 173.6432 | 59.7699 | 147.167 | 497.8521 | 902.2438 | 259.6773 | 2435.3521
2024-06-09 23:00 | 10.3479 | 141.0421 | 165.3374 | 75.0149 | 163.9019 | 59.1059 | 155.4914 | 519.9324 | 893.5535 | 286.1118 | 2469.8392
2024-06-16 23:00 | 9.7235 | 147.3627 | 173.4722 | 77.1592 | 170.0156 | 59.403 | 162.9952 | 527.1417 | 933.5364 | 278.8221 | 2539.6316
2024-06-23 23:00 | 9.8861 | 151.937 | 178.797 | 80.8247 | 166.6069 | 59.8281 | 165.5473 | 529.6555 | 970.0037 | 285.8594 | 2598.9455
2024-06-30 23:00 | 10.5905 | 155.4286 | 184.5982 | 80.8407 | 170.5417 | 60.8462 | 174.0341 | 544.8011 | 987.7055 | 293.2872 | 2662.6741
2024-07-07 23:00 | 7.8069 | 158.8807 | 182.4322 | 83.5103 | 174.0571 | 59.9005 | 173.3874 | 551.4919 | 981.2764 | 291.8077 | 2664.5511
2024-07-14 23:00 | 8.8728 | 162.5143 | 188.8551 | 87.441 | 173.4472 | 61.5913 | 170.9396 | 575.8773 | 1009.5806 | 309.6508 | 2748.7699
2024-07-21 23:00 | 9.4908 | 166.9175 | 193.0994 | 89.2069 | 175.8109 | 62.7754 | 170.8361 | 595.4274 | 1018.4251 | 323.5791 | 2805.5685
2024-07-28 23:00 | 9.479 | 169.9477 | 197.3804 | 88.3795 | 172.1827 | 62.1501 | 186.32 | 579.9028 | 1042.3603 | 315.8939 | 2823.9964
2024-08-04 23:00 | 10.8578 | 171.1619 | 198.4042 | 92.006 | 175.1564 | 63.3676 | 177.255 | 592.744 | 1047.8708 | 324.1276 | 2852.9512
2024-08-11 23:00 | 11.2877 | 169.1894 | 194.6285 | 91.6028 | 174.9978 | 62.9473 | 168.5804 | 578.9606 | 1023.0079 | 320.6014 | 2795.8037
2024-08-18 23:00 | 11.1903 | 168.4995 | 193.4487 | 91.2148 | 177.9003 | 62.8215 | 174.935 | 590.7595 | 1021.5835 | 325.0679 | 2817.4208
2024-08-25 23:00 | 11.3505 | 168.4212 | 191.9712 | 89.3167 | 179.4887 | 63.4095 | 176.7708 | 573.1702 | 1022.9243 | 311.207 | 2788.0301
2024-09-01 23:00 | 11.6054 | 166.9745 | 188.7106 | 88.6765 | 183.85 | 63.9712 | 172.8029 | 573.4763 | 1004.8111 | 309.9012 | 2764.7798
2024-09-08 23:00 | 11.8195 | 161.1439 | 181.2264 | 83.2352 | 176.0391 | 60.3771 | 171.9614 | 543.8623 | 959.0933 | 300.4286 | 2649.1867
2024-09-15 23:00 | 11.0789 | 156.233 | 177.0789 | 80.4956 | 179.7979 | 61.2363 | 161.3121 | 551.9673 | 946.3881 | 298.1891 | 2623.7774
2024-09-22 23:00 | 11.5037 | 157.5197 | 178.8578 | 75.7175 | 180.8147 | 61.2749 | 156.4734 | 519.3502 | 917.6522 | 279.4747 | 2538.6388
2024-09-29 23:00 | 10.8624 | 155.0002 | 175.3828 | 74.6095 | 180.6691 | 62.2519 | 150.6813 | 516.8033 | 902.3726 | 275.9183 | 2504.5514
2024-10-06 23:00 | 10.0978 | 153.6419 | 169.5144 | 76.2058 | 184.7956 | 61.7714 | 147.8963 | 514.2238 | 883.4649 | 277.5002 | 2479.1121
2024-10-13 23:00 | 11.1995 | 161.769 | 177.1256 | 74.3172 | 189.5698 | 62.9729 | 150.4543 | 500.4317 | 882.0217 | 264.2116 | 2474.0733
2024-10-20 23:00 | 10.063 | 158.3295 | 173.1035 | 73.5265 | 187.0796 | 63.127 | 152.2767 | 497.1764 | 865.277 | 261.5318 | 2441.491
2024-10-27 23:00 | 10.7874 | 164.5613 | 178.6811 | 75.9081 | 190.3951 | 67.0278 | 152.2652 | 514.8642 | 892.8483 | 271.382 | 2518.7203
2024-11-03 23:00 | 11.3381 | 168.9646 | 184.4898 | 76.3049 | 193.7138 | 67.2421 | 159.3739 | 518.8939 | 897.8913 | 272.6487 | 2550.8611
2024-11-10 23:00 | 11.148 | 172.2009 | 190.1844 | 76.6436 | 200.5324 | 74.2519 | 162.1314 | 520.3811 | 900.8965 | 281.8245 | 2590.1948
2024-11-17 23:00 | 11.7907 | 179.5846 | 197.1569 | 78.6 | 206.648 | 76.8736 | 165.323 | 529.5279 | 923.7494 | 286.0678 | 2655.3218
2024-11-24 23:00 | 12.7083 | 186.504 | 205.6933 | 82.0139 | 205.8307 | 75.5006 | 170.5159 | 543.8402 | 957.9301 | 295.5467 | 2736.0836
2024-12-01 23:00 | 13.301 | 194.1194 | 215.254 | 83.9124 | 213.1966 | 77.145 | 177.8523 | 547.616 | 971.3711 | 294.6563 | 2788.4241
2024-12-08 23:00 | 14.285 | 195.3621 | 229.5005 | 82.8643 | 223.1461 | 83.481 | 182.1322 | 563.4898 | 971.4395 | 301.6627 | 2847.3633
2024-12-15 23:00 | 14.8766 | 201.5627 | 237.4094 | 85.0848 | 226.1992 | 82.9295 | 187.1924 | 563.1762 | 977.1995 | 301.4346 | 2877.0649
2024-12-22 23:00 | 15.2698 | 205.3594 | 240.3823 | 86.0141 | 225.8128 | 83.5618 | 193.7839 | 568.6455 | 991.6966 | 304.0833 | 2914.6096
2024-12-29 23:00 | 14.1631 | 197.42 | 236.5439 | 77.5652 | 227.4632 | 84.9083 | 188.003 | 514.2231 | 901.063 | 277.2191 | 2718.5719
2025-01-05 23:00 | 14.7342 | 208.8258 | 241.9466 | 82.0632 | 231.2209 | 83.2166 | 189.9857 | 550.804 | 942.4899 | 291.5754 | 2836.8624
2025-01-12 23:00 | 15.7279 | 214.8234 | 242.2915 | 86.3421 | 230.2784 | 84.6775 | 193.1288 | 584.6933 | 1001.0472 | 303.81 | 2956.8201
2025-01-19 23:00 | 16.3298 | 216.5892 | 244.1807 | 87.0187 | 233.1615 | 86.6042 | 197.8752 | 585.837 | 1001.9954 | 305.8621 | 2975.4536
2025-01-26 23:00 | 17.5009 | 219.16 | 249.4419 | 88.3441 | 233.9726 | 86.1706 | 197.2505 | 589.0814 | 1006.3077 | 306.4354 | 2993.6651
2025-02-02 23:00 | 16.2283 | 220.2113 | 249.9176 | 86.3179 | 242.1922 | 87.2782 | 192.9346 | 582.9448 | 1004.5682 | 302.1238 | 2984.7169
2025-02-09 23:00 | 14.5131 | 207.21 | 235.9452 | 84.8271 | 235.4787 | 86.9034 | 196.7721 | 575.3635 | 994.1711 | 301.0821 | 2932.2663
2025-02-16 23:00 | 15.339 | 206.134 | 234.8707 | 86.4234 | 230.9785 | 84.399 | 191.9043 | 574.9267 | 1005.5983 | 301.338 | 2931.9119
2025-02-23 23:00 | 15.1278 | 201.7289 | 231.0756 | 84.972 | 232.197 | 80.9739 | 192.8855 | 565.1029 | 985.6161 | 294.8318 | 2884.5115
2025-03-02 23:00 | 15.4266 | 195.3435 | 222.9561 | 86.1718 | 227.9743 | 81.2705 | 187.1526 | 575.3077 | 991.3754 | 302.2613 | 2885.2398
2025-03-09 23:00 | 15.7212 | 187.6117 | 214.5953 | 80.8803 | 224.7617 | 78.4033 | 184.3039 | 554.3489 | 982.0772 | 286.7305 | 2809.434
2025-03-16 23:00 | 14.9588 | 185.0418 | 211.1697 | 79.1254 | 223.9658 | 78.5723 | 175.7044 | 555.4741 | 953.3726 | 286.5499 | 2763.9348
2025-03-23 23:00 | 14.9767 | 176.1122 | 199.2234 | 78.5749 | 215.1122 | 76.6162 | 170.2452 | 546.5321 | 936.8376 | 284.2252 | 2698.4557
2025-03-30 23:00 | 14.0951 | 165.1547 | 188.8911 | 76.063 | 214.0438 | 77.1096 | 170.3818 | 533.1702 | 918.1686 | 274.9905 | 2632.0685
2025-04-06 23:00 | 13.2004 | 162.6341 | 182.6697 | 75.6167 | 204.2816 | 69.6297 | 162.2576 | 534.0592 | 911.6426 | 267.3414 | 2583.333
2025-04-13 23:00 | 12.9787 | 159.7125 | 179.2809 | 74.3618 | 200.1598 | 67.2643 | 161.4641 | 531.5483 | 901.0362 | 266.0707 | 2553.8775
2025-04-20 23:00 | 13.2194 | 159.096 | 177.7218 | 71.3795 | 201.3364 | 67.4036 | 155.2389 | 506.4094 | 880.7985 | 253.7188 | 2486.3221
2025-04-27 23:00 | 11.5605 | 149.4468 | 168.9435 | 70.2667 | 194.8972 | 64.8332 | 153.5881 | 504.7588 | 882.0719 | 248.1829 | 2448.5497
2025-05-04 23:00 | 12.4908 | 146.917 | 169.9099 | 70.7889 | 188.9213 | 62.6204 | 151.7464 | 509.039 | 881.1705 | 257.7907 | 2451.3949
2025-05-11 23:00 | 11.7113 | 140.5766 | 166.2428 | 71.4941 | 175.8273 | 59.8823 | 153.625 | 501.2799 | 891.8552 | 256.7703 | 2429.2647
2025-05-18 23:00 | 12.6946 | 146.3345 | 173.4279 | 70.1344 | 183.7336 | 63.4818 | 151.5102 | 505.2656 | 889.2177 | 259.1832 | 2454.9836
2025-05-25 23:00 | 9.9426 | 136.343 | 163.0185 | 71.2396 | 173.6446 | 58.6828 | 147.9953 | 504.7791 | 868.2739 | 260.2417 | 2394.1612
2025-06-01 23:00 | 11.3051 | 143.7317 | 172.2338 | 72.7932 | 176.9253 | 60.4889 | 148.5934 | 509.6569 | 913.4249 | 263.2953 | 2472.4485
2025-06-08 23:00 | 10.3383 | 142.7798 | 169.1939 | 76.1629 | 166.5165 | 59.8698 | 157.3381 | 532.4183 | 906.7794 | 291.3472 | 2512.7441
2025-06-15 23:00 | 9.6908 | 149.0545 | 177.439 | 78.2945 | 172.6164 | 60.1878 | 164.787 | 539.8499 | 946.3083 | 283.9903 | 2582.2186
2025-06-22 23:00 | 9.8379 | 153.6641 | 182.6433 | 81.9947 | 169.094 | 60.6088 | 167.3289 | 542.0824 | 982.9053 | 290.9865 | 2641.1459
2025-06-29 23:00 | 10.5224 | 157.1281 | 188.4796 | 81.9997 | 172.9384 | 61.621 | 175.8282 | 557.5567 | 1000.4515 | 298.4637 | 2704.9894
2025-07-06 23:00 | 7.6518 | 159.2021 | 184.5126 | 83.5329 | 176.1546 | 60.2199 | 174.5371 | 558.2824 | 984.2604 | 294.5869 | 2682.9408
2025-07-13 23:00 | 8.7535 | 164.445 | 192.9038 | 88.7076 | 175.4691 | 62.2751 | 172.744 | 588.3744 | 1023.2516 | 314.4228 | 2791.347
2025-07-20 23:00 | 9.3683 | 168.9716 | 197.2674 | 90.4327 | 177.8594 | 63.4804 | 172.6887 | 608.2406 | 1032.2401 | 328.478 | 2849.0273
2025-07-27 23:00 | 9.3638 | 171.9858 | 201.5466 | 89.5964 | 174.1247 | 62.8757 | 188.2559 | 592.2873 | 1055.6494 | 320.7819 | 2866.4676
2025-08-03 23:00 | 10.5976 | 172.7897 | 201.8057 | 93.1008 | 177.1279 | 64.0674 | 179.266 | 605.1393 | 1061.1438 | 328.7845 | 2893.8227
2025-08-10 23:00 | 11.1715 | 170.986 | 198.5665 | 92.7907 | 176.7977 | 63.6628 | 170.249 | 591.2633 | 1035.5157 | 325.7401 | 2836.7434
2025-08-17 23:00 | 11.0614 | 170.1821 | 197.3099 | 92.3349 | 179.6617 | 63.548 | 176.4981 | 603.0405 | 1033.6672 | 330.2474 | 2857.5512
2025-08-24 23:00 | 11.2182 | 170.0037 | 195.8013 | 90.3287 | 181.2335 | 64.131 | 178.2149 | 585.1491 | 1034.3619 | 316.205 | 2826.6472
2025-08-31 23:00 | 11.5002 | 168.9247 | 193.077 | 90.1168 | 186.3553 | 65.061 | 174.1683 | 586.7662 | 1018.4529 | 314.8716 | 2809.2939
2025-09-07 23:00 | 11.8075 | 162.9439 | 184.9897 | 84.3748 | 178.1828 | 61.0912 | 173.4894 | 555.9026 | 970.9256 | 305.5734 | 2689.2809
2025-09-14 23:00 | 11.0607 | 158.0663 | 180.9208 | 81.663 | 182.1762 | 61.9583 | 162.8643 | 564.376 | 958.8228 | 303.3789 | 2665.2872
2025-09-21 23:00 | 11.479 | 159.3926 | 182.7641 | 76.8722 | 183.2456 | 62.0113 | 158.0704 | 531.7036 | 930.0202 | 284.6447 | 2580.2038
2025-09-28 23:00 | 10.8311 | 156.8294 | 179.209 | 75.7658 | 183.0939 | 62.9445 | 152.3272 | 529.1422 | 914.9445 | 281.0749 | 2546.1624
2025-10-05 23:00 | 10.1243 | 154.8918 | 173.4703 | 76.8496 | 186.4353 | 62.7824 | 149.5085 | 526.5926 | 896.3461 | 282.8149 | 2519.8159
Back to main menu

## Table 3.2
Back to main menu
Table 3.2 Forecasted Seasonal Peaks
Season | Normal Weather Peak (MW) | Extreme Weather Peak (MW)
Summer 2024 | 22753.1555 | 24668.5055
Winter 2024-25 | 21718.3357 | 22915.0657
Summer 2025 | 22872.0859 | 24854.2559
Back to main menu

## Table 3.3
Back to main menu
Table 3.3: Weekly Energy and Peak Demand Forecast
Week | Normal Peak | Extreme Peak | Load Forecast Uncertainty | Normal Energy Demand
Week Ending | (MW) | (MW) | (MW) | (GWh)
2024-04-07 23:00 | 17839.6154 | 18791.7954 | 566.6881 | 2523.9427
2024-04-14 23:00 | 17731.1854 | 18254.3754 | 471.407 | 2507.4255
2024-04-21 23:00 | 17689.3654 | 18323.5654 | 496.4143 | 2473.6627
2024-04-28 23:00 | 17395.8354 | 17798.9054 | 531.1471 | 2409.7229
2024-05-05 23:00 | 17363.8954 | 19062.1854 | 721.2879 | 2404.6213
2024-05-12 23:00 | 17274.1954 | 19568.0954 | 848.5104 | 2384.9025
2024-05-19 23:00 | 17474.8454 | 21026.6054 | 845.4734 | 2409.8972
2024-05-26 23:00 | 17543.2154 | 20992.5354 | 1174.6271 | 2349.4164
2024-06-02 23:00 | 19148.7554 | 21645.6954 | 1330.3168 | 2435.3598
2024-06-09 23:00 | 19554.0254 | 22045.0654 | 1291.8347 | 2469.8467
2024-06-16 23:00 | 21216.9855 | 22281.6655 | 1054.9133 | 2539.6391
2024-06-23 23:00 | 21880.0155 | 23109.8655 | 834.5212 | 2598.9531
2024-06-30 23:00 | 22502.1655 | 24016.7555 | 753.9586 | 2662.6817
2024-07-07 23:00 | 22449.0955 | 24194.4155 | 1015.7813 | 2664.5588
2024-07-14 23:00 | 22684.7555 | 24379.5355 | 813.8859 | 2748.7776
2024-07-21 23:00 | 22753.1555 | 24550.4355 | 838.2996 | 2805.5761
2024-07-28 23:00 | 22699.4355 | 24668.5055 | 1035.1434 | 2824.004
2024-08-04 23:00 | 22624.7655 | 24606.3555 | 840.7763 | 2852.9589
2024-08-11 23:00 | 22582.3655 | 24532.2755 | 958.4901 | 2795.8113
2024-08-18 23:00 | 22568.6155 | 24656.9055 | 984.73 | 2817.4285
2024-08-25 23:00 | 22538.8055 | 24507.9255 | 1361.9286 | 2788.0377
2024-09-01 23:00 | 22462.0255 | 24308.9255 | 1412.797 | 2764.7874
2024-09-08 23:00 | 21915.0355 | 23662.1355 | 1369.9914 | 2649.1944
2024-09-15 23:00 | 21956.7255 | 22987.1555 | 680.0262 | 2623.7851
2024-09-22 23:00 | 20480.8856 | 21891.5356 | 780.6026 | 2538.6464
2024-09-29 23:00 | 18884.0756 | 21119.0856 | 419.5083 | 2504.5591
2024-10-06 23:00 | 17978.2956 | 19574.3656 | 553.8457 | 2479.1196
2024-10-13 23:00 | 17689.6056 | 18675.8456 | 786.4353 | 2474.081
2024-10-20 23:00 | 17610.7756 | 18065.6956 | 507.0646 | 2441.4986
2024-10-27 23:00 | 17833.8756 | 19099.2456 | 391.8319 | 2518.7279
2024-11-03 23:00 | 17986.2756 | 19356.5256 | 318.0498 | 2550.8687
2024-11-10 23:00 | 18581.8956 | 19922.2956 | 416.0919 | 2590.2024
2024-11-17 23:00 | 19240.3256 | 19615.4956 | 601.0757 | 2655.3295
2024-11-24 23:00 | 19921.7856 | 20209.9056 | 342.1019 | 2736.0913
2024-12-01 23:00 | 20150.1856 | 20846.7456 | 606.7352 | 2788.4318
2024-12-08 23:00 | 20629.8356 | 21379.1856 | 409.0047 | 2847.371
2024-12-15 23:00 | 20817.6256 | 21916.0856 | 554.776 | 2877.0726
2024-12-22 23:00 | 20893.9156 | 21988.9056 | 690.1656 | 2914.6173
2024-12-29 23:00 | 18767.4056 | 20294.6657 | 361.8553 | 2718.5795
2025-01-05 23:00 | 20148.4357 | 21074.9157 | 528.3376 | 2836.87
2025-01-12 23:00 | 21434.0657 | 22461.0357 | 570.1898 | 2956.8278
2025-01-19 23:00 | 21455.8957 | 22498.6557 | 546.9287 | 2975.4613
2025-01-26 23:00 | 21718.3357 | 22915.0657 | 483.2935 | 2993.6727
2025-02-02 23:00 | 21688.3057 | 22675.2257 | 404.3657 | 2984.7246
2025-02-09 23:00 | 21286.7257 | 22090.0157 | 734.0046 | 2932.274
2025-02-16 23:00 | 20820.1057 | 21976.7657 | 634.9437 | 2931.9195
2025-02-23 23:00 | 20641.2757 | 22053.6257 | 581.2763 | 2884.5191
2025-03-02 23:00 | 20539.8057 | 22112.9557 | 501.4677 | 2885.2475
2025-03-09 23:00 | 19963.0357 | 21411.5857 | 531.477 | 2809.4416
2025-03-16 23:00 | 19436.5357 | 21089.3757 | 648.7024 | 2763.9425
2025-03-23 23:00 | 18881.1857 | 20369.9957 | 610.8327 | 2698.4635
2025-03-30 23:00 | 18407.3457 | 19548.0857 | 568.5487 | 2632.0762
2025-04-06 23:00 | 18139.3257 | 19015.3657 | 566.6881 | 2583.3407
2025-04-13 23:00 | 18027.6658 | 18479.6658 | 471.407 | 2553.8852
2025-04-20 23:00 | 17984.3058 | 18545.4658 | 496.4143 | 2486.3298
2025-04-27 23:00 | 17695.3358 | 18016.4858 | 531.1471 | 2448.5573
2025-05-04 23:00 | 17673.8158 | 19307.5658 | 721.2879 | 2451.4026
2025-05-11 23:00 | 17523.2658 | 19725.0558 | 848.5104 | 2429.2724
2025-05-18 23:00 | 17813.7058 | 21191.2858 | 845.4734 | 2454.9913
2025-05-25 23:00 | 17816.1758 | 21161.8058 | 1174.6271 | 2394.1689
2025-06-01 23:00 | 19429.7758 | 21872.2158 | 1330.3168 | 2472.4562
2025-06-08 23:00 | 19813.2858 | 22197.0258 | 1291.8347 | 2512.7518
2025-06-15 23:00 | 21492.5658 | 22441.5958 | 1054.9133 | 2582.2263
2025-06-22 23:00 | 22132.0858 | 23245.0358 | 834.5212 | 2641.1535
2025-06-29 23:00 | 22621.6558 | 24188.5658 | 753.9586 | 2704.9971
2025-07-06 23:00 | 22618.9858 | 24332.8758 | 1015.7813 | 2682.9485
2025-07-13 23:00 | 22821.4558 | 24570.1458 | 813.8859 | 2791.3547
2025-07-20 23:00 | 22872.0859 | 24739.0959 | 838.2996 | 2849.035
2025-07-27 23:00 | 22825.2959 | 24854.2559 | 1035.1434 | 2866.4752
2025-08-03 23:00 | 22734.2759 | 24772.6359 | 840.7763 | 2893.8304
2025-08-10 23:00 | 22695.0459 | 24695.2859 | 958.4901 | 2836.7511
2025-08-17 23:00 | 22673.6759 | 24816.3159 | 984.73 | 2857.5588
2025-08-24 23:00 | 22637.2759 | 24646.3059 | 1361.9286 | 2826.6549
2025-08-31 23:00 | 22721.6859 | 24469.9359 | 1412.797 | 2809.3017
2025-09-07 23:00 | 22012.2159 | 23843.9859 | 1369.9914 | 2689.2887
2025-09-14 23:00 | 22065.8959 | 23164.9459 | 680.0262 | 2665.2949
2025-09-21 23:00 | 20744.2459 | 22090.5059 | 780.6026 | 2580.2115
2025-09-28 23:00 | 19147.5159 | 21285.7959 | 419.5083 | 2546.1701
2025-10-05 23:00 | 18213.0259 | 20105.1959 | 553.8457 | 2519.8237
Back to main menu

## Table 3.3.1
Back to main menu
Table 3.3.1: Weekly Weather and Demand History
Week Number | Week Ending | Actual Energy (GWh) | Weekly Average Temperature (°C) | Normal Average Temperature | Peak Day | Actual Peak (MW) | Peak Day Temperature (°C) | Normal Peak Temperature (°C) | Notes for Week
18 | 2002-05-05 | 2700.772 | 9.5143 | 10.6321 | 2002-05-02 | 18887 | 8.7 | 10.9
19 | 2002-05-12 | 2669.77 | 12.4381 | 14.7881 | 2002-05-09 | 18580 | 22.7 | 30.4
20 | 2002-05-19 | 2679.594 | 9.2333 | 12.672 | 2002-05-13 | 18905 | 8.5 | 10.3
21 | 2002-05-26 | 2598.182 | 11.6714 | 15.5881 | 2002-05-24 | 18290 | 18.9 | 27 | Victoria Day
22 | 2002-06-02 | 2746.191 | 19.8857 | 13.6643 | 2002-05-30 | 20068 | 27.9 | 29.4
23 | 2002-06-09 | 2685.914 | 16.6571 | 16.8333 | 2002-06-05 | 18724 | 23.2 | 25
24 | 2002-06-16 | 2783.799 | 18.4 | 17.6929 | 2002-06-11 | 22160 | 31.2 | 22.9
25 | 2002-06-23 | 2890.051 | 21.5095 | 20.7536 | 2002-06-21 | 22272 | 29.8 | 30.7
26 | 2002-06-30 | 3112.651 | 24.5429 | 18.7821 | 2002-06-26 | 23578 | 30.7 | 29.5
27 | 2002-07-07 | 3188.614 | 27.1714 | 21.0045 | 2002-07-03 | 25226 | 34.7 | 31.6 | Canada Day
28 | 2002-07-14 | 2998.057 | 24.0429 | 22.2089 | 2002-07-08 | 23405 | 32.8 | 31.3
29 | 2002-07-21 | 3269.356 | 26.2524 | 21.3923 | 2002-07-17 | 25001 | 34.4 | 30.5
30 | 2002-07-28 | 3079.006 | 23.5619 | 23.0952 | 2002-07-22 | 24613 | 33.5 | 30.2
31 | 2002-08-04 | 3347.995 | 27.2714 | 22.3661 | 2002-08-01 | 25343 | 34.6 | 30.9
32 | 2002-08-11 | 2945.538 | 22.8143 | 21.5214 | 2002-08-11 | 21621 | 32.8 | 30.3 | Civic Holiday
33 | 2002-08-18 | 3437.647 | 27.4905 | 21.5494 | 2002-08-13 | 25414 | 33.4 | 32.1
34 | 2002-08-25 | 2949.467 | 21.2952 | 21.1952 | 2002-08-21 | 21331 | 25.8 | 28.8
35 | 2002-09-01 | 2952.166 | 22.0714 | 19.9125 | 2002-08-26 | 21992 | 29.8 | 26.6
36 | 2002-09-08 | 3016.893 | 23.7857 | 20.1685 | 2002-09-03 | 23194 | 31.3 | 29.5 | Labour Day
37 | 2002-09-15 | 3050.046 | 23.281 | 18.269 | 2002-09-09 | 25062 | 33.5 | 27.1 | All-Time September Peak
38 | 2002-09-22 | 2985.537 | 22.1429 | 14.6787 | 2002-09-20 | 22445 | 29.2 | 25.3
39 | 2002-09-29 | 2742.116 | 16.0667 | 14.6461 | 2002-09-26 | 19030 | 21.9 | 24.4
40 | 2002-10-06 | 2811.965 | 19.2952 | 15.4244 | 2002-10-01 | 21216 | 28.8 | 23.9 | All-Time October Peak
41 | 2002-10-13 | 2715.175 | 12.7333 | 11.5271 | 2002-10-10 | 19140 | 17.9 | 6.4
42 | 2002-10-20 | 2725.443 | 8.1286 | 10.6226 | 2002-10-16 | 19531 | 10.4 | 9.8 | Thanksgiving
43 | 2002-10-27 | 2856.467 | 5.1381 | 9.2086 | 2002-10-24 | 19904 | 5.2 | 8.5
44 | 2002-11-03 | 2920.712 | 2.4952 | 6.506 | 2002-10-29 | 20339 | 4.1 | 4.9
45 | 2002-11-10 | 2898.028 | 7.7048 | 7.1875 | 2002-11-05 | 21071 | 5 | 6.3
46 | 2002-11-17 | 2935.188 | 3.6762 | 6.3202 | 2002-11-13 | 20619 | 8.2 | 1 | Remembrance Day
47 | 2002-11-24 | 2959.757 | 3.9857 | 3.1232 | 2002-11-18 | 21259 | 2.8 | 0
48 | 2002-12-01 | 3065.574 | -0.89048 | 1.6381 | 2002-11-28 | 21862 | 0.1 | -0.3
49 | 2002-12-08 | 3218.88 | -4.5714 | 2.1229 | 2002-12-02 | 23070 | -7.9 | -4
50 | 2002-12-15 | 3141.709 | 0.80952 | -0.78274 | 2002-12-09 | 23334 | -1.2 | -4.8
51 | 2002-12-22 | 3127.637 | -0.80952 | -2.2914 | 2002-12-16 | 23172 | -7.1 | -2.2
52 | 2002-12-29 | 2767.997 | -1.281 | -0.92381 | 2002-12-23 | 20993 | 0.1 | -4.8 | Christmas & Boxing Day
1 | 2003-01-05 | 2911.293 | -1.2286 | -5.064 | 2003-01-02 | 22092 | -6.1 | -7.8 | New Years Day
2 | 2003-01-12 | 3163.367 | -3.1476 | -3.4333 | 2003-01-07 | 22435 | -1.3 | -5.1
3 | 2003-01-19 | 3338.21 | -8.9286 | -4.9378 | 2003-01-15 | 23013 | -5.6 | -11.6
4 | 2003-01-26 | 3435.012 | -11.8667 | -6.425 | 2003-01-22 | 24158 | -13.4 | -13.5
5 | 2003-02-02 | 3270.192 | -5.4333 | -4.7643 | 2003-01-27 | 23916 | -11.4 | -16.1
6 | 2003-02-09 | 3249.756 | -4.881 | -3.6732 | 2003-02-05 | 22839 | -6.9 | -10
7 | 2003-02-16 | 3437.075 | -11.3429 | -5.3833 | 2003-02-13 | 23469 | -10 | -6.8 | All-Time February Peak
8 | 2003-02-23 | 3207.475 | -1.9952 | -3.8012 | 2003-02-17 | 23290 | -7.1 | -8.6
9 | 2003-03-02 | 3254.163 | -7.481 | -3.0643 | 2003-02-24 | 22831 | -8.5 | -5.3
10 | 2003-03-09 | 3249.198 | -6.919 | -2.431 | 2003-03-03 | 23117 | -14.3 | -7.9 | All-Time March Peak
11 | 2003-03-16 | 3113.156 | -3.1524 | -1.4926 | 2003-03-10 | 22599 | -11.2 | -6.4
12 | 2003-03-23 | 2907.03 | 6.0095 | 0.17482 | 2003-03-20 | 20417 | 6.9 | -0.1
13 | 2003-03-30 | 2851.087 | 7.1857 | 3.1009 | 2003-03-24 | 19675 | 11.4 | -1.9
14 | 2003-04-06 | 3057.792 | -1.0619 | 3.9729 | 2003-04-03 | 21010 | -1.8 | 4.1 | All-Time April Peak
15 | 2003-04-13 | 2903.238 | 3.1286 | 6.1494 | 2003-04-07 | 20921 | -2 | 0
16 | 2003-04-20 | 2687.611 | 11.4571 | 4.7583 | 2003-04-17 | 19555 | 2.7 | 0.8 | Good Friday
17 | 2003-04-27 | 2717.604 | 9.2952 | 7.5583 | 2003-04-22 | 19075 | 7.1 | 6.2 | Easter Monday
18 | 2003-05-04 | 2655.842 | 12.3476 | 10.6321 | 2003-05-01 | 18191 | 19 | 10.9
19 | 2003-05-11 | 2659.131 | 13.4714 | 14.7881 | 2003-05-05 | 18741 | 13.1 | 30.4
20 | 2003-05-18 | 2624.716 | 11.8333 | 12.672 | 2003-05-12 | 18362 | 11.1 | 10.3
21 | 2003-05-25 | 2562.062 | 13.4762 | 15.5881 | 2003-05-20 | 18599 | 15.7 | 27 | Victoria Day
22 | 2003-06-01 | 2637.638 | 15.0952 | 13.6643 | 2003-05-29 | 18226 | 24.2 | 29.4
23 | 2003-06-08 | 2653.987 | 16.219 | 16.8333 | 2003-06-04 | 18410 | 16.1 | 25
24 | 2003-06-15 | 2676.371 | 18.0381 | 17.6929 | 2003-06-11 | 19042 | 24.6 | 22.9
25 | 2003-06-22 | 2749.041 | 19.4 | 20.7536 | 2003-06-18 | 19935 | 22.6 | 30.7
26 | 2003-06-29 | 3088.015 | 25.8857 | 18.7821 | 2003-06-26 | 24753 | 33.3 | 29.5
27 | 2003-07-06 | 2992.72 | 25.419 | 21.0045 | 2003-07-04 | 23175 | 31.3 | 31.6 | Canada Day
28 | 2003-07-13 | 2845.965 | 21.5524 | 22.2089 | 2003-07-08 | 22137 | 28.6 | 31.3
29 | 2003-07-20 | 2843.257 | 21.2667 | 21.3923 | 2003-07-14 | 21149 | 28 | 30.5
30 | 2003-07-27 | 2883.093 | 22.5905 | 23.0952 | 2003-07-25 | 20937 | 28.7 | 30.2
31 | 2003-08-03 | 2892.989 | 22.3905 | 22.3661 | 2003-07-30 | 21438 | 28.3 | 30.9
32 | 2003-08-10 | 3015.111 | 23.3 | 21.5214 | 2003-08-07 | 22380 | 26.9 | 30.3 | Civic Holiday
33 | 2003-08-17 | 2722.825 | 22.1 | 21.5494 | 2003-08-14 | 23891 | 31 | 32.1 | Blackout
34 | 2003-08-24 | 2749.298 | 23.4048 | 21.1952 | 2003-08-21 | 20726 | 31.7 | 28.8 | Conservation Appeals
35 | 2003-08-31 | 2845.273 | 21.7952 | 19.9125 | 2003-08-26 | 21910 | 30 | 26.6 | Conservation Appeals
36 | 2003-09-07 | 2689.096 | 20.1095 | 20.1685 | 2003-09-03 | 19761 | 23.2 | 29.5 | Labour Day
37 | 2003-09-14 | 2868.127 | 20.7381 | 18.269 | 2003-09-11 | 20700 | 26.8 | 27.1
38 | 2003-09-21 | 2771.794 | 17.9857 | 14.6787 | 2003-09-15 | 20243 | 19.6 | 25.3
39 | 2003-09-28 | 2678.926 | 15.6048 | 14.6461 | 2003-09-22 | 19194 | 18.4 | 24.4
40 | 2003-10-05 | 2731.316 | 8.3905 | 15.4244 | 2003-10-02 | 19062 | 9.4 | 23.9
41 | 2003-10-12 | 2695.012 | 15.3286 | 11.5271 | 2003-10-09 | 19033 | 23.6 | 6.4
42 | 2003-10-19 | 2667.045 | 9.2952 | 10.6226 | 2003-10-14 | 19339 | 16.2 | 9.8 | Thanksgiving
43 | 2003-10-26 | 2793.966 | 7.4905 | 9.2086 | 2003-10-23 | 19764 | 5.4 | 8.5
44 | 2003-11-02 | 2795.637 | 9.2762 | 6.506 | 2003-10-28 | 20408 | 9.7 | 4.9
45 | 2003-11-09 | 2891.451 | 4.019 | 7.1875 | 2003-11-04 | 20872 | 4.7 | 6.3
46 | 2003-11-16 | 2918.192 | 4.5857 | 6.3202 | 2003-11-13 | 21289 | 2 | 1 | Remembrance Day
47 | 2003-11-23 | 2870.551 | 8.0048 | 3.1232 | 2003-11-17 | 21051 | 5.3 | 0
48 | 2003-11-30 | 2973.146 | 4.1333 | 1.6381 | 2003-11-24 | 21584 | 13.4 | -0.3
49 | 2003-12-07 | 2651.851 | -2.919 | 2.1229 | 2003-12-02 | 22190 | -5.6 | -4
50 | 2003-12-14 | 3162.132 | -0.07619 | -0.78274 | 2003-12-08 | 22664 | 1.4 | -4.8
51 | 2003-12-21 | 3595.432 | -0.2619 | -2.2914 | 2003-12-15 | 22769 | 1.1 | -2.2
52 | 2003-12-28 | 2637.228 | 3.3333 | -0.92381 | 2003-12-22 | 20842 | 5.9 | -4.8 | Christmas & Boxing Day
1 | 2004-01-04 | 2707.239 | 4.4048 | -5.064 | 2003-12-30 | 19971 | 3 | -7.8 | New Years Day
2 | 2004-01-11 | 3368.949 | -10.2286 | -3.4333 | 2004-01-09 | 23957 | -18.3 | -5.1
3 | 2004-01-18 | 3444.685 | -10.7095 | -4.9378 | 2004-01-15 | 24937 | -19.7 | -11.6 | All-Time January Peak
4 | 2004-01-25 | 3445.842 | -12.0905 | -6.425 | 2004-01-22 | 23740 | -7.9 | -13.5
5 | 2004-02-01 | 3419.085 | -8.3667 | -4.7643 | 2004-01-26 | 24843 | -12.8 | -16.1
6 | 2004-02-08 | 3238.962 | -3.9905 | -3.6732 | 2004-02-04 | 22608 | -3.9 | -10
7 | 2004-02-15 | 3215.227 | -4.1857 | -5.3833 | 2004-02-11 | 22141 | -3.2 | -6.8
8 | 2004-02-22 | 3157.743 | -1.7619 | -3.8012 | 2004-02-16 | 22591 | -5.7 | -8.6
9 | 2004-02-29 | 3039.427 | 0.28571 | -3.0643 | 2004-02-23 | 21397 | -1.2 | -5.3
10 | 2004-03-07 | 2960.676 | 5.0048 | -2.431 | 2004-03-04 | 20576 | 6.8 | -7.9
11 | 2004-03-14 | 3026.829 | -0.10476 | -1.4926 | 2004-03-08 | 21033 | 0.2 | -6.4
12 | 2004-03-21 | 3069.497 | -1.1333 | 0.17482 | 2004-03-16 | 21634 | -3.1 | -0.1
13 | 2004-03-28 | 2921.41 | 5.9476 | 3.1009 | 2004-03-22 | 21411 | -2.8 | -1.9
14 | 2004-04-04 | 2847.062 | 5.4857 | 3.9729 | 2004-04-01 | 19867 | 5.2 | 4.1
15 | 2004-04-11 | 2746.072 | 4.5952 | 6.1494 | 2004-04-05 | 19911 | 3.2 | 0 | Good Friday
16 | 2004-04-18 | 2740.574 | 8.3476 | 4.7583 | 2004-04-13 | 19287 | 4.2 | 0.8 | Easter Monday
17 | 2004-04-25 | 2692.098 | 10.5048 | 7.5583 | 2004-04-21 | 18456 | 20 | 6.2
18 | 2004-05-02 | 2725.676 | 11.5095 | 10.6321 | 2004-04-26 | 18934 | 15.3 | 10.9
19 | 2004-05-09 | 2705.553 | 9.719 | 14.7881 | 2004-05-03 | 18664 | 8.3 | 30.4
20 | 2004-05-16 | 2745.956 | 18.7143 | 12.672 | 2004-05-13 | 20327 | 27.3 | 10.3 | All-Time May Peak
21 | 2004-05-23 | 2670.015 | 15.8571 | 15.5881 | 2004-05-20 | 19003 | 23.6 | 27
22 | 2004-05-30 | 2607.459 | 14.3905 | 13.6643 | 2004-05-27 | 18395 | 17.7 | 29.4 | Victoria Day
23 | 2004-06-06 | 2660.864 | 15.7048 | 16.8333 | 2004-05-31 | 18593 | 13.2 | 25
24 | 2004-06-13 | 2892.519 | 20.4048 | 17.6929 | 2004-06-09 | 23163 | 31.3 | 22.9
25 | 2004-06-20 | 2893.889 | 19.9476 | 20.7536 | 2004-06-14 | 21921 | 27.3 | 30.7
26 | 2004-06-27 | 2774.133 | 18.481 | 18.7821 | 2004-06-24 | 20212 | 25.8 | 29.5
27 | 2004-07-04 | 2757.229 | 20.8762 | 21.0045 | 2004-06-30 | 19602 | 23.9 | 31.6 | Canada Day
28 | 2004-07-11 | 2792.427 | 20.5143 | 22.2089 | 2004-07-05 | 19990 | 20.8 | 31.3
29 | 2004-07-18 | 2912.725 | 22.6857 | 21.3923 | 2004-07-12 | 22142 | 27.4 | 30.5
30 | 2004-07-25 | 2983.251 | 21.9143 | 23.0952 | 2004-07-22 | 23976 | 30.1 | 30.2
31 | 2004-08-01 | 2932.682 | 21.5 | 22.3661 | 2004-07-29 | 21790 | 26.7 | 30.9
32 | 2004-08-08 | 2843.438 | 20.7905 | 21.5214 | 2004-08-03 | 23159 | 28.6 | 30.3 | Civic Holiday
33 | 2004-08-15 | 2827.685 | 19.7857 | 21.5494 | 2004-08-10 | 21171 | 26.5 | 32.1
34 | 2004-08-22 | 2809.027 | 19.7381 | 21.1952 | 2004-08-18 | 20570 | 25.5 | 28.8
35 | 2004-08-29 | 3028.556 | 22.519 | 19.9125 | 2004-08-27 | 22613 | 27.6 | 26.6
36 | 2004-09-05 | 2949.417 | 21.4238 | 20.1685 | 2004-09-03 | 21467 | 28.4 | 29.5
37 | 2004-09-12 | 2847.235 | 20.6571 | 18.269 | 2004-09-07 | 21067 | 24.6 | 27.1
38 | 2004-09-19 | 2877.874 | 18.3095 | 14.6787 | 2004-09-15 | 21911 | 25.8 | 25.3
39 | 2004-09-26 | 2893.166 | 20.4905 | 14.6461 | 2004-09-23 | 21545 | 27.5 | 24.4
40 | 2004-10-03 | 2779.759 | 16.1 | 15.4244 | 2004-09-27 | 20063 | 23.6 | 23.9
41 | 2004-10-10 | 2744.985 | 15.4238 | 11.5271 | 2004-10-07 | 19594 | 26.8 | 6.4
42 | 2004-10-17 | 2716.372 | 10.481 | 10.6226 | 2004-10-14 | 19478 | 13.4 | 9.8 | Thanksgiving
43 | 2004-10-24 | 2826.453 | 8.4 | 9.2086 | 2004-10-18 | 19829 | 8.8 | 8.5
44 | 2004-10-31 | 2796.499 | 11.381 | 6.506 | 2004-10-27 | 19538 | 11.4 | 4.9
45 | 2004-11-07 | 2859.127 | 7.7952 | 7.1875 | 2004-11-04 | 20768 | 6.2 | 6.3
46 | 2004-11-14 | 2963.561 | 3.3857 | 6.3202 | 2004-11-08 | 21136 | 5.2 | 1 | Remembrance Day
47 | 2004-11-21 | 2884.594 | 8.8286 | 3.1232 | 2004-11-15 | 20691 | 13.4 | 0
48 | 2004-11-28 | 3004.607 | 4.2905 | 1.6381 | 2004-11-24 | 21881 | 3.4 | -0.3
49 | 2004-12-05 | 3096.026 | 2.0143 | 2.1229 | 2004-12-03 | 22118 | -0.6 | -4
50 | 2004-12-12 | 3627.275 | 2.1286 | -0.78274 | 2004-12-06 | 23445 | -1.7 | -4.8
51 | 2004-12-18 | 2801.794 | -3.7286 | -2.2914 | 2004-12-14 | 23431 | -4.9 | -2.2
52 | 2004-12-26 | 3163.126 | -7.8762 | -0.92381 | 2004-12-20 | 24979 | -12.3 | -4.8 | All-Time Winter Peak, Christmas & Boxing Day
53 | 2005-01-02 | 2905.83 | -0.25714 | -3.3235 | 2004-12-27 | 21348 | -8.5 | -7.8 | New Years Day
1 | 2005-01-09 | 3186.479 | -1.2714 | -5.064 | 2005-01-06 | 23233 | -2.7 | -7.8
2 | 2005-01-16 | 3215.276 | -1.7 | -3.4333 | 2005-01-11 | 22640 | -1.6 | -5.1
3 | 2005-01-23 | 3528.986 | -13.9905 | -4.9378 | 2005-01-18 | 24362 | -14.5 | -11.6 | All-Time Weekend Peak
4 | 2005-01-30 | 3422.362 | -9.7857 | -6.425 | 2005-01-27 | 24353 | -14.6 | -13.5
5 | 2005-02-06 | 3163.582 | -1.5905 | -4.7643 | 2005-01-31 | 22629 | -1.5 | -16.1
6 | 2005-02-13 | 3140.407 | -1.8048 | -3.6732 | 2005-02-09 | 22322 | -3.9 | -10
7 | 2005-02-20 | 3212.842 | -2.7238 | -5.3833 | 2005-02-18 | 22269 | -9.3 | -6.8
8 | 2005-02-27 | 3226.382 | -5.4238 | -3.8012 | 2005-02-24 | 22321 | -5.7 | -8.6
9 | 2005-03-06 | 3169.085 | -3.019 | -3.0643 | 2005-02-28 | 22187 | 1.8 | -5.3
10 | 2005-03-13 | 3205.861 | -4.2143 | -2.431 | 2005-03-08 | 22724 | -8.5 | -7.9
11 | 2005-03-20 | 3041.309 | -0.7619 | -1.4926 | 2005-03-14 | 20975 | -0.8 | -6.4 | Good Friday
12 | 2005-03-27 | 2883.571 | 2.181 | 0.17482 | 2005-03-23 | 20777 | 1.5 | -0.1 | Easter Monday
13 | 2005-04-03 | 2869.005 | 6.4333 | 3.1009 | 2005-03-28 | 19649 | 6.6 | -1.9
14 | 2005-04-10 | 2771.699 | 9.6524 | 3.9729 | 2005-04-04 | 19343 | 10.9 | 4.1 | 5% Voltage Reduction April 7
15 | 2005-04-17 | 2705.795 | 9.9 | 6.1494 | 2005-04-11 | 18695 | 7.9 | 0
16 | 2005-04-24 | 2738.094 | 10.4952 | 4.7583 | 2005-04-20 | 18534 | 16.2 | 0.8
17 | 2005-05-01 | 2756.087 | 7.9714 | 7.5583 | 2005-04-25 | 19336 | 6.5 | 6.2
18 | 2005-05-08 | 2662.369 | 10.4952 | 10.6321 | 2005-05-02 | 18341 | 8.6 | 10.9
19 | 2005-05-15 | 2676.024 | 12.5952 | 14.7881 | 2005-05-11 | 18623 | 22.6 | 30.4
20 | 2005-05-22 | 2637.275 | 12.9 | 12.672 | 2005-05-16 | 18362 | 11 | 10.3
21 | 2005-05-29 | 2616.97 | 16.5381 | 15.5881 | 2005-05-26 | 18779 | 24.2 | 27 | Victoria Day
22 | 2005-06-05 | 2827.185 | 20.0714 | 13.6643 | 2005-06-02 | 20001 | 26 | 29.4
23 | 2005-06-12 | 3347.839 | 26.3952 | 16.8333 | 2005-06-10 | 24793 | 30.5 | 25
24 | 2005-06-19 | 2964.203 | 20.219 | 17.6929 | 2005-06-14 | 24995 | 29.7 | 22.9
25 | 2005-06-26 | 3090.154 | 23.9857 | 20.7536 | 2005-06-24 | 23802 | 34 | 30.7 | Power Warning June 24
26 | 2005-07-03 | 3206.862 | 25.3905 | 18.7821 | 2005-06-27 | 26157 | 31.6 | 29.5 | All-Time June Peak, Power Warning June 28-29, Canada Day
27 | 2005-07-10 | 3049.868 | 24.081 | 21.0045 | 2005-07-04 | 23463 | 29.5 | 31.6
28 | 2005-07-17 | 3485.566 | 28.4 | 22.2089 | 2005-07-13 | 26160 | 34.6 | 31.3 | All-Time July Peak
29 | 2005-07-24 | 3352.97 | 26.5381 | 21.3923 | 2005-07-18 | 25857 | 33.3 | 30.5 | Power Warning July 18-21
30 | 2005-07-31 | 3069.293 | 23.3286 | 23.0952 | 2005-07-25 | 25068 | 33.8 | 30.2
31 | 2005-08-07 | 3312.494 | 26.2429 | 22.3661 | 2005-08-04 | 25050 | 32.8 | 30.9 | Power Warning & 5% Voltage Reduction August 3-4
32 | 2005-08-14 | 3309.015 | 25.0333 | 21.5214 | 2005-08-09 | 25816 | 32.9 | 30.3 | Power Warning August 9-10
33 | 2005-08-21 | 3050.647 | 22.5143 | 21.5494 | 2005-08-15 | 22134 | 27.6 | 32.1
34 | 2005-08-28 | 2967.815 | 21.0952 | 21.1952 | 2005-08-26 | 21485 | 27.4 | 28.8
35 | 2005-09-04 | 3016.176 | 21.8524 | 19.9125 | 2005-08-29 | 22913 | 28.4 | 26.6
36 | 2005-09-11 | 2900.963 | 20.4048 | 20.1685 | 2005-09-07 | 22213 | 27.5 | 29.5 | Labour Day
37 | 2005-09-18 | 3058.417 | 22.3429 | 18.269 | 2005-09-13 | 23914 | 30.1 | 27.1
38 | 2005-09-25 | 2915.73 | 20.0476 | 14.6787 | 2005-09-21 | 21282 | 28.5 | 25.3
39 | 2005-10-02 | 2771.723 | 16.7381 | 14.6461 | 2005-09-26 | 20064 | 22.3 | 24.4
40 | 2005-10-09 | 2805.346 | 16.7238 | 15.4244 | 2005-10-04 | 20752 | 25.8 | 23.9 | All-Time October peak
41 | 2005-10-16 | 2660.335 | 12.9905 | 11.5271 | 2005-10-12 | 19163 | 13.2 | 6.4 | Thanksgiving
42 | 2005-10-23 | 2757.193 | 8.8429 | 10.6226 | 2005-10-20 | 19211 | 11.9 | 9.8
43 | 2005-10-30 | 2837.915 | 7.419 | 9.2086 | 2005-10-26 | 19960 | 8.1 | 8.5
44 | 2005-11-06 | 2779.661 | 11.9 | 6.506 | 2005-11-02 | 20065 | 12.3 | 4.9
45 | 2005-11-13 | 2808.809 | 9.0571 | 7.1875 | 2005-11-10 | 20390 | 5.7 | 6.3 | Remembrance Day
46 | 2005-11-20 | 2909.556 | 4.1619 | 6.3202 | 2005-11-17 | 21279 | 2.7 | 1
47 | 2005-11-27 | 3060.538 | -2.4381 | 3.1232 | 2005-11-24 | 22564 | -6.3 | 0 | All-Time November peak
48 | 2005-12-04 | 3002.3 | 2.119 | 1.6381 | 2005-12-02 | 21746 | -0.8 | -0.3
49 | 2005-12-11 | 3204.637 | -3.7476 | 2.1229 | 2005-12-07 | 23173 | -4.3 | -4
50 | 2005-12-17 | 2856.728 | -5.3 | -0.78274 | 2005-12-14 | 23750 | -4.8 | -4.8
51 | 2005-12-25 | 3107.356 | -1.3286 | -2.2914 | 2005-12-19 | 23377 | -4.7 | -2.2 | Christmas Day
52 | 2006-01-01 | 3210.318 | -1.0048 | -0.92381 | 2005-12-28 | 20167 | 2.7 | -4.8 | Boxing Day & New Year's Day
1 | 2006-01-08 | 3063.984 | -0.042857 | -5.064 | 2006-01-06 | 21941 | -5.2 | -7.8
2 | 2006-01-15 | 3050.642 | 1.5524 | -3.4333 | 2006-01-09 | 21905 | 2.6 | -5.1
3 | 2006-01-22 | 3136.327 | 0.28571 | -4.9378 | 2006-01-16 | 23052 | -5 | -11.6
4 | 2006-01-29 | 3080.009 | 0.77619 | -6.425 | 2006-01-25 | 22404 | -0.6 | -13.5
5 | 2006-02-05 | 3001.687 | 2.7476 | -4.7643 | 2006-01-31 | 21398 | 1.3 | -16.1
6 | 2006-02-12 | 3173.087 | -5.3429 | -3.6732 | 2006-02-08 | 22230 | -6.1 | -10
7 | 2006-02-19 | 3183.164 | -3.5857 | -5.3833 | 2006-02-16 | 22321 | -0.9 | -6.8
8 | 2006-02-26 | 3138.194 | -2.5857 | -3.8012 | 2006-02-20 | 21928 | -3.4 | -8.6
9 | 2006-03-05 | 3166.484 | -4.1429 | -3.0643 | 2006-02-28 | 22264 | -5.3 | -5.3
10 | 2006-03-12 | 2958.632 | 4.2857 | -2.431 | 2006-03-06 | 21224 | 0.3 | -7.9
11 | 2006-03-19 | 2995.582 | 0.83333 | -1.4926 | 2006-03-14 | 20958 | 1.8 | -6.4
12 | 2006-03-26 | 2972.525 | 0.92857 | 0.17482 | 2006-03-20 | 21238 | -1.7 | -0.1
13 | 2006-04-02 | 2785.318 | 8.4048 | 3.1009 | 2006-03-27 | 19737 | 11.5 | -1.9
14 | 2006-04-09 | 2839.195 | 5.1476 | 3.9729 | 2006-04-05 | 19582 | 3.7 | 4.1
15 | 2006-04-16 | 2618.627 | 12.0143 | 6.1494 | 2006-04-12 | 18717 | 16.9 | 0 | Good Friday
16 | 2006-04-23 | 2652.478 | 11.7 | 4.7583 | 2006-04-18 | 17869 | 15.5 | 0.8 | Easter Monday
17 | 2006-04-30 | 2675.485 | 9.481 | 7.5583 | 2006-04-25 | 18796 | 7.2 | 6.2
18 | 2006-05-07 | 2605.022 | 14.1619 | 10.6321 | 2006-05-04 | 18063 | 23 | 10.9
19 | 2006-05-14 | 2625.406 | 15.5762 | 14.7881 | 2006-05-10 | 18303 | 23.4 | 30.4
20 | 2006-05-21 | 2603.907 | 12.0571 | 12.672 | 2006-05-18 | 17986 | 14.5 | 10.3 | Victoria Day
21 | 2006-05-28 | 2630.386 | 15.8857 | 15.5881 | 2006-05-26 | 18624 | 18.8 | 27
22 | 2006-06-04 | 3031.734 | 22.6476 | 13.6643 | 2006-05-30 | 24857 | 32.8 | 29.4 | All-Time May peak
23 | 2006-06-11 | 2791.955 | 18.2381 | 16.8333 | 2006-06-07 | 21249 | 27.1 | 25
24 | 2006-06-18 | 2959.324 | 22.1714 | 17.6929 | 2006-06-17 | 21635 | 33.3 | 22.9
25 | 2006-06-25 | 3023.5 | 22.1429 | 20.7536 | 2006-06-22 | 23349 | 30.6 | 30.7
26 | 2006-07-02 | 2981.162 | 23.3619 | 18.7821 | 2006-06-28 | 22298 | 26.2 | 29.5
27 | 2006-07-09 | 2900.553 | 23.0667 | 21.0045 | 2006-07-04 | 22299 | 28.9 | 31.6 | Canada Day
28 | 2006-07-16 | 3156.462 | 24.8476 | 22.2089 | 2006-07-14 | 23802 | 30 | 31.3
29 | 2006-07-23 | 3190.415 | 23.8095 | 21.3923 | 2006-07-17 | 25898 | 33.8 | 30.5
30 | 2006-07-30 | 3302.816 | 25.7 | 23.0952 | 2006-07-26 | 24630 | 30.5 | 30.2
31 | 2006-08-06 | 3371.762 | 26.619 | 22.3661 | 2006-08-01 | 27005 | 36.4 | 30.9 | All-Time August Peak, All-Time System Peak
32 | 2006-08-13 | 2892.412 | 21.7667 | 21.5214 | 2006-08-08 | 21444 | 24.6 | 30.3 | Civic Holiday
33 | 2006-08-20 | 2990.591 | 22.2429 | 21.5494 | 2006-08-18 | 23008 | 30.4 | 32.1
34 | 2006-08-27 | 2892.158 | 20.9048 | 21.1952 | 2006-08-22 | 21350 | 27.5 | 28.8
35 | 2006-09-03 | 2772.647 | 18.5286 | 19.9125 | 2006-08-28 | 20627 | 23.6 | 26.6
36 | 2006-09-10 | 2693.897 | 18.6381 | 20.1685 | 2006-09-08 | 19976 | 28 | 29.5 | Labour Day
37 | 2006-09-17 | 2717.944 | 17.819 | 18.269 | 2006-09-13 | 18863 | 20.9 | 27.1
38 | 2006-09-24 | 2700.424 | 16.4619 | 14.6787 | 2006-09-18 | 19743 | 26.3 | 25.3
39 | 2006-10-01 | 2662.719 | 13.1095 | 14.6461 | 2006-09-27 | 18666 | 22.3 | 24.4
40 | 2006-10-08 | 2648.709 | 13.3524 | 15.4244 | 2006-10-03 | 18838 | 23.3 | 23.9
41 | 2006-10-15 | 2639.209 | 9.7952 | 11.5271 | 2006-10-12 | 19050 | 7.8 | 6.4 | Thanksgiving
42 | 2006-10-22 | 2717.621 | 10.2095 | 10.6226 | 2006-10-17 | 19215 | 12.2 | 9.8
43 | 2006-10-29 | 2797.795 | 5.0286 | 9.2086 | 2006-10-25 | 19379 | 7.8 | 8.5
44 | 2006-11-05 | 2824.166 | 5.2762 | 6.506 | 2006-11-02 | 20449 | 4.4 | 4.9
45 | 2006-11-12 | 2785.054 | 7.5476 | 7.1875 | 2006-11-07 | 20130 | 10.8 | 6.3
46 | 2006-11-19 | 2843.089 | 5.619 | 6.3202 | 2006-11-13 | 20896 | 5.4 | 1
47 | 2006-11-26 | 2864.929 | 3.9476 | 3.1232 | 2006-11-20 | 21267 | 1.5 | 0
48 | 2006-12-03 | 2921.179 | 6.3714 | 1.6381 | 2006-12-01 | 20880 | 3.6 | -0.3
49 | 2006-12-10 | 3109.444 | -1.5333 | 2.1229 | 2006-12-07 | 22941 | -5.5 | -4
50 | 2006-12-17 | 3380.311 | 6.6714 | -0.78274 | 2006-12-11 | 21845 | 4.9 | -4.8
51 | 2006-12-23 | 2540.758 | 4.1619 | -2.2914 | 2006-12-19 | 21588 | 4.4 | -2.2
52 | 2006-12-30 | 2690.955 | 0.95714 | -0.92381 | 2006-12-29 | 19917 | -2.6 | -4.8 | Christmas & Boxing Day
1 | 2007-01-07 | 2782.659 | 6.181 | -5.064 | 2007-01-02 | 20544 | 5.6 | -7.8 | New Years Day
2 | 2007-01-14 | 3047.003 | 0.18095 | -3.4333 | 2007-01-10 | 22295 | -3 | -5.1
3 | 2007-01-21 | 3212.028 | -5.5381 | -4.9378 | 2007-01-16 | 23261 | -8.6 | -11.6
4 | 2007-01-28 | 3260.007 | -7.2095 | -6.425 | 2007-01-25 | 23537 | -13.1 | -13.5
5 | 2007-02-04 | 3289.278 | -8.5762 | -4.7643 | 2007-01-29 | 22996 | -6.3 | -16.1
6 | 2007-02-11 | 3347.443 | -9.3238 | -3.6732 | 2007-02-05 | 23913 | -10.5 | -10
7 | 2007-02-18 | 3340.727 | -10.5905 | -5.3833 | 2007-02-13 | 23935 | -14 | -6.8 | All-Time February Peak
8 | 2007-02-25 | 3162.039 | -3.1619 | -3.8012 | 2007-02-19 | 22715 | -5.3 | -8.6
9 | 2007-03-04 | 3075.472 | -1.4905 | -3.0643 | 2007-03-01 | 21909 | -0.8 | -5.3
10 | 2007-03-11 | 3173.628 | -4.8762 | -2.431 | 2007-03-06 | 22969 | -12.5 | -7.9
11 | 2007-03-18 | 2949.8 | 2.9381 | -1.4926 | 2007-03-16 | 20437 | -2.4 | -6.4
12 | 2007-03-25 | 2947.133 | 2.819 | 0.17482 | 2007-03-19 | 20678 | 1.1 | -0.1
13 | 2007-04-01 | 2768.752 | 7.9619 | 3.1009 | 2007-03-26 | 19014 | 19.2 | -1.9
14 | 2007-04-08 | 2839.424 | 0.95238 | 3.9729 | 2007-04-04 | 19635 | 6.7 | 4.1 | Good Friday
15 | 2007-04-15 | 2890.779 | 3.2143 | 6.1494 | 2007-04-11 | 20016 | 4.1 | 0 | Easter Monday
16 | 2007-04-22 | 2695.202 | 11.6571 | 4.7583 | 2007-04-16 | 19534 | 5.2 | 0.8
17 | 2007-04-29 | 2650.782 | 12.4524 | 7.5583 | 2007-04-26 | 18369 | 9.7 | 6.2
18 | 2007-05-06 | 2591.374 | 11.681 | 10.6321 | 2007-05-01 | 18108 | 9.7 | 10.9
19 | 2007-05-13 | 2615.301 | 16.381 | 14.7881 | 2007-05-11 | 18587 | 20.5 | 30.4
20 | 2007-05-20 | 2619.902 | 14.1667 | 12.672 | 2007-05-15 | 19315 | 28.4 | 10.3
21 | 2007-05-27 | 2696.184 | 18.5143 | 15.5881 | 2007-05-25 | 20971 | 27.4 | 27
22 | 2007-06-03 | 2932.251 | 21.7143 | 13.6643 | 2007-05-31 | 21490 | 27.5 | 29.4
23 | 2007-06-10 | 2744.531 | 18.0048 | 16.8333 | 2007-06-08 | 22022 | 31.2 | 25
24 | 2007-06-17 | 3064.998 | 24 | 17.6929 | 2007-06-13 | 23338 | 29.7 | 22.9
25 | 2007-06-24 | 2889.579 | 21.2381 | 20.7536 | 2007-06-18 | 23028 | 28.3 | 30.7
26 | 2007-07-01 | 3069.945 | 23.4048 | 18.7821 | 2007-06-26 | 25737 | 34.2 | 29.5
27 | 2007-07-08 | 2778.127 | 22.1952 | 21.0045 | 2007-07-06 | 20313 | 28.2 | 31.6 | Canada Day
28 | 2007-07-15 | 2918.681 | 22.9286 | 22.2089 | 2007-07-09 | 24473 | 33.7 | 31.3
29 | 2007-07-22 | 2836.807 | 22.1333 | 21.3923 | 2007-07-19 | 21461 | 25.8 | 30.5
30 | 2007-07-29 | 3013.801 | 22.9667 | 23.0952 | 2007-07-26 | 22116 | 27.5 | 30.2
31 | 2007-08-05 | 3292.641 | 26.6905 | 22.3661 | 2007-08-02 | 25584 | 34.5 | 30.9
32 | 2007-08-12 | 3091.343 | 24.8095 | 21.5214 | 2007-08-08 | 24623 | 31.7 | 30.3 | Civic Holiday
33 | 2007-08-19 | 2880.482 | 21.7476 | 21.5494 | 2007-08-16 | 22432 | 29.6 | 32.1
34 | 2007-08-26 | 2933.593 | 22.1381 | 21.1952 | 2007-08-24 | 23497 | 32.8 | 28.8
35 | 2007-09-02 | 2936.107 | 22.4333 | 19.9125 | 2007-08-29 | 25003 | 33.5 | 26.6
36 | 2007-09-09 | 2956.434 | 23.1 | 20.1685 | 2007-09-07 | 24046 | 32.9 | 29.5 | Labour Day
37 | 2007-09-16 | 2693.073 | 16.3429 | 18.269 | 2007-09-10 | 19486 | 23 | 27.1
38 | 2007-09-23 | 2762.211 | 19.4286 | 14.6787 | 2007-09-21 | 20239 | 27.5 | 25.3
39 | 2007-09-30 | 2789.302 | 19.219 | 14.6461 | 2007-09-25 | 22392 | 32.8 | 24.4
40 | 2007-10-07 | 2747.696 | 19.5238 | 15.4244 | 2007-10-05 | 19233 | 24.3 | 23.9
41 | 2007-10-14 | 2652.097 | 14.4048 | 11.5271 | 2007-10-09 | 19038 | 22.2 | 6.4 | Thanksgiving Day
42 | 2007-10-21 | 2656.07 | 15.6286 | 10.6226 | 2007-10-18 | 18845 | 18.3 | 9.8
43 | 2007-10-28 | 2665.771 | 11.981 | 9.2086 | 2007-10-22 | 18856 | 24.8 | 8.5
44 | 2007-11-04 | 2692.534 | 9.0667 | 6.506 | 2007-11-01 | 19130 | 8.9 | 4.9
45 | 2007-11-11 | 2820.843 | 4.181 | 7.1875 | 2007-11-07 | 20407 | 3.1 | 6.3
46 | 2007-11-18 | 2830.635 | 5.4 | 6.3202 | 2007-11-12 | 20341 | 10.4 | 1
47 | 2007-11-25 | 2967.198 | 0.92857 | 3.1232 | 2007-11-22 | 21600 | -3.4 | 0
48 | 2007-12-02 | 3520.067 | -0.97143 | 1.6381 | 2007-11-28 | 21814 | -0.3 | -0.3
49 | 2007-12-09 | 3153.262 | -3.8143 | 2.1229 | 2007-12-03 | 22679 | -2 | -4
50 | 2007-12-15 | 2752.481 | -2.8905 | -0.78274 | 2007-12-11 | 22534 | 1.1 | -4.8
51 | 2007-12-23 | 2613.488 | 0.37143 | -2.2914 | 2007-12-17 | 22935 | -3.4 | -2.2
52 | 2007-12-30 | 3137.178 | -0.18095 | -0.92381 | 2007-12-28 | 19708 | 2.1 | -4.8 | Christmas & Boxing Day
1 | 2008-01-06 | 2957.333 | -3.0143 | -5.064 | 2008-01-03 | 22716 | -7.7 | -7.8 | New Years Day
2 | 2008-01-13 | 2907.387 | 5.8143 | -3.4333 | 2008-01-10 | 20852 | 3.6 | -5.1
3 | 2008-01-20 | 3105.23 | -3.1762 | -4.9378 | 2008-01-20 | 21519 | -8.9 | -11.6
4 | 2008-01-27 | 3207.28 | -5.7905 | -6.425 | 2008-01-21 | 22778 | -7.4 | -13.5
5 | 2008-02-03 | 3102.421 | -1.8905 | -4.7643 | 2008-01-30 | 22782 | -8 | -16.1
6 | 2008-02-10 | 3051.217 | -1.8333 | -3.6732 | 2008-02-06 | 21287 | -1.7 | -10
7 | 2008-02-17 | 3187.347 | -6.4333 | -5.3833 | 2008-02-11 | 23054 | -9.3 | -6.8
8 | 2008-02-24 | 3075.375 | -4.7286 | -3.8012 | 2008-02-20 | 21949 | -6.8 | -8.6 | Family Day
9 | 2008-03-02 | 3125.877 | -5.3 | -3.0643 | 2008-02-27 | 22273 | -10.1 | -5.3
10 | 2008-03-09 | 3029.509 | -1.719 | -2.431 | 2008-03-04 | 20990 | -1.6 | -7.9
11 | 2008-03-16 | 2943.709 | -0.99524 | -1.4926 | 2008-03-10 | 20405 | -0.7 | -6.4
12 | 2008-03-23 | 2882.015 | -0.5381 | 0.17482 | 2008-03-18 | 20216 | 3 | -0.1 | Good Friday
13 | 2008-03-30 | 2904.051 | 0.47143 | 3.1009 | 2008-03-25 | 20381 | 2.6 | -1.9
14 | 2008-04-06 | 2802.28 | 5.519 | 3.9729 | 2008-04-01 | 19512 | 14.1 | 4.1
15 | 2008-04-13 | 2735.455 | 8.2429 | 6.1494 | 2008-04-11 | 19341 | 5.2 | 0
16 | 2008-04-20 | 2631.256 | 13.819 | 4.7583 | 2008-04-14 | 18334 | 9.7 | 0.8
17 | 2008-04-27 | 2592.821 | 16.2286 | 7.5583 | 2008-04-21 | 18106 | 20.4 | 6.2
18 | 2008-05-04 | 2643.388 | 8.1095 | 10.6321 | 2008-04-28 | 18445 | 6.9 | 10.9
19 | 2008-05-11 | 2559.939 | 12.3333 | 14.7881 | 2008-05-07 | 18004 | 15.6 | 30.4
20 | 2008-05-18 | 2565.533 | 13.2619 | 12.672 | 2008-05-14 | 17929 | 17 | 10.3
21 | 2008-05-25 | 2542.214 | 12.1619 | 15.5881 | 2008-05-21 | 17970 | 9.4 | 27 | Victoria Day
22 | 2008-06-01 | 2612.02 | 16.3 | 13.6643 | 2008-05-26 | 18650 | 26.9 | 29.4
23 | 2008-06-08 | 2872.279 | 22.0524 | 16.8333 | 2008-06-06 | 21583 | 32.7 | 25
24 | 2008-06-15 | 2979.695 | 22.3952 | 17.6929 | 2008-06-09 | 24195 | 33.1 | 22.9
25 | 2008-06-22 | 2694.382 | 17.0095 | 20.7536 | 2008-06-16 | 19898 | 22.9 | 30.7
26 | 2008-06-29 | 2932.887 | 22.3238 | 18.7821 | 2008-06-26 | 22450 | 29.4 | 29.5
27 | 2008-07-06 | 2723.235 | 20.6429 | 21.0045 | 2008-07-02 | 20851 | 27.8 | 31.6 | Canada Day
28 | 2008-07-13 | 3049.551 | 23.9381 | 22.2089 | 2008-07-08 | 23680 | 30.7 | 31.3
29 | 2008-07-20 | 3072.241 | 23.9714 | 21.3923 | 2008-07-17 | 23787 | 30 | 30.5
30 | 2008-07-27 | 2905.6 | 22.2333 | 23.0952 | 2008-07-21 | 21202 | 24.8 | 30.2
31 | 2008-08-03 | 2978.63 | 23.0905 | 22.3661 | 2008-07-31 | 21896 | 26.4 | 30.9
32 | 2008-08-10 | 2828.486 | 19.9571 | 21.5214 | 2008-08-05 | 22707 | 26.1 | 30.3 | Civic Holiday
33 | 2008-08-17 | 2785.971 | 20.4524 | 21.5494 | 2008-08-14 | 19694 | 23.4 | 32.1
34 | 2008-08-24 | 2938.029 | 21.581 | 21.1952 | 2008-08-18 | 22571 | 29.4 | 28.8
35 | 2008-08-31 | 2797.494 | 19.8095 | 19.9125 | 2008-08-29 | 19497 | 24.8 | 26.6
36 | 2008-09-07 | 2901.025 | 21.281 | 20.1685 | 2008-09-03 | 22975 | 30.3 | 29.5 | Labour Day
37 | 2008-09-14 | 2762.587 | 18.6619 | 18.269 | 2008-09-14 | 19676 | 28 | 27.1
38 | 2008-09-21 | 2675.699 | 16.3952 | 14.6787 | 2008-09-17 | 18795 | 23 | 25.3
39 | 2008-09-28 | 2681.601 | 17.1333 | 14.6461 | 2008-09-25 | 19143 | 23.5 | 24.4
40 | 2008-10-05 | 2615.765 | 11.6524 | 15.4244 | 2008-09-29 | 18338 | 14.3 | 23.9
41 | 2008-10-12 | 2601.063 | 13.0429 | 11.5271 | 2008-10-08 | 18706 | 14.6 | 6.4
42 | 2008-10-19 | 2542.466 | 11.7952 | 10.6226 | 2008-10-16 | 18228 | 13.7 | 9.8 | Thanksgiving Day
43 | 2008-10-26 | 2662.917 | 7.7905 | 9.2086 | 2008-10-21 | 19033 | 5.9 | 8.5
44 | 2008-11-02 | 2691.028 | 5.8095 | 6.506 | 2008-10-28 | 19366 | 4.8 | 4.9
45 | 2008-11-09 | 2607.69 | 10.4714 | 7.1875 | 2008-11-03 | 19036 | 15.6 | 6.3
46 | 2008-11-16 | 2703.31 | 5.9429 | 6.3202 | 2008-11-11 | 19829 | 5.6 | 1 | Remembrance Day
47 | 2008-11-23 | 2928.913 | -3.3476 | 3.1232 | 2008-11-19 | 21159 | -1.6 | 0
48 | 2008-11-30 | 2882.525 | 1.8238 | 1.6381 | 2008-11-24 | 21279 | 3.8 | -0.3
49 | 2008-12-07 | 3413.45 | -1.7048 | 2.1229 | 2008-12-02 | 21079 | 0.3 | -4
50 | 2008-12-14 | 3096.886 | -2.4048 | -0.78274 | 2008-12-08 | 22541 | -3.7 | -4.8
51 | 2008-12-21 | 2206.586 | -5.1 | -2.2914 | 2008-12-19 | 22222 | -8.9 | -2.2
52 | 2008-12-28 | 3540.354 | -0.44286 | -0.92381 | 2008-12-22 | 21757 | -7.7 | -4.8 | Christmas & Boxing Day
1 | 2009-01-04 | 2387.108 | -4.2571 | -5.064 | 2009-01-04 | 19983 | -2.1 | -7.8 | New Years Day
2 | 2009-01-11 | 3041.545 | -5.7524 | -3.4333 | 2009-01-08 | 21304 | -4.5 | -5.1
3 | 2009-01-18 | 3246.179 | -10.2429 | -4.9378 | 2009-01-15 | 22983 | -11.3 | -11.6
4 | 2009-01-25 | 3145.853 | -8.0571 | -6.425 | 2009-01-20 | 22248 | -10.4 | -13.5
5 | 2009-02-01 | 3107.07 | -6.6524 | -4.7643 | 2009-01-26 | 22304 | -8.9 | -16.1
6 | 2009-02-08 | 3005.53 | -5.0857 | -3.6732 | 2009-02-04 | 22110 | -13.1 | -10
7 | 2009-02-15 | 2851.197 | 0.82857 | -5.3833 | 2009-02-12 | 20093 | 4.5 | -6.8
8 | 2009-02-22 | 2902.241 | -3.1286 | -3.8012 | 2009-02-19 | 20878 | -5.2 | -8.6 | Family Day
9 | 2009-03-01 | 2951.565 | -4.0571 | -3.0643 | 2009-02-23 | 20920 | -6.1 | -5.3
10 | 2009-03-08 | 2896.054 | -0.40952 | -2.431 | 2009-03-02 | 21466 | -9.6 | -7.9
11 | 2009-03-15 | 2806.246 | 0.61429 | -1.4926 | 2009-03-12 | 19619 | -3.4 | -6.4
12 | 2009-03-22 | 2632.842 | 4.3143 | 0.17482 | 2009-03-19 | 18214 | 3.2 | -0.1
13 | 2009-03-29 | 2643.995 | 5.3143 | 3.1009 | 2009-03-24 | 18603 | 2.8 | -1.9
14 | 2009-04-05 | 2608.623 | 6.6429 | 3.9729 | 2009-03-30 | 18239 | 4.9 | 4.1
15 | 2009-04-12 | 2558.043 | 3.2905 | 6.1494 | 2009-04-07 | 18744 | -0.5 | 0 | Good Friday
16 | 2009-04-19 | 2456.32 | 10.4667 | 4.7583 | 2009-04-14 | 17190 | 11.4 | 0.8 | Easter Monday
17 | 2009-04-26 | 2480.453 | 10.3286 | 7.5583 | 2009-04-20 | 18186 | 5.6 | 6.2
18 | 2009-05-03 | 2404.345 | 13.219 | 10.6321 | 2009-04-27 | 16883 | 27.1 | 10.9
19 | 2009-05-10 | 2404.151 | 14.1143 | 14.7881 | 2009-05-07 | 16700 | 18.6 | 30.4
20 | 2009-05-17 | 2383.442 | 13.0524 | 12.672 | 2009-05-14 | 16865 | 21.1 | 10.3
21 | 2009-05-24 | 2353.277 | 17.9429 | 15.5881 | 2009-05-21 | 17560 | 28.6 | 27 | Victoria Day & Lowest May Peak
22 | 2009-05-31 | 2384.126 | 14.281 | 13.6643 | 2009-05-27 | 16857 | 16 | 29.4
23 | 2009-06-07 | 2388.46 | 14.9619 | 16.8333 | 2009-06-01 | 16859 | 15.3 | 25
24 | 2009-06-14 | 2415.087 | 16.7762 | 17.6929 | 2009-06-11 | 16980 | 19.8 | 22.9
25 | 2009-06-21 | 2494.456 | 18.6476 | 20.7536 | 2009-06-16 | 17814 | 23.4 | 30.7
26 | 2009-06-28 | 2844.559 | 23.3 | 18.7821 | 2009-06-24 | 22540 | 30.7 | 29.5
27 | 2009-07-05 | 2443.699 | 19.0667 | 21.0045 | 2009-06-29 | 18486 | 22.6 | 31.6 | Canada Day
28 | 2009-07-12 | 2562.889 | 20.3619 | 22.2089 | 2009-07-10 | 19058 | 25.9 | 31.3
29 | 2009-07-19 | 2518.426 | 19.519 | 21.3923 | 2009-07-16 | 19221 | 27 | 30.5
30 | 2009-07-26 | 2564.946 | 20.1619 | 23.0952 | 2009-07-22 | 18315 | 22.3 | 30.2
31 | 2009-08-02 | 2653.667 | 22.6857 | 22.3661 | 2009-07-28 | 20011 | 27.4 | 30.9 | Lowest July Peak
32 | 2009-08-09 | 2593.174 | 20.9905 | 21.5214 | 2009-08-04 | 20541 | 26.4 | 30.3 | Civic Holiday
33 | 2009-08-16 | 3010.378 | 24.2952 | 21.5494 | 2009-08-10 | 22306 | 29.9 | 32.1
34 | 2009-08-23 | 2983.327 | 23.9762 | 21.1952 | 2009-08-17 | 24380 | 31.2 | 28.8
35 | 2009-08-30 | 2587.498 | 18.8048 | 19.9125 | 2009-08-25 | 19991 | 25.5 | 26.6
36 | 2009-09-06 | 2554.015 | 19.1238 | 20.1685 | 2009-09-03 | 18680 | 23.7 | 29.5
37 | 2009-09-13 | 2588.843 | 20.0429 | 18.269 | 2009-09-08 | 19731 | 25.1 | 27.1 | Labour Day & Lowest September Peak
38 | 2009-09-20 | 2507.039 | 16.5238 | 14.6787 | 2009-09-14 | 18616 | 25 | 25.3
39 | 2009-09-27 | 2562.771 | 18.4286 | 14.6461 | 2009-09-23 | 19397 | 27.2 | 24.4
40 | 2009-10-04 | 2475.228 | 11.2571 | 15.4244 | 2009-10-01 | 17462 | 11.4 | 23.9
41 | 2009-10-11 | 2471.268 | 10.6286 | 11.5271 | 2009-10-07 | 17484 | 12.4 | 6.4
42 | 2009-10-18 | 2543.161 | 4.7 | 10.6226 | 2009-10-15 | 18420 | 4.1 | 9.8 | Thanksgiving Day
43 | 2009-10-25 | 2556.282 | 10.3524 | 9.2086 | 2009-10-22 | 18191 | 15.7 | 8.5
44 | 2009-11-01 | 2552.522 | 10.719 | 6.506 | 2009-10-26 | 18170 | 11.7 | 4.9
45 | 2009-11-08 | 2584.62 | 6.7429 | 7.1875 | 2009-11-04 | 19053 | 5.9 | 6.3
46 | 2009-11-15 | 2558.964 | 8.6048 | 6.3202 | 2009-11-09 | 18795 | 18.6 | 1
47 | 2009-11-22 | 2604.497 | 6.7571 | 3.1232 | 2009-11-19 | 19240 | 9.6 | 0
48 | 2009-11-29 | 2639.28 | 6.1714 | 1.6381 | 2009-11-24 | 19376 | 7.6 | -0.3
49 | 2009-12-06 | 2740.052 | 2.6714 | 2.1229 | 2009-12-03 | 19740 | 6.5 | -4
50 | 2009-12-13 | 3388.584 | -1.4952 | -0.78274 | 2009-12-10 | 21569 | -2.7 | -4.8
51 | 2009-12-20 | 3358.738 | -3.1857 | -2.2914 | 2009-12-17 | 21831 | -6.7 | -2.2
52 | 2009-12-27 | 1988.085 | -2.0048 | -0.92381 | 2009-12-22 | 21373 | -5.7 | -4.8 | Christmas & Boxing Day
53 | 2010-01-03 | 2800.83 | -6.0238 | -3.3235 | 2010-01-03 | 20885 | -8.6 | -7.8 | New Years Day
1 | 2010-01-10 | 3078.183 | -7.5952 | -5.064 | 2010-01-04 | 22045 | -7.3 | -7.8
2 | 2010-01-17 | 2942.677 | -1.3429 | -3.4333 | 2010-01-11 | 21570 | -4.7 | -5.1
3 | 2010-01-24 | 2901.727 | -0.53333 | -4.9378 | 2010-01-20 | 20887 | -2.5 | -11.6
4 | 2010-01-31 | 3028.241 | -5.6381 | -6.425 | 2010-01-28 | 22033 | -7 | -13.5
5 | 2010-02-07 | 3015.804 | -4.8048 | -4.7643 | 2010-02-01 | 21367 | -3.6 | -16.1
6 | 2010-02-14 | 2991.68 | -4.1476 | -3.6732 | 2010-02-09 | 21240 | -3.9 | -10
7 | 2010-02-21 | 2851.427 | -0.30476 | -5.3833 | 2010-02-17 | 20431 | 0.4 | -6.8 | Family Day
8 | 2010-02-28 | 2892.841 | -1.319 | -3.8012 | 2010-02-25 | 20748 | -5.8 | -8.6
9 | 2010-03-07 | 2739.995 | 1.7714 | -3.0643 | 2010-03-01 | 19393 | 2 | -5.3 | Lowest March Peak
10 | 2010-03-14 | 2622.761 | 6.7714 | -2.431 | 2010-03-10 | 18396 | 8.8 | -7.9
11 | 2010-03-21 | 2535.632 | 9.1429 | -1.4926 | 2010-03-15 | 17480 | 12.1 | -6.4
12 | 2010-03-28 | 2654.498 | 3.4762 | 0.17482 | 2010-03-25 | 18490 | 8.6 | -0.1
13 | 2010-04-04 | 2404.754 | 12.3048 | 3.1009 | 2010-03-29 | 17717 | 8.4 | -1.9 | Good Friday
14 | 2010-04-11 | 2493.767 | 10.6048 | 3.9729 | 2010-04-09 | 17398 | 3.6 | 4.1 | Easter Monday & Lowest April Peak
15 | 2010-04-18 | 2460.224 | 10.8905 | 6.1494 | 2010-04-16 | 16784 | 20.6 | 0
16 | 2010-04-25 | 2445.819 | 11.5762 | 4.7583 | 2010-04-22 | 16674 | 12.3 | 0.8
17 | 2010-05-02 | 2454.494 | 14.5476 | 7.5583 | 2010-04-27 | 16709 | 9.4 | 6.2
18 | 2010-05-09 | 2481.635 | 13.0619 | 10.6321 | 2010-05-05 | 17332 | 26.9 | 10.9
19 | 2010-05-16 | 2474.648 | 10.8143 | 14.7881 | 2010-05-14 | 17988 | 20.4 | 30.4
20 | 2010-05-23 | 2470.732 | 18.5524 | 12.672 | 2010-05-20 | 17812 | 28.3 | 10.3
21 | 2010-05-30 | 2867.008 | 24.0429 | 15.5881 | 2010-05-26 | 22904 | 31.4 | 27
22 | 2010-06-06 | 2735.265 | 20.3905 | 13.6643 | 2010-05-31 | 20993 | 27.6 | 29.4
23 | 2010-06-13 | 2547.381 | 17.1 | 16.8333 | 2010-06-11 | 17858 | 22.7 | 25
24 | 2010-06-20 | 2706.133 | 21.9286 | 17.6929 | 2010-06-18 | 19340 | 25 | 22.9
25 | 2010-06-27 | 2823.009 | 22.2571 | 20.7536 | 2010-06-23 | 21527 | 28.3 | 30.7 | Lowest June Peak
26 | 2010-07-04 | 2604.946 | 21.0905 | 18.7821 | 2010-06-28 | 21415 | 28.9 | 29.5 | Canada Day
27 | 2010-07-11 | 3267.842 | 26.9619 | 21.0045 | 2010-07-08 | 25075 | 33.3 | 31.6
28 | 2010-07-18 | 3104.913 | 25.1238 | 22.2089 | 2010-07-15 | 23661 | 28.9 | 31.3
29 | 2010-07-25 | 3011.922 | 24.5714 | 21.3923 | 2010-07-21 | 22329 | 30.1 | 30.5
30 | 2010-08-01 | 2840.623 | 22.3952 | 23.0952 | 2010-07-27 | 22472 | 28.3 | 30.2
31 | 2010-08-08 | 2936.261 | 24.3286 | 22.3661 | 2010-08-04 | 23661 | 31.5 | 30.9 | Civic Holiday
32 | 2010-08-15 | 3126.452 | 25.1429 | 21.5214 | 2010-08-10 | 23531 | 29.4 | 30.3
33 | 2010-08-22 | 2801.155 | 22.019 | 21.5494 | 2010-08-16 | 21052 | 27 | 32.1
34 | 2010-08-29 | 2721.586 | 21.1619 | 21.1952 | 2010-08-29 | 20151 | 30.1 | 28.8
35 | 2010-09-05 | 3035.483 | 23.8286 | 19.9125 | 2010-08-31 | 24917 | 32.9 | 26.6
36 | 2010-09-12 | 2504.841 | 18.1857 | 20.1685 | 2010-09-07 | 19476 | 29.6 | 29.5 | Labour Day
37 | 2010-09-19 | 2489.359 | 15.7571 | 18.269 | 2010-09-13 | 17627 | 23.6 | 27.1
38 | 2010-09-26 | 2541.1 | 17.6952 | 14.6787 | 2010-09-24 | 18811 | 30.5 | 25.3
39 | 2010-10-03 | 2474.349 | 13.3762 | 14.6461 | 2010-09-27 | 17718 | 15.7 | 24.4
40 | 2010-10-10 | 2465.115 | 14.119 | 15.4244 | 2010-10-05 | 17528 | 15 | 23.9
41 | 2010-10-17 | 2435.699 | 10.9381 | 11.5271 | 2010-10-13 | 17631 | 14.8 | 6.4 | Thanksgiving Day
42 | 2010-10-24 | 2513.619 | 9.1714 | 10.6226 | 2010-10-18 | 17704 | 11.4 | 9.8 | Lowest October Peak
43 | 2010-10-31 | 2499.002 | 11.4571 | 9.2086 | 2010-10-26 | 17510 | 20.5 | 8.5
44 | 2010-11-07 | 2598.049 | 4.3 | 6.506 | 2010-11-03 | 18147 | 9.4 | 4.9
45 | 2010-11-14 | 2578.05 | 6.2429 | 7.1875 | 2010-11-08 | 18417 | 10 | 6.3 | Remembrance Day
46 | 2010-11-21 | 2618.98 | 5.5333 | 6.3202 | 2010-11-18 | 18793 | 6.2 | 1
47 | 2010-11-28 | 2712.545 | 4.019 | 3.1232 | 2010-11-25 | 19970 | 4.2 | 0
48 | 2010-12-05 | 2794.369 | 1.2 | 1.6381 | 2010-12-02 | 20160 | 0.8 | -0.3
49 | 2010-12-12 | 2915.854 | -2.4 | 2.1229 | 2010-12-08 | 21409 | -3.6 | -4
50 | 2010-12-19 | 3434.205 | -6.3476 | -0.78274 | 2010-12-13 | 22114 | -11.6 | -4.8
51 | 2010-12-26 | 2821.777 | -4.6714 | -2.2914 | 2010-12-20 | 20813 | -0.7 | -2.2 | Christmas & Boxing Day
52 | 2011-01-02 | 2226.916 | 0.57143 | -0.92381 | 2010-12-28 | 19102 | #REF! | -4.8 | New Years Day
1 | 2011-01-09 | 2932.595 | -4.4905 | -5.064 | 2011-01-06 | 21010 | #REF! | -7.8
2 | 2011-01-16 | 3040.08 | -7.1476 | -3.4333 | 2011-01-12 | 21264 | -0.7 | -5.1
3 | 2011-01-23 | 3117.216 | -9.0762 | -4.9378 | 2011-01-17 | 21820 | -3.2 | -11.6
4 | 2011-01-30 | 3049.914 | -4.9571 | -6.425 | 2011-01-24 | 22733 | -7.7 | -13.5
5 | 2011-02-06 | 3058.923 | -7.2619 | -4.7643 | 2011-01-31 | 22045 | -7.1 | -16.1
6 | 2011-02-13 | 3008.044 | -6.8476 | -3.6732 | 2011-02-08 | 21651 | -9 | -10
7 | 2011-02-20 | 2844.013 | -0.033333 | -5.3833 | 2011-02-15 | 20898 | -10.7 | -6.8
8 | 2011-02-27 | 2909.114 | -3.9714 | -3.8012 | 2011-02-22 | 20526 | -9.9 | -8.6 | Family Day
9 | 2011-03-06 | 2883.238 | -1.1667 | -3.0643 | 2011-03-02 | 20667 | -4.9 | -5.3
10 | 2011-03-13 | 2834.345 | 0.45238 | -2.431 | 2011-03-09 | 20203 | -3.9 | -7.9
11 | 2011-03-20 | 2667.338 | 4.1524 | -1.4926 | 2011-03-14 | 18636 | -4.3 | -6.4 | March Break
12 | 2011-03-27 | 2788.855 | -1.9524 | 0.17482 | 2011-03-23 | 19380 | 2.8 | -0.1
13 | 2011-04-03 | 2657.294 | 3.5 | 3.1009 | 2011-03-28 | 18826 | 2.7 | -1.9
14 | 2011-04-10 | 2574.34 | 7.4286 | 3.9729 | 2011-04-05 | 17945 | -4.5 | 4.1
15 | 2011-04-17 | 2527.368 | 7.8381 | 6.1494 | 2011-04-13 | 16980 | 2.2 | 0
16 | 2011-04-24 | 2511.036 | 6.5 | 4.7583 | 2011-04-19 | 17932 | 5.2 | 0.8 | Good Friday and Easter
17 | 2011-05-01 | 2431.844 | 10.4619 | 7.5583 | 2011-04-26 | 16800 | 11.2 | 6.2
18 | 2011-05-08 | 2421.856 | 11.2286 | 10.6321 | 2011-05-03 | 17128 | 5.7 | 10.9
19 | 2011-05-15 | 2406.703 | 14.6667 | 14.7881 | 2011-05-13 | 16480 | 11.6 | 30.4
20 | 2011-05-22 | 2434.802 | 15.981 | 12.672 | 2011-05-16 | 16782 | 7 | 10.3
21 | 2011-05-29 | 2389.043 | 16.781 | 15.5881 | 2011-05-26 | 16733 | 25.8 | 27 | Victoria Day
22 | 2011-06-05 | 2578.219 | 20.5857 | 13.6643 | 2011-05-31 | 20847 | 10.2 | 29.4
23 | 2011-06-12 | 2672.622 | 21.2 | 16.8333 | 2011-06-08 | 22765 | 20.2 | 25
24 | 2011-06-19 | 2578.342 | 19.8048 | 17.6929 | 2011-06-16 | 18807 | 29.3 | 22.9
25 | 2011-06-26 | 2663.023 | 20.9238 | 20.7536 | 2011-06-21 | 19985 | 33.3 | 30.7
26 | 2011-07-03 | 2641.963 | 22.2429 | 18.7821 | 2011-06-28 | 19977 | 24.7 | 29.5 | Canada Day
27 | 2011-07-10 | 2886.323 | 24.2762 | 21.0045 | 2011-07-06 | 21326 | 25.6 | 31.6
28 | 2011-07-17 | 3015.908 | 25.819 | 22.2089 | 2011-07-12 | 22739 | 26.3 | 31.3
29 | 2011-07-24 | 3358.04 | 28.8381 | 21.3923 | 2011-07-21 | 25450 | 29.2 | 30.5
30 | 2011-07-31 | 2951.6 | 25.1714 | 23.0952 | 2011-07-29 | 21567 | 31.7 | 30.2
31 | 2011-08-07 | 2992.2 | 24.7476 | 22.3661 | 2011-08-02 | 22051 | 37.5 | 30.9 | Civic Holiday & Lowest August Peak
32 | 2011-08-14 | 2793.819 | 22.2286 | 21.5214 | 2011-08-08 | 21794 | 31.4 | 30.3
33 | 2011-08-21 | 2867.791 | 23.8857 | 21.5494 | 2011-08-18 | 21420 | 31.3 | 32.1
34 | 2011-08-28 | 2687.852 | 21.9095 | 21.1952 | 2011-08-24 | 19979 | 26.2 | 28.8
35 | 2011-09-04 | 2848.298 | 23.3381 | 19.9125 | 2011-09-02 | 21552 | 29.9 | 26.6
36 | 2011-09-11 | 2516.018 | 18.5333 | 20.1685 | 2011-09-09 | 18205 | 27.9 | 29.5 | Labour Day
37 | 2011-09-18 | 2553.008 | 16.4429 | 18.269 | 2011-09-12 | 20157 | 28.3 | 27.1
38 | 2011-09-25 | 2541.29 | 18.0286 | 14.6787 | 2011-09-21 | 18217 | 25.2 | 25.3
39 | 2011-10-02 | 2531.932 | 15.5333 | 14.6461 | 2011-09-26 | 18537 | 28.5 | 24.4
40 | 2011-10-09 | 2469.981 | 15.981 | 15.4244 | 2011-10-03 | 17481 | 21.7 | 23.9
41 | 2011-10-16 | 2463.933 | 15.4476 | 11.5271 | 2011-10-12 | 18048 | 24.1 | 6.4 | Thanksgiving Day
42 | 2011-10-23 | 2496.614 | 9.7476 | 10.6226 | 2011-10-19 | 17726 | 14 | 9.8
43 | 2011-10-30 | 2555.012 | 6.6667 | 9.2086 | 2011-10-27 | 18234 | 18.1 | 8.5
44 | 2011-11-06 | 2540.414 | 8.0762 | 6.506 | 2011-11-01 | 17911 | 11.7 | 4.9
45 | 2011-11-13 | 2549.575 | 9.9667 | 7.1875 | 2011-11-11 | 18381 | 4.7 | 6.3
46 | 2011-11-20 | 2579.849 | 7.581 | 6.3202 | 2011-11-17 | 18931 | 12.7 | 1
47 | 2011-11-27 | 2635.291 | 6.381 | 3.1232 | 2011-11-22 | 19501 | 5.5 | 0
48 | 2011-12-04 | 2710.482 | 4.1476 | 1.6381 | 2011-11-29 | 19673 | 4.3 | -0.3 | Lowest November Peak
49 | 2011-12-11 | 2799.235 | 0.80476 | 2.1229 | 2011-12-07 | 20004 | 1.3 | -4
50 | 2011-12-18 | 2785.644 | 2.681 | -0.78274 | 2011-12-12 | 19891 | 5.6 | -4.8
51 | 2011-12-25 | 3151.681 | 0.8619 | -2.2914 | 2011-12-20 | 20204 | 1.2 | -2.2 | Christmas Day & Lowest December Peak
52 | 2012-01-01 | 2204.338 | -0.25238 | -0.92381 | 2011-12-29 | 19463 | 6.5 | -4.8 | Boxing Day & New Years
1 | 2012-01-08 | 2830.124 | -1.7476 | -5.064 | 2012-01-03 | 21847 | -1.3 | -7.8 | Lowest January Peak
2 | 2012-01-15 | 2870.763 | -1.8952 | -3.4333 | 2012-01-15 | 20017 | -2.8 | -5.1
3 | 2012-01-22 | 2982.814 | -2.3333 | -4.9378 | 2012-01-18 | 20986 | -14.3 | -11.6
4 | 2012-01-29 | 2856.312 | 0.95238 | -6.425 | 2012-01-25 | 20150 | -7.5 | -13.5
5 | 2012-02-05 | 2797.059 | 1.7286 | -4.7643 | 2012-01-30 | 20213 | -4.5 | -16.1
6 | 2012-02-12 | 2852.416 | -1.7524 | -3.6732 | 2012-02-07 | 19852 | -0.9 | -10
7 | 2012-02-19 | 2790.992 | 0.64286 | -5.3833 | 2012-02-14 | 19605 | -1.4 | -6.8
8 | 2012-02-26 | 2759.291 | 0.98095 | -3.8012 | 2012-02-21 | 19603 | -0.3 | -8.6 | Family Day
9 | 2012-03-04 | 2802.624 | 1.4048 | -3.0643 | 2012-02-29 | 19956 | 1 | -5.3 | Lowest February Peak
10 | 2012-03-11 | 2750.492 | 3.3857 | -2.431 | 2012-03-05 | 20332 | 3 | -7.9
11 | 2012-03-18 | 2488.948 | 11.5429 | -1.4926 | 2012-03-12 | 17578 | 1.3 | -6.4
12 | 2012-03-25 | 2449.348 | 16.0571 | 0.17482 | 2012-03-22 | 17384 | -2.8 | -0.1
13 | 2012-04-01 | 2582.606 | 3.9857 | 3.1009 | 2012-03-26 | 18136 | 11.8 | -1.9
14 | 2012-04-08 | 2439.754 | 7.7857 | 3.9729 | 2012-04-03 | 17464 | 23.7 | 4.1 | Good Friday
15 | 2012-04-15 | 2491.448 | 9.9 | 6.1494 | 2012-04-10 | 17721 | 2.6 | 0 | Easter Monday
16 | 2012-04-22 | 2477.182 | 11.1857 | 4.7583 | 2012-04-18 | 17032 | 10.7 | 0.8
17 | 2012-04-29 | 2515.421 | 6.6048 | 7.5583 | 2012-04-23 | 17874 | 8 | 6.2
18 | 2012-05-06 | 2439.929 | 12.8714 | 10.6321 | 2012-04-30 | 17560 | 9 | 10.9
19 | 2012-05-13 | 2402.93 | 15.7048 | 14.7881 | 2012-05-07 | 16656 | 4.1 | 30.4
20 | 2012-05-20 | 2440.806 | 17.3905 | 12.672 | 2012-05-15 | 17097 | 9.4 | 10.3
21 | 2012-05-27 | 2629.116 | 22.3619 | 15.5881 | 2012-05-25 | 20295 | 15.3 | 27 | Victoria Day
22 | 2012-06-03 | 2586.719 | 18.3714 | 13.6643 | 2012-05-28 | 21106 | 23.7 | 29.4
23 | 2012-06-10 | 2570.046 | 19.8429 | 16.8333 | 2012-06-10 | 19276 | 30.7 | 25
24 | 2012-06-17 | 2729.994 | 21.6 | 17.6929 | 2012-06-11 | 21508 | 28.6 | 22.9
25 | 2012-06-24 | 3053.92 | 25.3905 | 20.7536 | 2012-06-20 | 24107 | 29 | 30.7
26 | 2012-07-01 | 2839.086 | 24.1095 | 18.7821 | 2012-06-28 | 22151 | 27.7 | 29.5
27 | 2012-07-08 | 3080.272 | 26.4571 | 21.0045 | 2012-07-04 | 23910 | 34.2 | 31.6 | Canada Day (Observed)
28 | 2012-07-15 | 3048.09 | 25.3476 | 22.2089 | 2012-07-13 | 22927 | 29.2 | 31.3
29 | 2012-07-22 | 3058.976 | 25.5857 | 21.3923 | 2012-07-17 | 24636 | 35.9 | 30.5
30 | 2012-07-29 | 2987.556 | 24.8476 | 23.0952 | 2012-07-23 | 23745 | 32.3 | 30.2
31 | 2012-08-05 | 3120.831 | 25.8952 | 22.3661 | 2012-08-03 | 23188 | 36.2 | 30.9
32 | 2012-08-12 | 2770.823 | 22.2143 | 21.5214 | 2012-08-08 | 22170 | 34.1 | 30.3 | Civic Holiday
33 | 2012-08-19 | 2712.196 | 21.1524 | 21.5494 | 2012-08-16 | 20242 | 30.1 | 32.1
34 | 2012-08-26 | 2840.436 | 23.1095 | 21.1952 | 2012-08-24 | 21277 | 28.2 | 28.8
35 | 2012-09-02 | 2836.455 | 23.1286 | 19.9125 | 2012-08-31 | 21800 | 26.8 | 26.6
36 | 2012-09-09 | 2790.678 | 21.1286 | 20.1685 | 2012-09-06 | 21183 | 28.7 | 29.5 | Labour Day
37 | 2012-09-16 | 2576.648 | 18.7333 | 18.269 | 2012-09-13 | 20078 | 32.6 | 27.1
38 | 2012-09-23 | 2469.232 | 14.9238 | 14.6787 | 2012-09-17 | 17899 | 27.1 | 25.3
39 | 2012-09-30 | 2452.893 | 13.9 | 14.6461 | 2012-09-25 | 17266 | 28.7 | 24.4
40 | 2012-10-07 | 2476.794 | 14.5524 | 15.4244 | 2012-10-03 | 17746 | 23.2 | 23.9
41 | 2012-10-14 | 2492.215 | 9.6857 | 11.5271 | 2012-10-11 | 17974 | 22 | 6.4 | Thanksgiving Day
42 | 2012-10-21 | 2489.396 | 11.2143 | 10.6226 | 2012-10-15 | 18069 | 18.5 | 9.8
43 | 2012-10-28 | 2537.019 | 10.6476 | 9.2086 | 2012-10-24 | 18081 | 12.8 | 8.5
44 | 2012-11-04 | 2630.347 | 5.0095 | 6.506 | 2012-10-29 | 18829 | 11 | 4.9
45 | 2012-11-11 | 2672.577 | 4.9714 | 7.1875 | 2012-11-06 | 19419 | 11.4 | 6.3 | Remembrance Day
46 | 2012-11-18 | 2633.982 | 5.5857 | 6.3202 | 2012-11-13 | 19359 | 4.3 | 1
47 | 2012-11-25 | 2641.862 | 5.5667 | 3.1232 | 2012-11-19 | 18859 | 2.7 | 0
48 | 2012-12-02 | 2812.124 | 1.6 | 1.6381 | 2012-11-30 | 20144 | 3 | -0.3
49 | 2012-12-09 | 2351.062 | 3.6524 | 2.1229 | 2012-12-05 | 20208 | 8.4 | -4
50 | 2012-12-16 | 3205.754 | 2.019 | -0.78274 | 2012-12-11 | 20382 | -3.7 | -4.8
51 | 2012-12-23 | 3173.023 | 2.6952 | -2.2914 | 2012-12-20 | 19916 | 1.5 | -2.2
52 | 2012-12-29 | 2669.562 | -3.1286 | -0.92381 | 2012-12-27 | 19223 | -1 | -4.8 | Christmas Day
1 | 2013-01-06 | 2413.989 | -2.2571 | -5.064 | 2013-01-02 | 20712 | 2.6 | -7.8 | New Year's Day
2 | 2013-01-13 | 2752.546 | 4.7095 | -3.4333 | 2013-01-07 | 20221 | -3.1 | -5.1
3 | 2013-01-20 | 2873.56 | -2.2524 | -4.9378 | 2013-01-17 | 20753 | -2.8 | -11.6
4 | 2013-01-27 | 3164.524 | -9.9381 | -6.425 | 2013-01-24 | 22610 | 0.3 | -13.5
5 | 2013-02-03 | 2959.042 | -1.8524 | -4.7643 | 2013-02-01 | 20816 | -7.3 | -16.1
6 | 2013-02-10 | 3047.304 | -6.3143 | -3.6732 | 2013-02-04 | 21426 | -11.6 | -10
7 | 2013-02-17 | 2885.633 | -2.5857 | -5.3833 | 2013-02-12 | 20258 | -7.1 | -6.8
8 | 2013-02-24 | 2898.829 | -2.9762 | -3.8012 | 2013-02-20 | 20941 | -5.8 | -8.6 | Family Day
9 | 2013-03-03 | 2824.951 | -1.3714 | -3.0643 | 2013-02-27 | 20003 | 0.6 | -5.3
10 | 2013-03-10 | 2723.712 | 1.7524 | -2.431 | 2013-03-04 | 19825 | -5.5 | -7.9
11 | 2013-03-17 | 2741.506 | 0 | -1.4926 | 2013-03-14 | 19027 | 1.5 | -6.4
12 | 2013-03-24 | 2776.972 | -1.081 | 0.17482 | 2013-03-18 | 19792 | -1.8 | -0.1
13 | 2013-03-31 | 2527.504 | 5.8 | 3.1009 | 2013-03-25 | 18379 | 0.1 | -1.9 | Good Friday
14 | 2013-04-07 | 2634.725 | 2.6 | 3.9729 | 2013-04-03 | 18854 | -0.1 | 4.1 | Easter Monday
15 | 2013-04-14 | 2626.098 | 5.0667 | 6.1494 | 2013-04-11 | 18574 | 5.4 | 0
16 | 2013-04-21 | 2516.299 | 9.0619 | 4.7583 | 2013-04-15 | 17358 | 2.3 | 0.8
17 | 2013-04-28 | 2457.206 | 9.219 | 7.5583 | 2013-04-24 | 17635 | 0.1 | 6.2
18 | 2013-05-05 | 2381.822 | 17.0143 | 10.6321 | 2013-04-29 | 16697 | 12.6 | 10.9
19 | 2013-05-12 | 2410.926 | 15.1762 | 14.7881 | 2013-05-08 | 16694 | 12.3 | 30.4
20 | 2013-05-19 | 2377.09 | 14.0905 | 12.672 | 2013-05-13 | 16609 | 13.1 | 10.3
21 | 2013-05-26 | 2422.755 | 15.9429 | 15.5881 | 2013-05-21 | 18234 | 21.8 | 27 | Victoria Day
22 | 2013-06-02 | 2615.755 | 21.0667 | 13.6643 | 2013-05-31 | 20488 | 10.8 | 29.4
23 | 2013-06-09 | 2417.703 | 15.5667 | 16.8333 | 2013-06-06 | 16632 | 24.6 | 25
24 | 2013-06-16 | 2519.511 | 19.4238 | 17.6929 | 2013-06-12 | 17728 | 29.9 | 22.9
25 | 2013-06-23 | 2649.498 | 20.8857 | 20.7536 | 2013-06-23 | 20208 | 14.8 | 30.7
26 | 2013-06-30 | 2875.621 | 23.5286 | 18.7821 | 2013-06-24 | 22662 | 22.4 | 29.5
27 | 2013-07-07 | 2778.647 | 23.0667 | 21.0045 | 2013-07-04 | 21386 | 31.9 | 31.6 | Canada Day
28 | 2013-07-14 | 2886.509 | 23.6619 | 22.2089 | 2013-07-10 | 21756 | 31.6 | 31.3 | Toronto Flooding
29 | 2013-07-21 | 3295.661 | 27.4 | 21.3923 | 2013-07-17 | 24927 | 27.8 | 30.5
30 | 2013-07-28 | 2631.863 | 20.181 | 23.0952 | 2013-07-23 | 20185 | 30.5 | 30.2
31 | 2013-08-04 | 2546.742 | 20.2667 | 22.3661 | 2013-08-01 | 18363 | 34.3 | 30.9
32 | 2013-08-11 | 2615.337 | 21.5238 | 21.5214 | 2013-08-08 | 20161 | 27.4 | 30.3 | Civic Holiday
33 | 2013-08-18 | 2580.999 | 19.9714 | 21.5494 | 2013-08-12 | 18265 | 25.7 | 32.1
34 | 2013-08-25 | 2857.266 | 23.7048 | 21.1952 | 2013-08-21 | 22179 | 26.5 | 28.8
35 | 2013-09-01 | 3000.435 | 24.1476 | 19.9125 | 2013-08-29 | 22833 | 23 | 26.6
36 | 2013-09-08 | 2497.939 | 18.4952 | 20.1685 | 2013-09-04 | 18225 | 31.4 | 29.5 | Labour Day
37 | 2013-09-15 | 2675.451 | 18.9095 | 18.269 | 2013-09-10 | 22682 | 28.2 | 27.1
38 | 2013-09-22 | 2477.862 | 15.1048 | 14.6787 | 2013-09-20 | 18024 | 25.3 | 25.3
39 | 2013-09-29 | 2444.005 | 15.6 | 14.6461 | 2013-09-26 | 17411 | 33.9 | 24.4
40 | 2013-10-06 | 2530.285 | 17.9048 | 15.4244 | 2013-10-02 | 18009 | 23.5 | 23.9
41 | 2013-10-13 | 2441.634 | 13.5048 | 11.5271 | 2013-10-08 | 17402 | 20.5 | 6.4
42 | 2013-10-20 | 2434.309 | 12.4619 | 10.6226 | 2013-10-15 | 17627 | 24.6 | 9.8 | Thanksgiving Day
43 | 2013-10-27 | 2575.909 | 6.6905 | 9.2086 | 2013-10-24 | 18299 | 16.5 | 8.5
44 | 2013-11-03 | 2585.146 | 4.3048 | 6.506 | 2013-10-29 | 18445 | 17.1 | 4.9
45 | 2013-11-10 | 2622.99 | 6.2381 | 7.1875 | 2013-11-04 | 19028 | 8.3 | 6.3
46 | 2013-11-17 | 2666.574 | 5.3476 | 6.3202 | 2013-11-12 | 19835 | 6.6 | 1 | Remembrance Day
47 | 2013-11-24 | 2777.843 | 1.0286 | 3.1232 | 2013-11-24 | 19971 | 5.2 | 0
48 | 2013-11-30 | 2513.456 | -1.4143 | 1.6381 | 2013-11-28 | 20615 | 0.5 | -0.3
49 | 2013-12-08 | 2840.343 | 0.71905 | 2.1229 | 2013-12-03 | 20055 | -5.2 | -4
50 | 2013-12-15 | 3086.135 | -7.5905 | -0.78274 | 2013-12-14 | 21881 | -3.3 | -4.8
51 | 2013-12-22 | 2531.092 | -3.0143 | -2.2914 | 2013-12-16 | 21964 | 3.2 | -2.2 | GTA Ice Storm
52 | 2013-12-29 | 3427.753 | -3.4048 | -0.92381 | 2013-12-24 | 18980 | -11.7 | -4.8 | Christmas & Boxing Day
1 | 2014-01-05 | 2974.702 | -9.9143 | -5.064 | 2014-01-02 | 22476 | -8.3 | -7.8 | New Year's Day
2 | 2014-01-12 | 3035.381 | -6.2667 | -3.4333 | 2014-01-07 | 22774 | -9.9 | -5.1
3 | 2014-01-19 | 2887.782 | -1.0524 | -4.9378 | 2014-01-15 | 20346 | -17.9 | -11.6
4 | 2014-01-26 | 3242.618 | -13.2571 | -6.425 | 2014-01-22 | 22737 | -17.4 | -13.5
5 | 2014-02-02 | 3104.944 | -7.5 | -4.7643 | 2014-01-28 | 22383 | -1.2 | -16.1
6 | 2014-02-09 | 3088.63 | -9.9333 | -3.6732 | 2014-02-05 | 21268 | -14.4 | -10
7 | 2014-02-16 | 3065.943 | -8.5905 | -5.3833 | 2014-02-11 | 21678 | -12.8 | -6.8
8 | 2014-02-23 | 2868.455 | -1.419 | -3.8012 | 2014-02-18 | 20358 | -6.8 | -8.6 | Family Day
9 | 2014-03-02 | 3072.745 | -10.3714 | -3.0643 | 2014-02-27 | 21905 | -10.2 | -5.3
10 | 2014-03-09 | 2978.494 | -7.2286 | -2.431 | 2014-03-03 | 21656 | -1.6 | -7.9
11 | 2014-03-16 | 2816.441 | -1.5952 | -1.4926 | 2014-03-12 | 20318 | -12.2 | -6.4
12 | 2014-03-23 | 2836.699 | -1.3905 | 0.17482 | 2014-03-17 | 20103 | -12.1 | -0.1
13 | 2014-03-30 | 2820.119 | -1.1238 | 3.1009 | 2014-03-26 | 20043 | -4.5 | -1.9
14 | 2014-04-06 | 2623.14 | 4.2762 | 3.9729 | 2014-04-03 | 18131 | -4.5 | 4.1
15 | 2014-04-13 | 2520.753 | 10.0714 | 6.1494 | 2014-04-07 | 18084 | -5.1 | 0
16 | 2014-04-20 | 2503.383 | 6.0381 | 4.7583 | 2014-04-15 | 18557 | 3.4 | 0.8 | Good Friday
17 | 2014-04-27 | 2467.213 | 8.7905 | 7.5583 | 2014-04-22 | 17310 | 9.1 | 6.2 | Easter Monday
18 | 2014-05-04 | 2474.902 | 9.119 | 10.6321 | 2014-04-30 | 17763 | -0.9 | 10.9
19 | 2014-05-11 | 2373.068 | 14.1714 | 14.7881 | 2014-05-07 | 16567 | 11.3 | 30.4
20 | 2014-05-18 | 2396.518 | 13.8714 | 12.672 | 2014-05-13 | 16966 | 6.6 | 10.3
21 | 2014-05-25 | 2335.051 | 17.0905 | 15.5881 | 2014-05-21 | 16619 | 13 | 27 | Victoria Day
22 | 2014-06-01 | 2479.806 | 19.6524 | 13.6643 | 2014-05-27 | 18844 | 20.6 | 29.4
23 | 2014-06-08 | 2519.315 | 19.8333 | 16.8333 | 2014-06-02 | 19000 | 19.6 | 25
24 | 2014-06-15 | 2544.051 | 19.8952 | 17.6929 | 2014-06-12 | 18517 | 29.4 | 22.9
25 | 2014-06-22 | 2600.272 | 21.0667 | 20.7536 | 2014-06-17 | 19966 | 29.1 | 30.7
26 | 2014-06-29 | 2817.435 | 23.1095 | 18.7821 | 2014-06-27 | 19944 | 26.2 | 29.5
27 | 2014-07-06 | 2707.65 | 23.3429 | 21.0045 | 2014-06-30 | 20807 | 31.2 | 31.6 | Canada Day
28 | 2014-07-13 | 2670.256 | 22.2 | 22.2089 | 2014-07-07 | 20195 | 27 | 31.3
29 | 2014-07-20 | 2553.167 | 19.6857 | 21.3923 | 2014-07-14 | 18506 | 30.3 | 30.5
30 | 2014-07-27 | 2743.999 | 22.7857 | 23.0952 | 2014-07-22 | 21300 | 28.4 | 30.2
31 | 2014-08-03 | 2570.062 | 20.5286 | 22.3661 | 2014-08-01 | 18545 | 22.4 | 30.9
32 | 2014-08-10 | 2647.753 | 21.681 | 21.5214 | 2014-08-06 | 18911 | 29.8 | 30.3 | Civic Holiday
33 | 2014-08-17 | 2566.413 | 19.481 | 21.5494 | 2014-08-11 | 19767 | 27 | 32.1
34 | 2014-08-24 | 2669.881 | 20.7238 | 21.1952 | 2014-08-21 | 19532 | 24.7 | 28.8
35 | 2014-08-31 | 2736.15 | 22.9857 | 19.9125 | 2014-08-26 | 21363 | 27.5 | 26.6
36 | 2014-09-07 | 2730.29 | 22.9905 | 20.1685 | 2014-09-05 | 21123 | 25.7 | 29.5 | Labour Day
37 | 2014-09-14 | 2507.102 | 15.7048 | 18.269 | 2014-09-10 | 19029 | 31.3 | 27.1
38 | 2014-09-21 | 2410.991 | 15.4762 | 14.6787 | 2014-09-15 | 17175 | 31.4 | 25.3
39 | 2014-09-28 | 2451.541 | 17.6095 | 14.6461 | 2014-09-25 | 17483 | 22.7 | 24.4
40 | 2014-10-05 | 2458.11 | 15.6 | 15.4244 | 2014-09-29 | 18241 | 17.8 | 23.9
41 | 2014-10-12 | 2407.026 | 10.8429 | 11.5271 | 2014-10-09 | 17491 | 20.9 | 6.4
42 | 2014-10-19 | 2414.227 | 13.6714 | 10.6226 | 2014-10-14 | 17763 | 23.9 | 9.8 | Thanksgiving Day
43 | 2014-10-26 | 2455.435 | 10.5667 | 9.2086 | 2014-10-20 | 17679 | 13.9 | 8.5
44 | 2014-11-02 | 2513.511 | 6.4143 | 6.506 | 2014-10-30 | 17784 | 22.1 | 4.9
45 | 2014-11-09 | 2558.203 | 6.1619 | 7.1875 | 2014-11-06 | 18293 | 11.8 | 6.3
46 | 2014-11-16 | 2649.283 | 4.2238 | 6.3202 | 2014-11-13 | 19142 | 9.1 | 1
47 | 2014-11-23 | 2816.888 | -3.4048 | 3.1232 | 2014-11-19 | 20102 | 13.7 | 0
48 | 2014-11-30 | 2771.427 | 2.7714 | 1.6381 | 2014-11-28 | 19947 | 16.5 | -0.3
49 | 2014-12-07 | 3278.741 | -0.72381 | 2.1229 | 2014-12-02 | 20938 | 0.8 | -4
50 | 2014-12-14 | 2855.009 | 0.39048 | -0.78274 | 2014-12-08 | 20319 | 1.3 | -4.8
51 | 2014-12-21 | 2412.558 | 0.33333 | -2.2914 | 2014-12-18 | 20063 | -1.2 | -2.2
52 | 2014-12-28 | 2813.059 | 4.4286 | -0.92381 | 2014-12-22 | 19439 | 2.3 | -4.8 | Christmas & Boxing Day
1 | 2015-01-04 | 2299.002 | -3.0095 | -5.064 | 2015-01-03 | 19538 | -0.7 | -7.8 | New Year's Day
2 | 2015-01-11 | 3050.519 | -10.5857 | -3.4333 | 2015-01-07 | 21814 | 1.6 | -5.1
3 | 2015-01-18 | 3015.763 | -6.4905 | -4.9378 | 2015-01-13 | 21028 | 0.1 | -11.6
4 | 2015-01-25 | 2926.691 | -5.0667 | -6.425 | 2015-01-21 | 20697 | -15.7 | -13.5
5 | 2015-02-01 | 3013.676 | -7.981 | -4.7643 | 2015-01-27 | 20803 | -11.6 | -16.1
6 | 2015-02-08 | 3028.802 | -8.3238 | -3.6732 | 2015-02-02 | 20857 | -3 | -10
7 | 2015-02-15 | 3070.739 | -11.6714 | -5.3833 | 2015-02-12 | 21018 | -6.8 | -6.8
8 | 2015-02-22 | 3117.976 | -13.0905 | -3.8012 | 2015-02-19 | 21494 | -11.3 | -8.6 | Family Day
9 | 2015-03-01 | 3075.247 | -12.0143 | -3.0643 | 2015-02-23 | 21272 | -14.5 | -5.3
10 | 2015-03-08 | 2903.955 | -5.5048 | -2.431 | 2015-03-05 | 20827 | -15.8 | -7.9
11 | 2015-03-15 | 2634.129 | 3.0333 | -1.4926 | 2015-03-09 | 18627 | -15.5 | -6.4
12 | 2015-03-22 | 2634.54 | 1.0476 | 0.17482 | 2015-03-18 | 18557 | -9.6 | -0.1
13 | 2015-03-29 | 2705.234 | -1.5143 | 3.1009 | 2015-03-23 | 19345 | 5.4 | -1.9
14 | 2015-04-05 | 2503.881 | 4.6714 | 3.9729 | 2015-03-30 | 18102 | 2 | 4.1 | Good Friday & Easter Sunday
15 | 2015-04-12 | 2542.408 | 6.8667 | 6.1494 | 2015-04-08 | 18462 | -2.9 | 0 | Easter Monday
16 | 2015-04-19 | 2325.347 | 12.8905 | 4.7583 | 2015-04-16 | 16688 | 6.9 | 0.8
17 | 2015-04-26 | 2429.933 | 6.4 | 7.5583 | 2015-04-23 | 17495 | 2.4 | 6.2
18 | 2015-05-03 | 2308.878 | 14.7286 | 10.6321 | 2015-04-27 | 16269 | 14.9 | 10.9
19 | 2015-05-10 | 2407.247 | 18.5333 | 14.7881 | 2015-05-08 | 16726 | 2.8 | 30.4
20 | 2015-05-17 | 2345.394 | 15.181 | 12.672 | 2015-05-11 | 17107 | 12.1 | 10.3
21 | 2015-05-24 | 2294.53 | 16.1762 | 15.5881 | 2015-05-18 | 16428 | 24.1 | 27 | Victoria Day
22 | 2015-05-31 | 2557.594 | 21.2905 | 13.6643 | 2015-05-26 | 19158 | 19.2 | 29.4
23 | 2015-06-07 | 2363.347 | 15.8952 | 16.8333 | 2015-06-05 | 17285 | 28.2 | 25
24 | 2015-06-14 | 2487.596 | 19.8905 | 17.6929 | 2015-06-10 | 18099 | 28.8 | 22.9
25 | 2015-06-21 | 2548.449 | 20.7619 | 20.7536 | 2015-06-15 | 18951 | 24.3 | 30.7
26 | 2015-06-28 | 2520.395 | 19.4143 | 18.7821 | 2015-06-22 | 19339 | 27.6 | 29.5
27 | 2015-07-05 | 2381.894 | 19.6 | 21.0045 | 2015-07-05 | 17329 | 24.1 | 31.6 | Canada Day
28 | 2015-07-12 | 2667.354 | 22.2762 | 22.2089 | 2015-07-06 | 19929 | 25.5 | 31.3
29 | 2015-07-19 | 2740.71 | 22.7905 | 21.3923 | 2015-07-13 | 20811 | 25.6 | 30.5
30 | 2015-07-26 | 2772.088 | 23.7429 | 23.0952 | 2015-07-20 | 20259 | 26.6 | 30.2
31 | 2015-08-02 | 2965.159 | 25.6143 | 22.3661 | 2015-07-28 | 22516 | 28.1 | 30.9
32 | 2015-08-09 | 2537.254 | 21.081 | 21.5214 | 2015-08-04 | 18189 | 28 | 30.3 | Civic Holiday
33 | 2015-08-16 | 2731.833 | 22.8476 | 21.5494 | 2015-08-16 | 20639 | 32.5 | 32.1
34 | 2015-08-23 | 2842.468 | 23.1333 | 21.1952 | 2015-08-17 | 22383 | 25.8 | 28.8
35 | 2015-08-30 | 2541.482 | 19.3762 | 19.9125 | 2015-08-30 | 18105 | 30.4 | 26.6
36 | 2015-09-06 | 3004.277 | 25.8 | 20.1685 | 2015-09-02 | 22063 | 32.1 | 29.5
37 | 2015-09-13 | 2692.002 | 20.5619 | 18.269 | 2015-09-08 | 21923 | 25.4 | 27.1 | Labour Day
38 | 2015-09-20 | 2566.432 | 20.8571 | 14.6787 | 2015-09-17 | 20010 | 32.6 | 25.3
39 | 2015-09-27 | 2435.821 | 17.6476 | 14.6461 | 2015-09-23 | 17809 | 28.7 | 24.4
40 | 2015-10-04 | 2415.258 | 13.7714 | 15.4244 | 2015-09-28 | 18073 | 27.2 | 23.9
41 | 2015-10-11 | 2388.608 | 14.2333 | 11.5271 | 2015-10-05 | 17301 | 24.2 | 6.4
42 | 2015-10-18 | 2374.39 | 9.8905 | 10.6226 | 2015-10-15 | 17022 | 21.7 | 9.8 | Thanksgiving Day
43 | 2015-10-25 | 2444.19 | 11.0286 | 9.2086 | 2015-10-22 | 17164 | 14.2 | 8.5
44 | 2015-11-01 | 2477.532 | 8.6429 | 6.506 | 2015-10-28 | 17667 | 17.6 | 4.9
45 | 2015-11-08 | 2402.246 | 11.919 | 7.1875 | 2015-11-03 | 17401 | 15.9 | 6.3
46 | 2015-11-15 | 2471.455 | 7.5571 | 6.3202 | 2015-11-10 | 17956 | 13.1 | 1
47 | 2015-11-22 | 2480.863 | 6.7762 | 3.1232 | 2015-11-17 | 17919 | 20.6 | 0
48 | 2015-11-29 | 2613.319 | 4.0429 | 1.6381 | 2015-11-23 | 19239 | 9.2 | -0.3
49 | 2015-12-06 | 2254.779 | 4.0333 | 2.1229 | 2015-12-01 | 19161 | 7.6 | -4
50 | 2015-12-13 | 2964.295 | 6.6667 | -0.78274 | 2015-12-07 | 19064 | 1.9 | -4.8
51 | 2015-12-20 | 2626.766 | 3.8429 | -2.2914 | 2015-12-15 | 18909 | 6.8 | -2.2
52 | 2015-12-27 | 2383.739 | 7.0238 | -0.92381 | 2015-12-21 | 18527 | 5.4 | -4.8 | Christmas & Boxing Day
53 | 2016-01-03 | 2536.227 | -0.48095 | -3.3235 | 2016-01-03 | 18512 | 8.6 | -7.8 | New Year's Day
1 | 2016-01-10 | 2792.544 | -1.4333 | -5.064 | 2016-01-04 | 20836 | 6.6 | -7.8
2 | 2016-01-17 | 2880.244 | -4.2095 | -3.4333 | 2016-01-11 | 20494 | 1.6 | -5.1
3 | 2016-01-24 | 2913.832 | -6.3286 | -4.9378 | 2016-01-19 | 20660 | -11.8 | -11.6
4 | 2016-01-31 | 2737.114 | 1.0238 | -6.425 | 2016-01-29 | 19439 | -6.6 | -13.5
5 | 2016-02-07 | 2658.074 | 2.9048 | -4.7643 | 2016-02-04 | 18818 | -4.3 | -16.1
6 | 2016-02-14 | 2926.304 | -8.2524 | -3.6732 | 2016-02-11 | 20766 | -5.1 | -10
7 | 2016-02-21 | 2771.124 | -0.43333 | -5.3833 | 2016-02-17 | 19863 | 2.9 | -6.8 | Family Day
8 | 2016-02-28 | 2729.417 | 0.31905 | -3.8012 | 2016-02-24 | 19675 | -10 | -8.6
9 | 2016-03-06 | 2775.399 | -3.5571 | -3.0643 | 2016-03-01 | 20063 | -1.4 | -5.3
10 | 2016-03-13 | 2477.737 | 8.8381 | -2.431 | 2016-03-10 | 17715 | 1.7 | -7.9
11 | 2016-03-20 | 2490.349 | 4.8952 | -1.4926 | 2016-03-15 | 17267 | -7.9 | -6.4
12 | 2016-03-27 | 2512.792 | 1.9524 | 0.17482 | 2016-03-21 | 18168 | 10.2 | -0.1 | Good Friday & Easter Sunday
13 | 2016-04-03 | 2474.205 | 5.0333 | 3.1009 | 2016-03-29 | 17381 | 9.3 | -1.9 | Easter Monday
14 | 2016-04-10 | 2600.996 | -0.86667 | 3.9729 | 2016-04-05 | 17821 | 3.5 | 4.1
15 | 2016-04-17 | 2422.258 | 8.0048 | 6.1494 | 2016-04-12 | 17743 | 7.2 | 0
16 | 2016-04-24 | 2301.342 | 11.7 | 4.7583 | 2016-04-19 | 16283 | 0.6 | 0.8
17 | 2016-05-01 | 2362.053 | 7.1381 | 7.5583 | 2016-04-25 | 16774 | 6.7 | 6.2
18 | 2016-05-08 | 2269.902 | 12 | 10.6321 | 2016-05-02 | 16116 | 15.8 | 10.9
19 | 2016-05-15 | 2263.831 | 12.219 | 14.7881 | 2016-05-12 | 15884 | 7.4 | 30.4
20 | 2016-05-22 | 2247.594 | 14.8667 | 12.672 | 2016-05-19 | 15949 | 12 | 10.3
21 | 2016-05-29 | 2578.516 | 23.9762 | 15.5881 | 2016-05-27 | 19681 | 20.5 | 27 | Victoria Day
22 | 2016-06-05 | 2598.813 | 21.6619 | 13.6643 | 2016-05-30 | 19885 | 19.7 | 29.4
23 | 2016-06-12 | 2370.344 | 17.9857 | 16.8333 | 2016-06-11 | 17454 | 28.9 | 25
24 | 2016-06-19 | 2588.049 | 21.9857 | 17.6929 | 2016-06-19 | 20038 | 27.2 | 22.9
25 | 2016-06-26 | 2742.731 | 23.8762 | 20.7536 | 2016-06-20 | 21692 | 30.2 | 30.7
26 | 2016-07-03 | 2562.398 | 22.3667 | 18.7821 | 2016-06-27 | 21582 | 32.1 | 29.5 | Canada Day
27 | 2016-07-10 | 2865.948 | 25.3 | 21.0045 | 2016-07-07 | 21368 | 34 | 31.6
28 | 2016-07-17 | 2830.064 | 24.7 | 22.2089 | 2016-07-13 | 22659 | 32.5 | 31.3
29 | 2016-07-24 | 2932.038 | 26.1476 | 21.3923 | 2016-07-22 | 22024 | 30.9 | 30.5
30 | 2016-07-31 | 2902.313 | 25.7333 | 23.0952 | 2016-07-27 | 21732 | 35 | 30.2
31 | 2016-08-07 | 2949.677 | 25.9571 | 22.3661 | 2016-08-04 | 22312 | 35.1 | 30.9 | Civic Holiday
32 | 2016-08-14 | 3106.524 | 27.3571 | 21.5214 | 2016-08-10 | 23100 | 33.7 | 30.3
33 | 2016-08-21 | 2932.132 | 24.2952 | 21.5494 | 2016-08-19 | 21614 | 31.9 | 32.1
34 | 2016-08-28 | 2850.898 | 24.3524 | 21.1952 | 2016-08-25 | 21590 | 34.8 | 28.8
35 | 2016-09-04 | 2650.752 | 21.9714 | 19.9125 | 2016-08-30 | 21373 | 29.3 | 26.6
36 | 2016-09-11 | 2882.216 | 25.2 | 20.1685 | 2016-09-07 | 23213 | 29.7 | 29.5 | Labour Day
37 | 2016-09-18 | 2525.202 | 20.2476 | 18.269 | 2016-09-13 | 19053 | 30.1 | 27.1
38 | 2016-09-25 | 2558.038 | 19.9476 | 14.6787 | 2016-09-19 | 19841 | 34.5 | 25.3
39 | 2016-10-02 | 2373.646 | 16.3238 | 14.6461 | 2016-09-27 | 16973 | 27.8 | 24.4
40 | 2016-10-09 | 2365.531 | 16.3762 | 15.4244 | 2016-10-06 | 17374 | 25.6 | 23.9
41 | 2016-10-16 | 2304.077 | 13.8333 | 11.5271 | 2016-10-11 | 16869 | 21.8 | 6.4 | Thanksgiving Day
42 | 2016-10-23 | 2380.85 | 13.9857 | 10.6226 | 2016-10-18 | 17412 | 23 | 9.8
43 | 2016-10-30 | 2467.506 | 7.2143 | 9.2086 | 2016-10-27 | 18189 | 16.5 | 8.5
44 | 2016-11-06 | 2410.534 | 10.1714 | 6.506 | 2016-11-02 | 17213 | 25.2 | 4.9
45 | 2016-11-13 | 2402.827 | 7.9476 | 7.1875 | 2016-11-09 | 17594 | 5.2 | 6.3
46 | 2016-11-20 | 2467.722 | 7.9143 | 6.3202 | 2016-11-20 | 17934 | 18 | 1
47 | 2016-11-27 | 2660.769 | 2.5286 | 3.1232 | 2016-11-23 | 19369 | 6.7 | 0
48 | 2016-12-04 | 2566.594 | 5.7238 | 1.6381 | 2016-11-28 | 18309 | 1.4 | -0.3
49 | 2016-12-10 | 2331.958 | -0.48095 | 2.1229 | 2016-12-09 | 19365 | 0.2 | -4
50 | 2016-12-18 | 2874.569 | -5.081 | -0.78274 | 2016-12-15 | 20688 | 7 | -4.8
51 | 2016-12-25 | 3501.955 | -1.5857 | -2.2914 | 2016-12-19 | 20682 | -1.4 | -2.2 | Christmas & Boxing Day
52 | 2017-01-01 | 2150.732 | 0.15714 | -0.92381 | 2016-12-28 | 18156 | -8.1 | -4.8 | New Year's Day
1 | 2017-01-08 | 2777.92 | -5.0571 | -5.064 | 2017-01-05 | 20090 | -7.8 | -7.8
2 | 2017-01-15 | 2794.716 | -1.5571 | -3.4333 | 2017-01-09 | 20372 | -1.8 | -5.1
3 | 2017-01-22 | 2689.899 | 2.3524 | -4.9378 | 2017-01-17 | 19370 | -6.6 | -11.6
4 | 2017-01-29 | 2683.895 | 0.59524 | -6.425 | 2017-01-24 | 18757 | -3.3 | -13.5
5 | 2017-02-05 | 2803.933 | -3.9333 | -4.7643 | 2017-01-30 | 19777 | 1.7 | -16.1
6 | 2017-02-12 | 2795.476 | -2.3667 | -3.6732 | 2017-02-07 | 19838 | 1.2 | -10
7 | 2017-02-19 | 2625.733 | 0.45714 | -5.3833 | 2017-02-16 | 19171 | -4.9 | -6.8
8 | 2017-02-26 | 2473.63 | 4.5333 | -3.8012 | 2017-02-21 | 17951 | -1.1 | -8.6 | Family Day
9 | 2017-03-05 | 2629.416 | -0.2381 | -3.0643 | 2017-03-02 | 18873 | -3.7 | -5.3
10 | 2017-03-12 | 2632.614 | -0.27619 | -2.431 | 2017-03-10 | 18803 | 5.5 | -7.9
11 | 2017-03-19 | 2686.46 | -2.681 | -1.4926 | 2017-03-14 | 19174 | -2.8 | -6.4
12 | 2017-03-26 | 2558.542 | 2.8857 | 0.17482 | 2017-03-22 | 18572 | -4.6 | -0.1
13 | 2017-04-02 | 2460.921 | 6.7571 | 3.1009 | 2017-03-30 | 17406 | -8.1 | -1.9
14 | 2017-04-09 | 2382.702 | 8.2048 | 3.9729 | 2017-04-06 | 17349 | -2.5 | 4.1
15 | 2017-04-16 | 2216.706 | 13.0762 | 6.1494 | 2017-04-12 | 16542 | 2.9 | 0 | Good Friday & Easter Sunday
16 | 2017-04-23 | 2294.285 | 10.0524 | 4.7583 | 2017-04-20 | 16607 | 7.3 | 0.8 | Easter Monday
17 | 2017-04-30 | 2253.631 | 11.581 | 7.5583 | 2017-04-25 | 16009 | 7.7 | 6.2
18 | 2017-05-07 | 2324.284 | 8.681 | 10.6321 | 2017-05-04 | 16392 | 5.4 | 10.9
19 | 2017-05-14 | 2279.793 | 10.1619 | 14.7881 | 2017-05-08 | 16112 | 9.3 | 30.4
20 | 2017-05-21 | 2277.058 | 16.3476 | 12.672 | 2017-05-18 | 17738 | 10 | 10.3
21 | 2017-05-28 | 2252.97 | 16.0667 | 15.5881 | 2017-05-25 | 16082 | 11.1 | 27 | Victoria Day
22 | 2017-06-04 | 2279.188 | 17.7857 | 13.6643 | 2017-05-29 | 16357 | 29.6 | 29.4
23 | 2017-06-11 | 2395.841 | 19.9714 | 16.8333 | 2017-06-11 | 19062 | 11.9 | 25
24 | 2017-06-18 | 2712.194 | 23.5667 | 17.6929 | 2017-06-12 | 21168 | 25.1 | 22.9
25 | 2017-06-25 | 2514.67 | 20.7524 | 20.7536 | 2017-06-19 | 18770 | 31.6 | 30.7
26 | 2017-07-02 | 2435.833 | 21.2333 | 18.7821 | 2017-06-30 | 18201 | 32.4 | 29.5
27 | 2017-07-09 | 2571.988 | 22.919 | 21.0045 | 2017-07-06 | 20366 | 25.8 | 31.6 | Canada Day
28 | 2017-07-16 | 2649.49 | 22.4524 | 22.2089 | 2017-07-11 | 20302 | 27.9 | 31.3
29 | 2017-07-23 | 2756.04 | 23.7905 | 21.3923 | 2017-07-19 | 20627 | 29.6 | 30.5
30 | 2017-07-30 | 2536.064 | 21.8524 | 23.0952 | 2017-07-27 | 19070 | 28.9 | 30.2
31 | 2017-08-06 | 2679.34 | 22.7905 | 22.3661 | 2017-07-31 | 20096 | 31.5 | 30.9
32 | 2017-08-13 | 2552.589 | 22.0524 | 21.5214 | 2017-08-10 | 19409 | 25.8 | 30.3 | Civic Holiday
33 | 2017-08-20 | 2627.517 | 22.0619 | 21.5494 | 2017-08-14 | 19317 | 30.8 | 32.1
34 | 2017-08-27 | 2479.98 | 19.8762 | 21.1952 | 2017-08-21 | 20158 | 26.7 | 28.8
35 | 2017-09-03 | 2337.4 | 17.7238 | 19.9125 | 2017-08-30 | 17858 | 25.7 | 26.6
36 | 2017-09-10 | 2247.134 | 16.6667 | 20.1685 | 2017-09-05 | 16406 | 30 | 29.5 | Labour Day
37 | 2017-09-17 | 2482.817 | 21.0095 | 18.269 | 2017-09-14 | 18473 | 23.9 | 27.1
38 | 2017-09-24 | 2768.227 | 24.2905 | 14.6787 | 2017-09-24 | 20457 | 21 | 25.3
39 | 2017-10-01 | 2569.129 | 18.5667 | 14.6461 | 2017-09-25 | 21786 | 27 | 24.4
40 | 2017-10-08 | 2376.245 | 19.4905 | 15.4244 | 2017-10-04 | 17418 | 33.3 | 23.9
41 | 2017-10-15 | 2329.751 | 15.8048 | 11.5271 | 2017-10-10 | 16746 | 31.3 | 6.4 | Thanksgiving Day
42 | 2017-10-22 | 2273.817 | 15.0333 | 10.6226 | 2017-10-16 | 16838 | 26.5 | 9.8
43 | 2017-10-29 | 2353.734 | 10.3095 | 9.2086 | 2017-10-26 | 16821 | 22.9 | 8.5
44 | 2017-11-05 | 2440.607 | 8.081 | 6.506 | 2017-11-01 | 17545 | 10.1 | 4.9
45 | 2017-11-12 | 2560.269 | 2.3333 | 7.1875 | 2017-11-10 | 18565 | 10.6 | 6.3 | Remembrance Day
46 | 2017-11-19 | 2588.331 | 4.0905 | 6.3202 | 2017-11-13 | 18696 | 6.7 | 1
47 | 2017-11-26 | 2575.255 | 4.1286 | 3.1232 | 2017-11-22 | 19092 | -4 | 0
48 | 2017-12-03 | 2935.407 | 4.6762 | 1.6381 | 2017-11-27 | 19115 | 5.3 | -0.3
49 | 2017-12-10 | 2303.412 | 1.1714 | 2.1229 | 2017-12-07 | 19094 | 0.1 | -4
50 | 2017-12-17 | 3354.162 | -7.419 | -0.78274 | 2017-12-11 | 20306 | 3 | -4.8
51 | 2017-12-24 | 2781.89 | -1.4714 | -2.2914 | 2017-12-18 | 19743 | 0.1 | -2.2
52 | 2017-12-31 | 2459.002 | -12.5476 | -0.92381 | 2017-12-28 | 20008 | -4.1 | -4.8 | Christmas & Boxing Day
1 | 2018-01-07 | 3031.584 | -13.0476 | -5.064 | 2018-01-05 | 20906 | 2.7 | -7.8 | New Year's Day
2 | 2018-01-14 | 2829.532 | -1.9143 | -3.4333 | 2018-01-14 | 19958 | -12.8 | -5.1
3 | 2018-01-21 | 2845.418 | -3.4571 | -4.9378 | 2018-01-15 | 20073 | -15.2 | -11.6
4 | 2018-01-28 | 2746.391 | 0.21905 | -6.425 | 2018-01-25 | 19999 | -6.7 | -13.5
5 | 2018-02-04 | 2858.867 | -5.0286 | -4.7643 | 2018-01-30 | 20202 | -7.3 | -16.1
6 | 2018-02-11 | 2914.425 | -6.9 | -3.6732 | 2018-02-05 | 20076 | -3.8 | -10
7 | 2018-02-18 | 2717.653 | -0.79524 | -5.3833 | 2018-02-13 | 19558 | -8.3 | -6.8
8 | 2018-02-25 | 2619.737 | 4.1095 | -3.8012 | 2018-02-21 | 18657 | -8.2 | -8.6 | Family Day
9 | 2018-03-04 | 2533.369 | 3.9667 | -3.0643 | 2018-03-02 | 17920 | -4.1 | -5.3
10 | 2018-03-11 | 2642.789 | -0.085714 | -2.431 | 2018-03-06 | 18462 | 3.6 | -7.9
11 | 2018-03-18 | 2608.358 | -0.17143 | -1.4926 | 2018-03-14 | 18131 | 2.8 | -6.4
12 | 2018-03-25 | 2558.427 | -0.24286 | 0.17482 | 2018-03-20 | 18052 | 0.2 | -0.1
13 | 2018-04-01 | 2447.122 | 3.9333 | 3.1009 | 2018-03-27 | 17482 | 1 | -1.9 | Good Friday & Easter Sunday
14 | 2018-04-08 | 2564.702 | 0.69048 | 3.9729 | 2018-04-04 | 18011 | 2.6 | 4.1 | Easter Monday
15 | 2018-04-15 | 2575.601 | 2.1762 | 6.1494 | 2018-04-09 | 17570 | 3 | 0
16 | 2018-04-22 | 2470.15 | 4.2286 | 4.7583 | 2018-04-17 | 17589 | 2.4 | 0.8
17 | 2018-04-29 | 2310.968 | 9.6381 | 7.5583 | 2018-04-25 | 16175 | 2.9 | 6.2
18 | 2018-05-06 | 2233.726 | 17.6238 | 10.6321 | 2018-05-02 | 16264 | 0.7 | 10.9
19 | 2018-05-13 | 2241.384 | 13.9381 | 14.7881 | 2018-05-08 | 15933 | 11 | 30.4
20 | 2018-05-20 | 2262.58 | 16.8667 | 12.672 | 2018-05-16 | 16167 | 27.5 | 10.3
21 | 2018-05-27 | 2378.627 | 20.5714 | 15.5881 | 2018-05-25 | 17985 | 18.5 | 27 | Victoria Day
22 | 2018-06-03 | 2694.234 | 23.0476 | 13.6643 | 2018-05-28 | 20473 | 19.5 | 29.4
23 | 2018-06-10 | 2327.884 | 17.3524 | 16.8333 | 2018-06-08 | 16734 | 30.2 | 25
24 | 2018-06-17 | 2574.106 | 22.3571 | 17.6929 | 2018-06-17 | 20154 | 30.7 | 22.9
25 | 2018-06-24 | 2597.14 | 20.6095 | 20.7536 | 2018-06-18 | 21369 | 21.9 | 30.7
26 | 2018-07-01 | 2798.736 | 24.5 | 18.7821 | 2018-06-29 | 21158 | 31.3 | 29.5
27 | 2018-07-08 | 2903.887 | 25.5048 | 21.0045 | 2018-07-05 | 23046 | 30.2 | 31.6 | Canada Day
28 | 2018-07-15 | 2950.892 | 25.5905 | 22.2089 | 2018-07-15 | 21508 | 31 | 31.3
29 | 2018-07-22 | 2796.117 | 23.5857 | 21.3923 | 2018-07-16 | 21536 | 33.2 | 30.5
30 | 2018-07-29 | 2794.197 | 23.5524 | 23.0952 | 2018-07-24 | 21451 | 29.9 | 30.2
31 | 2018-08-05 | 2896.119 | 25.219 | 22.3661 | 2018-08-05 | 21090 | 31.5 | 30.9
32 | 2018-08-12 | 2879.731 | 24.3524 | 21.5214 | 2018-08-09 | 21143 | 29.5 | 30.3 | Civic Holiday
33 | 2018-08-19 | 2941.831 | 24.6095 | 21.5494 | 2018-08-14 | 21361 | 34.3 | 32.1
34 | 2018-08-26 | 2693.222 | 22.6238 | 21.1952 | 2018-08-20 | 19897 | 29.3 | 28.8
35 | 2018-09-02 | 2860.953 | 23.8286 | 19.9125 | 2018-08-28 | 21990 | 30.8 | 26.6
36 | 2018-09-09 | 2757.129 | 22.0048 | 20.1685 | 2018-09-05 | 23240 | 25 | 29.5 | Labour Day
37 | 2018-09-16 | 2677.817 | 21.0952 | 18.269 | 2018-09-14 | 20846 | 31.7 | 27.1
38 | 2018-09-23 | 2567.153 | 19.4524 | 14.6787 | 2018-09-17 | 21102 | 33.9 | 25.3
39 | 2018-09-30 | 2366.462 | 15.619 | 14.6461 | 2018-09-25 | 17269 | 27.2 | 24.4
40 | 2018-10-07 | 2377.937 | 12.7381 | 15.4244 | 2018-10-02 | 16772 | 26.3 | 23.9
41 | 2018-10-14 | 2374.29 | 14.7 | 11.5271 | 2018-10-10 | 18205 | 20.4 | 6.4 | Thanksgiving Day
42 | 2018-10-21 | 2380.993 | 7.7714 | 10.6226 | 2018-10-17 | 17032 | 12.9 | 9.8
43 | 2018-10-28 | 2500.217 | 5.3143 | 9.2086 | 2018-10-24 | 17557 | 26.1 | 8.5
44 | 2018-11-04 | 2491.389 | 6.3857 | 6.506 | 2018-10-29 | 17370 | 8.5 | 4.9
45 | 2018-11-11 | 2542.85 | 5.1952 | 7.1875 | 2018-11-09 | 18310 | 5.2 | 6.3 | Remembrance Day
46 | 2018-11-18 | 2693.859 | 0.41905 | 6.3202 | 2018-11-14 | 19229 | 8.5 | 1
47 | 2018-11-25 | 2728.944 | -0.68095 | 3.1232 | 2018-11-22 | 20152 | 2.6 | 0
48 | 2018-12-02 | 2708.445 | 2.5476 | 1.6381 | 2018-11-27 | 19291 | 0.3 | -0.3
49 | 2018-12-07 | 2016.529 | -1.8905 | 2.1229 | 2018-12-07 | 19648 | -6.6 | -4
50 | 2018-12-16 | 3207.691 | 1.019 | -0.78274 | 2018-12-11 | 19891 | 1.2 | -4.8
51 | 2018-12-23 | 2721.963 | 1.019 | -2.2914 | 2018-12-17 | 19337 | -4 | -2.2
52 | 2018-12-30 | 2910.787 | 0.34286 | -0.92381 | 2018-12-27 | 18238 | -1.4 | -4.8 | Christmas & Boxing Day
1 | 2019-01-06 | 2608.875 | 0.071429 | -5.064 | 2019-01-02 | 19666 | 2.6 | -7.8 | New Year's Day
2 | 2019-01-13 | 2822.458 | -4.2524 | -3.4333 | 2019-01-10 | 20012 | -0.2 | -5.1
3 | 2019-01-20 | 2942.953 | -6.981 | -4.9378 | 2019-01-20 | 20879 | -3.9 | -11.6
4 | 2019-01-27 | 2978.414 | -7.0667 | -6.425 | 2019-01-21 | 21525 | -5.1 | -13.5
5 | 2019-02-03 | 3016.473 | -9.4762 | -4.7643 | 2019-01-28 | 21049 | -14.5 | -16.1
6 | 2019-02-10 | 2809.153 | -1.5571 | -3.6732 | 2019-02-06 | 19661 | -11.8 | -10
7 | 2019-02-17 | 2812.046 | -3.4714 | -5.3833 | 2019-02-12 | 19849 | -8.3 | -6.8
8 | 2019-02-24 | 2753.083 | -2.0905 | -3.8012 | 2019-02-19 | 19758 | -1.1 | -8.6 | Family Day
9 | 2019-03-03 | 2852.174 | -6.5167 | -3.0643 | 2019-02-27 | 20378 | -1.2 | -5.3
10 | 2019-03-10 | 2819.883 | -6.8929 | -2.431 | 2019-03-05 | 20263 | -4.4 | -7.9
11 | 2019-03-17 | 2597.645 | 1.8333 | -1.4926 | 2019-03-11 | 18295 | -7.7 | -6.4
12 | 2019-03-24 | 2553.127 | 3.1619 | 0.17482 | 2019-03-18 | 17951 | -9 | -0.1
13 | 2019-03-31 | 2521.743 | 3.3833 | 3.1009 | 2019-03-26 | 17592 | 2 | -1.9
14 | 2019-04-07 | 2473.484 | 5.1238 | 3.9729 | 2019-04-01 | 17645 | 2.6 | 4.1
15 | 2019-04-14 | 2432.078 | 7.019 | 6.1494 | 2019-04-11 | 17285 | 3.6 | 0
16 | 2019-04-21 | 2331.706 | 8.5762 | 4.7583 | 2019-04-16 | 16782 | 2.8 | 0.8 | Good Friday & Easter Sunday
17 | 2019-04-28 | 2320.054 | 9.1143 | 7.5583 | 2019-04-24 | 16074 | 1.3 | 6.2 | Easter Monday
18 | 2019-05-05 | 2391.374 | 8.2857 | 10.6321 | 2019-04-29 | 16936 | 8.6 | 10.9
19 | 2019-05-12 | 2280.305 | 11.0429 | 14.7881 | 2019-05-09 | 16033 | 12.8 | 30.4
20 | 2019-05-19 | 2306.975 | 12.8381 | 12.672 | 2019-05-13 | 16510 | 6.9 | 10.3
21 | 2019-05-26 | 2251.159 | 16.2048 | 15.5881 | 2019-05-22 | 15933 | 14.4 | 27 | Victoria Day
22 | 2019-06-02 | 2310.735 | 15.5857 | 13.6643 | 2019-05-27 | 15960 | 7.2 | 29.4
23 | 2019-06-09 | 2316.946 | 17.6571 | 16.8333 | 2019-06-07 | 16369 | 15.1 | 25
24 | 2019-06-16 | 2308.383 | 17.2286 | 17.6929 | 2019-06-10 | 16253 | 22.5 | 22.9
25 | 2019-06-23 | 2428.772 | 20.3857 | 20.7536 | 2019-06-19 | 17896 | 25.8 | 30.7
26 | 2019-06-30 | 2697.713 | 23.6095 | 18.7821 | 2019-06-27 | 20248 | 18.4 | 29.5
27 | 2019-07-07 | 2876.6 | 24.8952 | 21.0045 | 2019-07-05 | 21716 | 24.8 | 31.6 | Canada Day
28 | 2019-07-14 | 2768.034 | 23.5 | 22.2089 | 2019-07-10 | 21083 | 28.9 | 31.3
29 | 2019-07-21 | 3021.144 | 25.9286 | 21.3923 | 2019-07-20 | 21645 | 30.2 | 30.5
30 | 2019-07-28 | 2832.185 | 23.9476 | 23.0952 | 2019-07-28 | 21027 | 28.9 | 30.2
31 | 2019-08-04 | 2830.288 | 24.0619 | 22.3661 | 2019-07-29 | 21791 | 32.4 | 30.9
32 | 2019-08-11 | 2678.516 | 23.3524 | 21.5214 | 2019-08-07 | 21033 | 30.5 | 30.3 | Civic Holiday
33 | 2019-08-18 | 2761.275 | 23.0143 | 21.5494 | 2019-08-13 | 21000 | 31.4 | 32.1
34 | 2019-08-25 | 2667.342 | 21.9238 | 21.1952 | 2019-08-21 | 21354 | 27.7 | 28.8
35 | 2019-09-01 | 2496.654 | 20.3524 | 19.9125 | 2019-08-28 | 18748 | 28.1 | 26.6
36 | 2019-09-08 | 2384.701 | 18.1714 | 20.1685 | 2019-09-03 | 17642 | 30.2 | 29.5 | Labour Day
37 | 2019-09-15 | 2424.083 | 18.5333 | 18.269 | 2019-09-11 | 19717 | 26.9 | 27.1
38 | 2019-09-22 | 2463.975 | 20.481 | 14.6787 | 2019-09-22 | 18803 | 22 | 25.3
39 | 2019-09-29 | 2394.766 | 18.4524 | 14.6461 | 2019-09-23 | 17806 | 28.6 | 24.4
40 | 2019-10-06 | 2360.265 | 14.5905 | 15.4244 | 2019-10-01 | 18329 | 30.7 | 23.9
41 | 2019-10-13 | 2274.016 | 13.2667 | 11.5271 | 2019-10-07 | 16354 | 24.3 | 6.4
42 | 2019-10-20 | 2318.937 | 9.5905 | 10.6226 | 2019-10-17 | 16784 | 31.2 | 9.8 | Thanksgiving Day
43 | 2019-10-27 | 2335.461 | 11.1619 | 9.2086 | 2019-10-24 | 16518 | 17.7 | 8.5
44 | 2019-11-03 | 2432.839 | 7.4762 | 6.506 | 2019-11-01 | 17041 | 8.5 | 4.9
45 | 2019-11-10 | 2547.668 | 3.1095 | 7.1875 | 2019-11-07 | 18156 | 13.4 | 6.3
46 | 2019-11-17 | 2769.385 | -3.3333 | 6.3202 | 2019-11-13 | 19625 | 4.6 | 1 | Remembrance Day
47 | 2019-11-24 | 2634.991 | 2.9548 | 3.1232 | 2019-11-18 | 18982 | 2.4 | 0
48 | 2019-12-01 | 2656.333 | 2.2167 | 1.6381 | 2019-12-01 | 19160 | -4.1 | -0.3
49 | 2019-12-08 | 2780.29 | -0.61905 | 2.1229 | 2019-12-02 | 19551 | 2.1 | -4
50 | 2019-12-15 | 2792.675 | 0.02381 | -0.78274 | 2019-12-11 | 20297 | -1.3 | -4.8
51 | 2019-12-22 | 3230.225 | -3.519 | -2.2914 | 2019-12-19 | 20974 | -1.1 | -2.2
52 | 2019-12-29 | 2093.963 | 2.5952 | -0.92381 | 2019-12-29 | 17397 | -3 | -4.8 | Christmas & Boxing Day
1 | 2020-01-05 | 2505.795 | 2.1143 | -5.064 | 2020-01-05 | 17885 | -7.8 | -7.8 | New Year's Day
2 | 2020-01-12 | 2749.745 | 0.07619 | -3.4333 | 2020-01-08 | 19786 | 1.8 | -5.1
3 | 2020-01-19 | 2837.373 | -2.1476 | -4.9378 | 2020-01-17 | 19928 | 0.9 | -11.6
4 | 2020-01-26 | 2775.184 | -1.3429 | -6.425 | 2020-01-20 | 19756 | -4.5 | -13.5
5 | 2020-02-02 | 2766.715 | -1.3857 | -4.7643 | 2020-01-29 | 19340 | -8.5 | -16.1
6 | 2020-02-09 | 2782.854 | -3.2333 | -3.6732 | 2020-02-07 | 19435 | -5.3 | -10
7 | 2020-02-16 | 2752.901 | -2.7 | -5.3833 | 2020-02-14 | 19630 | -2.9 | -6.8
8 | 2020-02-23 | 2633.308 | -0.86667 | -3.8012 | 2020-02-20 | 19610 | -4.5 | -8.6 | Family Day
9 | 2020-03-01 | 2693.671 | -1.5714 | -3.0643 | 2020-02-27 | 19013 | -10.4 | -5.3
10 | 2020-03-08 | 2575.785 | 3.1667 | -2.431 | 2020-03-04 | 18183 | -4.7 | -7.9
11 | 2020-03-15 | 2500.999 | 4.9238 | -1.4926 | 2020-03-11 | 17632 | -3.8 | -6.4
12 | 2020-03-22 | 2505.867 | 2.5286 | 0.17482 | 2020-03-16 | 17400 | 5.4 | -0.1 | Schools are closed
13 | 2020-03-29 | 2367.945 | 6.3619 | 3.1009 | 2020-03-23 | 16975 | 3.4 | -1.9 | Non-essential businesses closed
14 | 2020-04-05 | 2223.488 | 7.5476 | 3.9729 | 2020-03-30 | 15998 | 3.9 | 4.1
15 | 2020-04-12 | 2127.344 | 7.8143 | 6.1494 | 2020-04-06 | 14841 | 3.5 | 0 | Non-essential list expanded
16 | 2020-04-19 | 2212.691 | 4.5476 | 4.7583 | 2020-04-15 | 15350 | 8 | 0.8
17 | 2020-04-26 | 2171.965 | 5.4238 | 7.5583 | 2020-04-21 | 15211 | 12.8 | 6.2
18 | 2020-05-03 | 2058.721 | 12.119 | 10.6321 | 2020-04-29 | 14634 | 4.4 | 10.9
19 | 2020-05-10 | 2132.257 | 6.1286 | 14.7881 | 2020-05-08 | 14589 | 3.6 | 30.4
20 | 2020-05-17 | 2123.727 | 9.4571 | 12.672 | 2020-05-14 | 15156 | 12.8 | 10.3
21 | 2020-05-24 | 2079.372 | 17.2714 | 15.5881 | 2020-05-24 | 15586 | 4.8 | 27 | Victoria Day - Phase 1 Re-Opening
22 | 2020-05-31 | 2468.258 | 20.7524 | 13.6643 | 2020-05-26 | 20649 | 12.3 | 29.4
23 | 2020-06-07 | 2360.263 | 21.3762 | 16.8333 | 2020-06-05 | 19028 | 25.7 | 25
24 | 2020-06-14 | 2351.455 | 19.4714 | 17.6929 | 2020-06-10 | 20511 | 30.6 | 22.9 | Phase 2 Re-Opening
25 | 2020-06-21 | 2624.201 | 22.7762 | 20.7536 | 2020-06-20 | 19957 | 27.6 | 30.7
26 | 2020-06-28 | 2633.576 | 23.619 | 18.7821 | 2020-06-22 | 20632 | 31.6 | 29.5
27 | 2020-07-05 | 2925.027 | 27.2571 | 21.0045 | 2020-07-03 | 22522 | 30.4 | 31.6 | Canada Day
28 | 2020-07-12 | 3168.317 | 27.4905 | 22.2089 | 2020-07-09 | 24446 | 29.7 | 31.3
29 | 2020-07-19 | 2894.608 | 25.219 | 21.3923 | 2020-07-17 | 22400 | 32.1 | 30.5 | Phase 3 Re-Opening
30 | 2020-07-26 | 2875.256 | 24.7905 | 23.0952 | 2020-07-26 | 22887 | 34 | 30.2
31 | 2020-08-02 | 2935.557 | 25.7048 | 22.3661 | 2020-07-27 | 23909 | 30.6 | 30.9
32 | 2020-08-09 | 2596.785 | 22.0048 | 21.5214 | 2020-08-09 | 20676 | 33.3 | 30.3 | Civic Holiday
33 | 2020-08-16 | 2957.47 | 25.181 | 21.5494 | 2020-08-10 | 23823 | 31.3 | 32.1
34 | 2020-08-23 | 2673.703 | 22.9286 | 21.1952 | 2020-08-23 | 21442 | 30.4 | 28.8
35 | 2020-08-30 | 2727.104 | 22.7714 | 19.9125 | 2020-08-24 | 23415 | 31.9 | 26.6
36 | 2020-09-06 | 2508.402 | 20.7857 | 20.1685 | 2020-09-01 | 20225 | 31.3 | 29.5
37 | 2020-09-13 | 2333.656 | 17.7429 | 18.269 | 2020-09-09 | 16558 | 32.4 | 27.1 | Labour Day
38 | 2020-09-20 | 2242.571 | 14.3762 | 14.6787 | 2020-09-16 | 15952 | 27.4 | 25.3
39 | 2020-09-27 | 2351.173 | 19.3476 | 14.6461 | 2020-09-24 | 16989 | 18.2 | 24.4
40 | 2020-10-04 | 2330.766 | 13.8238 | 15.4244 | 2020-09-28 | 17949 | 24.8 | 23.9
41 | 2020-10-11 | 2257.534 | 13.3476 | 11.5271 | 2020-10-08 | 16051 | 23.8 | 6.4
42 | 2020-10-18 | 2259.606 | 12.0095 | 10.6226 | 2020-10-15 | 16513 | 25.9 | 9.8 | Thanksgiving Day
43 | 2020-10-25 | 2378.59 | 10.081 | 9.2086 | 2020-10-19 | 16947 | 16 | 8.5
44 | 2020-11-01 | 2484.905 | 5.1714 | 6.506 | 2020-10-27 | 17679 | 11.9 | 4.9
45 | 2020-11-08 | 2359.89 | 12.1667 | 7.1875 | 2020-11-02 | 18084 | 8 | 6.3
46 | 2020-11-15 | 2374.022 | 10.2643 | 6.3202 | 2020-11-13 | 17275 | 7 | 1 | Remembrance Day
47 | 2020-11-22 | 2530.144 | 4.6367 | 3.1232 | 2020-11-18 | 18776 | 4.2 | 0 | Toronto and Peel re-enter Lockdown
48 | 2020-11-29 | 2557.599 | 4.75 | 1.6381 | 2020-11-24 | 19147 | 8.7 | -0.3
49 | 2020-12-06 | 2245.754 | 0.91905 | 2.1229 | 2020-12-01 | 18946 | 0.2 | -4
50 | 2020-12-13 | 3056.093 | 2.1429 | -0.78274 | 2020-12-07 | 19389 | 0.1 | -4.8
51 | 2020-12-20 | 2790.706 | -2.3 | -2.2914 | 2020-12-16 | 20738 | -0.5 | -2.2
52 | 2020-12-27 | 2603.814 | 0.96667 | -0.92381 | 2020-12-22 | 19013 | 0.9 | -4.8 | Christmas & Boxing Day
53 | 2021-01-03 | 2571.807 | 0.17143 | -3.3235 | 2020-12-29 | 19086 | -6.8 | -7.8 | New Year's Day
1 | 2021-01-10 | 2733.947 | -1.0857 | -5.064 | 2021-01-06 | 19369 | 2.6 | -7.8
2 | 2021-01-17 | 2682.738 | 1.0238 | -3.4333 | 2021-01-12 | 19426 | -1.8 | -5.1
3 | 2021-01-24 | 2760.538 | -2.8857 | -4.9378 | 2021-01-23 | 19264 | 1.6 | -11.6
4 | 2021-01-31 | 2845.853 | -5.7286 | -6.425 | 2021-01-28 | 20150 | -1.6 | -13.5
5 | 2021-02-07 | 2799.893 | -4.7 | -4.7643 | 2021-02-01 | 19825 | -4.8 | -16.1
6 | 2021-02-14 | 2933.933 | -8.4952 | -3.6732 | 2021-02-08 | 20318 | -8.4 | -10
7 | 2021-02-21 | 2845.853 | -5.9714 | -5.3833 | 2021-02-16 | 19976 | -4 | -6.8 | Family Day
8 | 2021-02-28 | 2653.444 | 1.9429 | -3.8012 | 2021-02-22 | 18762 | -6.9 | -8.6
9 | 2021-03-07 | 2699.372 | -2.6905 | -3.0643 | 2021-03-01 | 19344 | -7.1 | -5.3
10 | 2021-03-14 | 2492.428 | 5.6762 | -2.431 | 2021-03-08 | 18083 | 2.8 | -7.9
11 | 2021-03-21 | 2510.94 | 3.7143 | -1.4926 | 2021-03-15 | 17880 | -0.8 | -6.4
12 | 2021-03-28 | 2366.325 | 9.9524 | 0.17482 | 2021-03-26 | 16473 | 9.4 | -0.1
13 | 2021-04-04 | 2343.142 | 5.6571 | 3.1009 | 2021-04-01 | 16486 | -1.4 | -1.9 | Good Friday and Easter
14 | 2021-04-11 | 2211.568 | 13.7524 | 3.9729 | 2021-04-05 | 15557 | 9.6 | 4.1 | Provincial Stay-at-Home order
15 | 2021-04-18 | 2287.594 | 8.981 | 6.1494 | 2021-04-16 | 15811 | 1.8 | 0
16 | 2021-04-25 | 2313.442 | 7.1857 | 4.7583 | 2021-04-20 | 16644 | 12.8 | 0.8
17 | 2021-05-02 | 2262.297 | 9.8524 | 7.5583 | 2021-04-29 | 15501 | 9.6 | 6.2
18 | 2021-05-09 | 2255.95 | 9.6667 | 10.6321 | 2021-05-03 | 15882 | 4.8 | 10.9
19 | 2021-05-16 | 2180.385 | 13.3952 | 14.7881 | 2021-05-11 | 15567 | 10.5 | 30.4
20 | 2021-05-23 | 2451.065 | 22.5476 | 12.672 | 2021-05-21 | 19243 | 12.4 | 10.3
21 | 2021-05-30 | 2274.91 | 15.7381 | 15.5881 | 2021-05-25 | 19443 | 9.5 | 27 | Victoria Day
22 | 2021-06-06 | 2484.855 | 22.7 | 13.6643 | 2021-06-06 | 20556 | 31.5 | 29.4
23 | 2021-06-13 | 2776.909 | 23.981 | 16.8333 | 2021-06-07 | 21340 | 31.6 | 25
24 | 2021-06-20 | 2431.511 | 20.6667 | 17.6929 | 2021-06-20 | 18524 | 33.5 | 22.9
25 | 2021-06-27 | 2560.408 | 22.3714 | 20.7536 | 2021-06-27 | 20904 | 31.1 | 30.7
26 | 2021-07-04 | 2699.464 | 23.6476 | 18.7821 | 2021-06-28 | 22258 | 26.1 | 29.5 | Canada Day
27 | 2021-07-11 | 2597.302 | 21.4429 | 21.0045 | 2021-07-06 | 21655 | 30.7 | 31.6
28 | 2021-07-18 | 2739.968 | 23.5571 | 22.2089 | 2021-07-14 | 21368 | 31.6 | 31.3
29 | 2021-07-25 | 2689.413 | 22.7714 | 21.3923 | 2021-07-19 | 20849 | 31.7 | 30.5
30 | 2021-08-01 | 2551.464 | 21.0333 | 23.0952 | 2021-07-26 | 20804 | 29.2 | 30.2
31 | 2021-08-08 | 2691.493 | 23.0857 | 22.3661 | 2021-08-05 | 20846 | 28.9 | 30.9 | Civic Holiday
32 | 2021-08-15 | 2941.314 | 25.2476 | 21.5214 | 2021-08-09 | 22428 | 30.1 | 30.3
33 | 2021-08-22 | 2972.247 | 25.2429 | 21.5494 | 2021-08-19 | 21788 | 27.3 | 32.1
34 | 2021-08-29 | 3105.011 | 26.6333 | 21.1952 | 2021-08-24 | 22986 | 30.6 | 28.8
35 | 2021-09-05 | 2589.611 | 21.081 | 19.9125 | 2021-08-30 | 21576 | 30.8 | 26.6
36 | 2021-09-12 | 2450.299 | 20.3714 | 20.1685 | 2021-09-07 | 18615 | 33.1 | 29.5 | Labour Day
37 | 2021-09-19 | 2478.853 | 20.0381 | 18.269 | 2021-09-17 | 18769 | 28.7 | 27.1
38 | 2021-09-26 | 2354.543 | 16.5143 | 14.6787 | 2021-09-21 | 17978 | 25.5 | 25.3
39 | 2021-10-03 | 2344.343 | 16.8976 | 14.6461 | 2021-09-27 | 16877 | 26 | 24.4
40 | 2021-10-10 | 2410.128 | 17.619 | 15.4244 | 2021-10-07 | 16968 | 24.4 | 23.9
41 | 2021-10-17 | 2370.241 | 17.0571 | 11.5271 | 2021-10-12 | 17312 | 24.2 | 6.4 | Thanksgiving Day
42 | 2021-10-24 | 2338.7 | 11.6095 | 10.6226 | 2021-10-18 | 16450 | 19.8 | 9.8
43 | 2021-10-31 | 2402.699 | 9.4414 | 9.2086 | 2021-10-26 | 16997 | 21.95 | 8.5
44 | 2021-11-07 | 2465.842 | 6.1143 | 6.506 | 2021-11-03 | 17639 | 13.8 | 4.9
45 | 2021-11-14 | 2452.195 | 8.4762 | 7.1875 | 2021-11-14 | 17800 | 6.52 | 6.3 | Remembrance Day
46 | 2021-11-21 | 2556.854 | 5.0238 | 6.3202 | 2021-11-15 | 18649 | 6.4 | 1
47 | 2021-11-28 | 2675.839 | 1.0571 | 3.1232 | 2021-11-22 | 19055 | 4.7 | 0
48 | 2021-12-05 | 2742.067 | 1.5714 | 1.6381 | 2021-11-29 | 19644 | 5.5 | -0.3
49 | 2021-12-11 | 2851.75 | 1.7429 | 2.1229 | 2021-12-07 | 20455 | 1.4 | -4
50 | 2021-12-19 | 2669.703 | 3.8381 | -0.78274 | 2021-12-19 | 19272 | 0.15 | -4.8
51 | 2021-12-26 | 2266.193 | 0.59524 | -2.2914 | 2021-12-22 | 19511 | -2.3 | -2.2 | Christmas
52 | 2022-01-02 | 2977.183 | 0.20476 | -0.92381 | 2022-01-02 | 18923 | -3.4 | -4.8 | Boxing Day & New Years
1 | 2022-01-09 | 2857.269 | -3.8857 | -5.064 | 2022-01-07 | 20513 | -0.7 | -7.8
2 | 2022-01-16 | 3004.853 | -7.6524 | -3.4333 | 2022-01-11 | 21250 | -6.3 | -5.1
3 | 2022-01-23 | 2983.499 | -7.9667 | -4.9378 | 2022-01-20 | 21349 | -7 | -11.6
4 | 2022-01-30 | 3079.729 | -10.4095 | -6.425 | 2022-01-24 | 21261 | -10 | -13.5
5 | 2022-02-06 | 2954.37 | -4.6905 | -4.7643 | 2022-02-04 | 20585 | -12.1 | -16.1
6 | 2022-02-13 | 2834.605 | -2.0286 | -3.6732 | 2022-02-13 | 20272 | -6.1 | -10
7 | 2022-02-20 | 2880.296 | -3.5571 | -5.3833 | 2022-02-14 | 20918 | -10.6 | -6.8
8 | 2022-02-27 | 2827.88 | -3.2381 | -3.8012 | 2022-02-23 | 20059 | -9.5 | -8.6 | Family Day
9 | 2022-03-06 | 2767.504 | -1.0857 | -3.0643 | 2022-02-28 | 19996 | -9.8 | -5.3
10 | 2022-03-13 | 2753.03 | -1.1571 | -2.431 | 2022-03-07 | 18919 | -4.8 | -7.9
11 | 2022-03-20 | 2570.145 | 5.881 | -1.4926 | 2022-03-14 | 17985 | -5.9 | -6.4
12 | 2022-03-27 | 2579.449 | 3.4905 | 0.17482 | 2022-03-23 | 18107 | 1 | -0.1
13 | 2022-04-03 | 2640.859 | 1.4714 | 3.1009 | 2022-03-28 | 19011 | 6.2 | -1.9
14 | 2022-04-10 | 2447.411 | 7.2524 | 3.9729 | 2022-04-04 | 17077 | 3.3 | 4.1
15 | 2022-04-17 | 2297.796 | 9.0905 | 6.1494 | 2022-04-11 | 16430 | -5.4 | 0
16 | 2022-04-24 | 2399.082 | 7.9476 | 4.7583 | 2022-04-18 | 17256 | 7.9 | 0.8
17 | 2022-05-01 | 2356.59 | 8.0619 | 7.5583 | 2022-04-27 | 17060 | 12.1 | 6.2
18 | 2022-05-08 | 2279.399 | 11.7905 | 10.6321 | 2022-05-03 | 16376 | 6.6 | 10.9
19 | 2022-05-15 | 2417.227 | 19.7 | 14.7881 | 2022-05-15 | 18462 | 3.5 | 30.4
20 | 2022-05-22 | 2322.151 | 16.7381 | 12.672 | 2022-05-21 | 16303 | 12.1 | 10.3
21 | 2022-05-29 | 2317.172 | 18.0952 | 15.5881 | 2022-05-26 | 17080 | 28.9 | 27 | Victoria Day
22 | 2022-06-05 | 2523.683 | 21.119 | 13.6643 | 2022-05-31 | 21292 | 29.3 | 29.4
23 | 2022-06-12 | 2364.793 | 18.9286 | 16.8333 | 2022-06-06 | 16685 | 26.6 | 25
24 | 2022-06-19 | 2538.812 | 21.0762 | 17.6929 | 2022-06-16 | 21500 | 32.2 | 22.9
25 | 2022-06-26 | 2851.253 | 25.3667 | 20.7536 | 2022-06-22 | 21954 | 20.5 | 30.7
26 | 2022-07-03 | 2541.865 | 21.8905 | 18.7821 | 2022-06-30 | 19353 | 32.2 | 29.5 | Canada Day
27 | 2022-07-10 | 2628.174 | 22.2286 | 21.0045 | 2022-07-07 | 19476 | 34.6 | 31.6
28 | 2022-07-17 | 2791.062 | 23.5238 | 22.2089 | 2022-07-11 | 20695 | 25.7 | 31.3
29 | 2022-07-24 | 3093.701 | 27.8333 | 21.3923 | 2022-07-19 | 22607 | 25 | 30.5
30 | 2022-07-31 | 2763.318 | 22.7381 | 23.0952 | 2022-07-28 | 20645 | 30.8 | 30.2
31 | 2022-08-07 | 2993.78 | 25.8476 | 22.3661 | 2022-08-07 | 21778 | 34.2 | 30.9 | Civic Holiday
32 | 2022-08-14 | 2739.909 | 22.4857 | 21.5214 | 2022-08-08 | 21560 | 28.7 | 30.3
33 | 2022-08-21 | 2839.599 | 23.4476 | 21.5494 | 2022-08-18 | 20772 | 33 | 32.1
34 | 2022-08-28 | 2799.057 | 22.6286 | 21.1952 | 2022-08-24 | 21368 | 30.9 | 28.8
35 | 2022-09-04 | 2773.033 | 22.619 | 19.9125 | 2022-08-29 | 21871 | 27.4 | 26.6
36 | 2022-09-11 | 2631.445 | 21.2905 | 20.1685 | 2022-09-09 | 19921 | 28.7 | 29.5 | Labour Day
37 | 2022-09-18 | 2534.425 | 19.6905 | 18.269 | 2022-09-12 | 18846 | 30.5 | 27.1
38 | 2022-09-25 | 2432.33 | 17.8238 | 14.6787 | 2022-09-21 | 18873 | 26.5 | 25.3
39 | 2022-10-02 | 2318.126 | 13.3095 | 14.6461 | 2022-09-27 | 16330 | 23.7 | 24.4
40 | 2022-10-09 | 2358.464 | 12.8333 | 15.4244 | 2022-10-05 | 16624 | 28.3 | 23.9
41 | 2022-10-16 | 2302.017 | 13.2667 | 11.5271 | 2022-10-12 | 16289 | 16.5 | 6.4 | Thanksgiving Day
42 | 2022-10-23 | 2381.506 | 9.681 | 10.6226 | 2022-10-19 | 17294 | 21.6 | 9.8
43 | 2022-10-30 | 2360.376 | 10.3714 | 9.2086 | 2022-10-27 | 16592 | 19.8 | 8.5
44 | 2022-11-06 | 2373.902 | 13.8714 | 6.506 | 2022-11-02 | 16636 | 8.9 | 4.9
45 | 2022-11-13 | 2447.31 | 8.7333 | 7.1875 | 2022-11-13 | 17654 | 9.9 | 6.3 | Remembrance Day
46 | 2022-11-20 | 2741.254 | -0.90476 | 6.3202 | 2022-11-20 | 19441 | 14.1 | 1
47 | 2022-11-27 | 2656.974 | 4.4095 | 3.1232 | 2022-11-21 | 19255 | 4 | 0
48 | 2022-12-04 | 2715.506 | 2.5619 | 1.6381 | 2022-11-28 | 19360 | -3.6 | -0.3
49 | 2022-12-11 | 2388.336 | 1.8667 | 2.1229 | 2022-12-05 | 19353 | 7.2 | -4
50 | 2022-12-18 | 2867.744 | -1.3429 | -0.78274 | 2022-12-12 | 20173 | 1.9 | -4.8
51 | 2022-12-24 | 2484.352 | -3.5286 | -2.2914 | 2022-12-19 | 19840 | 5.2 | -2.2
52 | 2023-01-01 | 3347.667 | 3.9429 | -0.92381 | 2022-12-26 | 18578 | -2 | -4.8 | Christmas & Boxing Day
1 | 2023-01-08 | 2744.856 | 9.2381 | -5.064 | 2023-01-04 | 19267 | 0.8 | -7.8 | New Year's Day
2 | 2023-01-15 | 2879.144 | 7.1905 | -3.4333 | 2023-01-10 | 19651 | -5.8 | -5.1
3 | 2023-01-22 | 2833.753 | 7.9524 | -4.9378 | 2023-01-19 | 19562 | 10 | -11.6
4 | 2023-01-29 | 2848.669 | 8.8571 | -6.425 | 2023-01-25 | 19819 | 10 | -13.5
5 | 2023-02-05 | 3010.051 | -2.8048 | -4.7643 | 2023-02-03 | 21388 | 10 | -16.1
6 | 2023-02-12 | 2746.162 | 2.0381 | -3.6732 | 2023-02-06 | 19462 | 5 | -10
7 | 2023-02-19 | 2680.973 | 2.6905 | -5.3833 | 2023-02-17 | 19460 | -15.5 | -6.8
8 | 2023-02-26 | 2823.429 | -2.381 | -3.8012 | 2023-02-22 | 20267 | -1.7 | -8.6 | Family Day
9 | 2023-03-05 | 2758.605 | 0.56667 | -3.0643 | 2023-02-27 | 19568 | -5 | -5.3
10 | 2023-03-12 | 2700.274 | -0.8381 | -2.431 | 2023-03-10 | 18811 | -2.9 | -7.9
11 | 2023-03-19 | 2694.434 | 0.76667 | -1.4926 | 2023-03-14 | 18446 | -1.3 | -6.4
12 | 2023-03-26 | 2608.347 | 4.5857 | 0.17482 | 2023-03-22 | 17699 | -0.1 | -0.1
13 | 2023-04-02 | 2608.438 | 3.5095 | 3.1009 | 2023-03-29 | 18139 | -3.2 | -1.9
14 | 2023-04-09 | 2443.869 | 6.4524 | 3.9729 | 2023-04-05 | 17547 | 4.6 | 4.1 | Good Friday and Easter
15 | 2023-04-16 | 2309.261 | 19.3667 | 6.1494 | 2023-04-13 | 16488 | 8.3 | 0 | Easter Monday
16 | 2023-04-23 | 2407.835 | 7.6619 | 4.7583 | 2023-04-18 | 16811 | 5.4 | 0.8
17 | 2023-04-30 | 2417.505 | 8.0714 | 7.5583 | 2023-04-25 | 16667 | 25.6 | 6.2
18 | 2023-05-07 | 2364.04 | 9.5762 | 10.6321 | 2023-05-02 | 16342 | 4.1 | 10.9
19 | 2023-05-14 | 2292.261 | 17.3333 | 14.7881 | 2023-05-12 | 16714 | 10 | 30.4
20 | 2023-05-21 | 2283.65 | 14.4571 | 12.672 | 2023-05-17 | 15793 | 6.5 | 10.3
21 | 2023-05-28 | 2267.856 | 15.9619 | 15.5881 | 2023-05-28 | 16547 | 27 | 27 | Victoria Day
22 | 2023-06-04 | 2702.359 | 23.0333 | 13.6643 | 2023-06-02 | 21463 | 11 | 29.4
23 | 2023-06-11 | 2423.537 | 18.8905 | 16.8333 | 2023-06-05 | 17801 | 27.6 | 25
24 | 2023-06-18 | 2417.762 | 18.0333 | 17.6929 | 2023-06-18 | 16918 | 31.6 | 22.9
25 | 2023-06-25 | 2770.294 | 22.5524 | 20.7536 | 2023-06-25 | 20313 | 24.3 | 30.7
26 | 2023-07-02 | 2717.666 | 22.0952 | 18.7821 | 2023-06-30 | 19789 | 24.3 | 29.5 | Canada Day
27 | 2023-07-09 | 2900.151 | 24.15 | 21.0045 | 2023-07-05 | 22686 | 27.5 | 31.6
28 | 2023-07-16 | 2766.81 | 22.7476 | 22.2089 | 2023-07-10 | 21021 | 25.2 | 31.3
29 | 2023-07-23 | 2777.255 | 22.8048 | 21.3923 | 2023-07-20 | 20794 | 30.95 | 30.5
30 | 2023-07-30 | 2924.81 | 24.1381 | 23.0952 | 2023-07-27 | 21558 | 28.35 | 30.2
31 | 2023-08-06 | 2686.766 | 22.0286 | 22.3661 | 2023-08-03 | 21364 | 27 | 30.9
32 | 2023-08-13 | 2735.923 | 22.9905 | 21.5214 | 2023-08-09 | 21281 | 29 | 30.3 | Civic Holiday
33 | 2023-08-20 | 2667.588 | 21.3571 | 21.5494 | 2023-08-16 | 20781 | 29.1 | 32.1
34 | 2023-08-27 | 2633.262 | 20.1952 | 21.1952 | 2023-08-21 | 19381 | 28.2 | 28.8
35 | 2023-09-03 | 2584.728 | 20.0905 | 19.9125 | 2023-09-03 | 19321 | 26.8 | 26.6
36 | 2023-09-10 | 2907.846 | 23.681 | 20.1685 | 2023-09-05 | 23713 | 24 | 29.5 | Labour Day
37 | 2023-09-17 | 2478.081 | 18.1476 | 18.269 | 2023-09-11 | 19016 | 31.1 | 27.1
38 | 2023-09-24 | 2410.667 | 17.5857 | 14.6787 | 2023-09-21 | 17238 | 32.1 | 25.3
39 | 2023-10-01 | 2439.465 | 18.5333 | 14.6461 | 2023-10-01 | 17211 | 23 | 24.4
40 | 2023-10-08 | 2584.822 | 19.0714 | 15.4244 | 2023-10-03 | 20849 | 21.9 | 23.9
41 | 2023-10-15 | 2398.476 | 10.6143 | 11.5271 | 2023-10-10 | 17004 | 26.9 | 6.4 | Thanksgiving Day
42 | 2023-10-22 | 2424.181 | 11.381 | 10.6226 | 2023-10-16 | 16904 | 30 | 9.8
43 | 2023-10-29 | 2425.983 | 14.281 | 9.2086 | 2023-10-23 | 16950 | 12.8 | 8.5
44 | 2023-11-05 | 2574.99 | 6.2857 | 6.506 | 2023-11-01 | 18216 | 11.5 | 4.9 | Remembrance Day
45 | 2023-11-12 | 2643.634 | 5.2762 | 7.1875 | 2023-11-08 | 19462 | 13.7 | 6.3
46 | 2023-11-19 | 2584.291 | 7.1476 | 6.3202 | 2023-11-13 | 18285 | 4.4 | 1
47 | 2023-11-26 | 2768.615 | 2.1381 | 3.1232 | 2023-11-20 | 19536 | 0.6 | 0
48 | 2023-12-03 | 2818.631 | 1.181 | 1.6381 | 2023-11-28 | 20579 | 13.8 | -0.3
49 | 2023-12-10 | 2809.289 | 3.7381 | 2.1229 | 2023-12-06 | 19865 | 0.4 | -4
50 | 2023-12-17 | 2357.399 | 3.3714 | -0.78274 | 2023-12-13 | 20004 | -1.5 | -4.8
51 | 2023-12-24 | 3195.778 | 1.119 | -2.2914 | 2023-12-19 | 19625 | 0.2 | -2.2
52 | 2023-12-31 | 2526.061 | 4.4571 | -0.92381 | 2023-12-30 | 18138 | 3 | -4.8 | Christmas & Boxing Day
1 | 2024-01-07 | 2828.647 | -1.4905 | -5.064 | 2024-01-04 | 19981 | -0.9 | -7.8 | New Year's Day
2 | 2024-01-14 | 2888.957 | 0.1381 | -3.4333 | 2024-01-09 | 19996 | 0.2 | -5.1
3 | 2024-01-21 | 3090.02 | -8.9571 | -4.9378 | 2024-01-15 | 20880 | -3.1 | -11.6
4 | 2024-01-28 | 2893.512 | 1.0667 | -6.425 | 2024-01-22 | 20368 | 2.2 | -13.5
5 | 2024-02-04 | 2800.641 | 1.5333 | -4.7643 | 2024-01-30 | 19401 | -9 | -16.1
6 | 2024-02-11 | 2704.567 | 3.6762 | -3.6732 | 2024-02-05 | 19030 | -1.2 | -10
7 | 2024-02-18 | 2866.765 | -1.9381 | -5.3833 | 2024-02-16 | 19703 | 1.9 | -6.8
8 | 2024-02-25 | 2737.246 | 0.65714 | -3.8012 | 2024-02-19 | 18745 | 3.1 | -8.6 | Family Day
Back to main menu

## Table 3.3.2
Back to main menu
Table 3.3.2: Monthly Weather and Demand History
Month | Energy Demand (GWh) | Reported Embedded Generation (GWh) | Peak Demand (MW) | Average Hour (MW) | Minimum Hour (MW) | 90th Percentile (MW) | # of Hours Above 20,000 (MW) | Average Temperature (°C) | Normal Average Temperature (°C) | Weather Corrected Energy (GWh) | Forecasted Energy (GWh) | Energy Forecast MAPE | Peak Temperature (°C) | Normal Peak Temperature (°C) | Weather Corrected Peak (MW) | Forecasted Peak (MW) | Peak Forecast MAPE
2002-05-31 | 11875 |  | 20068 | 15961 | 12092 | 18344 | 1 | 12.5 | 14.6 | 11662 | 11526 | 1.2% | 27.9 | 28.4 | 20245 | 19777 | 2.3%
2002-06-30 | 12185 |  | 23578 | 16924 | 11537 | 20698 | 97 | 20.2 | 19.1 | 12056 | 11831 | 1.9% | 30.7 | 31.3 | 23273 | 21897 | 5.9%
2002-07-31 | 14033 |  | 25226 | 18862 | 12348 | 23310 | 261 | 25.5 | 23.1 | 13532 | 12956 | 4.3% | 34.7 | 30.9 | 23654 | 23007 | 2.7%
2002-08-31 | 13749 |  | 25414 | 18480 | 13077 | 22695 | 207 | 23.9 | 22.6 | 13322 | 12823 | 3.7% | 33.4 | 30.8 | 24272 | 22720 | 6.4%
2002-09-30 | 12593 |  | 25062 | 17490 | 12409 | 20801 | 114 | 21.4 | 18 | 12144 | 11393 | 6.2% | 33.5 | 29.8 | 21739 | 21100 | 2.9%
2002-10-31 | 12398 |  | 21216 | 16664 | 12244 | 19077 | 25 | 9.9 | 11.9 | 12155 | 12043 | 0.9% | 28.8 | 23.3 | 19902 | 20319 | 2.1%
2002-11-30 | 12656 |  | 21862 | 17577 | 12709 | 20027 | 75 | 3.7 | 5.2 | 12836 | 12370 | 3.6% | 0.1 | -2 | 22314 | 22422 | 0.5%
2002-12-31 | 13484 |  | 23334 | 18071 | 13057 | 21022 | 197 | -1.3 | 0 | 13501 | 13363 | 1% | -1.2 | -8.4 | 23551 | 23523 | 0.1%
2003-01-31 | 14487 |  | 24158 | 19471 | 13236 | 22223 | 346 | -7.3 | -5.2 | 14211 | 13920 | 2.1% | -13.4 | -13.5 | 23893 | 23850 | 0.2%
2003-02-28 | 13123 |  | 23469 | 19528 | 14523 | 21982 | 315 | -6.1 | -3.4 | 12808 | 12427 | 3% | -10 | -13.5 | 22950 | 23273 | 1.4%
2003-03-31 | 13414 |  | 23117 | 18030 | 13289 | 20781 | 142 | 0.4 | 0.6 | 13159 | 12902 | 2% | -14.3 | -5.5 | 21752 | 22090 | 1.6%
2003-04-30 | 12097 |  | 21010 | 16802 | 12290 | 19541 | 53 | 6.7 | 7.6 | 12070 | 11760 | 2.6% | -1.8 | 0.2 | 20847 | 19851 | 4.8%
2003-05-31 | 11627 |  | 18741 | 15628 | 11604 | 17986 | 0 | 13.3 | 14.6 | 11742 | 11691 | 0.4% | 13.1 | 8.7 | 19845 | 19853 | 0%
2003-06-30 | 11885 |  | 24753 | 16507 | 11821 | 19405 | 58 | 19.7 | 19.1 | 11842 | 12214 | 3.1% | 33.3 | 31.3 | 23523 | 22799 | 3.1%
2003-07-31 | 12898 |  | 23175 | 17335 | 11957 | 20681 | 139 | 22.8 | 23.1 | 12969 | 13433 | 3.6% | 31.3 | 30.9 | 23763 | 23684 | 0.3%
2003-08-31 | 12514 |  | 23891 | 16820 | 2270 | 21001 | 144 | 22.5 | 22.6 | 12172 | 13156 | 8.1% | 31 | 30.8 | 23561 | 23347 | 0.9%
2003-09-30 | 11794 |  | 20700 | 16381 | 11802 | 19023 | 14 | 18 | 18 | 11779 | 11789 | 0.1% | 26.8 | 29.8 | 20307 | 21600 | 6.4%
2003-10-31 | 12160 |  | 20408 | 16344 | 11941 | 18584 | 4 | 10 | 11.9 | 12135 | 12368 | 1.9% | 9.7 | 4 | 21259 | 20667 | 2.8%
2003-11-30 | 12390 |  | 21584 | 17208 | 12724 | 19670 | 54 | 5.5 | 5.2 | 12865 | 12585 | 2.2% | 13.4 | -2 | 22716 | 22681 | 0.2%
2003-12-31 | 13328 |  | 22798 | 17780 | 12550 | 20959 | 165 | 0.5 | 0 | 13534 | 13768 | 1.7% | -5.6 | -8.4 | 23431 | 23858 | 1.8%
2004-01-31 | 14767 |  | 24937 | 19849 | 13219 | 22977 | 399 | -8.6 | -5.2 | 14323 | 14192 | 0.9% | -19.7 | -13.5 | 24409 | 24078 | 1.4%
2004-02-29 | 13088 |  | 22608 | 18805 | 14243 | 21146 | 249 | -2.6 | -3.4 | 13173 | 13034 | 1.1% | -3.9 | -13.5 | 23057 | 23556 | 2.2%
2004-03-31 | 13225 |  | 21634 | 17775 | 13238 | 20123 | 84 | 2.9 | 0.6 | 13203 | 13279 | 0.6% | -3.1 | -5.5 | 21870 | 22452 | 2.7%
2004-04-30 | 11792 |  | 19911 | 16378 | 12427 | 18638 | 0 | 7.9 | 7.6 | 11875 | 11891 | 0.1% | 3.2 | 0.2 | 20526 | 19943 | 2.8%
2004-05-31 | 11835 |  | 20327 | 15908 | 11983 | 18401 | 4 | 14.4 | 14.6 | 11791 | 11844 | 0.5% | 27.3 | 28.4 | 20053 | 20167 | 0.6%
2004-06-30 | 12046 |  | 23163 | 16730 | 12059 | 19989 | 72 | 18.8 | 19.1 | 12218 | 12553 | 2.7% | 31.3 | 31.3 | 23163 | 23585 | 1.8%
2004-07-31 | 12770 |  | 23976 | 17164 | 12385 | 20584 | 94 | 21.7 | 23.1 | 12930 | 13366 | 3.4% | 30.1 | 30.9 | 24618 | 23677 | 3.8%
2004-08-31 | 12746 |  | 23159 | 17132 | 12223 | 20350 | 97 | 20.8 | 22.6 | 12965 | 13301 | 2.6% | 28.6 | 30.8 | 23230 | 23298 | 0.3%
2004-09-30 | 12370 |  | 21911 | 17180 | 12285 | 20296 | 102 | 19.8 | 18 | 12205 | 11893 | 2.6% | 25.8 | 29.8 | 20959 | 21881 | 4.4%
2004-10-31 | 12215 |  | 19829 | 16418 | 12343 | 18771 | 0 | 11.8 | 11.9 | 12457 | 12358 | 0.8% | 8.8 | 4 | 20926 | 21212 | 1.4%
2004-11-30 | 12601 |  | 22066 | 17501 | 12969 | 19981 | 71 | 5.9 | 5.2 | 13149 | 12864 | 2.2% | 5 | -2 | 23334 | 22749 | 2.5%
2004-12-31 | 13982 |  | 24979 | 18705 | 14169 | 21867 | 261 | -2.1 | 0 | 13837 | 13652 | 1.3% | -12.3 | -8.4 | 24073 | 23404 | 2.8%
2005-01-31 | 14619 |  | 24362 | 19649 | 13545 | 22555 | 356 | -6.1 | -5.2 | 14521 | 14278 | 1.7% | -14.5 | -13.5 | 24173 | 23844 | 1.4%
2005-02-28 | 12732 |  | 22322 | 18946 | 14854 | 21242 | 249 | -2.7 | -3.4 | 12866 | 12800 | 0.5% | -3.9 | -13.5 | 22791 | 23518 | 3.2%
2005-03-31 | 13494 |  | 22724 | 18137 | 13959 | 20632 | 143 | -0.3 | 0.6 | 13288 | 13409 | 0.9% | -8.5 | -5.5 | 22667 | 22413 | 1.1%
2005-04-30 | 11828 |  | 19343 | 16428 | 12279 | 18455 | 0 | 9.1 | 7.6 | 12209 | 11934 | 2.3% | 10.9 | 0.2 | 20932 | 20534 | 1.9%
2005-05-31 | 11745 |  | 19007 | 15786 | 11950 | 18140 | 0 | 13.2 | 14.6 | 11734 | 12027 | 2.5% | 22.3 | 28.4 | 18688 | 20648 | 10.5%
2005-06-30 | 13499 |  | 26157 | 18749 | 12066 | 23350 | 260 | 23.7 | 19.1 | 12680 | 12366 | 2.5% | 31.6 | 31.3 | 24411 | 23422 | 4.1%
2005-07-31 | 14094 |  | 26160 | 18944 | 12109 | 23811 | 277 | 25.3 | 23.1 | 13573 | 13266 | 2.3% | 34.6 | 30.9 | 25823 | 23784 | 7.9%
2005-08-31 | 14031 |  | 25816 | 18859 | 13487 | 22804 | 274 | 23.7 | 22.6 | 13565 | 13533 | 0.2% | 32.9 | 30.8 | 24780 | 23374 | 5.7%
2005-09-30 | 12553 |  | 23914 | 17434 | 12541 | 20722 | 140 | 20.1 | 18 | 12368 | 12180 | 1.5% | 30.1 | 29.8 | 21720 | 22114 | 1.8%
2005-10-31 | 12187 |  | 20752 | 16381 | 12112 | 18944 | 22 | 11.9 | 11.9 | 12127 | 12478 | 2.9% | 25.8 | 23.3 | 21108 | 20935 | 0.8%
2005-11-30 | 12441 |  | 22564 | 17279 | 12548 | 20020 | 74 | 5.6 | 5.2 | 12682 | 12878 | 1.5% | -6.3 | -2 | 22614 | 22917 | 1.3%
2005-12-31 | 13746 |  | 23766 | 18422 | 12673 | 21485 | 250 | -2.7 | 0 | 13620 | 13796 | 1.3% | -4.8 | -8.4 | 24097 | 23673 | 1.8%
2006-01-31 | 13596 |  | 23052 | 18274 | 13644 | 20907 | 189 | 0.8 | -5.2 | 14274 | 14416 | 1% | -5 | -13.5 | 24238 | 24255 | 0.1%
2006-02-28 | 12568 | 197 | 22321 | 18703 | 14051 | 20958 | 220 | -3 | -3.4 | 12600 | 12940 | 2.7% | -0.9 | -13.5 | 22387 | 23797 | 6.3%
2006-03-31 | 13200 | 175 | 21772 | 17742 | 13274 | 20091 | 83 | 2.3 | 0.6 | 13175 | 13631 | 3.5% | -2.2 | -5.5 | 22054 | 22775 | 3.3%
2006-04-30 | 11513 | 210 | 19582 | 15990 | 12020 | 18469 | 0 | 9.5 | 7.6 | 11956 | 12052 | 0.8% | 3.7 | 0.2 | 20333 | 20923 | 2.9%
2006-05-31 | 11927 | 183 | 24857 | 16032 | 11812 | 18116 | 42 | 15.7 | 14.6 | 11824 | 12305 | 4.1% | 32.8 | 28.4 | 21889 | 21702 | 0.9%
2006-06-30 | 12542 | 157 | 23349 | 17419 | 11957 | 20688 | 143 | 20.9 | 19.1 | 12478 | 12553 | 0.6% | 30.6 | 31.3 | 23613 | 24215 | 2.6%
2006-07-31 | 13854 | 106 | 26092 | 18620 | 12470 | 22949 | 269 | 24.6 | 23.1 | 13348 | 13632 | 2.1% | 33.6 | 30.9 | 25257 | 25044 | 0.8%
2006-08-31 | 13308 | 102 | 27005 | 17887 | 12545 | 21104 | 172 | 22.3 | 22.6 | 13263 | 13659 | 3% | 36.4 | 30.8 | 23881 | 24579 | 2.9%
2006-09-30 | 11521 | 75 | 19976 | 16001 | 11796 | 18524 | 0 | 16.6 | 18 | 11662 | 12283 | 5.3% | 28 | 29.8 | 21527 | 23395 | 8.7%
2006-10-31 | 11962 | 112 | 19590 | 16078 | 11621 | 18410 | 0 | 9.7 | 11.9 | 11803 | 12599 | 6.7% | 13.5 | 5.6 | 20459 | 21602 | 5.6%
2006-11-30 | 12179 | 217 | 21267 | 16915 | 12720 | 19351 | 30 | 6 | 5.2 | 12634 | 12956 | 2.5% | 1.5 | -2 | 22968 | 23175 | 0.9%
2006-12-31 | 12884 | 213 | 22941 | 18010 | 12246 | 20322 | 107 | 2.4 | 0 | 13332 | 13870 | 4% | -5.5 | -8.4 | 23626 | 24226 | 2.5%
2007-01-31 | 13758 | 206 | 23537 | 17914 | 12941 | 21448 | 243 | -2.3 | -5.2 | 14060 | 14425 | 2.6% | -13.1 | -13.5 | 23777 | 24617 | 3.5%
2007-02-28 | 13038 | 188 | 23935 | 19401 | 14894 | 21908 | 280 | -7.2 | -3.4 | 12658 | 12871 | 1.7% | -14 | -13.5 | 23053 | 24064 | 4.4%
2007-03-31 | 13193 | 130 | 22969 | 17732 | 13331 | 20433 | 121 | 1.6 | 0.6 | 13158 | 13390 | 1.8% | -12.5 | -5.5 | 22680 | 22831 | 0.7%
2007-04-30 | 11828 | 155 | 20016 | 16427 | 11819 | 18975 | 1 | 7.3 | 7.6 | 11884 | 11925 | 0.3% | 4.1 | 0.2 | 21219 | 20530 | 3.2%
2007-05-31 | 11819 | 187 | 21490 | 15885 | 11814 | 18654 | 33 | 15.9 | 14.6 | 11716 | 12101 | 3.3% | 27.5 | 28.4 | 18882 | 21186 | 12.2%
2007-06-30 | 12693 | 117 | 25737 | 17629 | 11699 | 21773 | 166 | 22 | 19.1 | 12370 | 12491 | 1% | 34.2 | 31.3 | 24968 | 24546 | 1.7%
2007-07-31 | 12841 | 118 | 24561 | 17259 | 11710 | 21065 | 133 | 22.6 | 23.1 | 13021 | 13489 | 3.6% | 32.6 | 30.9 | 24937 | 25492 | 2.2%
2007-08-31 | 13455 | 95 | 25584 | 18084 | 12293 | 22076 | 206 | 23.6 | 22.6 | 13117 | 13388 | 2.1% | 34.5 | 30.8 | 24567 | 24694 | 0.5%
2007-09-30 | 11916 | 60 | 24046 | 16550 | 11867 | 19637 | 51 | 19.6 | 18 | 11730 | 11893 | 1.4% | 32.9 | 29.8 | 20976 | 22602 | 7.8%
2007-10-31 | 11908 | 93 | 19233 | 16006 | 11788 | 18411 | 0 | 15 | 11.9 | 12052 | 12468 | 3.4% | 24.3 | 23.3 | 19608 | 21468 | 9.5%
2007-11-30 | 12350 | 134 | 21814 | 17153 | 12371 | 19848 | 60 | 3.5 | 5.2 | 12535 | 12776 | 1.9% | -0.3 | -2 | 22402 | 22808 | 1.8%
2007-12-31 | 13408 | 151 | 22935 | 17932 | 13146 | 20761 | 189 | -1.8 | 0 | 13303 | 13657 | 2.7% | -3.4 | -8.4 | 23143 | 24220 | 4.7%
2008-01-31 | 13610 | 193 | 22782 | 18293 | 13556 | 20970 | 196 | -1.7 | -5.3 | 13996 | 14007 | 0.1% | -8 | -13.5 | 23324 | 24001 | 2.9%
2008-02-29 | 12897 | 183 | 23054 | 18530 | 14295 | 21007 | 204 | -4.3 | -3.1 | 12775 | 12997 | 1.7% | -9.3 | -13.5 | 22662 | 23494 | 3.7%
2008-03-31 | 13004 | 196 | 20990 | 17478 | 13902 | 19568 | 31 | -0.6 | 1.1 | 12635 | 13005 | 2.9% | -1.6 | -5.5 | 21209 | 22067 | 4%
2008-04-30 | 11520 | 176 | 19512 | 16001 | 11571 | 18117 | 0 | 10.6 | 7.6 | 11872 | 11751 | 1% | 14.1 | 0.2 | 21077 | 20324 | 3.6%
2008-05-31 | 11407 | 183 | 18650 | 15332 | 11465 | 17576 | 0 | 13 | 14.9 | 11443 | 11824 | 3.3% | 26.9 | 28.4 | 20140 | 20535 | 2%
2008-06-30 | 12189 | 160 | 24195 | 16929 | 11764 | 20434 | 101 | 20.7 | 19.6 | 11982 | 12220 | 2% | 33.1 | 31.3 | 23724 | 24175 | 1.9%
2008-07-31 | 13156 | 136 | 23787 | 17682 | 12035 | 21320 | 176 | 22.9 | 23.5 | 13124 | 13264 | 1.1% | 30 | 30.9 | 24988 | 25077 | 0.4%
2008-08-31 | 12549 | 152 | 22707 | 16866 | 11986 | 19787 | 65 | 20.7 | 22.2 | 12703 | 13024 | 2.5% | 26.1 | 30.8 | 23580 | 24324 | 3.2%
2008-09-30 | 11793 | 123 | 22975 | 16380 | 12061 | 18964 | 41 | 18.1 | 17.9 | 11693 | 11656 | 0.3% | 30.3 | 29.8 | 21404 | 22189 | 3.7%
2008-10-31 | 11634 | 132 | 19366 | 15637 | 11450 | 17924 | 0 | 10.1 | 11.2 | 11692 | 12091 | 3.4% | 4.8 | 4 | 19512 | 20828 | 6.7%
2008-11-30 | 11829 | 145 | 21279 | 16429 | 11881 | 19037 | 24 | 3.8 | 5.1 | 12096 | 12312 | 1.8% | 3.8 | -2 | 22489 | 22041 | 2%
2008-12-31 | 13088 | 170 | 22541 | 17556 | 11992 | 20509 | 121 | -2.5 | -1.1 | 12908 | 13315 | 3.2% | -3.7 | -8.4 | 22165 | 23056 | 4%
2009-01-31 | 13730 | 170 | 22983 | 18455 | 13872 | 21037 | 199 | -7.6 | -4.6 | 13535 | 13728 | 1.4% | -11.3 | -13.5 | 22667 | 23740 | 4.7%
2009-02-28 | 11698 | 165 | 22110 | 17408 | 13312 | 19676 | 48 | -2.5 | -3.1 | 11749 | 12342 | 5% | -13.1 | -13.5 | 21809 | 23209 | 6.4%
2009-03-31 | 12167 | 173 | 21466 | 16353 | 11855 | 18907 | 21 | 2.1 | 1.2 | 12165 | 12797 | 5.2% | -9.6 | -5.5 | 20869 | 21840 | 4.7%
2009-04-30 | 10747 | 181 | 18744 | 14926 | 10790 | 17106 | 0 | 8.7 | 7.8 | 10901 | 11377 | 4.4% | -0.5 | 0.2 | 20345 | 20089 | 1.3%
2009-05-31 | 10504 | 198 | 17560 | 14119 | 10794 | 16433 | 0 | 14.7 | 15 | 10536 | 11436 | 8.5% | 28.6 | 28.4 | 18785 | 20314 | 8.1%
2009-06-30 | 10884 | 147 | 22540 | 15117 | 10678 | 17998 | 35 | 18.4 | 20.1 | 11162 | 11790 | 5.6% | 30.7 | 31.3 | 23485 | 23754 | 1.1%
2009-07-31 | 11315 | 141 | 20011 | 15209 | 10786 | 18132 | 1 | 20.3 | 23.4 | 12092 | 12826 | 6.1% | 27.4 | 30.9 | 22352 | 24774 | 10.8%
2009-08-31 | 12226 | 144 | 24380 | 16433 | 11040 | 20683 | 122 | 21.9 | 22.2 | 12113 | 12563 | 3.7% | 31.2 | 30.8 | 24121 | 24006 | 0.5%
2009-09-30 | 10932 | 113 | 19731 | 15183 | 10890 | 18072 | 0 | 18 | 17.9 | 10838 | 11178 | 3.1% | 25.1 | 29.8 | 19978 | 21505 | 7.6%
2009-10-31 | 11182 | 146 | 18420 | 15029 | 11295 | 17251 | 0 | 9.3 | 10.9 | 11214 | 11614 | 3.6% | 4.1 | 4 | 19465 | 20431 | 5%
2009-11-30 | 11113 | 186 | 19710 | 15435 | 11333 | 17813 | 0 | 6.9 | 4.8 | 11606 | 11911 | 2.6% | 3.7 | -2 | 21501 | 21427 | 0.3%
2009-12-31 | 12689 | 197 | 21831 | 17055 | 12293 | 19724 | 56 | -1.5 | -1.4 | 12678 | 12653 | 0.2% | -6.7 | -8.4 | 21731 | 21907 | 0.8%
2010-01-31 | 13145 | 206 | 22045 | 17669 | 13075 | 20120 | 84 | -4.3 | -4.2 | 13228 | 13145 | 0.6% | -7.3 | -13.5 | 22298 | 22817 | 2.3%
2010-02-28 | 11752 | 176 | 21367 | 17488 | 13243 | 19688 | 46 | -2.6 | -3 | 11778 | 11841 | 0.5% | -3.6 | -13.5 | 22020 | 22564 | 2.5%
2010-03-31 | 11686 | 97 | 19393 | 15707 | 11951 | 17745 | 0 | 5.6 | 1 | 12011 | 12439 | 3.6% | 2 | -5.5 | 21346 | 21395 | 0.2%
2010-04-30 | 10475 | 174 | 17398 | 14548 | 10618 | 16557 | 0 | 11.9 | 8.1 | 10898 | 10834 | 0.6% | 3.6 | 0.2 | 19259 | 18815 | 2.3%
2010-05-31 | 11368 | 153 | 22904 | 15280 | 10914 | 18076 | 44 | 17 | 15.2 | 10951 | 10785 | 1.5% | 31.4 | 28.4 | 21295 | 18888 | 11.3%
2010-06-30 | 11556 | 145 | 21527 | 16050 | 11506 | 19165 | 44 | 20.2 | 20.4 | 11538 | 11323 | 1.9% | 28.3 | 31.3 | 22475 | 22516 | 0.2%
2010-07-31 | 13307 | 173 | 25075 | 17886 | 11400 | 22220 | 224 | 24.5 | 23.2 | 12903 | 12324 | 4.5% | 33.3 | 30.9 | 24050 | 23554 | 2.1%
2010-08-31 | 12922 | 148 | 24917 | 17368 | 11813 | 21949 | 155 | 23.5 | 22.2 | 12462 | 12159 | 2.4% | 32.9 | 30.8 | 24202 | 22960 | 5.1%
2010-09-30 | 11049 | 178 | 24444 | 15346 | 11124 | 17784 | 35 | 17.7 | 17.6 | 10950 | 11050 | 0.9% | 32.4 | 29.8 | 21702 | 21553 | 0.7%
2010-10-31 | 10929 | 221 | 17704 | 14690 | 10816 | 16635 | 0 | 11.4 | 10.9 | 10984 | 11263 | 2.5% | 11.4 | 4 | 19200 | 19061 | 0.7%
2010-11-30 | 11304 | 237 | 19970 | 15700 | 11584 | 17897 | 0 | 5.1 | 4.3 | 11457 | 11626 | 1.5% | 4.2 | -2 | 20713 | 20841 | 0.6%
2010-12-31 | 12694 | 265 | 22114 | 17062 | 12614 | 19769 | 56 | -3.2 | -1.5 | 12581 | 12667 | 0.7% | -11.6 | -8.4 | 21967 | 21810 | 0.7%
2011-01-31 | 13302 | 252 | 22733 | 17879 | 11835 | 20362 | 114 | -6 | -4.2 | 13238 | 13354 | 0.9% | -9 | -13.5 | 22877 | 22406 | 2.1%
2011-02-28 | 11775 | 234 | 21871 | 17523 | 13358 | 19880 | 53 | -4 | -3 | 11711 | 11984 | 2.3% | -7.7 | -13.5 | 21660 | 22137 | 2.2%
2011-03-31 | 12352 | 267 | 20667 | 16603 | 12736 | 18529 | 8 | 0.5 | 1.1 | 12319 | 12499 | 1.5% | -4.3 | -5.5 | 21180 | 20696 | 2.3%
2011-04-30 | 10789 | 283 | 17945 | 14985 | 11276 | 17113 | 0 | 7.8 | 8.5 | 11023 | 10962 | 0.6% | 5.2 | 0.2 | 19571 | 18317 | 6.4%
2011-05-31 | 10782 | 261 | 20847 | 14492 | 10799 | 16552 | 9 | 15.1 | 15.5 | 10594 | 10941 | 3.3% | 29.3 | 28.4 | 18743 | 18527 | 1.2%
2011-06-30 | 11238 | 219 | 22765 | 15609 | 10890 | 18749 | 18 | 20.5 | 20.6 | 11254 | 11507 | 2.2% | 33.3 | 31.3 | 22294 | 22504 | 0.9%
2011-07-31 | 13298 | 201 | 25450 | 17874 | 11529 | 21828 | 190 | 25.8 | 23 | 12809 | 12449 | 2.8% | 37.5 | 30.9 | 23631 | 23527 | 0.4%
2011-08-31 | 12532 | 189 | 22051 | 16844 | 12205 | 20167 | 84 | 23.1 | 22.4 | 12292 | 12512 | 1.8% | 31.3 | 30.8 | 22209 | 22967 | 3.4%
2011-09-30 | 11145 | 169 | 21552 | 15479 | 11300 | 18072 | 24 | 18.7 | 17.2 | 11031 | 11062 | 0.3% | 28.3 | 29.8 | 21317 | 21057 | 1.2%
2011-10-31 | 11013 | 211 | 18234 | 14802 | 11124 | 16971 | 0 | 11.6 | 10.7 | 10973 | 11290 | 2.9% | 4.7 | 4 | 18168 | 18676 | 2.8%
2011-11-30 | 11117 | 267 | 19673 | 15440 | 11284 | 17789 | 0 | 7.6 | 3.9 | 11452 | 11738 | 2.5% | 5.6 | -2 | 21347 | 20715 | 3%
2011-12-31 | 12122 | 279 | 20204 | 16293 | 11974 | 18902 | 4 | 1.3 | -0.9 | 12314 | 12852 | 4.4% | -1.3 | -8.4 | 20772 | 21929 | 5.6%
2012-01-31 | 12715 | 290 | 21847 | 17090 | 12439 | 19423 | 31 | -0.8 | -4.6 | 12932 | 13419 | 3.8% | -14.3 | -13.5 | 22085 | 22322 | 1.1%
2012-02-29 | 11610 | 260 | 19956 | 16681 | 13228 | 18709 | 0 | 0.4 | -3.8 | 11380 | 12336 | 8.4% | 1.3 | -13.5 | 20757 | 21981 | 5.9%
2012-03-31 | 11488 | 304 | 20332 | 15440 | 11250 | 17580 | 2 | 7.9 | 0.6 | 11726 | 12387 | 5.6% | -2.8 | -5.5 | 20595 | 20829 | 1.1%
2012-04-30 | 10641 | 287 | 17874 | 14780 | 11248 | 16598 | 0 | 8.6 | 7.6 | 10883 | 10950 | 0.6% | 4.1 | 0.2 | 19830 | 18818 | 5.1%
2012-05-31 | 11137 | 274 | 21106 | 14969 | 10998 | 17581 | 13 | 18 | 14.6 | 10839 | 11034 | 1.8% | 28.6 | 28.4 | 19737 | 19123 | 3.1%
2012-06-30 | 11800 | 280 | 24107 | 16389 | 11017 | 20405 | 94 | 21.8 | 19.1 | 11511 | 11460 | 0.4% | 34.2 | 31.3 | 22832 | 22741 | 0.4%
2012-07-31 | 13457 | 225 | 24636 | 18087 | 12425 | 22075 | 212 | 25.6 | 23.1 | 13058 | 12374 | 5.2% | 36.2 | 30.9 | 23630 | 23411 | 0.9%
2012-08-31 | 12633 | 218 | 23188 | 16980 | 11676 | 20667 | 109 | 23 | 22.6 | 12373 | 12472 | 0.8% | 30.1 | 30.8 | 22727 | 23104 | 1.7%
2012-09-30 | 11041 | 216 | 21183 | 15334 | 11012 | 18710 | 23 | 17.6 | 18 | 10900 | 10883 | 0.2% | 27.1 | 29.8 | 20370 | 20754 | 1.9%
2012-10-31 | 11142 | 278 | 18829 | 14976 | 11436 | 16975 | 0 | 11.1 | 11.9 | 11150 | 11218 | 0.6% | 4.3 | 4 | 18684 | 18446 | 1.3%
2012-11-30 | 11487 | 271 | 20144 | 15954 | 11824 | 18350 | 2 | 4.3 | 5.2 | 11663 | 11628 | 0.3% | -3.7 | -2 | 20258 | 20690 | 2.1%
2012-12-29 | 12157 | 285 | 20382 | 17466 | 12670 | 18765 | 10 | 1.4 | 0 | 12307 | 12620 | 2.5% | -1 | -8.4 | 20911 | 21728 | 3.9%
2013-01-31 | 12890 | 301 | 22610 | 16275 | 12270 | 20124 | 83 | -1.8 | -5.3 | 13061 | 13366 | 2.3% | -11.6 | -13.5 | 22610 | 22098 | 2.3%
2013-02-28 | 11742 | 289 | 21426 | 17474 | 13638 | 19633 | 39 | -3.6 | -3.2 | 11669 | 11839 | 1.5% | -5.8 | -13.5 | 21333 | 21840 | 2.4%
2013-03-31 | 11958 | 353 | 19825 | 16073 | 11963 | 18101 | 0 | 1 | 0.9 | 11870 | 12285 | 3.5% | -1.8 | -5.5 | 20784 | 20674 | 0.5%
2013-04-30 | 10945 | 489 | 18854 | 15201 | 11209 | 17186 | 0 | 7 | 7.6 | 11090 | 11000 | 0.8% | 2.3 | 0.2 | 19285 | 18521 | 4%
2013-05-31 | 10785 | 363 | 20488 | 14497 | 10765 | 16611 | 4 | 16.5 | 14.7 | 10534 | 10895 | 3.4% | 29.9 | 28.4 | 18342 | 19127 | 4.3%
2013-06-30 | 11175 | 290 | 22662 | 15520 | 10816 | 18354 | 43 | 20 | 19.4 | 11283 | 11321 | 0.3% | 31.6 | 31.3 | 22719 | 22543 | 0.8%
2013-07-31 | 12723 | 357 | 24927 | 17100 | 11506 | 21288 | 123 | 23.2 | 23.4 | 12736 | 12381 | 2.8% | 34.3 | 30.9 | 24352 | 23251 | 4.5%
2013-08-31 | 12100 | 399 | 22833 | 16264 | 11139 | 20243 | 85 | 22.1 | 22.4 | 12085 | 12130 | 0.4% | 28.2 | 30.8 | 23255 | 22394 | 3.7%
2013-09-30 | 10837 | 336 | 22682 | 15052 | 11003 | 17400 | 21 | 17.3 | 17.9 | 10767 | 10940 | 1.6% | 33.9 | 29.8 | 20422 | 20462 | 0.2%
2013-10-31 | 11136 | 352 | 18445 | 14967 | 11018 | 17040 | 0 | 11.8 | 11.5 | 11114 | 11233 | 1.1% | 6.6 | 4 | 18981 | 18381 | 3.2%
2013-11-30 | 11641 | 422 | 20615 | 16168 | 11571 | 18660 | 9 | 2.5 | 5.2 | 11710 | 11554 | 1.3% | -3.3 | -2 | 20035 | 20314 | 1.4%
2013-12-31 | 12702 | 329 | 21964 | 17073 | 12626 | 19937 | 66 | -3.5 | -0.5 | 12529 | 12659 | 1% | -8.3 | -8.4 | 21185 | 21394 | 1%
2014-01-31 | 13614 | 401 | 22774 | 18298 | 13381 | 20876 | 172 | -7.9 | -5 | 13410 | 13419 | 0.1% | -17.4 | -13.5 | 22044 | 22280 | 1.1%
2014-02-28 | 12067 | 337 | 21905 | 17957 | 13981 | 20113 | 76 | -7.1 | -3.1 | 11813 | 11794 | 0.2% | -12.2 | -13.5 | 21218 | 21026 | 0.9%
2014-03-31 | 12672 | 436 | 21656 | 17032 | 13296 | 19185 | 26 | -2.9 | 1.1 | 12242 | 12099 | 1.2% | -12.1 | -5.5 | 20728 | 19966 | 3.7%
2014-04-30 | 10837 | 478 | 18557 | 15051 | 11944 | 17048 | 0 | 7.3 | 7.6 | 11039 | 10749 | 2.6% | -0.9 | 0.2 | 19250 | 17659 | 8.3%
2014-05-31 | 10643 | 485 | 18844 | 14305 | 10719 | 16260 | 0 | 15.4 | 14.9 | 10546 | 10795 | 2.4% | 29.4 | 28.4 | 18750 | 18968 | 1.2%
2014-06-30 | 11229 | 468 | 20807 | 15595 | 10723 | 18696 | 8 | 21.1 | 19.6 | 11141 | 11459 | 2.9% | 30.3 | 31.3 | 20705 | 22475 | 8.5%
2014-07-31 | 11717 | 448 | 21300 | 15749 | 11321 | 18362 | 26 | 21.5 | 23.5 | 12325 | 12327 | 0% | 29.8 | 30.9 | 22295 | 22964 | 3%
2014-08-31 | 11718 | 386 | 21363 | 15750 | 11362 | 18644 | 11 | 21.3 | 22.2 | 11819 | 11904 | 0.7% | 31.3 | 30.8 | 21644 | 21420 | 1%
2014-09-30 | 10837 | 424 | 21123 | 15051 | 11112 | 17826 | 12 | 18 | 17.9 | 10671 | 10643 | 0.3% | 31.4 | 29.8 | 19449 | 19020 | 2.2%
2014-10-31 | 10820 | 439 | 17784 | 14543 | 10769 | 16659 | 0 | 11.7 | 11.2 | 10814 | 11212 | 3.7% | 9.1 | 4 | 18447 | 18563 | 0.6%
2014-11-30 | 11488 | 408 | 20102 | 15955 | 12082 | 18256 | 2 | 2.3 | 5.1 | 11410 | 11599 | 1.7% | 0.8 | -2 | 19923 | 20319 | 2%
2014-12-31 | 12132 | 426 | 20938 | 16306 | 11398 | 19037 | 17 | 0.5 | -1.1 | 12256 | 12776 | 4.2% | -1.2 | -8.4 | 21583 | 21169 | 1.9%
2015-01-31 | 13120 | 463 | 21814 | 17634 | 13344 | 20100 | 84 | -6.7 | -4.6 | 12937 | 13090 | 1.2% | -15.7 | -13.5 | 21503 | 22238 | 3.4%
2015-02-28 | 12302 | 400 | 21494 | 18307 | 14588 | 20279 | 103 | -11.4 | -3.1 | 11741 | 11557 | 1.6% | -15.8 | -13.5 | 19710 | 20946 | 6.3%
2015-03-31 | 12045 | 496 | 20827 | 16189 | 12675 | 18117 | 5 | -0.6 | 1.2 | 11748 | 11874 | 1.1% | -9.6 | -5.5 | 20110 | 19842 | 1.3%
2015-04-30 | 10405 | 654 | 18462 | 14451 | 10975 | 16390 | 0 | 8.6 | 7.8 | 10625 | 10569 | 0.5% | 2.4 | 0.2 | 19363 | 18100 | 6.5%
2015-05-31 | 10547 | 531 | 19158 | 14176 | 10657 | 16588 | 0 | 17.8 | 15 | 10232 | 10673 | 4.3% | 28.8 | 28.4 | 17882 | 19384 | 8.4%
2015-06-30 | 10624 | 579 | 19339 | 14756 | 10804 | 17221 | 0 | 19 | 20.1 | 10909 | 11471 | 5.2% | 25.5 | 31.3 | 20555 | 22333 | 8.7%
2015-07-31 | 12105 | 523 | 22516 | 16270 | 11010 | 19757 | 62 | 23.1 | 23.4 | 12274 | 12244 | 0.2% | 32.5 | 30.9 | 22639 | 22965 | 1.4%
2015-08-31 | 11797 | 473 | 22383 | 15856 | 11414 | 19007 | 47 | 21.8 | 22.2 | 11783 | 11899 | 1% | 32.1 | 30.8 | 22383 | 21546 | 3.7%
2015-09-30 | 11362 | 505 | 22063 | 15780 | 10927 | 19813 | 62 | 20.8 | 17.9 | 10719 | 10558 | 1.5% | 32.6 | 29.8 | 19300 | 18508 | 4.1%
2015-10-31 | 10687 | 498 | 17667 | 14365 | 10539 | 16384 | 0 | 10.8 | 10.9 | 10732 | 11133 | 3.7% | 13.1 | 4 | 18444 | 18303 | 0.8%
2015-11-30 | 10682 | 478 | 19239 | 14836 | 11338 | 17157 | 0 | 7.5 | 4.8 | 10868 | 11622 | 6.9% | 1.9 | -2 | 19632 | 20300 | 3.4%
2015-12-31 | 11314 | 437 | 19161 | 15207 | 10811 | 17642 | 0 | 4.8 | -1.4 | 11785 | 12679 | 7.6% | 6.8 | -8.4 | 20418 | 21070 | 3.2%
2016-01-31 | 12385 | 473 | 20836 | 16646 | 12116 | 19066 | 25 | -2.6 | -4.2 | 12524 | 13085 | 4.5% | -11.8 | -13.5 | 21250 | 22376 | 5.3%
2016-02-29 | 11472 | 479 | 20766 | 16482 | 12533 | 18708 | 5 | -1.2 | -2.9 | 11503 | 11889 | 3.4% | -10 | -13.5 | 20195 | 20987 | 3.9%
2016-03-31 | 11303 | 531 | 20063 | 15192 | 11717 | 17387 | 1 | 3.6 | 1.1 | 11446 | 11818 | 3.3% | -7.9 | -5.5 | 20325 | 20017 | 1.5%
2016-04-30 | 10410 | 662 | 17821 | 14458 | 11286 | 16583 | 0 | 6 | 8.5 | 10579 | 10393 | 1.8% | 0.6 | 0.2 | 18912 | 17456 | 7.7%
2016-05-31 | 10471 | 666 | 19885 | 14074 | 10461 | 17171 | 0 | 16 | 15.5 | 10116 | 10622 | 5% | 27.2 | 28.4 | 19708 | 19284 | 2.1%
2016-06-30 | 11102 | 614 | 21692 | 15419 | 10596 | 18447 | 24 | 21.5 | 20.6 | 11141 | 11407 | 2.4% | 34 | 31.3 | 21569 | 22351 | 3.6%
2016-07-31 | 12498 | 548 | 22659 | 16798 | 10985 | 20860 | 144 | 25.1 | 23 | 12345 | 11889 | 3.7% | 35 | 30.9 | 22289 | 22612 | 1.4%
2016-08-31 | 13113 | 535 | 23100 | 17625 | 12287 | 21279 | 184 | 25.4 | 22.4 | 12296 | 11768 | 4.3% | 34.8 | 30.8 | 22376 | 21414 | 4.3%
2016-09-30 | 11072 | 526 | 23213 | 15378 | 10855 | 18825 | 42 | 20.7 | 17.2 | 10659 | 10403 | 2.4% | 34.5 | 29.8 | 19713 | 18300 | 7.2%
2016-10-31 | 10519 | 418 | 18189 | 14138 | 10663 | 16351 | 0 | 12.6 | 10.7 | 10453 | 10918 | 4.4% | 5.2 | 4 | 18395 | 18147 | 1.3%
2016-11-30 | 10698 | 424 | 19369 | 14858 | 11211 | 17155 | 0 | 7.5 | 3.9 | 10914 | 11504 | 5.4% | 0.2 | -2 | 19545 | 20383 | 4.3%
2016-12-31 | 11978 | 440 | 20688 | 16100 | 11684 | 18666 | 10 | -1.1 | -1.3 | 11951 | 12410 | 3.8% | -8.1 | -8.4 | 20287 | 20896 | 3%
2017-01-31 | 12108 | 470 | 20372 | 16274 | 12246 | 18425 | 2 | -1.1 | -4.5 | 12370 | 12852 | 3.9% | -3.3 | -13.5 | 20966 | 22032 | 5.1%
2017-02-28 | 10608 | 494 | 19838 | 15785 | 11867 | 18065 | 0 | 0.5 | -3 | 10787 | 11329 | 5% | -1.1 | -13.5 | 20379 | 21029 | 3.2%
2017-03-31 | 11591 | 562 | 19174 | 15579 | 12158 | 17608 | 0 | 0.5 | 1.5 | 11413 | 11835 | 3.7% | -8.1 | -5.5 | 18692 | 20147 | 7.8%
2017-04-30 | 9789 | 596 | 17349 | 13595 | 10167 | 15576 | 0 | 10.6 | 8.7 | 10106 | 10357 | 2.5% | 7.3 | 0.2 | 18483 | 17958 | 2.8%
2017-05-31 | 10153 | 621 | 17738 | 13647 | 10249 | 15623 | 0 | 13.5 | 15.8 | 10013 | 10569 | 5.6% | 29.6 | 28.4 | 18260 | 19182 | 5%
2017-06-30 | 10657 | 580 | 21168 | 14802 | 10518 | 17663 | 7 | 20.6 | 20.5 | 10683 | 11177 | 4.6% | 32.4 | 31.3 | 21145 | 22411 | 6%
2017-07-31 | 11588 | 584 | 20627 | 15575 | 10806 | 19029 | 17 | 22.8 | 23.1 | 11852 | 11969 | 1% | 31.5 | 30.9 | 22153 | 22540 | 1.7%
2017-08-31 | 11350 | 560 | 20158 | 15255 | 10829 | 18578 | 5 | 21.2 | 22.4 | 11514 | 12085 | 5% | 30 | 30.8 | 21323 | 22344 | 4.8%
2017-09-30 | 10679 | 485 | 21786 | 14832 | 10487 | 18796 | 25 | 20 | 16.9 | 10156 | 10497 | 3.4% | 31.3 | 29.8 | 17821 | 19398 | 8.8%
2017-10-31 | 10339 | 535 | 17418 | 13897 | 10534 | 15858 | 0 | 14.5 | 10.4 | 10260 | 10928 | 6.5% | 26.5 | 4 | 17408 | 18060 | 3.7%
2017-11-30 | 10956 | 499 | 19115 | 15217 | 11199 | 17381 | 0 | 4.6 | 3.9 | 10947 | 11381 | 4% | 3 | -2 | 19195 | 20292 | 5.7%
2017-12-31 | 12339 | 405 | 20306 | 16585 | 12093 | 18876 | 6 | -4.2 | -1.3 | 12096 | 12296 | 1.7% | -4.1 | -8.4 | 21440 | 20904 | 2.5%
2018-01-31 | 12701 | 535 | 20906 | 17071 | 12453 | 19338 | 15 | -4.6 | -4.9 | 12680 | 12766 | 0.7% | -15.2 | -13.5 | 20178 | 21702 | 7.6%
2018-02-28 | 10951 | 497 | 20076 | 16296 | 12716 | 18609 | 1 | -0.7 | -2.9 | 11081 | 11141 | 0.5% | -8.2 | -13.5 | 20042 | 20299 | 1.3%
2018-03-31 | 11372 | 598 | 18462 | 15286 | 12158 | 17160 | 0 | 0.9 | 2.2 | 11267 | 11462 | 1.7% | 0.2 | -5.5 | 19331 | 19631 | 1.6%
2018-04-30 | 10578 | 588 | 18011 | 14692 | 11497 | 16647 | 0 | 4.4 | 8.9 | 10586 | 10192 | 3.7% | 2.4 | 0.2 | 18108 | 17758 | 1.9%
2018-05-31 | 10421 | 666 | 20473 | 14007 | 10541 | 16770 | 10 | 18.4 | 15.7 | 10081 | 10317 | 2.3% | 30.7 | 28.4 | 19262 | 18905 | 1.9%
2018-06-30 | 10923 | 604 | 21369 | 15171 | 10698 | 18437 | 37 | 20.8 | 20.7 | 10980 | 10876 | 0.9% | 30.2 | 31.3 | 20627 | 21977 | 6.5%
2018-07-31 | 12686 | 520 | 22909 | 17051 | 11413 | 20705 | 141 | 24.6 | 23.3 | 12484 | 11667 | 6.5% | 33.2 | 30.9 | 22409 | 22085 | 1.4%
2018-08-31 | 12689 | 534 | 21990 | 17055 | 11966 | 20623 | 121 | 24.2 | 22.3 | 12041 | 11706 | 2.8% | 31.7 | 30.8 | 21386 | 21973 | 2.7%
2018-09-30 | 11147 | 483 | 23240 | 15482 | 10701 | 19597 | 57 | 19.9 | 16.9 | 10579 | 10146 | 4.1% | 33.9 | 29.8 | 19506 | 19013 | 2.5%
2018-10-31 | 10717 | 489 | 18205 | 14405 | 10847 | 16419 | 0 | 9.9 | 9.9 | 10527 | 10709 | 1.7% | 26.1 | 4 | 17751 | 17810 | 0.3%
2018-11-30 | 11360 | 425 | 20152 | 15778 | 11765 | 17927 | 1 | 2.1 | 3.8 | 11185 | 11116 | 0.6% | -6.6 | -2 | 19266 | 19792 | 2.7%
2018-12-31 | 11939 | 410 | 19891 | 16047 | 12284 | 18215 | 0 | 0.5 | -1.5 | 12020 | 11891 | 1.1% | -1.4 | -8.4 | 20375 | 20481 | 0.5%
2019-01-31 | 12777 | 466 | 21525 | 17174 | 12291 | 19588 | 42 | -5.9 | -5.1 | 12689 | 12820 | 1% | -11.8 | -13.5 | 21058 | 21389 | 1.6%
2019-02-28 | 11292 | 458 | 20500 | 16803 | 13041 | 19051 | 9 | -3.4 | -2.8 | 11212 | 11110 | 0.9% | -10.1 | -13.5 | 20420 | 20017 | 2%
2019-03-31 | 11659 | 591 | 20263 | 15670 | 12210 | 17519 | 2 | 0 | 2.7 | 11458 | 11473 | 0.1% | -9 | -5.5 | 19574 | 19443 | 0.7%
2019-04-30 | 10265 | 599 | 17645 | 14256 | 11079 | 16134 | 0 | 7.3 | 9.2 | 10432 | 10233 | 1.9% | 2.8 | 0.2 | 18796 | 17581 | 6.5%
2019-05-31 | 10220 | 577 | 16784 | 13736 | 10328 | 15587 | 0 | 13 | 15.7 | 10219 | 10394 | 1.7% | 8.2 | 28.4 | 17977 | 18655 | 3.8%
2019-06-30 | 10366 | 602 | 20248 | 14397 | 10564 | 17337 | 3 | 19.5 | 20.7 | 10609 | 10920 | 2.9% | 28.9 | 31.3 | 21239 | 21583 | 1.6%
2019-07-31 | 12793 | 608 | 21791 | 17195 | 11565 | 20646 | 146 | 24.6 | 23.4 | 12446 | 11862 | 4.7% | 31.4 | 30.9 | 21121 | 22041 | 4.4%
2019-08-31 | 11825 | 557 | 21354 | 15894 | 11280 | 19306 | 41 | 22.4 | 22 | 11799 | 11646 | 1.3% | 30.2 | 30.8 | 22490 | 21431 | 4.7%
2019-09-30 | 10319 | 486 | 19717 | 14331 | 10477 | 16722 | 0 | 18.7 | 16.7 | 10168 | 10296 | 1.3% | 28.6 | 29.8 | 18959 | 19072 | 0.6%
2019-10-31 | 10351 | 508 | 18329 | 13913 | 10739 | 15950 | 0 | 11.8 | 9.7 | 10447 | 10730 | 2.7% | 31.2 | 4 | 18815 | 17572 | 6.6%
2019-11-30 | 11255 | 454 | 19625 | 15632 | 11711 | 17850 | 0 | 1.6 | 3.8 | 11094 | 11146 | 0.5% | -4.1 | -2 | 19002 | 19677 | 3.6%
2019-12-31 | 11997 | 450 | 20974 | 16125 | 11787 | 18658 | 11 | -0.2 | -1.7 | 12094 | 12092 | 0% | -7.8 | -8.4 | 20974 | 20370 | 2.9%
2020-01-31 | 12179 | 429 | 19928 | 16369 | 12353 | 18558 | 0 | -0.8 | -5 | 12461 | 12879 | 3.4% | -8.5 | -13.5 | 21138 | 21135 | 0%
2020-02-29 | 11240 | 493 | 19630 | 16149 | 12683 | 18163 | 0 | -2 | -3 | 11253 | 11595 | 3% | -10.4 | -13.5 | 19776 | 19822 | 0.2%
2020-03-31 | 10989 | 589 | 18183 | 14771 | 11120 | 16703 | 0 | 4.2 | 1.2 | 11058 | 11524 | 4.2% | 5.4 | -5.5 | 19681 | 19277 | 2.1%
2020-04-30 | 9283 | 647 | 15350 | 12893 | 10379 | 14231 | 0 | 7 | 7.8 | 9383 | 10243 | 9.2% | 4.4 | 0.2 | 16516 | 17294 | 4.7%
2020-05-31 | 9642 | 674 | 20649 | 12960 | 9831 | 15247 | 4 | 13.4 | 15 | 9306 | 10046 | 7.9% | 30.6 | 28.4 | 18761 | 18173 | 3.1%
2020-06-30 | 10800 | 640 | 21292 | 15000 | 10340 | 18997 | 21 | 22.1 | 20.1 | 10597 | 10918 | 3% | 31.2 | 31.3 | 20742 | 21035 | 1.4%
2020-07-31 | 13203 | 620 | 24446 | 17746 | 12154 | 21827 | 188 | 26.2 | 23.4 | 12530 | 11926 | 4.8% | 34 | 30.9 | 24058 | 22251 | 7.5%
2020-08-31 | 12081 | 583 | 23823 | 16238 | 11221 | 20134 | 83 | 23.2 | 22.2 | 12338 | 11562 | 6.3% | 31.9 | 30.8 | 25318 | 21456 | 15.3%
2020-09-30 | 10114 | 555 | 20225 | 14048 | 10834 | 16341 | 1 | 17.9 | 17.9 | 10011 | 10352 | 3.4% | 27.4 | 29.8 | 19254 | 19325 | 0.4%
2020-10-31 | 10339 | 532 | 17679 | 13897 | 10645 | 16043 | 0 | 10.4 | 10.9 | 10350 | 10294 | 0.5% | 7 | 4 | 17587 | 17038 | 3.1%
2020-11-30 | 10529 | 527 | 19147 | 14624 | 10808 | 17009 | 0 | 7.8 | 4.8 | 10694 | 10779 | 0.8% | 0.1 | -2 | 19416 | 19088 | 1.7%
2020-12-31 | 11812 | 568 | 20738 | 15876 | 12389 | 18200 | 4 | 0.3 | -1.7 | 11933 | 11967 | 0.3% | -6.8 | -8.4 | 20975 | 19907 | 5.1%
2021-01-31 | 12105 | 448 | 20150 | 16270 | 12798 | 18345 | 1 | -2 | -5 | 12308 | 12452 | 1.2% | -8.4 | -13.5 | 20952 | 20857 | 0.5%
2021-02-28 | 11233 | 494 | 20318 | 16716 | 13200 | 18800 | 3 | -4.3 | -3 | 11144 | 10957 | 1.7% | -6.9 | -13.5 | 20175 | 20439 | 1.3%
2021-03-31 | 11102 | 701 | 19344 | 14922 | 11659 | 16933 | 0 | 4.6 | 1.2 | 11250 | 11284 | 0.3% | -0.8 | -5.5 | 19868 | 19044 | 4.1%
2021-04-30 | 9782 | 646 | 16644 | 13586 | 10498 | 15264 | 0 | 9 | 7.8 | 10098 | 10042 | 0.6% | 4.8 | 0.2 | 17619 | 16893 | 4.1%
2021-05-31 | 10086 | 683 | 19443 | 13557 | 10782 | 15777 | 0 | 15.2 | 15 | 9987 | 10112 | 1.2% | 31.6 | 28.4 | 18022 | 18121 | 0.6%
2021-06-30 | 11262 | 609 | 22258 | 15642 | 11304 | 19636 | 60 | 23 | 20.1 | 10841 | 10745 | 0.9% | 31.6 | 31.3 | 21528 | 21996 | 2.2%
2021-07-31 | 11636 | 671 | 21655 | 15640 | 11108 | 19488 | 50 | 22.2 | 23.4 | 11971 | 11860 | 0.9% | 31.7 | 30.9 | 22251 | 22502 | 1.1%
2021-08-31 | 12857 | 686 | 22986 | 17280 | 10853 | 21313 | 189 | 24.8 | 22.2 | 12072 | 11702 | 3.1% | 33.1 | 30.8 | 21854 | 22292 | 2%
2021-09-30 | 10389 | 553 | 18769 | 14429 | 10426 | 16782 | 0 | 18.7 | 17.9 | 10401 | 10472 | 0.7% | 26 | 29.8 | 18980 | 21256 | 12%
2021-10-31 | 10516 | 532 | 17312 | 14135 | 10779 | 16117 | 0 | 14.3 | 10.9 | 10429 | 10408 | 0.2% | 22 | 4 | 17607 | 17244 | 2.1%
2021-11-30 | 10957 | 524 | 19644 | 15218 | 11605 | 17496 | 0 | 4.7 | 4.8 | 11017 | 10897 | 1.1% | 0.2 | -2 | 19685 | 19275 | 2.1%
2021-12-31 | 11970 | 480 | 20455 | 16088 | 12517 | 18343 | 3 | 2 | -1.7 | 12186 | 11973 | 1.7% | -2.3 | -8.4 | 21332 | 20113 | 5.7%
2022-01-31 | 13085 | 530 | 21349 | 17588 | 12491 | 19797 | 55 | -7 | -5 | 12929 | 12533 | 3.1% | -12.1 | -13.5 | 21334 | 20939 | 1.9%
2022-02-28 | 11488 | 569 | 20918 | 17095 | 13761 | 19171 | 14 | -3.5 | -3 | 11401 | 11205 | 1.7% | -9.8 | -13.5 | 20782 | 20359 | 2%
2022-03-31 | 11817 | 681 | 19763 | 15883 | 12285 | 17932 | 0 | 1.9 | 1.2 | 11794 | 11617 | 1.5% | -5.2 | -5.5 | 19941 | 19442 | 2.5%
2022-04-30 | 10265 | 750 | 17256 | 14257 | 11430 | 16016 | 0 | 7.5 | 7.8 | 10311 | 10239 | 0.7% | 6.6 | 0.2 | 17752 | 17260 | 2.8%
2022-05-31 | 10470 | 732 | 21292 | 14072 | 10485 | 16297 | 9 | 17 | 15 | 10138 | 10391 | 2.5% | 32.2 | 28.4 | 20136 | 18271 | 9.3%
2022-06-30 | 10930 | 707 | 21954 | 15180 | 10627 | 18995 | 43 | 21.1 | 20.1 | 11002 | 10980 | 0.2% | 34.6 | 31.3 | 22102 | 22173 | 0.3%
2022-07-31 | 12344 | 640 | 22607 | 16591 | 11449 | 20039 | 77 | 24.1 | 23.4 | 12411 | 11891 | 4.2% | 34.2 | 30.9 | 22485 | 22548 | 0.3%
2022-08-31 | 12624 | 651 | 21871 | 16968 | 11830 | 20450 | 100 | 23.7 | 22.2 | 11999 | 12021 | 0.2% | 30.5 | 30.8 | 23478 | 22409 | 4.6%
2022-09-30 | 10814 | 493 | 20350 | 15020 | 11082 | 17965 | 3 | 18.7 | 17.9 | 10678 | 10507 | 1.6% | 29.2 | 29.8 | 20446 | 21392 | 4.6%
2022-10-31 | 10384 | 564 | 17294 | 13957 | 10820 | 15961 | 0 | 11.6 | 10.9 | 10447 | 10568 | 1.2% | 8.9 | 4 | 17725 | 17516 | 1.2%
2022-11-30 | 11044 | 490 | 19441 | 15339 | 10931 | 17734 | 0 | 6.1 | 4.8 | 11128 | 11121 | 0.1% | -3.6 | -2 | 19390 | 19741 | 1.8%
2022-12-31 | 12273 | 461 | 20173 | 16496 | 12417 | 18629 | 2 | 0.2 | -1.7 | 12413 | 12162 | 2% | 0.8 | -8.4 | 20585 | 20190 | 1.9%
2023-01-31 | 12519.712 | 380.2626 | 20486 | 16827.5699 | 12603 | 18821.9 | 4.464 | 8.3011 | -4.9516 | 13052.768 | 12723.9641 | 2.519% | 8 | -13.5 | 23733.3437 | 21235.1116 | 10.53%
2023-02-28 | 11225.17 | 507.5833 | 21388 | 16704.122 | 12990 | 19014 | 10.08 | -0.72976 | -3.008 | 11325.8235 | 11427.998 | 0.9021% | -15.5 | -13.5 | 20433.0112 | 20962.1116 | 2.589%
2023-03-31 | 11846.269 | 631.3624 | 18811 | 15922.4046 | 12940 | 17656 | 0 | 1.6882 | 1.1677 | 11814.7494 | 11912.6161 | 0.8283% | -0.1 | -5.5 | 19000.8853 | 19789.6832 | 4.151%
2023-04-30 | 10271.638 | 593.2414 | 17547 | 14266.1639 | 11117 | 15920.1 | 0 | 10.0411 | 7.8322 | 10374.8437 | 10393.9477 | 0.1841% | 5.4 | 0.2 | 19103.3719 | 17851.3335 | 6.554%
2023-05-31 | 10356.75 | 678.8373 | 20787 | 13920.3629 | 10859 | 15783.1 | 5.208 | 15.1742 | 15.028 | 10473.6584 | 10463.3841 | 0.0981% | 29.9 | 28.4 | 18001.5877 | 18926.3335 | 5.137%
2023-06-30 | 11119.814 | 599.734 | 21463 | 15444.1861 | 11438 | 18666.1 | 23.04 | 20.5444 | 20.0656 | 11230.6805 | 10693.8855 | 4.78% | 31.6 | 31.3 | 22417.4764 | 21951.3335 | 2.079%
2023-07-31 | 12507.785 | 591.5725 | 22686 | 16811.539 | 11987 | 20318.4 | 102.672 | 23.3629 | 23.3957 | 12455.0186 | 11858.9002 | 4.786% | 30.95 | 30.9 | 23368.3724 | 22445.9996 | 3.947%
2023-08-31 | 11828.62 | 581 | 21364 | 15898.6828 | 11629 | 18779.7 | 17.856 | 13.4688 | 22.1688 | 12005.3253 | 12249.9171 | 2.037% | 29.1 | 30.8 | 21865.1956 | 22396.9996 | 2.432%
2023-09-30 | 10997.556 | 495.1681 | 23713 | 15274.3833 | 11402 | 18088.3 | 43.92 | 19.6733 | 17.8533 | 10685.1004 | 10718.9739 | 0.317% | 32.1 | 29.8 | 21317.3942 | 21479.9996 | 0.7628%
2023-10-31 | 10932.34 | 461.1317 | 20849 | 14694.0054 | 11260 | 16853.6 | 5.952 | 13.4688 | 10.9495 | 10757.1302 | 10593.967 | 1.517% | 30 | 4 | 19208.5675 | 17668.0452 | 8.02%
2023-11-30 | 11456.562 | 487.1772 | 20579 | 15911.8917 | 12555 | 18103 | 2.88 | 1.231 | 4.7844 | 11478.5016 | 11007.299 | 4.105% | -1.5 | -2 | 20453.2108 | 19742.0453 | 3.477%
2023-12-31 | 12065.5 | 428.8085 | 20004 | 16217.0699 | 12029 | 18506.6 | 0.744 | 3.0699 | -1.6505 | 12384.2261 | 12018.94 | 2.95% | 3 | -8.4 | 21211.1571 | 20346.0453 | 4.079%
2024-01-31 | 12932.636 | 436.294 | 20880 | 17382.5753 | 13500 | 19526.1 | 26.04 | -1.8882 | -4.9516 | 13105.3696 | 12929.406 | 1.343% | -9 | -13.5 | 21204.4347 | 21418.2553 | 1.008%
2024-02-29 | 11437.175 | 515.7809 | 19703 | 16432.7227 | 12854 | 18418 | 0 | 1.231 | -3.008 | 11650.3599 | 11956.6273 | 2.629% | -1 | -13.5 | 20151.4548 | 20987.7553 | 4.15%
Back to main menu

## Table 3.3.3
Back to main menu
Table 3.3.3: Monthly Consumption by Market Participant Type
| Monthly Energy Demand (GWh) |  |  |  |  | Monthly Peak Demand (MW)
Month | Energy Demand | LDC Consumption | Wholesale Consumption | Generator Consumption | Losses | Peak Demand | LDC Consumption | Wholesale Consumption | Generator Consumption | Losses
2002-05-31 | 11875 | 9467 | 2082 | 140 | 186 | 20068 | 16708 | 2841 | 158 | 361
2002-06-30 | 12185 | 9864 | 2012 | 135 | 175 | 23578 | 20429 | 2643 | 138 | 368
2002-07-31 | 14033 | 11576 | 2019 | 150 | 288 | 25226 | 22064 | 2415 | 135 | 612
2002-08-31 | 13749 | 11167 | 2097 | 177 | 308 | 25414 | 21695 | 2595 | 196 | 928
2002-09-30 | 12593 | 10114 | 2051 | 142 | 286 | 25062 | 21577 | 2561 | 145 | 779
2002-10-31 | 12398 | 9862 | 2137 | 149 | 249 | 21216 | 17642 | 2821 | 142 | 612
2002-11-30 | 12656 | 10127 | 2113 | 144 | 272 | 21862 | 18381 | 2756 | 169 | 556
2002-12-31 | 13484 | 11037 | 2023 | 170 | 253 | 23334 | 19815 | 2741 | 147 | 631
2003-01-31 | 14487 | 11889 | 2188 | 168 | 243 | 24158 | 20779 | 2817 | 155 | 407
2003-02-28 | 13123 | 10716 | 1981 | 156 | 270 | 23469 | 20025 | 2806 | 216 | 422
2003-03-31 | 13414 | 10768 | 2192 | 167 | 286 | 23117 | 19690 | 2886 | 187 | 354
2003-04-30 | 12097 | 9624 | 2089 | 162 | 223 | 21010 | 17771 | 2658 | 197 | 385
2003-05-31 | 11627 | 9166 | 2115 | 144 | 203 | 18741 | 15388 | 2817 | 187 | 349
2003-06-30 | 11885 | 9583 | 1922 | 168 | 212 | 24753 | 21587 | 2263 | 189 | 714
2003-07-31 | 12898 | 10665 | 1836 | 158 | 239 | 23175 | 20435 | 2213 | 162 | 365
2003-08-31 | 12514 | 10341 | 1784 | 170 | 219 | 23891 | 20915 | 2359 | 184 | 433
2003-09-30 | 11794 | 9431 | 1977 | 168 | 218 | 20700 | 17455 | 2612 | 164 | 469
2003-10-31 | 12160 | 9686 | 2067 | 198 | 208 | 20408 | 16887 | 2775 | 299 | 447
2003-11-30 | 12390 | 9948 | 2037 | 176 | 229 | 21584 | 17991 | 2782 | 190 | 621
2003-12-31 | 13328 | 10933 | 1970 | 184 | 241 | 22798 | 19265 | 2834 | 176 | 522
2004-01-31 | 14767 | 12198 | 2104 | 199 | 266 | 24937 | 21481 | 2721 | 264 | 470
2004-02-29 | 13088 | 10673 | 1970 | 178 | 268 | 22608 | 19037 | 2699 | 255 | 616
2004-03-31 | 13225 | 10655 | 2122 | 170 | 278 | 21634 | 18017 | 2626 | 277 | 714
2004-04-30 | 11792 | 9441 | 1966 | 135 | 251 | 19911 | 16644 | 2708 | 178 | 381
2004-05-31 | 11835 | 9343 | 2044 | 155 | 293 | 20327 | 17064 | 2517 | 166 | 581
2004-06-30 | 12046 | 9547 | 2053 | 164 | 281 | 23163 | 19708 | 2663 | 158 | 634
2004-07-31 | 12770 | 10307 | 1967 | 177 | 319 | 23976 | 20506 | 2492 | 166 | 812
2004-08-31 | 12746 | 10241 | 2047 | 178 | 280 | 23159 | 19645 | 2632 | 186 | 696
2004-09-30 | 12370 | 9861 | 2065 | 157 | 287 | 21911 | 18335 | 2713 | 146 | 716
2004-10-31 | 12215 | 9634 | 2154 | 167 | 261 | 19829 | 16246 | 2899 | 159 | 525
2004-11-30 | 12601 | 10046 | 2070 | 188 | 296 | 22066 | 18138 | 2941 | 298 | 688
2004-12-31 | 13982 | 11435 | 2017 | 194 | 336 | 24979 | 21447 | 2662 | 197 | 673
2005-01-31 | 14619 | 12017 | 2090 | 199 | 313 | 24362 | 21030 | 2558 | 209 | 564
2005-02-28 | 12732 | 10393 | 1913 | 153 | 272 | 22322 | 18829 | 2715 | 226 | 552
2005-03-31 | 13494 | 10953 | 2056 | 196 | 290 | 22724 | 19267 | 2706 | 203 | 549
2005-04-30 | 11828 | 9388 | 1980 | 189 | 270 | 19343 | 15821 | 2790 | 261 | 472
2005-05-31 | 11745 | 9333 | 1989 | 175 | 248 | 19007 | 15618 | 2700 | 152 | 537
2005-06-30 | 13499 | 11095 | 1907 | 170 | 327 | 26157 | 22536 | 2563 | 200 | 857
2005-07-31 | 14094 | 11642 | 1879 | 192 | 382 | 26160 | 22580 | 2334 | 242 | 1004
2005-08-31 | 14031 | 11408 | 2030 | 208 | 385 | 25816 | 22244 | 2430 | 216 | 926
2005-09-30 | 12553 | 10025 | 1983 | 197 | 348 | 23914 | 20336 | 2513 | 216 | 849
2005-10-31 | 12187 | 9837 | 1904 | 177 | 269 | 20752 | 17598 | 2427 | 178 | 548
2005-11-30 | 12441 | 10179 | 1832 | 165 | 265 | 22564 | 19415 | 2460 | 173 | 516
2005-12-31 | 13746 | 11401 | 1858 | 197 | 290 | 23766 | 20461 | 2428 | 253 | 624
2006-01-31 | 13596 | 11189 | 1906 | 188 | 314 | 23052 | 19543 | 2540 | 211 | 758
2006-02-28 | 12568 | 10422 | 1719 | 164 | 264 | 22321 | 18801 | 2538 | 239 | 742
2006-03-31 | 13200 | 10803 | 1939 | 174 | 284 | 21772 | 18543 | 2488 | 178 | 563
2006-04-30 | 11513 | 9216 | 1861 | 154 | 282 | 19582 | 16299 | 2557 | 160 | 566
2006-05-31 | 11927 | 9647 | 1868 | 177 | 236 | 24857 | 21656 | 2408 | 238 | 555
2006-06-30 | 12542 | 10216 | 1876 | 193 | 257 | 23349 | 20112 | 2383 | 177 | 677
2006-07-31 | 13854 | 11539 | 1830 | 187 | 297 | 26092 | 22601 | 2399 | 186 | 907
2006-08-31 | 13308 | 10969 | 1904 | 162 | 273 | 27005 | 23709 | 2400 | 171 | 725
2006-09-30 | 11521 | 9386 | 1789 | 159 | 186 | 19976 | 16932 | 2457 | 175 | 411
2006-10-31 | 11962 | 9830 | 1745 | 150 | 237 | 19590 | 16651 | 2371 | 188 | 380
2006-11-30 | 12179 | 10019 | 1735 | 164 | 261 | 21267 | 18187 | 2295 | 204 | 580
2006-12-31 | 12884 | 10733 | 1708 | 162 | 281 | 22941 | 19874 | 2164 | 207 | 695
2007-01-31 | 13758 | 11458 | 1823 | 162 | 315 | 23537 | 20372 | 2394 | 186 | 585
2007-02-28 | 13038 | 11013 | 1620 | 143 | 262 | 23935 | 20829 | 2384 | 165 | 556
2007-03-31 | 13193 | 10932 | 1834 | 179 | 248 | 22969 | 19866 | 2417 | 260 | 426
2007-04-30 | 11828 | 9669 | 1777 | 166 | 217 | 20016 | 16661 | 2684 | 161 | 510
2007-05-31 | 11819 | 9590 | 1804 | 202 | 223 | 21490 | 18257 | 2306 | 237 | 690
2007-06-30 | 12693 | 10503 | 1730 | 186 | 274 | 25737 | 22461 | 2385 | 177 | 713
2007-07-31 | 12841 | 10640 | 1720 | 188 | 293 | 24561 | 21501 | 2264 | 200 | 596
2007-08-31 | 13455 | 11203 | 1742 | 200 | 310 | 25584 | 22472 | 2136 | 233 | 743
2007-09-30 | 11916 | 9815 | 1676 | 184 | 240 | 24046 | 20806 | 2325 | 196 | 719
2007-10-31 | 11908 | 9826 | 1715 | 148 | 218 | 19233 | 16516 | 2203 | 132 | 381
2007-11-30 | 12350 | 10288 | 1677 | 170 | 216 | 21814 | 19071 | 2103 | 159 | 481
2007-12-31 | 13408 | 11284 | 1674 | 171 | 278 | 22935 | 19842 | 2254 | 206 | 633
2008-01-31 | 13610 | 11444 | 1729 | 167 | 271 | 22782 | 19743 | 2260 | 188 | 591
2008-02-29 | 12897 | 10838 | 1634 | 148 | 277 | 23054 | 19969 | 2349 | 165 | 570
2008-03-31 | 13004 | 10838 | 1720 | 173 | 272 | 20990 | 17995 | 2205 | 217 | 573
2008-04-30 | 11520 | 9367 | 1699 | 151 | 302 | 19512 | 16522 | 2327 | 195 | 468
2008-05-31 | 11407 | 9211 | 1733 | 162 | 301 | 18650 | 15592 | 2432 | 171 | 456
2008-06-30 | 12189 | 9971 | 1736 | 170 | 312 | 24195 | 21012 | 2344 | 182 | 658
2008-07-31 | 13156 | 10881 | 1771 | 178 | 326 | 23787 | 20810 | 2201 | 153 | 623
2008-08-31 | 12549 | 10287 | 1787 | 173 | 301 | 22707 | 19448 | 2289 | 232 | 738
2008-09-30 | 11793 | 9611 | 1755 | 170 | 256 | 22975 | 20077 | 2198 | 162 | 538
2008-10-31 | 11634 | 9612 | 1645 | 165 | 213 | 19366 | 16642 | 2072 | 179 | 473
2008-11-30 | 11829 | 9990 | 1418 | 179 | 242 | 21279 | 18309 | 1826 | 228 | 916
2008-12-31 | 13088 | 11171 | 1414 | 191 | 312 | 22541 | 19783 | 1874 | 199 | 685
2009-01-31 | 13730 | 11752 | 1506 | 185 | 288 | 22983 | 20228 | 1948 | 244 | 563
2009-02-28 | 11698 | 10038 | 1243 | 160 | 258 | 22110 | 19489 | 1762 | 191 | 667
2009-03-31 | 12167 | 10357 | 1376 | 158 | 276 | 21466 | 19038 | 1734 | 197 | 497
2009-04-30 | 10747 | 9088 | 1225 | 201 | 232 | 18744 | 16209 | 1774 | 189 | 572
2009-05-31 | 10504 | 8780 | 1252 | 206 | 266 | 17560 | 15162 | 1654 | 290 | 454
2009-06-30 | 10884 | 9217 | 1206 | 189 | 272 | 22540 | 20012 | 1553 | 226 | 750
2009-07-31 | 11315 | 9621 | 1210 | 221 | 263 | 20011 | 17721 | 1495 | 228 | 566
2009-08-31 | 12226 | 10435 | 1302 | 212 | 278 | 24380 | 21685 | 1625 | 326 | 744
2009-09-30 | 10932 | 9278 | 1240 | 178 | 236 | 19731 | 17200 | 1775 | 210 | 546
2009-10-31 | 11182 | 9508 | 1260 | 179 | 235 | 18420 | 16094 | 1662 | 195 | 469
2009-11-30 | 11113 | 9475 | 1262 | 174 | 202 | 19710 | 17406 | 1698 | 197 | 409
2009-12-31 | 12689 | 10947 | 1225 | 204 | 313 | 21831 | 19291 | 1711 | 217 | 612
2010-01-31 | 13145 | 11330 | 1309 | 225 | 282 | 22045 | 19479 | 1825 | 239 | 502
2010-02-28 | 11752 | 10068 | 1248 | 172 | 263 | 21367 | 18884 | 1763 | 256 | 464
2010-03-31 | 11686 | 9928 | 1347 | 179 | 233 | 19393 | 16832 | 1781 | 222 | 558
2010-04-30 | 10475 | 8748 | 1306 | 201 | 219 | 17398 | 15030 | 1775 | 296 | 297
2010-05-31 | 11368 | 9536 | 1350 | 185 | 297 | 22904 | 20039 | 1886 | 228 | 751
2010-06-30 | 11556 | 9798 | 1335 | 175 | 248 | 21527 | 19057 | 1848 | 132 | 490
2010-07-31 | 13307 | 11458 | 1359 | 196 | 295 | 25075 | 22713 | 1582 | 159 | 621
2010-08-31 | 12922 | 11047 | 1380 | 227 | 268 | 24917 | 21904 | 1812 | 229 | 971
2010-09-30 | 11049 | 9272 | 1364 | 223 | 190 | 24444 | 21858 | 1676 | 239 | 671
2010-10-31 | 10929 | 9167 | 1416 | 195 | 152 | 17704 | 15174 | 1945 | 229 | 356
2010-11-30 | 11304 | 9632 | 1343 | 197 | 132 | 19970 | 17340 | 1920 | 234 | 475
2010-12-31 | 12694 | 10968 | 1333 | 214 | 179 | 22114 | 19730 | 1749 | 252 | 383
2011-01-31 | 13302 | 11431 | 1397 | 228 | 245 | 22733 | 19938 | 1798 | 258 | 739
2011-02-28 | 11775 | 10128 | 1258 | 199 | 190 | 21871 | 19082 | 1932 | 277 | 580
2011-03-31 | 12352 | 10488 | 1406 | 202 | 256 | 20667 | 17996 | 1925 | 237 | 509
2011-04-30 | 10789 | 9101 | 1314 | 195 | 179 | 17945 | 15383 | 1839 | 222 | 501
2011-05-31 | 10782 | 9047 | 1317 | 205 | 213 | 20847 | 18581 | 1505 | 254 | 508
2011-06-30 | 11238 | 9545 | 1219 | 195 | 280 | 22765 | 20342 | 1415 | 253 | 755
2011-07-31 | 13298 | 11449 | 1313 | 208 | 329 | 25450 | 23323 | 1198 | 204 | 725
2011-08-31 | 12532 | 10718 | 1371 | 192 | 251 | 22051 | 19563 | 1721 | 249 | 518
2011-09-30 | 11145 | 9377 | 1367 | 174 | 226 | 21552 | 19001 | 1771 | 181 | 599
2011-10-31 | 11013 | 9287 | 1366 | 151 | 208 | 18234 | 15872 | 1827 | 178 | 358
2011-11-30 | 11117 | 9428 | 1308 | 148 | 232 | 19673 | 17155 | 1837 | 219 | 462
2011-12-31 | 12122 | 10413 | 1296 | 185 | 229 | 20204 | 17926 | 1726 | 223 | 329
2012-01-31 | 12715 | 10948 | 1363 | 186 | 219 | 21847 | 19151 | 1791 | 309 | 596
2012-02-29 | 11610 | 9923 | 1283 | 163 | 241 | 19956 | 17274 | 1856 | 237 | 589
2012-03-31 | 11488 | 9660 | 1406 | 197 | 225 | 20332 | 17720 | 1987 | 261 | 364
2012-04-30 | 10641 | 8874 | 1366 | 191 | 211 | 17874 | 15231 | 1915 | 237 | 490
2012-05-31 | 11137 | 9304 | 1414 | 204 | 215 | 21106 | 18637 | 1687 | 242 | 539
2012-06-30 | 11800 | 10039 | 1339 | 179 | 244 | 24107 | 21813 | 1276 | 182 | 836
2012-07-31 | 13457 | 11553 | 1422 | 191 | 291 | 24636 | 22491 | 1276 | 198 | 671
2012-08-31 | 12633 | 10730 | 1429 | 213 | 262 | 23188 | 20436 | 1870 | 260 | 622
2012-09-30 | 11041 | 9272 | 1330 | 211 | 228 | 21183 | 18752 | 1724 | 241 | 466
2012-10-31 | 11142 | 9298 | 1426 | 177 | 241 | 18829 | 16115 | 1924 | 242 | 548
2012-11-30 | 11487 | 9711 | 1409 | 159 | 209 | 20144 | 17668 | 1763 | 239 | 475
2012-12-29 | 12157 | 10354 | 1378 | 174 | 251 | 20382 | 17918 | 1894 | 199 | 372
2013-01-31 | 12890 | 11004 | 1470 | 174 | 242 | 22610 | 19640 | 2147 | 197 | 626
2013-02-28 | 11742 | 9983 | 1378 | 154 | 227 | 21426 | 18760 | 2045 | 263 | 359
2013-03-31 | 11958 | 10134 | 1439 | 185 | 201 | 19825 | 17449 | 1936 | 223 | 218
2013-04-30 | 10945 | 9161 | 1367 | 212 | 205 | 18854 | 16001 | 2106 | 277 | 469
2013-05-31 | 10785 | 8991 | 1394 | 184 | 217 | 20488 | 18010 | 1884 | 200 | 394
2013-06-30 | 11175 | 9355 | 1365 | 163 | 291 | 22662 | 20487 | 1446 | 197 | 533
2013-07-31 | 12723 | 10867 | 1384 | 175 | 297 | 24927 | 22516 | 1374 | 260 | 777
2013-08-31 | 12100 | 10222 | 1421 | 180 | 278 | 22833 | 20220 | 1890 | 210 | 514
2013-09-30 | 10837 | 9077 | 1393 | 156 | 211 | 22682 | 20069 | 1821 | 206 | 586
2013-10-31 | 11136 | 9198 | 1502 | 177 | 258 | 18445 | 15816 | 2026 | 254 | 349
2013-11-30 | 11641 | 9791 | 1462 | 148 | 240 | 20615 | 18030 | 1922 | 268 | 394
2013-12-31 | 12702 | 10913 | 1448 | 188 | 154 | 21964 | 19570 | 2142 | 275 | -23
2014-01-31 | 13614 | 11658 | 1477 | 191 | 288 | 22774 | 20230 | 1760 | 277 | 507
2014-02-28 | 12067 | 10225 | 1396 | 207 | 240 | 21905 | 19060 | 1893 | 348 | 604
2014-03-31 | 12672 | 10666 | 1547 | 199 | 260 | 21656 | 18943 | 1956 | 351 | 405
2014-04-30 | 10837 | 8963 | 1461 | 212 | 201 | 18557 | 15839 | 2089 | 359 | 270
2014-05-31 | 10643 | 8791 | 1448 | 190 | 214 | 18844 | 16341 | 1953 | 240 | 311
2014-06-30 | 11229 | 9413 | 1454 | 166 | 195 | 20807 | 18623 | 1657 | 247 | 280
2014-07-31 | 11717 | 9846 | 1479 | 166 | 227 | 21300 | 19332 | 1235 | 224 | 510
2014-08-31 | 11718 | 9805 | 1488 | 174 | 251 | 21363 | 19502 | 1281 | 252 | 328
2014-09-30 | 10837 | 9080 | 1437 | 139 | 180 | 21123 | 19362 | 1344 | 216 | 201
2014-10-31 | 10820 | 9042 | 1447 | 151 | 180 | 17784 | 15264 | 1960 | 218 | 342
2014-11-30 | 11488 | 9707 | 1437 | 143 | 201 | 20102 | 17734 | 1807 | 246 | 315
2014-12-31 | 12132 | 10359 | 1426 | 155 | 192 | 20938 | 18328 | 1917 | 242 | 451
2015-01-31 | 13120 | 11250 | 1433 | 165 | 272 | 21814 | 19602 | 1284 | 239 | 689
2015-02-28 | 12302 | 10600 | 1336 | 143 | 223 | 21494 | 19379 | 1447 | 236 | 432
2015-03-31 | 12045 | 10213 | 1453 | 161 | 218 | 20827 | 18298 | 1955 | 289 | 284
2015-04-30 | 10405 | 8679 | 1405 | 152 | 169 | 18462 | 15709 | 1925 | 271 | 557
2015-05-31 | 10547 | 8799 | 1413 | 171 | 165 | 19158 | 16908 | 1889 | 229 | 133
2015-06-30 | 10624 | 8942 | 1351 | 148 | 183 | 19339 | 16892 | 1862 | 253 | 332
2015-07-31 | 12105 | 10312 | 1395 | 169 | 228 | 22516 | 20657 | 1190 | 228 | 441
2015-08-31 | 11797 | 9966 | 1418 | 167 | 246 | 22383 | 20499 | 1202 | 203 | 479
2015-09-30 | 11362 | 9626 | 1369 | 185 | 182 | 22063 | 19974 | 1258 | 211 | 620
2015-10-31 | 10687 | 8879 | 1453 | 195 | 160 | 17667 | 14885 | 1924 | 349 | 509
2015-11-30 | 10682 | 8964 | 1381 | 147 | 189 | 19239 | 16566 | 1879 | 273 | 521
2015-12-31 | 11314 | 9547 | 1393 | 168 | 206 | 19161 | 16356 | 1904 | 321 | 581
2016-01-31 | 12385 | 10508 | 1440 | 155 | 281 | 20836 | 18203 | 1839 | 318 | 476
2016-02-29 | 11472 | 9726 | 1372 | 150 | 222 | 20766 | 18094 | 1993 | 287 | 392
2016-03-31 | 11303 | 9496 | 1452 | 148 | 207 | 20063 | 17468 | 1862 | 293 | 439
2016-04-30 | 10410 | 8680 | 1437 | 154 | 139 | 17821 | 15475 | 1931 | 271 | 145
2016-05-31 | 10471 | 8758 | 1400 | 153 | 160 | 19885 | 17004 | 2012 | 355 | 514
2016-06-30 | 11102 | 9375 | 1386 | 147 | 194 | 21692 | 19771 | 1250 | 279 | 391
2016-07-31 | 12498 | 10734 | 1375 | 139 | 251 | 22659 | 20956 | 1104 | 161 | 438
2016-08-31 | 13113 | 11249 | 1405 | 165 | 295 | 23100 | 21333 | 1123 | 196 | 449
2016-09-30 | 11072 | 9297 | 1378 | 140 | 257 | 23213 | 21261 | 1153 | 143 | 657
2016-10-31 | 10519 | 8755 | 1410 | 158 | 195 | 18189 | 15452 | 1928 | 271 | 539
2016-11-30 | 10698 | 8920 | 1404 | 166 | 207 | 19369 | 16600 | 2002 | 267 | 501
2016-12-31 | 11978 | 10094 | 1404 | 192 | 289 | 20688 | 18146 | 1878 | 358 | 306
2017-01-31 | 12108 | 10236 | 1426 | 167 | 279 | 20372 | 17605 | 1904 | 284 | 579
2017-02-28 | 10608 | 8933 | 1327 | 158 | 190 | 19838 | 16763 | 2027 | 334 | 714
2017-03-31 | 11591 | 9771 | 1477 | 159 | 184 | 19174 | 16596 | 1936 | 286 | 356
2017-04-30 | 9789 | 8176 | 1362 | 157 | 93 | 17349 | 14586 | 2041 | 288 | 434
2017-05-31 | 10153 | 8442 | 1392 | 178 | 141 | 17738 | 15261 | 1980 | 285 | 212
2017-06-30 | 10657 | 8977 | 1341 | 158 | 181 | 21168 | 18989 | 1545 | 242 | 392
2017-07-31 | 11588 | 9826 | 1378 | 151 | 232 | 20627 | 18447 | 1426 | 212 | 542
2017-08-31 | 11350 | 9622 | 1359 | 157 | 211 | 20158 | 18607 | 1078 | 201 | 273
2017-09-30 | 10679 | 9122 | 1230 | 146 | 181 | 21786 | 20018 | 1008 | 215 | 545
2017-10-31 | 10339 | 8601 | 1427 | 140 | 172 | 17418 | 15048 | 1944 | 223 | 203
2017-11-30 | 10956 | 9214 | 1408 | 158 | 176 | 19115 | 16384 | 2051 | 276 | 403
2017-12-31 | 12339 | 10437 | 1409 | 197 | 297 | 20306 | 17561 | 1810 | 358 | 577
2018-01-31 | 12701 | 10883 | 1418 | 185 | 216 | 20906 | 18729 | 1274 | 375 | 528
2018-02-28 | 10951 | 9286 | 1323 | 160 | 181 | 20076 | 17390 | 1925 | 313 | 447
2018-03-31 | 11372 | 9566 | 1481 | 151 | 174 | 18462 | 15935 | 1912 | 271 | 344
2018-04-30 | 10578 | 8906 | 1369 | 139 | 164 | 18011 | 15476 | 1864 | 260 | 411
2018-05-31 | 10421 | 8725 | 1401 | 145 | 151 | 20473 | 18194 | 1599 | 212 | 467
2018-06-30 | 10923 | 9206 | 1374 | 147 | 197 | 21369 | 18537 | 1806 | 254 | 772
2018-07-31 | 12686 | 10951 | 1362 | 156 | 217 | 22909 | 21057 | 1149 | 275 | 427
2018-08-31 | 12689 | 10901 | 1390 | 149 | 249 | 21990 | 20346 | 1148 | 182 | 314
2018-09-30 | 11147 | 9441 | 1368 | 124 | 214 | 23240 | 21160 | 1117 | 169 | 794
2018-10-31 | 10717 | 9029 | 1441 | 138 | 109 | 18205 | 15964 | 1743 | 215 | 283
2018-11-30 | 11360 | 9613 | 1413 | 142 | 193 | 20152 | 17441 | 1925 | 292 | 494
2018-12-31 | 11939 | 10067 | 1440 | 165 | 267 | 19891 | 17186 | 1853 | 294 | 558
2019-01-31 | 12777 | 10984 | 1425 | 158 | 211 | 21525 | 18835 | 1825 | 233 | 632
2019-02-28 | 11292 | 9679 | 1303 | 133 | 177 | 20500 | 17987 | 1882 | 243 | 388
2019-03-31 | 11659 | 9872 | 1445 | 151 | 190 | 20263 | 17523 | 2050 | 240 | 451
2019-04-30 | 10265 | 8609 | 1338 | 171 | 147 | 17645 | 14957 | 2012 | 274 | 402
2019-05-31 | 10220 | 8467 | 1405 | 177 | 170 | 16784 | 14069 | 1849 | 312 | 554
2019-06-30 | 10366 | 8682 | 1388 | 146 | 150 | 20248 | 18015 | 1546 | 210 | 476
2019-07-31 | 12793 | 11053 | 1356 | 148 | 236 | 21791 | 19819 | 1055 | 235 | 681
2019-08-31 | 11825 | 10104 | 1379 | 141 | 201 | 21354 | 19287 | 1418 | 164 | 485
2019-09-30 | 10319 | 8735 | 1287 | 129 | 167 | 19717 | 17233 | 1866 | 179 | 439
2019-10-31 | 10351 | 8695 | 1377 | 133 | 145 | 18329 | 15859 | 1799 | 169 | 502
2019-11-30 | 11255 | 9566 | 1345 | 144 | 200 | 19625 | 17204 | 1869 | 265 | 286
2019-12-31 | 11997 | 10168 | 1391 | 185 | 253 | 20974 | 18132 | 1887 | 329 | 626
2020-01-31 | 12179 | 10383 | 1421 | 155 | 219 | 19928 | 17249 | 2038 | 256 | 386
2020-02-29 | 11240 | 9623 | 1334 | 130 | 153 | 19630 | 17210 | 1933 | 257 | 231
2020-03-31 | 10989 | 9283 | 1394 | 147 | 166 | 18183 | 15454 | 1831 | 259 | 639
2020-04-30 | 9283 | 7848 | 1153 | 157 | 125 | 15350 | 13281 | 1583 | 267 | 219
2020-05-31 | 9642 | 8168 | 1165 | 180 | 129 | 20649 | 18474 | 1380 | 272 | 523
2020-06-30 | 10800 | 9266 | 1204 | 159 | 171 | 21292 | 19035 | 1670 | 215 | 372
2020-07-31 | 13203 | 11611 | 1218 | 134 | 240 | 24446 | 22413 | 1344 | 212 | 478
2020-08-31 | 12081 | 10405 | 1293 | 147 | 236 | 23823 | 21209 | 1739 | 160 | 715
2020-09-30 | 10114 | 8539 | 1272 | 156 | 147 | 20225 | 17908 | 1726 | 208 | 382
2020-10-31 | 10339 | 8709 | 1347 | 136 | 147 | 17679 | 15259 | 1701 | 205 | 513
2020-11-30 | 10529 | 8953 | 1298 | 118 | 160 | 19147 | 16767 | 1779 | 198 | 403
2020-12-31 | 11812 | 10133 | 1324 | 160 | 195 | 20738 | 18150 | 1714 | 258 | 617
2021-01-31 | 12105 | 10361 | 1380 | 146 | 217 | 20150 | 17617 | 1905 | 202 | 426
2021-02-28 | 11233 | 9628 | 1286 | 128 | 191 | 20318 | 17713 | 1955 | 224 | 426
2021-03-31 | 11102 | 9383 | 1403 | 168 | 147 | 19344 | 16810 | 2016 | 209 | 309
2021-04-30 | 9782 | 8232 | 1335 | 145 | 69 | 16644 | 14039 | 1743 | 260 | 602
2021-05-31 | 10086 | 8499 | 1382 | 154 | 52 | 19443 | 16862 | 1797 | 185 | 599
2021-06-30 | 11262 | 9736 | 1259 | 133 | 135 | 22258 | 20483 | 1054 | 173 | 548
2021-07-31 | 11636 | 10068 | 1281 | 140 | 147 | 21655 | 20129 | 1025 | 175 | 326
2021-08-31 | 12857 | 11257 | 1276 | 146 | 177 | 22986 | 21153 | 1129 | 186 | 519
2021-09-30 | 10389 | 8817 | 1283 | 133 | 156 | 18769 | 16423 | 1697 | 169 | 480
2021-10-31 | 10516 | 8813 | 1349 | 146 | 208 | 17312 | 14837 | 1808 | 181 | 486
2021-11-30 | 10957 | 9290 | 1331 | 132 | 204 | 19644 | 17057 | 1887 | 180 | 520
2021-12-31 | 11970 | 10163 | 1394 | 150 | 263 | 20455 | 17849 | 1939 | 179 | 488
2022-01-31 | 13085 | 11310 | 1429 | 142 | 204 | 21349 | 18569 | 1848 | 277 | 655
2022-02-28 | 11488 | 9869 | 1280 | 140 | 200 | 20918 | 18284 | 1830 | 190 | 613
2022-03-31 | 11817 | 10022 | 1420 | 167 | 208 | 19763 | 17226 | 1876 | 247 | 413
2022-04-30 | 10265 | 8644 | 1302 | 139 | 180 | 17256 | 14532 | 1783 | 207 | 734
2022-05-31 | 10470 | 8743 | 1412 | 164 | 151 | 21292 | 19076 | 1585 | 177 | 455
2022-06-30 | 10930 | 9322 | 1299 | 149 | 160 | 21954 | 20048 | 1089 | 242 | 575
2022-07-31 | 12344 | 10601 | 1342 | 145 | 256 | 22607 | 20964 | 1024 | 154 | 465
2022-08-31 | 12624 | 10831 | 1352 | 144 | 298 | 21871 | 19880 | 1139 | 176 | 676
2022-09-30 | 10814 | 9116 | 1330 | 135 | 233 | 20350 | 17812 | 1858 | 219 | 462
2022-10-31 | 10384 | 8717 | 1337 | 115 | 216 | 17294 | 14594 | 1728 | 201 | 771
2022-11-30 | 11044 | 9332 | 1358 | 150 | 203 | 19441 | 16658 | 1886 | 226 | 672
2022-12-31 | 12273 | 10425 | 1424 | 178 | 246 | 20173 | 17385 | 1951 | 273 | 563
2023-01-31 | 12519.712 | 10663.928 | 1442.76 | 147.664 | 265.36 | 20486 | 17788.22 | 1880.245 | 151.231 | 666.304
2023-02-28 | 11225.17 | 9600.149 | 1293.065 | 135.588 | 196.368 | 21388 | 18906.97 | 1669.987 | 145.129 | 665.914
2023-03-31 | 11846.269 | 10020.454 | 1460.08 | 185.437 | 180.298 | 18811 | 15981.11 | 1879.742 | 213.3 | 736.848
2023-04-30 | 10271.638 | 8627.354 | 1342.37 | 129.821 | 172.093 | 17547 | 14758.89 | 1640.215 | 160.789 | 987.106
2023-05-31 | 10356.75 | 8682.996 | 1389.064 | 131.776 | 152.914 | 20787 | 18495 | 1637.15 | 84.434 | 570.416
2023-06-30 | 11119.814 | 9405.382 | 1361.029 | 72.359 | 281.044 | 21463 | 19510.7 | 1274.048 | 79.631 | 598.621
2023-07-31 | 12507.785 | 10774.228 | 1327.965 | 90.737 | 314.855 | 22686 | 20839.71 | 902.9529 | 83.897 | 859.4401
2023-08-31 | 11828.62 | 9727.361 | 1348.464 | 83.058 | 669.737 | 21364 | 19049.8 | 1538.945 | 88.381 | 686.874
2023-09-30 | 10997.556 | 9302.352 | 1313.765 | 153.072 | 228.367 | 23713 | 21787.11 | 915.2879 | 90.527 | 920.0751
2023-10-31 | 10932.34 | 9206.375 | 1384.079 | 125.788 | 216.098 | 20849 | 18263.33 | 1804.525 | 74.231 | 706.914
2023-11-30 | 11456.562 | 9678.918 | 1398.557 | 132.346 | 246.741 | 20579 | 17749.98 | 1866.072 | 127.035 | 835.913
2023-12-31 | 12065.5 | 10241.873 | 1447.234 | 146.712 | 229.681 | 20004 | 17422.09 | 1872.359 | 242.0844 | 467.4666
2024-01-31 | 12932.636 | 11101.806 | 1422.981 | 144.741 | 263.108 | 20880 | 18632.9 | 1745.48 | 182.106 | 319.514
2024-02-29 | 11437.175 | 9706.571 | 1361.857 | 137.808 | 230.939 | 19703 | 16778.25 | 1980.514 | 216.707 | 727.529
Back to main menu

## Table 3.3.4
Back to main menu
Table 3.3.4: Economic Assumptions
| Ontario Employment |  | Ontario Housing Starts |  | Ontario Growth Index
Year | Thousands | Annual Growth (%) | Thousands | Annual Growth (%) | Index | Annual Growth (%)
2011 | 6657.975 |  | 65.241 |  | 1.313
2012 | 6702.925 | 0.67513 | 74.414 | 14.0602 | 1.3274 | 1.0968
2013 | 6806.8583 | 1.5506 | 61.277 | -17.6539 | 1.3459 | 1.3917
2014 | 6840.025 | 0.48725 | 56.165 | -8.3424 | 1.3566 | 0.80135
2015 | 6886.9583 | 0.68616 | 68.291 | 21.59 | 1.3704 | 1.0138
2016 | 6956.3833 | 1.0081 | 71.86 | 5.2262 | 1.3869 | 1.2008
2017 | 7117.2833 | 2.313 | 75.204 | 4.6535 | 1.4129 | 1.8749
2018 | 7245.9 | 1.8071 | 75.958 | 1.0026 | 1.4357 | 1.6197
2019 | 7429.1667 | 2.5292 | 67.864 | -10.6559 | 1.4629 | 1.8936
2020 | 7025.8833 | -5.4284 | 78.918 | 16.2885 | 1.4329 | -2.05
2021 | 7393.2833 | 5.2292 | 92.284 | 16.9366 | 1.4822 | 3.4345
2022 | 7731.6333 | 4.5765 | 91.888 | -0.42911 | 1.528 | 3.0956
2023 | 7914.7833 | 2.3688 | 85.77 | -6.6581 | 1.5576 | 1.9347
2024 (f) | 7990.9448 | 0.96227 | 85.686 | -0.097936 | 1.5766 | 1.2201
2025 (f) | 8122.8336 | 1.6505 | 87.789 | 2.4543 | 1.6014 | 1.5716
Note: Labour Force data was rebased in January of 2021
Back to main menu

## Table 3.3.5
Back to main menu
Table 3.3.5: Weather Scenarios
Week Ending | Normal Peak Date | Normal Peak Temperature (°C) | Normal Average Temperature (°C) | Extreme Peak Date | Extreme Peak Temperature (°C)
2024-04-07 | 2013-03-23 | 4.1 | 3.9729 | 2014-03-27 | 3.1
2024-04-14 | 1994-04-06 | 0 | 6.1494 | 1982-04-06 | -7.4
2024-04-21 | 1996-04-06 | 0.8 | 4.7583 | 1982-04-04 | -5.1
2024-04-28 | 2011-04-15 | 6.2 | 7.5583 | 1982-04-05 | -2.4
2024-05-05 | 2014-04-06 | 10.9 | 10.6321 | 2018-04-16 | 2.6
2024-05-12 | 2001-05-03 | 30.4 | 14.7881 | 2006-05-30 | 32.8
2024-05-19 | 2017-05-07 | 10.3 | 12.672 | 1991-05-24 | 30
2024-05-26 | 1994-05-31 | 27 | 15.5881 | 1987-05-28 | 32.1
2024-06-02 | 2014-05-27 | 29.4 | 13.6643 | 2006-05-29 | 33.9
2024-06-09 | 2010-06-18 | 25 | 16.8333 | 2005-06-14 | 29.7
2024-06-16 | 2011-06-23 | 22.9 | 17.6929 | 2005-06-29 | 29.8
2024-06-23 | 2002-06-26 | 30.7 | 20.7536 | 1994-06-16 | 32.5
2024-06-30 | 1999-06-28 | 29.5 | 18.7821 | 1994-06-17 | 32.6
2024-07-07 | 2017-06-11 | 31.6 | 21.0045 | 1994-06-18 | 35.2
2024-07-14 | 1998-07-14 | 31.3 | 22.2089 | 2010-07-07 | 32
2024-07-21 | 2001-07-23 | 30.5 | 21.3923 | 2002-07-03 | 34.7
2024-07-28 | 1993-07-06 | 30.2 | 23.0952 | 2011-07-21 | 37.5
2024-08-04 | 2016-07-07 | 30.9 | 22.3661 | 2002-07-01 | 35.1
2024-08-11 | 2003-08-20 | 30.3 | 21.5214 | 2001-08-08 | 37.2
2024-08-18 | 2015-08-17 | 32.1 | 21.5494 | 2006-08-01 | 36.4
2024-08-25 | 1998-08-08 | 28.8 | 21.1952 | 2006-08-02 | 33.1
2024-09-01 | 2003-08-04 | 26.6 | 19.9125 | 1988-08-14 | 33.5
2024-09-08 | 1989-09-09 | 29.5 | 20.1685 | 1973-09-02 | 33.3
2024-09-15 | 2012-09-06 | 27.1 | 18.269 | 1973-09-03 | 32.8
2024-09-22 | 2000-09-10 | 25.3 | 14.6787 | 2015-09-02 | 32.6
2024-09-29 | 1989-09-05 | 24.4 | 14.6461 | 2018-09-17 | 26.3
2024-10-06 | 1989-09-12 | 23.9 | 15.4244 | 2018-09-01 | 27
2024-10-13 | 2011-10-26 | 6.4 | 11.5271 | 1976-10-17 | 5.6
2024-10-20 | 2008-10-30 | 9.8 | 10.6226 | 1976-10-19 | 4.4
2024-10-27 | 1990-10-19 | 8.5 | 9.2086 | 1974-10-18 | 3.3
2024-11-03 | 2015-10-17 | 4.9 | 6.506 | 2002-10-01 | 28.8
2024-11-10 | 1990-11-06 | 6.3 | 7.1875 | 1976-11-20 | -0.6
2024-11-17 | 1993-11-30 | 1 | 6.3202 | 1989-11-18 | -1.2
2024-11-24 | 1991-11-04 | 0 | 3.1232 | 1976-11-29 | -6.1
2024-12-01 | 2007-11-28 | -0.3 | 1.6381 | 1987-11-21 | -8
2024-12-08 | 2014-12-11 | -4 | 2.1229 | 1989-12-13 | -8.9
2024-12-15 | 2005-12-13 | -4.8 | -0.78274 | 2017-12-26 | -11.6
2024-12-22 | 1992-12-27 | -2.2 | -2.2914 | 2017-12-31 | -14.8
2024-12-29 | 2016-12-18 | -4.8 | -0.92381 | 2017-12-30 | -7.9
2025-01-05 | 2019-12-19 | -7.8 | -5.064 | 1993-12-26 | -17
2025-01-12 | 2007-01-21 | -5.1 | -3.4333 | 2014-01-24 | -11.2
2025-01-19 | 2013-01-24 | -11.6 | -4.9378 | 1994-01-16 | -13.8
2025-01-26 | 1991-01-21 | -13.5 | -6.425 | 1994-01-15 | -21.4
2025-02-02 | 1996-01-05 | -16.1 | -4.7643 | 1982-01-10 | -15.8
2025-02-09 | 2006-02-18 | -10 | -3.6732 | 1995-02-05 | -17.6
2025-02-16 | 1991-02-16 | -6.8 | -5.3833 | 2015-02-20 | -13.9
2025-02-23 | 2001-02-17 | -8.6 | -3.8012 | 2015-02-19 | -15.8
2025-03-02 | 2006-02-28 | -5.3 | -3.0643 | 2015-02-16 | -13.7
2025-03-09 | 2016-03-01 | -7.9 | -2.431 | 2003-03-03 | -14.3
2025-03-16 | 2008-03-08 | -6.4 | -1.4926 | 1984-03-12 | -11.3
2025-03-23 | 2013-03-18 | -0.1 | 0.17482 | 1984-03-07 | -12.8
2025-03-30 | 2011-03-27 | -1.9 | 3.1009 | 2017-03-04 | -7.2
2025-04-06 | 2013-03-23 | 4.1 | 3.9729 | 2014-03-27 | 3.1
2025-04-13 | 1994-04-06 | 0 | 6.1494 | 1982-04-06 | -7.4
2025-04-20 | 1996-04-06 | 0.8 | 4.7583 | 1982-04-04 | -5.1
2025-04-27 | 2011-04-15 | 6.2 | 7.5583 | 1982-04-05 | -2.4
2025-05-04 | 2014-04-06 | 10.9 | 10.6321 | 2018-04-16 | 2.6
2025-05-11 | 2001-05-03 | 30.4 | 14.7881 | 2006-05-30 | 32.8
2025-05-18 | 2017-05-07 | 10.3 | 12.672 | 1991-05-24 | 30
2025-05-25 | 1994-05-31 | 27 | 15.5881 | 1987-05-28 | 32.1
2025-06-01 | 2014-05-27 | 29.4 | 13.6643 | 2006-05-29 | 33.9
2025-06-08 | 2010-06-18 | 25 | 16.8333 | 2005-06-14 | 29.7
2025-06-15 | 2011-06-23 | 22.9 | 17.6929 | 2005-06-29 | 29.8
2025-06-22 | 2002-06-26 | 30.7 | 20.7536 | 1994-06-16 | 32.5
2025-06-29 | 1999-06-28 | 29.5 | 18.7821 | 1994-06-17 | 32.6
2025-07-06 | 2017-06-11 | 31.6 | 21.0045 | 1994-06-18 | 35.2
2025-07-13 | 1998-07-14 | 31.3 | 22.2089 | 2010-07-07 | 32
2025-07-20 | 2001-07-23 | 30.5 | 21.3923 | 2002-07-03 | 34.7
2025-07-27 | 1993-07-06 | 30.2 | 23.0952 | 2011-07-21 | 37.5
2025-08-03 | 2016-07-07 | 30.9 | 22.3661 | 2002-07-01 | 35.1
2025-08-10 | 2003-08-20 | 30.3 | 21.5214 | 2001-08-08 | 37.2
2025-08-17 | 2015-08-17 | 32.1 | 21.5494 | 2006-08-01 | 36.4
2025-08-24 | 1998-08-08 | 28.8 | 21.1952 | 2006-08-02 | 33.1
2025-08-31 | 2003-08-04 | 26.6 | 19.9125 | 1988-08-14 | 33.5
2025-09-07 | 1989-09-09 | 29.5 | 20.1685 | 1973-09-02 | 33.3
2025-09-14 | 2012-09-06 | 27.1 | 18.269 | 1973-09-03 | 32.8
2025-09-21 | 2000-09-10 | 25.3 | 14.6787 | 2015-09-02 | 32.6
2025-09-28 | 1989-09-05 | 24.4 | 14.6461 | 2018-09-17 | 26.3
2025-10-05 | 1989-09-12 | 23.9 | 15.4244 | 2018-09-01 | 27
Back to main menu

## Table 3.3.6
Back to main menu
Table 3.3.6: Estimate of Contracted Embedded Generation Capacity (MW)
| Biogas | Cogeneration | Solar | Hydro | Wind | Total
2007-01-01 | 0 | 0 | 0 | 129.3052 | 0 | 129.3052
2007-02-01 | 0 | 0 | 0 | 130.66 | 0 | 130.66
2007-03-01 | 0.90726 | 0 | 0 | 130.66 | 0 | 131.5673
2007-04-01 | 5.625 | 0 | 0 | 130.66 | 0.34202 | 136.627
2007-05-01 | 9.0187 | 0 | 0 | 132.86 | 5.3586 | 147.2373
2007-06-01 | 13.8342 | 0 | 0 | 133.76 | 6.5102 | 154.1044
2007-07-01 | 15.0394 | 0 | 0 | 133.869 | 6.5102 | 155.4186
2007-08-01 | 15.0394 | 0 | 0.031821 | 134.061 | 6.5102 | 155.6424
2007-09-01 | 15.1834 | 0 | 0.052 | 134.19 | 6.5102 | 155.9356
2007-10-01 | 16.8194 | 0 | 0.053205 | 134.19 | 6.6312 | 157.6938
2007-11-01 | 17.3184 | 0 | 0.063128 | 134.834 | 6.7602 | 158.9757
2007-12-01 | 17.7642 | 0 | 0.1447 | 135.4645 | 6.7602 | 160.1336
2008-01-01 | 18.3814 | 0 | 0.22003 | 135.859 | 8.9957 | 163.4562
2008-02-01 | 18.4642 | 0 | 0.22314 | 135.859 | 16.6604 | 171.2067
2008-03-01 | 18.4814 | 1.5581 | 0.2255 | 135.859 | 22.7573 | 178.8813
2008-04-01 | 18.4814 | 2.3 | 0.25908 | 135.859 | 25.6606 | 182.5601
2008-05-01 | 18.4814 | 2.3 | 0.29779 | 135.859 | 25.6606 | 182.5988
2008-06-01 | 18.4814 | 6.8 | 0.29779 | 135.859 | 38.2008 | 199.639
2008-07-01 | 18.4814 | 7.3 | 0.3041 | 135.859 | 45.461 | 207.4055
2008-08-01 | 18.4814 | 7.3 | 0.30801 | 135.9509 | 45.461 | 207.5013
2008-09-01 | 18.4814 | 7.3 | 0.31292 | 136.809 | 46.836 | 209.7393
2008-10-01 | 18.4814 | 7.6645 | 0.33256 | 136.809 | 56.266 | 219.5535
2008-11-01 | 19.7619 | 18.6 | 0.33423 | 140.209 | 69.2214 | 248.1266
2008-12-01 | 21.6827 | 18.6 | 3.2547 | 140.809 | 73.5115 | 257.858
2009-01-01 | 21.6827 | 18.6 | 11.6173 | 140.809 | 73.5115 | 266.2205
2009-02-01 | 21.6827 | 18.6 | 11.746 | 140.809 | 73.5115 | 266.3493
2009-03-01 | 21.6827 | 18.6 | 11.7735 | 140.809 | 73.5502 | 266.4155
2009-04-01 | 21.7289 | 18.6 | 11.7753 | 140.809 | 74.1115 | 267.0247
2009-05-01 | 22.0287 | 18.6 | 11.7789 | 142.68 | 74.1115 | 269.1992
2009-06-01 | 22.0287 | 56.4 | 11.7789 | 146.609 | 74.1115 | 310.9282
2009-07-01 | 22.0287 | 81.6 | 11.7789 | 146.609 | 74.1115 | 336.1282
2009-08-01 | 22.0287 | 81.6 | 11.7789 | 146.609 | 74.1115 | 336.1282
2009-09-01 | 22.0287 | 81.6 | 12.7353 | 147.7423 | 74.1115 | 338.2179
2009-10-01 | 22.0287 | 81.6 | 21.343 | 148.609 | 74.1115 | 347.6923
2009-11-01 | 22.0287 | 81.6 | 23.5941 | 148.609 | 74.1115 | 349.9434
2009-12-01 | 22.0287 | 81.6 | 33.2843 | 148.8671 | 87.5441 | 373.3241
2010-01-01 | 22.0287 | 93.3 | 47.339 | 189.759 | 104.9057 | 457.3325
2010-02-01 | 22.0287 | 93.3 | 53.8522 | 190.281 | 120.7125 | 480.1744
2010-03-01 | 22.0287 | 93.3 | 53.8522 | 202.197 | 120.7125 | 492.0904
2010-04-01 | 25.8531 | 93.3 | 53.8522 | 223.2703 | 120.7125 | 516.9881
2010-05-01 | 29.1077 | 93.3 | 53.8522 | 239.197 | 142.7484 | 558.2054
2010-06-01 | 29.1077 | 93.3 | 53.8683 | 240.3126 | 160.3133 | 576.9019
2010-07-01 | 30.4239 | 93.3 | 64.8368 | 240.7634 | 160.3133 | 589.6373
2010-08-01 | 36.0078 | 93.3 | 104.3353 | 240.815 | 160.3133 | 634.7714
2010-09-01 | 41.1242 | 93.3 | 121.7703 | 241.505 | 160.3133 | 658.0127
2010-10-01 | 41.3572 | 93.3 | 130.6664 | 243.47 | 162.4165 | 671.2101
2010-11-01 | 41.3572 | 93.3 | 151.2086 | 243.62 | 175.1136 | 704.5993
2010-12-01 | 41.3572 | 93.3 | 166.625 | 244.22 | 186.9202 | 732.4224
2011-01-01 | 42.3094 | 93.3 | 195.2829 | 248.52 | 204.34 | 783.7523
2011-02-01 | 42.9972 | 93.3 | 209.3788 | 248.52 | 221.1145 | 815.3105
2011-03-01 | 42.9972 | 93.3 | 215.2092 | 249.638 | 221.1145 | 822.2589
2011-04-01 | 42.9972 | 93.3 | 223.7383 | 249.638 | 221.1145 | 830.788
2011-05-01 | 43.094 | 93.3 | 226.8546 | 249.638 | 234.018 | 846.9045
2011-06-01 | 43.0972 | 93.3 | 230.5665 | 250.758 | 241.1149 | 858.8366
2011-07-01 | 43.0972 | 93.3 | 262.3273 | 250.758 | 241.1149 | 890.5974
2011-08-01 | 43.0972 | 93.3 | 289.5994 | 250.758 | 241.1149 | 917.8695
2011-09-01 | 43.1221 | 93.3 | 317.9877 | 250.758 | 241.1149 | 946.2827
2011-10-01 | 43.4712 | 93.3 | 325.5623 | 250.758 | 241.1149 | 954.2064
2011-11-01 | 43.4962 | 93.3 | 330.6827 | 251.223 | 241.1149 | 959.8167
2011-12-01 | 43.8132 | 93.3 | 359.6949 | 251.223 | 241.1149 | 989.1461
2012-01-01 | 46.6067 | 93.3 | 378.349 | 251.223 | 242.8569 | 1012.3355
2012-02-01 | 46.7084 | 93.3 | 384.5746 | 251.223 | 250.1151 | 1025.921
2012-03-01 | 46.7084 | 93.3 | 442.1847 | 251.223 | 265.967 | 1099.383
2012-04-01 | 47.9747 | 93.3 | 463.651 | 251.223 | 287.9158 | 1144.0645
2012-05-01 | 48.5892 | 93.3 | 490.3709 | 251.223 | 293.3998 | 1176.8829
2012-06-01 | 49.673 | 93.3 | 521.3291 | 251.223 | 297.916 | 1213.4412
2012-07-01 | 50.5917 | 93.3 | 526.9563 | 251.223 | 297.916 | 1219.987
2012-08-01 | 51.2509 | 93.3 | 538.5604 | 251.473 | 297.916 | 1232.5003
2012-09-01 | 51.8614 | 93.3 | 547.813 | 251.473 | 301.5161 | 1245.9634
2012-10-01 | 51.9743 | 93.3 | 558.5288 | 251.473 | 301.9161 | 1257.1922
2012-11-01 | 52.1115 | 93.3 | 577.462 | 251.473 | 301.9161 | 1276.2625
2012-12-01 | 52.4503 | 93.3 | 589.3165 | 251.473 | 310.8195 | 1297.3593
2013-01-01 | 53.6716 | 93.3 | 606.1154 | 252.048 | 327.8198 | 1332.9548
2013-02-01 | 57.0568 | 93.3 | 650.0398 | 254.0123 | 334.9168 | 1389.3256
2013-03-01 | 57.0568 | 93.3 | 711.1347 | 259.6581 | 334.9168 | 1456.0663
2013-04-01 | 57.3059 | 93.3 | 747.1507 | 260.051 | 334.9168 | 1492.7243
2013-05-01 | 58.7995 | 93.3 | 765.8263 | 265.551 | 334.9168 | 1518.3935
2013-06-01 | 60.2948 | 93.3 | 798.1708 | 271.451 | 334.9168 | 1558.1334
2013-07-01 | 60.4032 | 93.3 | 833.8125 | 274.9494 | 334.9168 | 1597.3818
2013-08-01 | 60.4032 | 93.3 | 857.399 | 279.901 | 334.9168 | 1625.9199
2013-09-01 | 60.4032 | 93.3 | 883.9364 | 280.501 | 334.9168 | 1653.0573
2013-10-01 | 60.5967 | 93.3 | 908.125 | 285.4687 | 335.0458 | 1682.5362
2013-11-01 | 60.6532 | 93.4167 | 917.8435 | 292.601 | 335.4168 | 1699.9312
2013-12-01 | 60.6532 | 93.506 | 956.9454 | 292.601 | 335.4168 | 1739.1224
2014-01-01 | 65.8941 | 93.506 | 996.8529 | 292.601 | 335.4168 | 1784.2708
2014-02-01 | 70.1512 | 93.506 | 1053.2145 | 292.601 | 339.9169 | 1849.3895
2014-03-01 | 74.1512 | 93.506 | 1131.8205 | 292.601 | 368.5196 | 1960.5983
2014-04-01 | 76.3386 | 93.506 | 1166.539 | 292.601 | 371.4235 | 2000.4081
2014-05-01 | 77.0043 | 93.506 | 1192.4114 | 292.601 | 371.4235 | 2026.9462
2014-06-01 | 77.0043 | 93.506 | 1208.3129 | 292.601 | 373.4235 | 2044.8478
2014-07-01 | 77.0043 | 93.506 | 1229.0265 | 294.251 | 381.4237 | 2075.2115
2014-08-01 | 77.0366 | 93.506 | 1282.2475 | 294.251 | 386.9283 | 2133.9694
2014-09-01 | 77.2543 | 93.506 | 1326.0248 | 294.251 | 395.904 | 2186.9402
2014-10-01 | 77.2543 | 93.506 | 1406.9063 | 294.251 | 410.9063 | 2282.8239
2014-11-01 | 77.2543 | 93.506 | 1471.6655 | 294.251 | 415.6897 | 2352.3665
2014-12-01 | 77.2543 | 93.506 | 1509.2005 | 294.251 | 425.2566 | 2399.4684
2015-01-01 | 77.2543 | 93.506 | 1535.1743 | 294.251 | 425.2566 | 2425.4422
2015-02-01 | 77.2543 | 93.506 | 1590.6188 | 294.251 | 425.2566 | 2480.8867
2015-03-01 | 77.2543 | 93.506 | 1635.6988 | 294.251 | 425.2566 | 2525.9667
2015-04-01 | 77.4043 | 93.506 | 1662.0311 | 294.251 | 425.2566 | 2552.449
2015-05-01 | 77.5043 | 93.506 | 1679.3807 | 294.251 | 425.2566 | 2569.8986
2015-06-01 | 88.7853 | 93.506 | 1702.5037 | 301.513 | 429.7566 | 2616.0646
2015-07-01 | 95.9214 | 93.506 | 1726.1469 | 304.762 | 449.5474 | 2669.8837
2015-08-01 | 96.0667 | 93.506 | 1747.8219 | 312.373 | 470.722 | 2720.4896
2015-09-01 | 96.0667 | 93.506 | 1776.8475 | 312.373 | 483.5577 | 2762.3509
2015-10-01 | 103.2408 | 93.506 | 1801.2743 | 312.373 | 483.5577 | 2793.9518
2015-11-01 | 110.1847 | 95.9861 | 1829.2949 | 312.373 | 483.5577 | 2831.3964
2015-12-01 | 111.1017 | 97.422 | 1862.6591 | 313.9214 | 485.0126 | 2870.1167
2016-01-01 | 111.1017 | 97.422 | 1874.4277 | 313.973 | 487.6578 | 2884.5822
2016-02-01 | 111.1017 | 97.422 | 1881.1182 | 313.973 | 489.0371 | 2892.652
2016-03-01 | 111.1017 | 97.422 | 1888.9902 | 313.973 | 497.658 | 2909.1449
2016-04-01 | 111.1017 | 97.422 | 1895.7047 | 313.973 | 497.658 | 2915.8593
2016-05-01 | 111.1017 | 97.422 | 1899.4423 | 313.973 | 512.4208 | 2934.3597
2016-06-01 | 111.1017 | 97.422 | 1901.5249 | 313.973 | 515.2598 | 2939.2813
2016-07-01 | 111.1017 | 97.422 | 1907.1641 | 313.973 | 515.2598 | 2944.9205
2016-08-01 | 111.2978 | 97.422 | 1916.6348 | 313.973 | 515.2598 | 2954.5874
2016-09-01 | 111.4817 | 97.422 | 1932.7295 | 313.973 | 521.4099 | 2977.0161
2016-10-01 | 111.4897 | 97.422 | 1941.1175 | 313.973 | 542.4218 | 3006.424
2016-11-01 | 111.7317 | 97.422 | 1948.6437 | 313.973 | 553.9126 | 3025.6829
2016-12-01 | 111.7317 | 97.422 | 1956.7377 | 314.038 | 569.1322 | 3049.0616
2017-01-01 | 111.7317 | 97.422 | 1961.349 | 314.038 | 571.7129 | 3056.2535
2017-02-01 | 111.7317 | 97.422 | 1966.3294 | 314.038 | 571.7129 | 3061.2339
2017-03-01 | 111.7317 | 99.6546 | 1973.5886 | 314.038 | 571.7129 | 3070.7257
2017-04-01 | 111.7317 | 101.267 | 1989.4945 | 314.038 | 578.647 | 3095.1781
2017-05-01 | 111.7317 | 101.5799 | 2003.2176 | 314.3138 | 579.9718 | 3110.8148
2017-06-01 | 111.7317 | 104.5 | 2008.4069 | 315.2713 | 580.2138 | 3120.1237
2017-07-01 | 111.7317 | 104.5 | 2010.2863 | 315.488 | 580.2138 | 3122.2197
2017-08-01 | 111.7317 | 105.6472 | 2013.5036 | 328.7428 | 580.2138 | 3139.8391
2017-09-01 | 111.7317 | 107.733 | 2019.3656 | 344.838 | 580.2138 | 3163.882
2017-10-01 | 111.7317 | 107.733 | 2024.4529 | 344.838 | 580.2138 | 3168.9693
2017-11-01 | 111.7317 | 107.9908 | 2030.0221 | 344.838 | 587.7312 | 3182.3137
2017-12-01 | 111.7317 | 110.311 | 2034.1186 | 344.838 | 590.4648 | 3191.464
2018-01-01 | 111.7317 | 110.311 | 2040.2457 | 344.838 | 590.4648 | 3197.5911
2018-02-01 | 111.7317 | 110.311 | 2048.5413 | 344.838 | 590.4648 | 3205.8867
2018-03-01 | 111.7317 | 110.311 | 2056.8134 | 344.838 | 590.4648 | 3214.1589
2018-04-01 | 111.915 | 110.311 | 2061.5168 | 344.838 | 590.4648 | 3219.0456
2018-05-01 | 111.9817 | 110.311 | 2064.1593 | 344.838 | 590.4648 | 3221.7547
2018-06-01 | 111.9817 | 110.311 | 2070.5387 | 344.838 | 590.4648 | 3228.1341
2018-07-01 | 112.2075 | 110.311 | 2077.6889 | 344.838 | 590.4648 | 3235.5102
2018-08-01 | 112.7318 | 110.311 | 2091.1308 | 344.838 | 590.4648 | 3249.4764
2018-09-01 | 112.8068 | 110.311 | 2099.0136 | 344.838 | 590.4648 | 3257.4342
2018-10-01 | 112.9818 | 110.311 | 2104.8985 | 344.838 | 590.4648 | 3263.494
2018-11-01 | 113.0768 | 110.311 | 2105.5257 | 344.838 | 590.4648 | 3264.2163
2018-12-01 | 113.3318 | 110.311 | 2106.4052 | 344.838 | 590.4648 | 3265.3508
2019-01-01 | 113.3318 | 110.311 | 2128.8121 | 347.438 | 590.4648 | 3290.3577
2019-02-01 | 113.3318 | 110.311 | 2139.0097 | 347.438 | 590.4648 | 3300.5552
2019-03-01 | 113.5818 | 110.311 | 2145.8589 | 347.438 | 590.4648 | 3307.6545
2019-04-01 | 113.7985 | 111.763 | 2149.1518 | 347.438 | 590.4648 | 3312.6161
2019-05-01 | 114.0657 | 112.291 | 2151.3408 | 347.438 | 590.4648 | 3315.6002
2019-06-01 | 114.0818 | 112.291 | 2152.7918 | 347.438 | 590.4648 | 3317.0674
2019-07-01 | 114.0818 | 112.291 | 2153.6798 | 347.438 | 590.4648 | 3317.9554
2019-08-01 | 114.106 | 112.291 | 2155.4126 | 347.438 | 590.4648 | 3319.7124
2019-09-01 | 114.4402 | 113.383 | 2158.5087 | 347.438 | 590.4648 | 3324.2348
2019-10-01 | 114.5819 | 115.021 | 2159.5697 | 347.438 | 590.4648 | 3327.0754
2019-11-01 | 114.5819 | 115.021 | 2160.7028 | 347.438 | 590.4648 | 3328.2085
2019-12-01 | 114.5819 | 115.021 | 2160.8838 | 347.438 | 590.4648 | 3328.3894
2020-01-01 | 114.5819 | 115.021 | 2160.8838 | 347.438 | 590.4648 | 3328.3894
2020-02-01 | 114.5819 | 115.021 | 2160.8838 | 347.438 | 590.4648 | 3328.3894
2020-03-01 | 114.5819 | 115.021 | 2160.9523 | 350.5348 | 590.4648 | 3331.5548
2020-04-01 | 114.5819 | 115.021 | 2161.4151 | 351.438 | 590.4648 | 3332.9208
2020-05-01 | 114.5819 | 115.021 | 2161.4151 | 351.4432 | 590.4648 | 3332.9259
2020-06-01 | 114.5819 | 116.1191 | 2161.4151 | 351.598 | 590.4648 | 3334.1789
2020-07-01 | 114.5819 | 147.965 | 2161.4151 | 351.598 | 590.4648 | 3366.0248
2020-08-01 | 114.5819 | 147.965 | 2161.4151 | 351.598 | 590.4648 | 3366.0248
2020-09-01 | 114.5819 | 147.965 | 2161.4378 | 351.598 | 590.4648 | 3366.0475
2020-10-01 | 114.8159 | 147.965 | 2166.664 | 351.598 | 590.4648 | 3371.5077
2020-11-01 | 114.832 | 147.965 | 2168.979 | 356.448 | 590.4648 | 3378.6888
2020-12-01 | 114.832 | 147.965 | 2168.979 | 356.9964 | 590.4648 | 3379.2372
2021-01-01 | 114.832 | 147.965 | 2170.8429 | 373.448 | 590.4648 | 3397.5527
2021-02-01 | 114.832 | 147.965 | 2171.1387 | 373.448 | 590.4648 | 3397.8485
2021-03-01 | 114.832 | 147.965 | 2171.1387 | 373.448 | 590.4648 | 3397.8485
2021-04-01 | 114.832 | 147.965 | 2171.1387 | 373.448 | 590.4648 | 3397.8485
2021-05-01 | 114.832 | 147.965 | 2171.1387 | 393.4803 | 590.4648 | 3417.8807
2021-06-01 | 114.832 | 147.965 | 2171.1387 | 400.448 | 590.4648 | 3424.8485
2021-07-01 | 114.832 | 147.965 | 2171.1387 | 400.448 | 590.4648 | 3424.8485
2021-08-01 | 114.832 | 147.965 | 2171.1387 | 400.448 | 590.4648 | 3424.8485
2021-09-01 | 114.832 | 147.965 | 2171.1387 | 400.448 | 590.4648 | 3424.8485
2021-10-01 | 114.832 | 147.965 | 2171.1387 | 400.448 | 590.4648 | 3424.8485
2021-11-01 | 114.832 | 147.965 | 2171.1387 | 400.448 | 590.4648 | 3424.8485
2021-12-01 | 114.832 | 147.965 | 2171.1387 | 400.448 | 590.4648 | 3424.8485
2022-01-01 | 114.832 | 147.965 | 2171.1387 | 400.448 | 590.4648 | 3424.8485
2022-02-01 | 114.832 | 147.965 | 2171.1387 | 400.448 | 590.4648 | 3424.8485
2022-03-01 | 114.832 | 147.965 | 2171.1387 | 400.448 | 590.4648 | 3424.8485
2022-04-01 | 114.832 | 147.965 | 2171.1387 | 400.448 | 590.4648 | 3424.8485
2022-05-01 | 114.832 | 147.965 | 2171.1387 | 400.448 | 590.4648 | 3424.8485
2022-06-01 | 114.832 | 147.965 | 2171.1387 | 400.448 | 590.4648 | 3424.8485
2022-07-01 | 114.832 | 147.965 | 2171.1387 | 400.448 | 590.4648 | 3424.8485
2022-08-01 | 114.832 | 147.965 | 2171.1387 | 400.448 | 590.4648 | 3424.8485
2022-09-01 | 114.832 | 147.965 | 2171.1387 | 400.448 | 590.4648 | 3424.8485
2022-10-01 | 114.832 | 147.965 | 2171.1387 | 400.448 | 590.4648 | 3424.8485
2022-11-01 | 114.832 | 147.965 | 2171.1387 | 400.448 | 590.4648 | 3424.8485
2022-12-01 | 114.832 | 147.965 | 2171.1387 | 400.448 | 590.4648 | 3424.8485
2023-01-01 | 114.832 | 147.965 | 2171.1387 | 410.448 | 590.4648 | 3434.8485
2023-02-01 | 114.832 | 147.965 | 2171.1387 | 410.448 | 590.4648 | 3434.8485
2023-03-01 | 114.832 | 147.965 | 2171.1387 | 410.448 | 590.4648 | 3434.8485
2023-04-01 | 114.832 | 147.965 | 2171.1387 | 410.448 | 590.4648 | 3434.8485
2023-05-01 | 114.832 | 147.965 | 2171.1387 | 410.448 | 590.4648 | 3434.8485
2023-06-01 | 114.832 | 147.965 | 2171.1387 | 410.448 | 590.4648 | 3434.8485
2023-07-01 | 114.832 | 147.965 | 2171.1387 | 410.448 | 590.4648 | 3434.8485
2023-08-01 | 114.832 | 147.965 | 2171.1387 | 410.448 | 590.4648 | 3434.8485
2023-09-01 | 114.832 | 147.965 | 2171.1387 | 410.448 | 590.4648 | 3434.8485
2023-10-01 | 114.832 | 147.965 | 2171.1387 | 410.448 | 590.4648 | 3434.8485
2023-11-01 | 114.832 | 147.965 | 2171.1387 | 410.448 | 590.4648 | 3434.8485
2023-12-01 | 114.832 | 147.965 | 2171.1387 | 410.448 | 590.4648 | 3434.8485
2024-01-01 | 114.832 | 147.965 | 2171.1387 | 410.448 | 590.4648 | 3434.8485
2024-02-01 | 118.9699 | 147.965 | 2171.1387 | 410.448 | 590.4648 | 3438.9864
2024-03-01 | 122.832 | 147.965 | 2171.1387 | 410.448 | 590.4648 | 3442.8485
2024-04-01 | 122.832 | 147.965 | 2171.1387 | 410.448 | 590.4648 | 3442.8485
2024-05-01 | 122.832 | 147.965 | 2171.1387 | 410.448 | 590.4648 | 3442.8485
2024-06-01 | 122.832 | 147.965 | 2171.1387 | 410.448 | 590.4648 | 3442.8485
2024-07-01 | 122.832 | 147.965 | 2171.1387 | 410.448 | 590.4648 | 3442.8485
2024-08-01 | 122.832 | 147.965 | 2171.1387 | 410.448 | 590.4648 | 3442.8485
2024-09-01 | 122.832 | 147.965 | 2171.1387 | 410.448 | 590.4648 | 3442.8485
2024-10-01 | 122.832 | 147.965 | 2171.1387 | 410.448 | 590.4648 | 3442.8485
2024-11-01 | 122.832 | 147.965 | 2171.1387 | 410.448 | 590.4648 | 3442.8485
2024-12-01 | 122.832 | 147.965 | 2171.1387 | 410.448 | 590.4648 | 3442.8485
2025-01-01 | 122.832 | 147.965 | 2171.1387 | 410.448 | 590.4648 | 3442.8485
2025-02-01 | 122.832 | 147.965 | 2171.1387 | 410.448 | 590.4648 | 3442.8485
2025-03-01 | 122.832 | 147.965 | 2171.1387 | 410.448 | 590.4648 | 3442.8485
2025-04-01 | 122.832 | 147.965 | 2171.1387 | 410.448 | 590.4648 | 3442.8485
2025-05-01 | 122.832 | 147.965 | 2171.1387 | 410.448 | 590.4648 | 3442.8485
2025-06-01 | 122.832 | 147.965 | 2171.1387 | 410.448 | 590.4648 | 3442.8485
2025-07-01 | 122.832 | 147.965 | 2171.1387 | 410.448 | 590.4648 | 3442.8485
2025-08-01 | 122.832 | 147.965 | 2171.1387 | 410.448 | 590.4648 | 3442.8485
2025-09-01 | 122.832 | 147.965 | 2171.1387 | 410.448 | 590.4648 | 3442.8485
2025-10-01 | 122.832 | 147.965 | 2171.1387 | 410.448 | 590.4648 | 3442.8485
2025-11-01 | 122.832 | 147.965 | 2171.1387 | 410.448 | 590.4648 | 3442.8485
2025-12-01 | 122.832 | 147.965 | 2171.1387 | 410.448 | 590.4648 | 3442.8485
2026-01-01 | 122.832 | 147.965 | 2171.1387 | 410.448 | 590.4648 | 3442.8485
2026-02-01 | 122.832 | 147.965 | 2171.1387 | 410.448 | 590.4648 | 3442.8485
2026-03-01 | 122.832 | 147.965 | 2171.1387 | 410.448 | 590.4648 | 3442.8485
2026-04-01 | 122.832 | 147.965 | 2171.1387 | 410.448 | 590.4648 | 3442.8485
2026-05-01 | 122.832 | 147.965 | 2171.1387 | 410.448 | 590.4648 | 3442.8485
2026-06-01 | 122.832 | 147.965 | 2171.1387 | 410.448 | 590.4648 | 3442.8485
2026-07-01 | 122.832 | 147.965 | 2171.1387 | 410.448 | 590.4648 | 3442.8485
2026-08-01 | 122.832 | 147.965 | 2171.1387 | 410.448 | 590.4648 | 3442.8485
2026-09-01 | 122.832 | 147.965 | 2171.1387 | 410.448 | 590.4648 | 3442.8485
2026-10-01 | 122.832 | 147.965 | 2171.1387 | 410.448 | 590.4648 | 3442.8485
2026-11-01 | 122.832 | 147.965 | 2171.1387 | 410.448 | 590.4648 | 3442.8485
2026-12-01 | 122.832 | 147.965 | 2171.1387 | 410.448 | 590.4648 | 3442.8485
Back to main menu

## Table 4.1
Back to main menu
Table 4.1: Existing Grid-Connected Resource Capacity
Fuel Type | Total Installed Capacity (MW) | Forecast Capability at 2024 Summer Peak [Normal] (MW) | Forecast Capability at 2024 Summer Peak [Extreme] (MW) | Number of Stations | Change in Number of Stations | Change in Installed Capacity (MW)
Nuclear | 13144.2 | 10443.6 | 10443.6 | 5 | 0 | 0
Hydroelectric | 8921.57 | 5162.5343 | 4770.2163 | 76 | 0 | 0
Gas/Oil | 10470.37 | 9659.8667 | 9261.5367 | 33 | 0 | 0
Wind | 4882.811 | 720.4713 | 720.4713 | 41 | 0 | 0
Biofuel | 296.2 | 245.56 | 245.56 | 7 | 0 | 0
Solar | 478.04 | 65.851 | 65.851 | 10 | 0 | 0
Demand Measures | - | 995.95 | 995.95 | - | - | -
Firm Imports (+) / Exports (-) (MW) | - | 600 | 0 | - | - | -
Total | 38193.191 | 27893.8333 | 26503.1852 | 172 | 0 | 0

## Table 4.2
Back to main menu
Table 4.2: Committed Generation Resources Status
|  |  |  | Estimated |  | Capacity Considered
Project Name |  | Zone | Fuel Type | Effective Date | Project Status | Firm | Planned
Romney Wind Energy Center | 0 | West | Wind |  | Commercial Operation | 0 | 60
Oneida Storage | 0 | Southwest | Storage | 2025-Q2 | Under Development | 0 | 235
Total | 0 | 0 | 0 | 0 | 0 | 0 | 295

## Table 4.3
Back to main menu
Table 4.3: Monthly Historical Hydroelectric Median Values for Normal Weather Conditions
Month | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Historical Hydroelectric Median Contribution (MW) | 6166.5284 | 6090.4068 | 5909.5705 | 5926.836 | 5958.1367 | 5769.2934 | 5603.5292 | 5306.0853 | 5086.7795 | 5452.7796 | 5708.374 | 6162.4318
Historical Hydroelectric Median Contribution without Outages (MW) | 6669.9518 | 6672.6903 | 6433.8406 | 6444.1294 | 6404.0723 | 6274.2006 | 6142.2428 | 5894.208 | 5944.9993 | 6265.9591 | 6487.6807 | 6679.1905

## Figure 4.1
Back to main menu
Figure 4.1: Monthly Wind Capacity Contribution Values
Month | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Wind Capacity Contribution (% of Installed Capacity) | 39.84% | 39.84% | 37.76% | 32.06% | 22.9% | 14.76% | 14.76% | 14.76% | 16.18% | 31.19% | 43.1% | 39.84%

## Figure 4.2
Back to main menu
Figure 4.2: Monthly Solar Capacity Contribution Values
Month | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Solar Capacity Contribution (% of Installed Capacity) | 0% | 0% | 0.1592% | 1.159% | 2.727% | 13.78% | 13.78% | 13.78% | 8.456% | 2.223% | 0% | 0%

## Table 4.4
Back to main menu
Table 4.4: Summary of Available Resources under Normal Weather
| Description [Normal] | Summer Peak 2024 | Summer Peak 2024 | Winter Peak 2025 | Winter Peak 2025 | Summer Peak 2025 | Summer Peak 2025
# |  | Firm Scenario | Planned Scenario | Firm Scenario | Planned Scenario | Firm Scenario | Planned Scenario
1 | Installed Resources (MW) | 38193 | 38253 | 38193 | 38253 | 38193 | 38488
2 | Total Reductions in Resources (MW) | 11337 | 11388 | 12019 | 11834 | 12651 | 12561
3 | Demand Measures (MW) | 995.95 | 995.95 | 915.4104 | 915.4104 | 1790.825 | 1790.825
4 | Firm Imports (+) / Exports (-) (MW) | 600 | 600 | 150 | -450 | 0 | 0
5 | Available Resources (MW) | 28451.95 | 28460.95 | 27239.4104 | 26884.4104 | 27332.825 | 27717.825
6 | Bottling | 41.8095 | 81.8095 | 382.8548 | 406.7571 | 0 | 34.0628
7 | Available Resources without Bottling (MW) | 28493.7595 | 28542.7595 | 27622.2652 | 27291.1675 | 27332.825 | 27751.8878

## Table 4.5
Back to main menu
Table 4.5: Summary of Zonal Energy for Firm Scenario Normal Weather
| 18-Month Energy Demand |  | 18-Month Energy Production |  | Net Inter-Zonal Energy Transfer | Zonal Energy Demand on Peak Day of 18-Month Period | Available Energy on Peak Day of 18 Month Period
| TWh | Average MW | TWh | Average MW | TWh | GWh | GWh
Ontario | 208.8 | 15878 | 208.8 | 15879 | 0 | 464.5 | 591.9
Bruce | 0.9 | 71 | 62.2 | 4729 | 61.3 | 1.3 | 118.4
East | 13.1 | 1000 | 18.2 | 1380 | 5.1 | 27.7 | 105.4
Essa | 15.1 | 1146 | 3.6 | 271 | -11.5 | 33.5 | 17
Niagara | 6.4 | 483 | 21.1 | 1604 | 14.7 | 15 | 48.7
Northeast | 15.1 | 1145 | 15.1 | 1151 | 0 | 26.4 | 37.8
Northwest | 5.3 | 403 | 6.5 | 497 | 1.2 | 9.4 | 15.4
Ottawa | 13.2 | 1004 | 0.7 | 50 | -12.5 | 30.4 | 1.6
Southwest | 42.7 | 3244 | 8 | 606 | -34.7 | 96.9 | 22
Toronto | 74.5 | 5665 | 57.3 | 4358 | -17.2 | 171.1 | 145.3
West | 22.6 | 1717 | 16.2 | 1232 | -6.4 | 52.8 | 80.4

## Table 4.6
Back to main menu
Table 4.6: Ontario Energy Production by Fuel Type for the Firm Scenario Normal Weather
Fuel Type (Grid Connected) | 2024 | 2025 | 2026 | Total
Nuclear | 58615.49 | 56417.74 | 0 | 115033.23
Hydro | 27230.38 | 27796.87 | 0 | 55027.25
Gas & Oil | 9441.44 | 13436.27 | 0 | 22877.71
Wind | 6941.28 | 7379.09 | 0 | 14320.37
Bio Fuel | 251.85 | 221.75 | 0 | 473.6
Other (Solar & DR) | 525.45 | 577.79 | 0 | 1103.24
Total | 103005.89 | 105829.51 | 0 | 208835.4

## Figure 6.3
Back to main menu
Figure 6.3: Monthly Off-Peak Wind Capacity Contribution Values
Month | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Off-Peak WCC (% of Installed Capacity) | 40.56% | 40.56% | 38.6% | 34.28% | 28.57% | 16.81% | 16.81% | 16.81% | 20.77% | 32.58% | 42.93% | 40.56%

## Table A1
Back to main menu
Table A1: Assessment of Resource Adequacy: Normal Weather, Firm Scenario
Week | Ontario | Total Installed | Total Reductions | Demand | Firm Imports (+) | Total Available | Required | Available | Available | Required | Required | Reserve Above
Ending | Demand | Capacity | in Resources | Measures | Exports (-) | Resources | Resources | Reserve | Reserve | Reserve | Reserve | Requirement
Day | MW | MW | MW | MW | MW | MW | MW | % | MW | % | MW | MW
2024-04-07 | 17840 | 38193 | 14710 | 770.5514 | -62 | 24191.5514 | 20523 | 35.61 | 6352 | 15.04 | 2683 | 3669
2024-04-14 | 17731 | 38193 | 16127 | 770.5514 | -62 | 22774.5514 | 20318 | 28.45 | 5044 | 14.59 | 2587 | 2457
2024-04-21 | 17689 | 38193 | 15897 | 770.5514 | -62 | 23004.5514 | 20301 | 30.05 | 5316 | 14.77 | 2612 | 2704
2024-04-28 | 17396 | 38193 | 17440 | 770.5514 | -62 | 21461.5514 | 20043 | 23.37 | 4066 | 15.22 | 2647 | 1419
2024-05-05 | 17364 | 38193 | 17032 | 940.0544 | -62 | 22039.0544 | 20201 | 26.92 | 4675 | 16.34 | 2837 | 1838
2024-05-12 | 17274 | 38193 | 17357 | 940.0544 | 600 | 22376.0544 | 20239 | 29.54 | 5102 | 17.16 | 2965 | 2137
2024-05-19 | 17475 | 38193 | 16290 | 940.0544 | 600 | 23443.0544 | 20436 | 34.15 | 5968 | 16.94 | 2961 | 3007
2024-05-26 | 17543 | 38193 | 15882 | 940.0544 | 600 | 23851.0544 | 20838 | 35.96 | 6308 | 18.78 | 3295 | 3013
2024-06-02 | 19149 | 38193 | 16103 | 940.0544 | 600 | 23630.0544 | 22600 | 23.4 | 4481 | 18.02 | 3451 | 1030
2024-06-09 | 19554 | 38193 | 14514 | 1032.3044 | 600 | 25311.3044 | 22966 | 29.44 | 5757 | 17.45 | 3412 | 2345
2024-06-16 | 21217 | 38193 | 14428 | 1032.3044 | 600 | 25397.3044 | 24392 | 19.7 | 4180 | 14.96 | 3175 | 1005
2024-06-23 | 21880 | 38193 | 13548 | 1032.3044 | 600 | 26277.3044 | 24835 | 20.1 | 4397 | 13.51 | 2955 | 1442
2024-06-30 | 22502 | 38193 | 11364 | 1018.15 | 600 | 28447.15 | 25376 | 26.42 | 5945 | 12.77 | 2874 | 3071
2024-07-07 | 22449 | 38193 | 11163 | 1018.15 | 600 | 28648.15 | 25519 | 27.61 | 6199 | 13.68 | 3070 | 3129
2024-07-14 | 22685 | 38193 | 11039 | 995.95 | 600 | 28749.95 | 25567 | 26.74 | 6065 | 12.7 | 2882 | 3183
2024-07-21 | 22753 | 38193 | 11337 | 995.95 | 600 | 28451.95 | 25654 | 25.05 | 5699 | 12.75 | 2901 | 2798
2024-07-28 | 22699 | 38193 | 11037 | 995.95 | 600 | 28751.95 | 25791 | 26.67 | 6053 | 13.62 | 3092 | 2961
2024-08-04 | 22625 | 38193 | 11239 | 995.95 | 600 | 28549.95 | 25531 | 26.19 | 5925 | 12.84 | 2906 | 3019
2024-08-11 | 22582 | 38193 | 11486 | 1018.15 | 600 | 28325.15 | 25580 | 25.43 | 5743 | 13.28 | 2998 | 2745
2024-08-18 | 22569 | 38193 | 11943 | 995.95 | 600 | 27845.95 | 25593 | 23.38 | 5277 | 13.4 | 3024 | 2253
2024-08-25 | 22539 | 38193 | 11918 | 1018.15 | 600 | 27893.15 | 25958 | 23.75 | 5354 | 15.17 | 3419 | 1935
2024-09-01 | 22462 | 38193 | 12190 | 1018.15 | 600 | 27621.15 | 25937 | 22.97 | 5159 | 15.47 | 3475 | 1684
2024-09-08 | 21915 | 38193 | 12078 | 1032.3044 | 600 | 27747.3044 | 25353 | 26.61 | 5832 | 15.69 | 3438 | 2394
2024-09-15 | 21957 | 38193 | 13145 | 1108.6794 | 600 | 26756.6794 | 24668 | 21.86 | 4800 | 12.35 | 2711 | 2089
2024-09-22 | 20481 | 38193 | 12880 | 1032.3044 | 600 | 26945.3044 | 23272 | 31.56 | 6464 | 13.63 | 2791 | 3673
2024-09-29 | 18884 | 38193 | 14291 | 1032.3044 | 600 | 25534.3044 | 21158 | 35.21 | 6650 | 12.04 | 2274 | 4376
2024-10-06 | 17978 | 38193 | 15282 | 940.0544 | 600 | 24451.0544 | 20386 | 36.01 | 6473 | 13.39 | 2408 | 4065
2024-10-13 | 17690 | 38193 | 14886 | 940.0544 | 600 | 24847.0544 | 20331 | 40.46 | 7157 | 14.93 | 2641 | 4516
2024-10-20 | 17611 | 38193 | 15591 | 940.0544 | 600 | 24142.0544 | 19973 | 37.08 | 6531 | 13.41 | 2362 | 4169
2024-10-27 | 17834 | 38193 | 15285 | 940.0544 | 600 | 24448.0544 | 20080 | 37.09 | 6614 | 12.59 | 2246 | 4368
2024-11-03 | 17986 | 38193 | 15259 | 940.0544 | 150 | 24024.0544 | 20325 | 33.57 | 6038 | 13 | 2339 | 3699
2024-11-10 | 18582 | 38193 | 15347 | 839.0354 | 150 | 23835.0354 | 21019 | 28.27 | 5253 | 13.11 | 2437 | 2816
2024-11-17 | 19240 | 38193 | 15500 | 839.0354 | 150 | 23682.0354 | 21862 | 23.09 | 4442 | 13.63 | 2622 | 1820
2024-11-24 | 19922 | 38193 | 13368 | 839.0354 | 150 | 25814.0354 | 22285 | 29.58 | 5892 | 11.86 | 2363 | 3529
2024-12-01 | 20150 | 38193 | 12845 | 839.0354 | 150 | 26337.0354 | 22777 | 30.7 | 6187 | 13.04 | 2627 | 3560
2024-12-08 | 20630 | 38193 | 12530 | 839.0354 | 150 | 26652.0354 | 23060 | 29.19 | 6022 | 11.78 | 2430 | 3592
2024-12-15 | 20818 | 38193 | 12049 | 839.0354 | 150 | 27133.0354 | 23393 | 30.33 | 6315 | 12.37 | 2575 | 3740
2024-12-22 | 20894 | 38193 | 12141 | 839.0354 | 150 | 27041.0354 | 23605 | 29.42 | 6147 | 12.98 | 2711 | 3436
2024-12-29 | 18767 | 38193 | 11598 | 839.0354 | 150 | 27584.0354 | 21333 | 46.98 | 8817 | 13.67 | 2566 | 6251
2025-01-05 | 20148 | 38193 | 11575 | 839.0354 | 150 | 27607.0354 | 22731 | 37.02 | 7459 | 12.82 | 2583 | 4876
2025-01-12 | 21434 | 38193 | 11202 | 839.0354 | 150 | 27980.0354 | 24045 | 30.54 | 6546 | 12.18 | 2611 | 3935
2025-01-19 | 21456 | 38193 | 11293 | 839.0354 | 150 | 27889.0354 | 24052 | 29.98 | 6433 | 12.1 | 2596 | 3837
2025-01-26 | 21718 | 38193 | 12019 | 915.4104 | 150 | 27239.4104 | 24235 | 25.42 | 5521 | 11.59 | 2517 | 3004
2025-02-02 | 21688 | 38193 | 12213 | 839.0354 | 150 | 26969.0354 | 24153 | 24.35 | 5281 | 11.37 | 2465 | 2816
2025-02-09 | 21287 | 38193 | 12241 | 915.4104 | 150 | 27017.4104 | 24000 | 26.92 | 5730 | 12.74 | 2713 | 3017
2025-02-16 | 20820 | 38193 | 12321 | 839.0354 | 150 | 26861.0354 | 23448 | 29.02 | 6041 | 12.62 | 2628 | 3413
2025-02-23 | 20641 | 38193 | 11644 | 839.0354 | 150 | 27538.0354 | 23226 | 33.41 | 6897 | 12.52 | 2585 | 4312
2025-03-02 | 20540 | 38193 | 11798 | 839.0354 | 150 | 27384.0354 | 23034 | 33.32 | 6844 | 12.14 | 2494 | 4350
2025-03-09 | 19963 | 38193 | 13363 | 839.0354 | 150 | 25819.0354 | 22362 | 29.33 | 5856 | 12.02 | 2399 | 3457
2025-03-16 | 19437 | 38193 | 13151 | 839.0354 | 150 | 26031.0354 | 21954 | 33.92 | 6594 | 12.95 | 2517 | 4077
2025-03-23 | 18881 | 38193 | 14091 | 839.0354 | 150 | 25091.0354 | 21360 | 32.89 | 6210 | 13.13 | 2479 | 3731
2025-03-30 | 18407 | 38193 | 14720 | 839.0354 | 150 | 24462.0354 | 20844 | 32.9 | 6055 | 13.24 | 2437 | 3618
2025-04-06 | 18139 | 38193 | 15712 | 839.0354 | 150 | 23470.0354 | 20840 | 29.39 | 5331 | 14.89 | 2701 | 2630
2025-04-13 | 18028 | 38193 | 13532 | 839.0354 | 150 | 25650.0354 | 20633 | 42.28 | 7622 | 14.45 | 2605 | 5017
2025-04-20 | 17984 | 38193 | 16007 | 839.0354 | 150 | 23175.0354 | 20614 | 28.86 | 5191 | 14.62 | 2630 | 2561
2025-04-27 | 17695 | 38193 | 15071 | 839.0354 | 150 | 24111.0354 | 20360 | 36.26 | 6416 | 15.06 | 2665 | 3751
2025-05-04 | 17674 | 38193 | 12799 | 839.0354 | 150 | 26383.0354 | 20529 | 49.28 | 8709 | 16.15 | 2855 | 5854
2025-05-11 | 17523 | 38193 | 14755 | 1734.9294 | 0 | 25172.9294 | 20506 | 43.66 | 7650 | 17.02 | 2983 | 4667
2025-05-18 | 17814 | 38193 | 13000 | 1734.9294 | 0 | 26927.9294 | 20793 | 51.16 | 9114 | 16.72 | 2979 | 6135
2025-05-25 | 17816 | 38193 | 12863 | 1734.9294 | 0 | 27064.9294 | 21125 | 51.91 | 9249 | 18.57 | 3309 | 5940
2025-06-01 | 19430 | 38193 | 12197 | 1734.9294 | 0 | 27730.9294 | 22894 | 42.72 | 8301 | 17.83 | 3464 | 4837
2025-06-08 | 19813 | 38193 | 12924 | 1827.1794 | 0 | 27096.1794 | 23239 | 36.76 | 7283 | 17.29 | 3426 | 3857
2025-06-15 | 21493 | 38193 | 12852 | 1827.1794 | 0 | 27168.1794 | 24682 | 26.4 | 5675 | 14.84 | 3189 | 2486
2025-06-22 | 22132 | 38193 | 12812 | 1827.1794 | 0 | 27208.1794 | 25101 | 22.94 | 5076 | 13.41 | 2969 | 2107
2025-06-29 | 22622 | 38193 | 12335 | 1790.825 | 0 | 27648.825 | 25510 | 22.22 | 5027 | 12.77 | 2888 | 2139
2025-07-06 | 22619 | 38193 | 12440 | 1813.025 | 0 | 27566.025 | 25601 | 21.87 | 4947 | 13.18 | 2982 | 1965
2025-07-13 | 22821 | 38193 | 12512 | 1790.825 | 0 | 27471.825 | 25606 | 20.38 | 4651 | 12.2 | 2785 | 1866
2025-07-20 | 22872 | 38193 | 12651 | 1790.825 | 0 | 27332.825 | 25679 | 19.5 | 4461 | 12.27 | 2807 | 1654
2025-07-27 | 22825 | 38193 | 12595 | 1790.825 | 0 | 27388.825 | 25819 | 20 | 4564 | 13.12 | 2994 | 1570
2025-08-03 | 22734 | 38193 | 12800 | 1790.825 | 0 | 27183.825 | 25543 | 19.57 | 4450 | 12.36 | 2809 | 1641
2025-08-10 | 22695 | 38193 | 12848 | 1813.025 | 0 | 27158.025 | 25614 | 19.67 | 4463 | 12.86 | 2919 | 1544
2025-08-17 | 22674 | 38193 | 12913 | 1813.025 | 0 | 27093.025 | 25618 | 19.49 | 4419 | 12.98 | 2944 | 1475
2025-08-24 | 22637 | 38193 | 12960 | 1813.025 | 0 | 27046.025 | 25975 | 19.48 | 4409 | 14.75 | 3338 | 1071
2025-08-31 | 22722 | 38193 | 12890 | 1813.025 | 0 | 27116.025 | 26116 | 19.34 | 4394 | 14.94 | 3394 | 1000
2025-09-07 | 22012 | 38193 | 12675 | 1827.1794 | 0 | 27345.1794 | 25368 | 24.23 | 5333 | 15.25 | 3356 | 1977
2025-09-14 | 22066 | 38193 | 12805 | 1903.5544 | 0 | 27291.5544 | 24747 | 23.68 | 5226 | 12.15 | 2681 | 2545
2025-09-21 | 20744 | 38193 | 13296 | 1827.1794 | 0 | 26724.1794 | 23460 | 28.83 | 5980 | 13.09 | 2716 | 3264
2025-09-28 | 19148 | 38193 | 14545 | 1827.1794 | 0 | 25475.1794 | 21436 | 33.04 | 6327 | 11.95 | 2288 | 4039
2025-10-05 | 18213 | 38193 | 15407 | 1734.9294 | 0 | 24520.9294 | 20635 | 34.63 | 6308 | 13.3 | 2422 | 3886
Note: The reader should be aware that security and adequacy assessments are published on the IESO web site on a daily basis that progressively supersedes information presented
in this report.
Back to main menu

## Table A2
Back to main menu
Table A2: Assessment of Resource Adequacy: Normal Weather, Planned Scenario
Week | Ontario | Total Installed | Total Reductions | Demand | Firm Imports (+) | Total Available | Required | Available | Available | Required | Required | Reserve Above
Ending | Demand | Capacity | in Resources | Measures | Exports (-) | Resources | Resources | Reserve | Reserve | Reserve | Reserve | Requirement
Day | MW | MW | MW | MW | MW | MW | MW | % | MW | % | MW | MW
2024-04-07 | 17840 | 38193 | 14710 | 770.5514 | -62 | 24191.5514 | 20523 | 35.61 | 6352 | 15.04 | 2683 | 3669
2024-04-14 | 17731 | 38193 | 16087 | 770.5514 | -62 | 22814.5514 | 20318 | 28.67 | 5084 | 14.59 | 2587 | 2497
2024-04-21 | 17689 | 38193 | 15857 | 770.5514 | -62 | 23044.5514 | 20301 | 30.28 | 5356 | 14.77 | 2612 | 2744
2024-04-28 | 17396 | 38193 | 17400 | 770.5514 | -62 | 21501.5514 | 20043 | 23.6 | 4106 | 15.22 | 2647 | 1459
2024-05-05 | 17364 | 38193 | 16992 | 940.0544 | -62 | 22079.0544 | 20201 | 27.15 | 4715 | 16.34 | 2837 | 1878
2024-05-12 | 17274 | 38193 | 17318 | 940.0544 | 600 | 22415.0544 | 20239 | 29.76 | 5141 | 17.16 | 2965 | 2176
2024-05-19 | 17475 | 38193 | 16237 | 940.0544 | 600 | 23496.0544 | 20436 | 34.45 | 6021 | 16.94 | 2961 | 3060
2024-05-26 | 17543 | 38193 | 15882 | 940.0544 | 600 | 23851.0544 | 20838 | 35.96 | 6308 | 18.78 | 3295 | 3013
2024-06-02 | 19149 | 38193 | 16089 | 940.0544 | 600 | 23644.0544 | 22600 | 23.47 | 4495 | 18.02 | 3451 | 1044
2024-06-09 | 19554 | 38193 | 14505 | 1032.3044 | 600 | 25320.3044 | 22966 | 29.49 | 5766 | 17.45 | 3412 | 2354
2024-06-16 | 21217 | 38193 | 14379 | 1032.3044 | 600 | 25446.3044 | 24392 | 19.93 | 4229 | 14.96 | 3175 | 1054
2024-06-23 | 21880 | 38193 | 13500 | 1032.3044 | 600 | 26325.3044 | 24835 | 20.32 | 4445 | 13.51 | 2955 | 1490
2024-06-30 | 22502 | 38193 | 11316 | 1018.15 | 600 | 28495.15 | 25376 | 26.63 | 5993 | 12.77 | 2874 | 3119
2024-07-07 | 22449 | 38253 | 11214 | 1018.15 | 600 | 28657.15 | 25520 | 27.65 | 6208 | 13.68 | 3071 | 3137
2024-07-14 | 22685 | 38253 | 11090 | 995.95 | 600 | 28758.95 | 25568 | 26.78 | 6074 | 12.71 | 2883 | 3191
2024-07-21 | 22753 | 38253 | 11388 | 995.95 | 600 | 28460.95 | 25655 | 25.09 | 5708 | 12.75 | 2902 | 2806
2024-07-28 | 22699 | 38253 | 11088 | 995.95 | 600 | 28760.95 | 25792 | 26.71 | 6062 | 13.63 | 3093 | 2969
2024-08-04 | 22625 | 38253 | 11290 | 995.95 | 600 | 28558.95 | 25532 | 26.23 | 5934 | 12.85 | 2907 | 3027
2024-08-11 | 22582 | 38253 | 11306 | 1018.15 | 600 | 28565.15 | 25598 | 26.49 | 5983 | 13.36 | 3016 | 2967
2024-08-18 | 22569 | 38253 | 11749 | 995.95 | 600 | 28099.95 | 25611 | 24.51 | 5531 | 13.48 | 3042 | 2489
2024-08-25 | 22539 | 38253 | 11929 | 1018.15 | 600 | 27942.15 | 25959 | 23.97 | 5403 | 15.17 | 3420 | 1983
2024-09-01 | 22462 | 38253 | 11996 | 1018.15 | 600 | 27875.15 | 25955 | 24.1 | 5413 | 15.55 | 3493 | 1920
2024-09-08 | 21915 | 38253 | 11939 | 1032.3044 | 600 | 27946.3044 | 25370 | 27.52 | 6031 | 15.77 | 3455 | 2576
2024-09-15 | 21957 | 38253 | 12950 | 1108.6794 | 600 | 27011.6794 | 24686 | 23.02 | 5055 | 12.43 | 2729 | 2326
2024-09-22 | 20481 | 38253 | 12759 | 1032.3044 | 600 | 27126.3044 | 23290 | 32.44 | 6645 | 13.72 | 2809 | 3836
2024-09-29 | 18884 | 38253 | 14157 | 1032.3044 | 600 | 25728.3044 | 21158 | 36.24 | 6844 | 12.04 | 2274 | 4570
2024-10-06 | 17978 | 38253 | 15351 | 940.0544 | 600 | 24442.0544 | 20386 | 35.96 | 6464 | 13.39 | 2408 | 4056
2024-10-13 | 17690 | 38253 | 14946 | 940.0544 | 600 | 24847.0544 | 20331 | 40.46 | 7157 | 14.93 | 2641 | 4516
2024-10-20 | 17611 | 38253 | 15632 | 940.0544 | 600 | 24161.0544 | 19973 | 37.19 | 6550 | 13.41 | 2362 | 4188
2024-10-27 | 17834 | 38253 | 15345 | 940.0544 | 600 | 24448.0544 | 20080 | 37.09 | 6614 | 12.59 | 2246 | 4368
2024-11-03 | 17986 | 38253 | 15286 | 940.0544 | -450 | 23457.0544 | 20325 | 30.42 | 5471 | 13 | 2339 | 3132
2024-11-10 | 18582 | 38253 | 15205 | 839.0354 | -450 | 23437.0354 | 21019 | 26.13 | 4855 | 13.11 | 2437 | 2418
2024-11-17 | 19240 | 38253 | 15338 | 839.0354 | -450 | 23304.0354 | 21862 | 21.12 | 4064 | 13.63 | 2622 | 1442
2024-11-24 | 19922 | 38253 | 13183 | 839.0354 | -450 | 25459.0354 | 22285 | 27.79 | 5537 | 11.86 | 2363 | 3174
2024-12-01 | 20150 | 38253 | 12700 | 839.0354 | -450 | 25942.0354 | 22777 | 28.74 | 5792 | 13.04 | 2627 | 3165
2024-12-08 | 20630 | 38253 | 12415 | 839.0354 | -450 | 26227.0354 | 23060 | 27.13 | 5597 | 11.78 | 2430 | 3167
2024-12-15 | 20818 | 38253 | 11927 | 839.0354 | -450 | 26715.0354 | 23393 | 28.33 | 5897 | 12.37 | 2575 | 3322
2024-12-22 | 20894 | 38253 | 12004 | 839.0354 | -450 | 26638.0354 | 23605 | 27.49 | 5744 | 12.98 | 2711 | 3033
2024-12-29 | 18767 | 38253 | 11482 | 839.0354 | -450 | 27160.0354 | 21351 | 44.72 | 8393 | 13.77 | 2584 | 5809
2025-01-05 | 20148 | 38253 | 11492 | 839.0354 | -450 | 27150.0354 | 22750 | 34.75 | 7002 | 12.91 | 2602 | 4400
2025-01-12 | 21434 | 38253 | 11092 | 839.0354 | -450 | 27550.0354 | 24063 | 28.53 | 6116 | 12.27 | 2629 | 3487
2025-01-19 | 21456 | 38253 | 11135 | 839.0354 | -450 | 27507.0354 | 24070 | 28.2 | 6051 | 12.18 | 2614 | 3437
2025-01-26 | 21718 | 38253 | 11834 | 915.4104 | -450 | 26884.4104 | 24251 | 23.79 | 5166 | 11.66 | 2533 | 2633
2025-02-02 | 21688 | 38253 | 12028 | 839.0354 | -450 | 26614.0354 | 24171 | 22.71 | 4926 | 11.45 | 2483 | 2443
2025-02-09 | 21287 | 38253 | 12261 | 915.4104 | -450 | 26457.4104 | 24002 | 24.29 | 5170 | 12.75 | 2715 | 2455
2025-02-16 | 20820 | 38253 | 12192 | 839.0354 | -450 | 26450.0354 | 23466 | 27.04 | 5630 | 12.71 | 2646 | 2984
2025-02-23 | 20641 | 38253 | 11553 | 839.0354 | -450 | 27089.0354 | 23244 | 31.24 | 6448 | 12.61 | 2603 | 3845
2025-03-02 | 20540 | 38253 | 11671 | 839.0354 | -450 | 26971.0354 | 23052 | 31.31 | 6431 | 12.23 | 2512 | 3919
2025-03-09 | 19963 | 38253 | 13199 | 839.0354 | -450 | 25443.0354 | 22362 | 27.45 | 5480 | 12.02 | 2399 | 3081
2025-03-16 | 19437 | 38253 | 12972 | 839.0354 | -450 | 25670.0354 | 21954 | 32.07 | 6233 | 12.95 | 2517 | 3716
2025-03-23 | 18881 | 38253 | 13942 | 839.0354 | -450 | 24700.0354 | 21360 | 30.82 | 5819 | 13.13 | 2479 | 3340
2025-03-30 | 18407 | 38253 | 14600 | 839.0354 | -450 | 24042.0354 | 20844 | 30.61 | 5635 | 13.24 | 2437 | 3198
2025-04-06 | 18139 | 38253 | 15713 | 839.0354 | -450 | 22929.0354 | 20840 | 26.41 | 4790 | 14.89 | 2701 | 2089
2025-04-13 | 18028 | 38253 | 13552 | 839.0354 | -450 | 25090.0354 | 20633 | 39.17 | 7062 | 14.45 | 2605 | 4457
2025-04-20 | 17984 | 38253 | 16008 | 839.0354 | -450 | 22634.0354 | 20614 | 25.86 | 4650 | 14.62 | 2630 | 2020
2025-04-27 | 17695 | 38253 | 15091 | 839.0354 | -450 | 23551.0354 | 20360 | 33.09 | 5856 | 15.06 | 2665 | 3191
2025-05-04 | 17674 | 38253 | 12819 | 839.0354 | -450 | 25823.0354 | 20529 | 46.11 | 8149 | 16.15 | 2855 | 5294
2025-05-11 | 17523 | 38253 | 14775 | 1734.9294 | 0 | 25212.9294 | 20506 | 43.89 | 7690 | 17.02 | 2983 | 4707
2025-05-18 | 17814 | 38253 | 13020 | 1734.9294 | 0 | 26967.9294 | 20793 | 51.39 | 9154 | 16.72 | 2979 | 6175
2025-05-25 | 17816 | 38253 | 12883 | 1734.9294 | 0 | 27104.9294 | 21125 | 52.14 | 9289 | 18.57 | 3309 | 5980
2025-06-01 | 19430 | 38253 | 12203 | 1734.9294 | 0 | 27784.9294 | 22894 | 43 | 8355 | 17.83 | 3464 | 4891
2025-06-08 | 19813 | 38488 | 13006 | 1827.1794 | 0 | 27309.1794 | 23239 | 37.83 | 7496 | 17.29 | 3426 | 4070
2025-06-15 | 21493 | 38488 | 12774 | 1827.1794 | 0 | 27541.1794 | 24682 | 28.14 | 6048 | 14.84 | 3189 | 2859
2025-06-22 | 22132 | 38488 | 12749 | 1827.1794 | 0 | 27566.1794 | 25101 | 24.55 | 5434 | 13.41 | 2969 | 2465
2025-06-29 | 22622 | 38488 | 12309 | 1790.825 | 0 | 27969.825 | 25510 | 23.64 | 5348 | 12.77 | 2888 | 2460
2025-07-06 | 22619 | 38488 | 12384 | 1813.025 | 0 | 27917.025 | 25619 | 23.42 | 5298 | 13.26 | 3000 | 2298
2025-07-13 | 22821 | 38488 | 12413 | 1790.825 | 0 | 27865.825 | 25624 | 22.11 | 5045 | 12.28 | 2803 | 2242
2025-07-20 | 22872 | 38488 | 12561 | 1790.825 | 0 | 27717.825 | 25697 | 21.19 | 4846 | 12.35 | 2825 | 2021
2025-07-27 | 22825 | 38488 | 12523 | 1790.825 | 0 | 27755.825 | 25837 | 21.6 | 4931 | 13.2 | 3012 | 1919
2025-08-03 | 22734 | 38488 | 12677 | 1790.825 | 0 | 27601.825 | 25561 | 21.41 | 4868 | 12.44 | 2827 | 2041
2025-08-10 | 22695 | 38488 | 12725 | 1813.025 | 0 | 27576.025 | 25631 | 21.51 | 4881 | 12.94 | 2936 | 1945
2025-08-17 | 22674 | 38488 | 12789 | 1813.025 | 0 | 27512.025 | 25636 | 21.34 | 4838 | 13.06 | 2962 | 1876
2025-08-24 | 22637 | 38488 | 12837 | 1813.025 | 0 | 27464.025 | 25992 | 21.32 | 4827 | 14.82 | 3355 | 1472
2025-08-31 | 22722 | 38488 | 12766 | 1813.025 | 0 | 27535.025 | 26133 | 21.18 | 4813 | 15.01 | 3411 | 1402
2025-09-07 | 22012 | 38723 | 12872 | 1827.1794 | 0 | 27678.1794 | 25385 | 25.74 | 5666 | 15.32 | 3373 | 2293
2025-09-14 | 22066 | 38723 | 12967 | 1903.5544 | 0 | 27659.5544 | 24765 | 25.35 | 5594 | 12.23 | 2699 | 2895
2025-09-21 | 20744 | 38723 | 13455 | 1827.1794 | 0 | 27095.1794 | 23477 | 30.62 | 6351 | 13.17 | 2733 | 3618
2025-09-28 | 19148 | 38723 | 14861 | 1827.1794 | 0 | 25689.1794 | 21436 | 34.16 | 6541 | 11.95 | 2288 | 4253
2025-10-05 | 18213 | 38723 | 15723 | 1734.9294 | 0 | 24734.9294 | 20635 | 35.81 | 6522 | 13.3 | 2422 | 4100
Note: The reader should be aware that security and adequacy assessments are published on the IESO web site on a daily basis that progressively supersedes
information presented in this report.
Back to main menu

## Table A3
Back to main menu
Table A3: Zonal Bottled Generation: Normal Weather, Both Scenarios
Week | Firm Scenario | Firm Scenario | Firm Scenario | Planned Scenario | Planned Scenario | Planned Scenario
Ending | Bruce & West | Northeast | Northwest | Bruce & West | Northeast | Northwest
Day | MW | MW | MW | MW | MW | MW
2024-04-07 | 523.0902 | 0 | 21.9128 | 523.0902 | 0 | 61.9128
2024-04-14 | 727.5228 | 0 | 0 | 727.5228 | 0 | 0
2024-04-21 | 714.6822 | 0 | 0 | 714.6822 | 0 | 0
2024-04-28 | 715.9379 | 0 | 0 | 715.9379 | 0 | 0
2024-05-05 | 388.8354 | 0 | 0 | 402.5761 | 0 | 0
2024-05-12 | 0 | 0 | 0 | 0 | 0 | 14.6057
2024-05-19 | 0 | 0 | 0 | 0 | 0 | 0
2024-05-26 | 548.9336 | 861.8347 | 0 | 562.6742 | 901.8347 | 0
2024-06-02 | 229.454 | 784.827 | 0 | 229.454 | 824.827 | 0
2024-06-09 | 0 | 288.1704 | 0 | 0 | 328.1704 | 0
2024-06-16 | 0 | 0 | 0 | 0 | 0 | 0
2024-06-23 | 590.7591 | 0 | 0 | 590.7591 | 0 | 0
2024-06-30 | 380.7611 | 0 | 0 | 380.7611 | 0 | 0
2024-07-07 | 0 | 0 | 61.0398 | 0 | 0 | 101.0398
2024-07-14 | 0 | 0 | 32.3676 | 0 | 0 | 72.3676
2024-07-21 | 0 | 0 | 41.8095 | 0 | 0 | 81.8095
2024-07-28 | 0 | 0 | 56.0783 | 0 | 0 | 96.0783
2024-08-04 | 0 | 0 | 2.6092 | 0 | 0 | 42.6092
2024-08-11 | 0 | 0 | 0 | 0 | 0 | 13.8475
2024-08-18 | 0 | 0 | 0 | 0 | 0 | 0
2024-08-25 | 0 | 0 | 0 | 0 | 0 | 0
2024-09-01 | 472.2882 | 0 | 0 | 472.2882 | 0 | 0
2024-09-08 | 517.0846 | 0 | 0 | 517.0846 | 0 | 55.9963
2024-09-15 | 516.257 | 0 | 0 | 516.257 | 0 | 0
2024-09-22 | 515.3344 | 0 | 0 | 515.3344 | 0 | 73.6928
2024-09-29 | 529.0026 | 0 | 0 | 529.0026 | 0 | 60.8852
2024-10-06 | 62.081 | 195.1628 | 0 | 80.7928 | 410.2257 | 29.9371
2024-10-13 | 535.2632 | 83.3627 | 0 | 553.975 | 243.1616 | 85.2011
2024-10-20 | 0 | 103.7971 | 0 | 0 | 260.0126 | 88.7845
2024-10-27 | 464.4294 | 67.5986 | 0 | 483.1413 | 294.6312 | 17.9674
2024-11-03 | 1856.7906 | 0 | 0 | 1882.6481 | 0 | 0
2024-11-10 | 1611.7899 | 0 | 0 | 1637.6474 | 0 | 43.3449
2024-11-17 | 1766.2468 | 0 | 0 | 1792.1043 | 0 | 22.8773
2024-11-24 | 1587.5246 | 0 | 0 | 1613.3821 | 0 | 0
2024-12-01 | 1679.5111 | 0 | 0 | 1703.4134 | 0 | 42.6865
2024-12-08 | 1780.0147 | 0 | 0 | 1803.917 | 0 | 70.0091
2024-12-15 | 1578.7506 | 0 | 0 | 1602.6529 | 0 | 62.9533
2024-12-22 | 1814.575 | 0 | 0 | 1838.4773 | 0 | 47.3913
2024-12-29 | 2353.3624 | 0 | 0 | 2377.2647 | 0 | 68.9189
2025-01-05 | 1201.4103 | 0 | 0 | 1225.3126 | 0 | 102.5381
2025-01-12 | 708.3229 | 0 | 0 | 732.2252 | 0 | 75.3651
2025-01-19 | 814.2636 | 0 | 0 | 838.1659 | 0 | 27.1119
2025-01-26 | 382.8548 | 0 | 0 | 406.7571 | 0 | 0
2025-02-02 | 397.5498 | 0 | 0 | 421.4521 | 0 | 0
2025-02-09 | 378.0928 | 0 | 0 | 401.9951 | 0 | 0
2025-02-16 | 514.8488 | 0 | 0 | 538.7511 | 0 | 55.9411
2025-02-23 | 214.1278 | 0 | 0 | 238.0301 | 0 | 93.9273
2025-03-02 | 0 | 0 | 0 | 0 | 0 | 81.4471
2025-03-09 | 160.3292 | 0 | 0 | 182.9829 | 0 | 20.9606
2025-03-16 | 196.2074 | 0 | 0 | 218.8611 | 0 | 5.7723
2025-03-23 | 0 | 0 | 0 | 0 | 0 | 58.7783
2025-03-30 | 0 | 0 | 0 | 0 | 0 | 87.5397
2025-04-06 | 0 | 0 | 0 | 0 | 0 | 0
2025-04-13 | 413.438 | 0 | 0 | 432.6768 | 0 | 0
2025-04-20 | 0 | 0 | 0 | 0 | 0 | 0
2025-04-27 | 795.7187 | 0 | 0 | 814.9574 | 0 | 0
2025-05-04 | 333.8625 | 0 | 0 | 347.6032 | 0 | 0
2025-05-11 | 428.924 | 0 | 0 | 442.6647 | 0 | 0
2025-05-18 | 291.4209 | 0 | 0 | 305.1615 | 0 | 0
2025-05-25 | 703.3767 | 0 | 0 | 717.1174 | 0 | 0
2025-06-01 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-08 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-15 | 0 | 0 | 0 | 0 | 0 | 45.6075
2025-06-22 | 0 | 0 | 0 | 0 | 0 | 60.5738
2025-06-29 | 0 | 0 | 0 | 0 | 0 | 98.1554
2025-07-06 | 0 | 0 | 0 | 0 | 0 | 67.13
2025-07-13 | 0 | 0 | 0 | 0 | 0 | 24.7355
2025-07-20 | 0 | 0 | 0 | 0 | 0 | 34.0628
2025-07-27 | 0 | 0 | 0 | 0 | 0 | 51.7923
2025-08-03 | 0 | 0 | 0 | 0 | 0 | 0
2025-08-10 | 0 | 0 | 0 | 0 | 0 | 0
2025-08-17 | 0 | 0 | 0 | 0 | 0 | 0
2025-08-24 | 0 | 0 | 0 | 0 | 0 | 0
2025-08-31 | 0 | 0 | 0 | 0 | 0 | 0
2025-09-07 | 0 | 0 | 0 | 0 | 0 | 86.5422
2025-09-14 | 0 | 0 | 0 | 0 | 0 | 50.3801
2025-09-21 | 0 | 0 | 0 | 0 | 0 | 48.0441
2025-09-28 | 0 | 0 | 0 | 0 | 0 | 0
2025-10-05 | 0 | 0 | 0 | 0 | 0 | 0
Note: The bottled generation values indicated in the table are capacity values calculated at the hour of weekly peak.
In real time operation, the actual amount of bottled generation will depend on many conditions prevailing at the time,
including the local generation levels, overall generation dispatch and the direction and
levels of flows into and out of Ontario.
Zonal information is found in the Ontario Transmission System document.
Back to main menu

## Table A4
Back to main menu
Table A4: Assessment of Resource Adequacy: Extreme Weather, Firm Scenario
Week | Ontario | Total Internal | Total Reductions | Demand | Firm Imports (+) | Total Available | Required | Available | Available | Required | Required | Reserve Above
Ending | Demand | Resources | in Resources | Measures | Exports (-) | Resources | Resources | Reserve | Reserve | Reserve | Reserve | Requirement
Day | MW | MW | MW | MW | MW | MW | MW | % | MW | % | MW | MW
2024-04-07 | 18792 | 38193 | 14816 | 657.822 | -79 | 23956 | 20908 | 27 | 5164 | 11 | 2116 | 3048
2024-04-14 | 18254 | 38193 | 16376 | 657.822 | -79 | 22396 | 20370 | 23 | 4142 | 12 | 2116 | 2026
2024-04-21 | 18324 | 38193 | 15839 | 657.822 | -79 | 22933 | 20440 | 25 | 4609 | 12 | 2116 | 2493
2024-04-28 | 17799 | 38193 | 17635 | 657.822 | -79 | 21137 | 19915 | 19 | 3338 | 12 | 2116 | 1222
2024-05-05 | 19062 | 38193 | 17372 | 657.822 | -79 | 21400 | 21178 | 12 | 2338 | 11 | 2116 | 222
2024-05-12 | 19568 | 38193 | 18398 | 827.325 | 0 | 20622 | 21684 | 5 | 1054 | 11 | 2116 | -1062
2024-05-19 | 21027 | 38193 | 17342 | 827.325 | 0 | 21678 | 23143 | 3 | 651 | 10 | 2116 | -1465
2024-05-26 | 20993 | 38193 | 16343 | 827.325 | 0 | 22677 | 23114 | 8 | 1684 | 10 | 2121 | -437
2024-06-02 | 21646 | 38193 | 16289 | 995.95 | 0 | 22900 | 23627 | 6 | 1254 | 9 | 1981 | -727
2024-06-09 | 22045 | 38193 | 15910 | 995.95 | 0 | 23279 | 24092 | 6 | 1234 | 9 | 2047 | -813
2024-06-16 | 22282 | 38193 | 16088 | 995.95 | 0 | 23101 | 24329 | 4 | 819 | 9 | 2047 | -1228
2024-06-23 | 23110 | 38193 | 15180 | 995.95 | 0 | 24009 | 25325 | 4 | 899 | 10 | 2215 | -1316
2024-06-30 | 24017 | 38193 | 13106 | 995.95 | 0 | 26083 | 26453 | 9 | 2066 | 10 | 2436 | -370
2024-07-07 | 24194 | 38193 | 12796 | 995.95 | 0 | 26393 | 26636 | 9 | 2199 | 10 | 2442 | -243
2024-07-14 | 24380 | 38193 | 12708 | 995.95 | 0 | 26481 | 26824 | 9 | 2101 | 10 | 2444 | -343
2024-07-21 | 24550 | 38193 | 12961 | 995.95 | 0 | 26228 | 26992 | 7 | 1678 | 10 | 2442 | -764
2024-07-28 | 24669 | 38193 | 12686 | 995.95 | 0 | 26503 | 27113 | 7 | 1834 | 10 | 2444 | -610
2024-08-04 | 24606 | 38193 | 12941 | 995.95 | 0 | 26248 | 27050 | 7 | 1642 | 10 | 2444 | -802
2024-08-11 | 24532 | 38193 | 13195 | 995.95 | 0 | 25994 | 26955 | 6 | 1462 | 10 | 2423 | -961
2024-08-18 | 24657 | 38193 | 13594 | 995.95 | 0 | 25595 | 27080 | 4 | 938 | 10 | 2423 | -1485
2024-08-25 | 24508 | 38193 | 13574 | 995.95 | 0 | 25615 | 26931 | 5 | 1107 | 10 | 2423 | -1316
2024-09-01 | 24309 | 38193 | 13863 | 995.95 | 0 | 25326 | 26732 | 4 | 1017 | 10 | 2423 | -1406
2024-09-08 | 23662 | 38193 | 13802 | 995.95 | 0 | 25387 | 26092 | 7 | 1725 | 10 | 2430 | -705
2024-09-15 | 22987 | 38193 | 14806 | 995.95 | 0 | 24383 | 25362 | 6 | 1396 | 10 | 2375 | -979
2024-09-22 | 21892 | 38193 | 14590 | 995.95 | 0 | 24599 | 24263 | 12 | 2707 | 11 | 2371 | 336
2024-09-29 | 21119 | 38193 | 15988 | 995.95 | 0 | 23201 | 23181 | 10 | 2082 | 10 | 2062 | 20
2024-10-06 | 19574 | 38193 | 16927 | 827.325 | 0 | 22093 | 21537 | 13 | 2519 | 10 | 1963 | 556
2024-10-13 | 18676 | 38193 | 15302 | 827.325 | 0 | 23718 | 20613 | 27 | 5042 | 10 | 1937 | 3105
2024-10-20 | 18066 | 38193 | 16472 | 827.325 | 0 | 22548 | 19973 | 25 | 4482 | 11 | 1907 | 2575
2024-10-27 | 19099 | 38193 | 15754 | 827.325 | 0 | 23266 | 21055 | 22 | 4167 | 10 | 1956 | 2211
2024-11-03 | 19357 | 38193 | 14749 | 827.325 | 0 | 24271 | 21558 | 25 | 4914 | 11 | 2201 | 2713
2024-11-10 | 19922 | 38193 | 14923 | 726.306 | 0 | 23996 | 22067 | 20 | 4074 | 11 | 2145 | 1929
2024-11-17 | 19615 | 38193 | 15617 | 726.306 | 0 | 23302 | 21769 | 19 | 3687 | 11 | 2154 | 1533
2024-11-24 | 20210 | 38193 | 13418 | 726.306 | 0 | 25501 | 22467 | 26 | 5291 | 11 | 2257 | 3034
2024-12-01 | 20847 | 38193 | 12566 | 726.306 | 0 | 26353 | 23115 | 26 | 5506 | 11 | 2268 | 3238
2024-12-08 | 21379 | 38193 | 12460 | 726.306 | 0 | 26459 | 23658 | 24 | 5080 | 11 | 2279 | 2801
2024-12-15 | 21916 | 38193 | 11973 | 726.306 | 0 | 26946 | 24205 | 23 | 5030 | 10 | 2289 | 2741
2024-12-22 | 21989 | 38193 | 11680 | 726.306 | 0 | 27239 | 24278 | 24 | 5250 | 10 | 2289 | 2961
2024-12-29 | 20295 | 38193 | 11415 | 726.306 | 0 | 27504 | 22776 | 36 | 7209 | 12 | 2481 | 4728
2025-01-05 | 21075 | 38193 | 11540 | 726.306 | 0 | 27379 | 23461 | 30 | 6304 | 11 | 2386 | 3918
2025-01-12 | 22461 | 38193 | 11105 | 802.681 | 0 | 27891 | 24844 | 24 | 5430 | 11 | 2383 | 3047
2025-01-19 | 22499 | 38193 | 11335 | 802.681 | 0 | 27661 | 24885 | 23 | 5162 | 11 | 2386 | 2776
2025-01-26 | 22915 | 38193 | 12094 | 802.681 | 0 | 26902 | 25262 | 17 | 3987 | 10 | 2347 | 1640
2025-02-02 | 22675 | 38193 | 12199 | 802.681 | 0 | 26797 | 25022 | 18 | 4122 | 10 | 2347 | 1775
2025-02-09 | 22090 | 38193 | 12284 | 802.681 | 0 | 26712 | 24437 | 21 | 4622 | 11 | 2347 | 2275
2025-02-16 | 21977 | 38193 | 12202 | 802.681 | 0 | 26794 | 24324 | 22 | 4817 | 11 | 2347 | 2470
2025-02-23 | 22054 | 38193 | 11506 | 802.681 | 0 | 27490 | 24401 | 25 | 5436 | 11 | 2347 | 3089
2025-03-02 | 22113 | 38193 | 11824 | 802.681 | 0 | 27172 | 24427 | 23 | 5059 | 10 | 2314 | 2745
2025-03-09 | 21412 | 38193 | 13133 | 726.306 | 0 | 25786 | 23575 | 20 | 4374 | 10 | 2163 | 2211
2025-03-16 | 21089 | 38193 | 12885 | 726.306 | 0 | 26034 | 23252 | 23 | 4945 | 10 | 2163 | 2782
2025-03-23 | 20370 | 38193 | 14041 | 726.306 | 0 | 24878 | 22506 | 22 | 4508 | 10 | 2136 | 2372
2025-03-30 | 19548 | 38193 | 14689 | 726.306 | 0 | 24230 | 21643 | 24 | 4682 | 11 | 2095 | 2587
2025-04-06 | 19015 | 38193 | 15737 | 726.306 | 0 | 23182 | 21149 | 22 | 4167 | 11 | 2134 | 2033
2025-04-13 | 18480 | 38193 | 14075 | 726.306 | 0 | 24844 | 20614 | 34 | 6364 | 12 | 2134 | 4230
2025-04-20 | 18545 | 38193 | 16665 | 726.306 | 0 | 22254 | 20679 | 20 | 3709 | 12 | 2134 | 1575
2025-04-27 | 18016 | 38193 | 15232 | 726.306 | 0 | 23687 | 20150 | 31 | 5671 | 12 | 2134 | 3537
2025-05-04 | 19308 | 38193 | 13232 | 726.306 | 0 | 25687 | 21597 | 33 | 6379 | 12 | 2289 | 4090
2025-05-11 | 19725 | 38193 | 14808 | 1622.2 | 0 | 25007 | 21864 | 27 | 5282 | 11 | 2139 | 3143
2025-05-18 | 21191 | 38193 | 13248 | 1622.2 | 0 | 26567 | 23397 | 25 | 5376 | 10 | 2206 | 3170
2025-05-25 | 21162 | 38193 | 12740 | 1622.2 | 0 | 27075 | 23380 | 28 | 5913 | 10 | 2218 | 3695
2025-06-01 | 21872 | 38193 | 12778 | 1790.825 | 0 | 27206 | 24090 | 24 | 5334 | 10 | 2218 | 3116
2025-06-08 | 22197 | 38193 | 14110 | 1790.825 | 0 | 25874 | 24415 | 17 | 3677 | 10 | 2218 | 1459
2025-06-15 | 22442 | 38193 | 14047 | 1790.825 | 0 | 25937 | 24660 | 16 | 3495 | 10 | 2218 | 1277
2025-06-22 | 23245 | 38193 | 14011 | 1790.825 | 0 | 25973 | 25463 | 12 | 2728 | 10 | 2218 | 510
2025-06-29 | 24189 | 38193 | 13528 | 1790.825 | 0 | 26456 | 26542 | 9 | 2267 | 10 | 2353 | -86
2025-07-06 | 24333 | 38193 | 13635 | 1790.825 | 0 | 26349 | 26686 | 8 | 2016 | 10 | 2353 | -337
2025-07-13 | 24570 | 38193 | 13658 | 1790.825 | 0 | 26326 | 26919 | 7 | 1756 | 10 | 2349 | -593
2025-07-20 | 24739 | 38193 | 13780 | 1790.825 | 0 | 26204 | 27088 | 6 | 1465 | 10 | 2349 | -884
2025-07-27 | 24854 | 38193 | 13731 | 1790.825 | 0 | 26253 | 27203 | 6 | 1399 | 9 | 2349 | -950
2025-08-03 | 24773 | 38193 | 13942 | 1790.825 | 0 | 26042 | 27122 | 5 | 1269 | 9 | 2349 | -1080
2025-08-10 | 24695 | 38193 | 13995 | 1790.825 | 0 | 25989 | 27042 | 5 | 1294 | 10 | 2347 | -1053
2025-08-17 | 24816 | 38193 | 14050 | 1790.825 | 0 | 25934 | 27163 | 5 | 1118 | 9 | 2347 | -1229
2025-08-24 | 24646 | 38193 | 14091 | 1790.825 | 0 | 25893 | 26993 | 5 | 1247 | 10 | 2347 | -1100
2025-08-31 | 24470 | 38193 | 14030 | 1790.825 | 0 | 25954 | 26817 | 6 | 1484 | 10 | 2347 | -863
2025-09-07 | 23844 | 38193 | 13879 | 1790.825 | 0 | 26105 | 26197 | 9 | 2261 | 10 | 2353 | -92
2025-09-14 | 23165 | 38193 | 13993 | 1790.825 | 0 | 25991 | 25518 | 12 | 2826 | 10 | 2353 | 473
2025-09-21 | 22091 | 38193 | 14486 | 1790.825 | 0 | 25498 | 24389 | 15 | 3407 | 10 | 2298 | 1109
2025-09-28 | 21286 | 38193 | 15744 | 1790.825 | 0 | 24240 | 23387 | 14 | 2954 | 10 | 2101 | 853
2025-10-05 | 20105 | 38193 | 16666 | 1790.825 | 0 | 23318 | 22154 | 16 | 3213 | 10 | 2049 | 1164
Back to main menu

## Table A5
Back to main menu
Table A5: Assessment of Resource Adequacy: Extreme Weather, Planned Scenario
Week | Ontario | Total Internal | Total Reductions | Demand | Firm Imports (+) | Total Available | Required | Available | Available | Required | Required | Reserve Above
Ending | Demand | Resources | in Resources | Measures | Exports (-) | Resources | Resources | Reserve | Reserve | Reserve | Reserve | Requirement
Day | MW | MW | MW | MW | MW | MW | MW | % | MW | % | MW | MW
2024-04-07 | 18792 | 38193 | 14816 | 657.822 | -79 | 23955.822 | 20908 | 27.48 | 5164 | 11.26 | 2116 | 3048
2024-04-14 | 18254 | 38193 | 16336 | 657.822 | -79 | 22435.822 | 20370 | 22.91 | 4182 | 11.59 | 2116 | 2066
2024-04-21 | 18324 | 38193 | 15799 | 657.822 | -79 | 22972.822 | 20440 | 25.37 | 4649 | 11.55 | 2116 | 2533
2024-04-28 | 17799 | 38193 | 17595 | 657.822 | -79 | 21176.822 | 19915 | 18.98 | 3378 | 11.89 | 2116 | 1262
2024-05-05 | 19062 | 38193 | 17332 | 657.822 | -79 | 21439.822 | 21178 | 12.48 | 2378 | 11.1 | 2116 | 262
2024-05-12 | 19568 | 38193 | 18344 | 827.325 | 0 | 20676.325 | 21684 | 5.66 | 1108 | 10.81 | 2116 | -1008
2024-05-19 | 21027 | 38193 | 17288 | 827.325 | 0 | 21732.325 | 23143 | 3.35 | 705 | 10.06 | 2116 | -1411
2024-05-26 | 20993 | 38193 | 16289 | 827.325 | 0 | 22731.325 | 23114 | 8.28 | 1738 | 10.1 | 2121 | -383
2024-06-02 | 21646 | 38193 | 16235 | 995.95 | 0 | 22953.95 | 23628 | 6.04 | 1308 | 9.16 | 1982 | -674
2024-06-09 | 22045 | 38193 | 15861 | 995.95 | 0 | 23327.95 | 24093 | 5.82 | 1283 | 9.29 | 2048 | -765
2024-06-16 | 22282 | 38193 | 16039 | 995.95 | 0 | 23149.95 | 24330 | 3.9 | 868 | 9.19 | 2048 | -1180
2024-06-23 | 23110 | 38193 | 15131 | 995.95 | 0 | 24057.95 | 25326 | 4.1 | 948 | 9.59 | 2216 | -1268
2024-06-30 | 24017 | 38193 | 13057 | 995.95 | 0 | 26131.95 | 26454 | 8.81 | 2115 | 10.15 | 2437 | -322
2024-07-07 | 24194 | 38253 | 12807 | 995.95 | 0 | 26441.95 | 26637 | 9.29 | 2248 | 10.1 | 2443 | -195
2024-07-14 | 24380 | 38253 | 12719 | 995.95 | 0 | 26529.95 | 26825 | 8.82 | 2150 | 10.03 | 2445 | -295
2024-07-21 | 24550 | 38253 | 12972 | 995.95 | 0 | 26276.95 | 26993 | 7.03 | 1727 | 9.95 | 2443 | -716
2024-07-28 | 24669 | 38253 | 12697 | 995.95 | 0 | 26551.95 | 27114 | 7.63 | 1883 | 9.91 | 2445 | -562
2024-08-04 | 24606 | 38253 | 12952 | 995.95 | 0 | 26296.95 | 27051 | 6.87 | 1691 | 9.94 | 2445 | -754
2024-08-11 | 24532 | 38253 | 13002 | 995.95 | 0 | 26246.95 | 26973 | 6.99 | 1715 | 9.95 | 2441 | -726
2024-08-18 | 24657 | 38253 | 13400 | 995.95 | 0 | 25848.95 | 27098 | 4.83 | 1192 | 9.9 | 2441 | -1249
2024-08-25 | 24508 | 38253 | 13585 | 995.95 | 0 | 25663.95 | 26932 | 4.72 | 1156 | 9.89 | 2424 | -1268
2024-09-01 | 24309 | 38253 | 13670 | 995.95 | 0 | 25578.95 | 26750 | 5.22 | 1270 | 10.04 | 2441 | -1171
2024-09-08 | 23662 | 38253 | 13607 | 995.95 | 0 | 25641.95 | 26111 | 8.37 | 1980 | 10.35 | 2449 | -469
2024-09-15 | 22987 | 38253 | 14611 | 995.95 | 0 | 24637.95 | 25381 | 7.18 | 1651 | 10.41 | 2394 | -743
2024-09-22 | 21892 | 38253 | 14395 | 995.95 | 0 | 24853.95 | 24282 | 13.53 | 2962 | 10.92 | 2390 | 572
2024-09-29 | 21119 | 38253 | 15793 | 995.95 | 0 | 23455.95 | 23201 | 11.07 | 2337 | 9.86 | 2082 | 255
2024-10-06 | 19574 | 38253 | 16733 | 827.325 | 0 | 22347.325 | 21555 | 14.17 | 2773 | 10.12 | 1981 | 792
2024-10-13 | 18676 | 38253 | 15171 | 827.325 | 0 | 23909.325 | 20630 | 28.02 | 5233 | 10.46 | 1954 | 3279
2024-10-20 | 18066 | 38253 | 16302 | 827.325 | 0 | 22778.325 | 19993 | 26.08 | 4712 | 10.67 | 1927 | 2785
2024-10-27 | 19099 | 38253 | 15569 | 827.325 | 0 | 23511.325 | 21073 | 23.1 | 4412 | 10.34 | 1974 | 2438
2024-11-03 | 19357 | 38253 | 14777 | 827.325 | -600 | 23703.325 | 21559 | 22.45 | 4346 | 11.38 | 2202 | 2144
2024-11-10 | 19922 | 38253 | 14738 | 726.306 | -600 | 23641.306 | 22087 | 18.67 | 3719 | 10.87 | 2165 | 1554
2024-11-17 | 19615 | 38253 | 15432 | 726.306 | -600 | 22947.306 | 21789 | 16.99 | 3332 | 11.08 | 2174 | 1158
2024-11-24 | 20210 | 38253 | 13233 | 726.306 | -600 | 25146.306 | 22485 | 24.42 | 4936 | 11.26 | 2275 | 2661
2024-12-01 | 20847 | 38253 | 12428 | 726.306 | -600 | 25951.306 | 23133 | 24.48 | 5104 | 10.97 | 2286 | 2818
2024-12-08 | 21379 | 38253 | 12285 | 726.306 | -600 | 26094.306 | 23675 | 22.05 | 4715 | 10.74 | 2296 | 2419
2024-12-15 | 21916 | 38253 | 11788 | 726.306 | -600 | 26591.306 | 24223 | 21.33 | 4675 | 10.53 | 2307 | 2368
2024-12-22 | 21989 | 38253 | 11507 | 726.306 | -600 | 26872.306 | 24296 | 22.21 | 4883 | 10.49 | 2307 | 2576
2024-12-29 | 20295 | 38253 | 11243 | 726.306 | -600 | 27136.306 | 22794 | 33.71 | 6841 | 12.31 | 2499 | 4342
2025-01-05 | 21075 | 38253 | 11355 | 726.306 | -600 | 27024.306 | 23480 | 28.23 | 5949 | 11.41 | 2405 | 3544
2025-01-12 | 22461 | 38253 | 10920 | 802.681 | -600 | 27535.681 | 24863 | 22.59 | 5075 | 10.69 | 2402 | 2673
2025-01-19 | 22499 | 38253 | 11150 | 802.681 | -600 | 27305.681 | 24904 | 21.37 | 4807 | 10.69 | 2405 | 2402
2025-01-26 | 22915 | 38253 | 11909 | 802.681 | -600 | 26546.681 | 25280 | 15.85 | 3632 | 10.32 | 2365 | 1267
2025-02-02 | 22675 | 38253 | 12014 | 802.681 | -600 | 26441.681 | 25040 | 16.61 | 3767 | 10.43 | 2365 | 1402
2025-02-09 | 22090 | 38253 | 12304 | 802.681 | -600 | 26151.681 | 24438 | 18.39 | 4062 | 10.63 | 2348 | 1714
2025-02-16 | 21977 | 38253 | 12032 | 802.681 | -600 | 26423.681 | 24342 | 20.23 | 4447 | 10.76 | 2365 | 2082
2025-02-23 | 22054 | 38253 | 11349 | 802.681 | -600 | 27106.681 | 24419 | 22.91 | 5053 | 10.72 | 2365 | 2688
2025-03-02 | 22113 | 38253 | 11636 | 802.681 | -600 | 26819.681 | 24445 | 21.29 | 4707 | 10.55 | 2332 | 2375
2025-03-09 | 21412 | 38253 | 12939 | 726.306 | -600 | 25440.306 | 23594 | 18.81 | 4028 | 10.19 | 2182 | 1846
2025-03-16 | 21089 | 38253 | 12678 | 726.306 | -600 | 25701.306 | 23271 | 21.87 | 4612 | 10.35 | 2182 | 2430
2025-03-23 | 20370 | 38253 | 13867 | 726.306 | -600 | 24512.306 | 22526 | 20.33 | 4142 | 10.58 | 2156 | 1986
2025-03-30 | 19548 | 38253 | 14524 | 726.306 | -600 | 23855.306 | 21661 | 22.03 | 4307 | 10.81 | 2113 | 2194
2025-04-06 | 19015 | 38253 | 15738 | 726.306 | -600 | 22641.306 | 21149 | 19.07 | 3626 | 11.22 | 2134 | 1492
2025-04-13 | 18480 | 38253 | 14095 | 726.306 | -600 | 24284.306 | 20614 | 31.41 | 5804 | 11.55 | 2134 | 3670
2025-04-20 | 18545 | 38253 | 16666 | 726.306 | -600 | 21713.306 | 20679 | 17.08 | 3168 | 11.51 | 2134 | 1034
2025-04-27 | 18016 | 38253 | 15252 | 726.306 | -600 | 23127.306 | 20150 | 28.37 | 5111 | 11.85 | 2134 | 2977
2025-05-04 | 19308 | 38253 | 13238 | 726.306 | -600 | 25141.306 | 21598 | 30.21 | 5833 | 11.86 | 2290 | 3543
2025-05-11 | 19725 | 38253 | 14815 | 1622.2 | 0 | 25060.2 | 21866 | 27.05 | 5335 | 10.85 | 2141 | 3194
2025-05-18 | 21191 | 38253 | 13254 | 1622.2 | 0 | 26621.2 | 23399 | 25.62 | 5430 | 10.42 | 2208 | 3222
2025-05-25 | 21162 | 38253 | 12746 | 1622.2 | 0 | 27129.2 | 23381 | 28.2 | 5967 | 10.49 | 2219 | 3748
2025-06-01 | 21872 | 38253 | 12784 | 1790.825 | 0 | 27259.825 | 24091 | 24.63 | 5388 | 10.15 | 2219 | 3169
2025-06-08 | 22197 | 38488 | 14192 | 1790.825 | 0 | 26086.825 | 24416 | 17.52 | 3890 | 10 | 2219 | 1671
2025-06-15 | 22442 | 38488 | 13926 | 1790.825 | 0 | 26352.825 | 24678 | 17.43 | 3911 | 9.96 | 2236 | 1675
2025-06-22 | 23245 | 38488 | 13903 | 1790.825 | 0 | 26375.825 | 25481 | 13.47 | 3131 | 9.62 | 2236 | 895
2025-06-29 | 24189 | 38488 | 13405 | 1790.825 | 0 | 26873.825 | 26562 | 11.1 | 2685 | 9.81 | 2373 | 312
2025-07-06 | 24333 | 38488 | 13512 | 1790.825 | 0 | 26766.825 | 26706 | 10 | 2434 | 9.75 | 2373 | 61
2025-07-13 | 24570 | 38488 | 13535 | 1790.825 | 0 | 26743.825 | 26938 | 8.85 | 2174 | 9.64 | 2368 | -194
2025-07-20 | 24739 | 38488 | 13657 | 1790.825 | 0 | 26621.825 | 27107 | 7.61 | 1883 | 9.57 | 2368 | -485
2025-07-27 | 24854 | 38488 | 13608 | 1790.825 | 0 | 26670.825 | 27222 | 7.31 | 1817 | 9.53 | 2368 | -551
2025-08-03 | 24773 | 38488 | 13818 | 1790.825 | 0 | 26460.825 | 27141 | 6.81 | 1688 | 9.56 | 2368 | -680
2025-08-10 | 24695 | 38488 | 13872 | 1790.825 | 0 | 26406.825 | 27060 | 6.93 | 1712 | 9.58 | 2365 | -653
2025-08-17 | 24816 | 38488 | 13927 | 1790.825 | 0 | 26351.825 | 27181 | 6.19 | 1536 | 9.53 | 2365 | -829
2025-08-24 | 24646 | 38488 | 13968 | 1790.825 | 0 | 26310.825 | 27011 | 6.76 | 1665 | 9.6 | 2365 | -700
2025-08-31 | 24470 | 38488 | 13907 | 1790.825 | 0 | 26371.825 | 26835 | 7.77 | 1902 | 9.66 | 2365 | -463
2025-09-07 | 23844 | 38723 | 13990 | 1790.825 | 0 | 26523.825 | 26216 | 11.24 | 2680 | 9.95 | 2372 | 308
2025-09-14 | 23165 | 38723 | 14104 | 1790.825 | 0 | 26409.825 | 25537 | 14.01 | 3245 | 10.24 | 2372 | 873
2025-09-21 | 22091 | 38723 | 14597 | 1790.825 | 0 | 25916.825 | 24408 | 17.32 | 3826 | 10.49 | 2317 | 1509
2025-09-28 | 21286 | 38723 | 16060 | 1790.825 | 0 | 24453.825 | 23388 | 14.88 | 3168 | 9.88 | 2102 | 1066
2025-10-05 | 20105 | 38723 | 16981 | 1790.825 | 0 | 23532.825 | 22156 | 17.05 | 3428 | 10.2 | 2051 | 1377
Back to main menu

## Table A6
Back to main menu
Table A6: Zonal Bottled Generation: Extreme Weather, Both Scenarios
Week | Firm Scenario |  |  | Planned Scenario
Ending | Bruce, West & Southwest | Northeast | Northwest | Bruce, West & Southwest | Northeast | Northwest
Day | MW | MW | MW | MW | MW | MW
2024-04-07 | 178.2529 | 0 | 33.2332 | 178.2529 | 0 | 73.2332
2024-04-14 | 573.3078 | 0 | 0 | 573.3078 | 0 | 0
2024-04-21 | 211.7849 | 0 | 0 | 211.7849 | 0 | 0
2024-04-28 | 424.3979 | 0 | 0 | 424.3979 | 0 | 0
2024-05-05 | 170.8024 | 0 | 0 | 184.5431 | 0 | 0
2024-05-12 | 0 | 0 | 0 | 0 | 0 | 0
2024-05-19 | 0 | 0 | 0 | 0 | 0 | 0
2024-05-26 | 306.328 | 530.6412 | 0 | 306.328 | 530.6412 | 0
2024-06-02 | 190.6648 | 0 | 0 | 190.6648 | 0 | 0
2024-06-09 | 0 | 0 | 0 | 0 | 0 | 0
2024-06-16 | 0 | 0 | 0 | 0 | 0 | 0
2024-06-23 | 586.1527 | 0 | 0 | 586.1527 | 0 | 0
2024-06-30 | 373.1177 | 0 | 0 | 373.1177 | 0 | 0
2024-07-07 | 0 | 0 | 0 | 0 | 0 | 0
2024-07-14 | 0 | 0 | 0 | 0 | 0 | 0
2024-07-21 | 0 | 0 | 0 | 0 | 0 | 0
2024-07-28 | 0 | 0 | 0 | 0 | 0 | 0
2024-08-04 | 0 | 0 | 0 | 0 | 0 | 0
2024-08-11 | 0 | 0 | 0 | 0 | 0 | 0
2024-08-18 | 0 | 0 | 0 | 0 | 0 | 0
2024-08-25 | 0 | 0 | 0 | 0 | 0 | 0
2024-09-01 | 465.9277 | 0 | 0 | 465.9277 | 0 | 0
2024-09-08 | 504.6846 | 0 | 0 | 504.6846 | 0 | 0
2024-09-15 | 511.6737 | 0 | 0 | 511.6737 | 0 | 0
2024-09-22 | 522.3577 | 0 | 0 | 522.3577 | 0 | 0
2024-09-29 | 534.1131 | 0 | 0 | 534.1131 | 0 | 0
2024-10-06 | 0 | 105.1543 | 0 | 0 | 105.1543 | 0
2024-10-13 | 0 | 0 | 0 | 0 | 0 | 72.1635
2024-10-20 | 0 | 24.9838 | 0 | 0 | 24.9838 | 33.7012
2024-10-27 | 4.2085 | 0 | 0 | 22.9203 | 0 | 0
2024-11-03 | 1420.2557 | 0 | 0 | 1446.1132 | 0 | 0
2024-11-10 | 1261.168 | 0 | 0 | 1287.0255 | 0 | 0
2024-11-17 | 1960.7308 | 0 | 0 | 1986.5883 | 0 | 0
2024-11-24 | 1747.8793 | 0 | 0 | 1773.7368 | 0 | 0
2024-12-01 | 1517.566 | 0 | 0 | 1541.4683 | 0 | 48.9278
2024-12-08 | 1732.7294 | 0 | 0 | 1756.6317 | 0 | 9.8816
2024-12-15 | 1530.4375 | 0 | 0 | 1554.3398 | 0 | 0
2024-12-22 | 1380.7037 | 0 | 0 | 1404.606 | 0 | 11.819
2024-12-29 | 2197.9989 | 0 | 0 | 2221.9012 | 0 | 12.9619
2025-01-05 | 1121.7368 | 0 | 0 | 1145.6391 | 0 | 0
2025-01-12 | 565.074 | 0 | 0 | 588.9763 | 0 | 0
2025-01-19 | 810.5134 | 0 | 0 | 834.4157 | 0 | 0
2025-01-26 | 412.7198 | 0 | 0 | 436.6221 | 0 | 0
2025-02-02 | 338.4228 | 0 | 0 | 362.3251 | 0 | 0
2025-02-09 | 399.0488 | 0 | 0 | 422.9511 | 0 | 0
2025-02-16 | 374.0358 | 0 | 0 | 397.9381 | 0 | 14.2663
2025-02-23 | 54.0508 | 0 | 0 | 77.9531 | 0 | 28.167
2025-03-02 | 0 | 0 | 0 | 0 | 0 | 21.2227
2025-03-09 | 0 | 0 | 0 | 0 | 0 | 13.591
2025-03-16 | 0 | 0 | 0 | 0 | 0 | 0
2025-03-23 | 0 | 0 | 0 | 0 | 0 | 33.5364
2025-03-30 | 0 | 0 | 0 | 0 | 0 | 42.3609
2025-04-06 | 0 | 0 | 0 | 0 | 0 | 0
2025-04-13 | 226.2521 | 0 | 0 | 245.4908 | 0 | 0
2025-04-20 | 0 | 0 | 0 | 0 | 0 | 0
2025-04-27 | 234.3758 | 0 | 0 | 253.6146 | 0 | 0
2025-05-04 | 0 | 0 | 0 | 0 | 0 | 0
2025-05-11 | 0 | 0 | 0 | 0 | 0 | 0
2025-05-18 | 0 | 0 | 0 | 0 | 0 | 0
2025-05-25 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-01 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-08 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-15 | 0 | 0 | 0 | 0 | 0 | 2.5372
2025-06-22 | 0 | 0 | 0 | 0 | 0 | 16.0217
2025-06-29 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-06 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-13 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-20 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-27 | 0 | 0 | 0 | 0 | 0 | 0
2025-08-03 | 0 | 0 | 0 | 0 | 0 | 0
2025-08-10 | 0 | 0 | 0 | 0 | 0 | 0
2025-08-17 | 0 | 0 | 0 | 0 | 0 | 0
2025-08-24 | 0 | 0 | 0 | 0 | 0 | 0
2025-08-31 | 0 | 0 | 0 | 0 | 0 | 0
2025-09-07 | 0 | 0 | 0 | 0 | 0 | 0
2025-09-14 | 0 | 0 | 0 | 0 | 0 | 0
2025-09-21 | 0 | 0 | 0 | 0 | 0 | 0
2025-09-28 | 0 | 0 | 0 | 0 | 0 | 0
2025-10-05 | 0 | 0 | 0 | 0 | 0 | 0
Note: The bottled generation values indicated in the table are capacity values calculated at the hour of weekly peak.
In real time operation, the actual amount of bottled generation will depend on many conditions prevailing at the time,
including the local generation levels, overall generation dispatch and the direction and
levels of flows into and out of Ontario.
Zonal information is found in the Ontario Transmission System document.
Back to main menu

## Table A7
Back to main menu
Table A7: Energy Production Capability Forecast
Month | Firm Scenario Forecast Energy Production Capability (GWh)
2024-04-01 | 15559.64
2024-05-01 | 15640.92
2024-06-01 | 17341.1
2024-07-01 | 18749.95
2024-08-01 | 18394.16
2024-09-01 | 17463.53
2024-10-01 | 16541.74
2024-11-01 | 16969.27
2024-12-01 | 18763.76
2025-01-01 | 18248.53
2025-02-01 | 16186.28
2025-03-01 | 16233.15
2025-04-01 | 15980.41
2025-05-01 | 17719.02
2025-06-01 | 17312.6
2025-07-01 | 17469.25
2025-08-01 | 17241.2
2025-09-01 | 16418.4
Back to main menu

## Table A8
Back to main menu
Table A8: Reductions by Fuel Type: Normal Weather, Firm Scenario
Week | Ontario | Total Internal | Total Reductions | Nuclear | Biomass, Oil & Gas | Hydro, Wind & Solar | Total Bottled
Ending | Demand | Resources | in Resources | Reductions | Reductions | Capacity Unavailable | Generation
Day | MW | MW | MW | MW | MW | MW | MW
2024-04-07 | 17840 | 38193 | 14710 | 4821.78 | 2426.1533 | 6917.1201 | 545.003
2024-04-14 | 17731 | 38193 | 16127 | 4821.78 | 3241.86 | 7336.439 | 727.5228
2024-04-21 | 17689 | 38193 | 15897 | 4818.88 | 3181.41 | 7182.5258 | 714.6822
2024-04-28 | 17396 | 38193 | 17440 | 7286.08 | 2529.2533 | 6908.7095 | 715.9379
2024-05-05 | 17364 | 38193 | 17032 | 7286.08 | 2222.5033 | 7135.1836 | 388.8354
2024-05-12 | 17274 | 38193 | 17357 | 7289.25 | 3150.6033 | 7517.3698 | 0
2024-05-19 | 17475 | 38193 | 16290 | 7289.25 | 2520.1633 | 7081.047 | 0
2024-05-26 | 17543 | 38193 | 15882 | 4825.125 | 2912.1533 | 7333.7678 | 1410.7683
2024-06-02 | 19149 | 38193 | 16103 | 4825.125 | 3182.1333 | 7681.4253 | 1014.281
2024-06-09 | 19554 | 38193 | 14514 | 4837.975 | 2103.0533 | 7884.8242 | 288.1704
2024-06-16 | 21217 | 38193 | 14428 | 4837.975 | 2103.0533 | 8086.8761 | 0
2024-06-23 | 21880 | 38193 | 13548 | 3162.475 | 2103.0533 | 8292.2584 | 590.7591
2024-06-30 | 22502 | 38193 | 11364 | 2646.475 | 934.3633 | 8002.9808 | 380.7611
2024-07-07 | 22449 | 38193 | 11163 | 2700.6 | 865.1833 | 8136.007 | 61.0398
2024-07-14 | 22685 | 38193 | 11039 | 2700.6 | 823.3033 | 8082.8054 | 32.3676
2024-07-21 | 22753 | 38193 | 11337 | 2700.6 | 861.1433 | 8333.5644 | 41.8095
2024-07-28 | 22699 | 38193 | 11037 | 2700.6 | 823.3033 | 8057.3218 | 56.0783
2024-08-04 | 22625 | 38193 | 11239 | 2700.6 | 823.3033 | 8312.7865 | 2.6092
2024-08-11 | 22582 | 38193 | 11486 | 2759.17 | 984.4633 | 8342.4835 | 0
2024-08-18 | 22569 | 38193 | 11943 | 2759.17 | 984.4633 | 8799.1011 | 0
2024-08-25 | 22539 | 38193 | 11918 | 2759.17 | 984.4633 | 8774.4262 | 0
2024-09-01 | 22462 | 38193 | 12190 | 2759.17 | 984.4633 | 8573.7847 | 472.2882
2024-09-08 | 21915 | 38193 | 12078 | 2718.675 | 862.0733 | 8580.4729 | 517.0846
2024-09-15 | 21957 | 38193 | 13145 | 3233.675 | 862.0733 | 9132.9487 | 516.257
2024-09-22 | 20481 | 38193 | 12880 | 3233.675 | 939.1133 | 8791.9839 | 515.3344
2024-09-29 | 18884 | 38193 | 14291 | 3233.675 | 2441.2733 | 8687.5394 | 529.0026
2024-10-06 | 17978 | 38193 | 15282 | 3707.225 | 3382.76 | 8534.9609 | 257.2438
2024-10-13 | 17690 | 38193 | 14886 | 3707.225 | 3733.92 | 7426.0308 | 618.6259
2024-10-20 | 17611 | 38193 | 15591 | 3707.225 | 4878.45 | 7501.4013 | 103.7971
2024-10-27 | 17834 | 38193 | 15285 | 3707.225 | 4185.61 | 7460.5127 | 532.028
2024-11-03 | 17986 | 38193 | 15259 | 3677.48 | 2539.76 | 7335.414 | 1856.7906
2024-11-10 | 18582 | 38193 | 15347 | 3677.48 | 3058.11 | 7149.8253 | 1611.7899
2024-11-17 | 19240 | 38193 | 15500 | 3677.48 | 3112.08 | 7094.7543 | 1766.2468
2024-11-24 | 19922 | 38193 | 13368 | 3677.48 | 1703.24 | 6550.0973 | 1587.5246
2024-12-01 | 20150 | 38193 | 12845 | 3677.48 | 1398.54 | 6239.2203 | 1679.5111
2024-12-08 | 20630 | 38193 | 12530 | 3670.175 | 1016.4 | 6213.6615 | 1780.0147
2024-12-15 | 20818 | 38193 | 12049 | 3670.175 | 849.7133 | 6101.0344 | 1578.7506
2024-12-22 | 20894 | 38193 | 12141 | 3670.175 | 849.7133 | 5957.183 | 1814.575
2024-12-29 | 18767 | 38193 | 11598 | 3155.175 | 324.7133 | 5915.3437 | 2353.3624
2025-01-05 | 20148 | 38193 | 11575 | 4421 | 251.8533 | 5850.4563 | 1201.4103
2025-01-12 | 21434 | 38193 | 11202 | 4421 | 295.8533 | 5926.981 | 708.3229
2025-01-19 | 21456 | 38193 | 11293 | 4421 | 251.8533 | 5956.3736 | 814.2636
2025-01-26 | 21718 | 38193 | 12019 | 5234.54 | 251.8533 | 6300.2304 | 382.8548
2025-02-02 | 21688 | 38193 | 12213 | 5234.54 | 251.8533 | 6479.5481 | 397.5498
2025-02-09 | 21287 | 38193 | 12241 | 5230.725 | 274.3233 | 6508.0615 | 378.0928
2025-02-16 | 20820 | 38193 | 12321 | 5230.725 | 274.3233 | 6451.6936 | 514.8488
2025-02-23 | 20641 | 38193 | 11644 | 5230.725 | 274.3233 | 6075.3141 | 214.1278
2025-03-02 | 20540 | 38193 | 11798 | 5230.725 | 655.1533 | 6062.5192 | 0
2025-03-09 | 19963 | 38193 | 13363 | 5226.825 | 1517.9533 | 6608.5667 | 160.3292
2025-03-16 | 19437 | 38193 | 13151 | 5226.825 | 1517.9533 | 6360.6667 | 196.2074
2025-03-23 | 18881 | 38193 | 14091 | 5226.825 | 2399.4433 | 6614.6374 | 0
2025-03-30 | 18407 | 38193 | 14720 | 5226.825 | 3021.1633 | 6622.1695 | 0
2025-04-06 | 18139 | 38193 | 15712 | 5226.825 | 3756.1533 | 6879.5024 | 0
2025-04-13 | 18028 | 38193 | 13532 | 4406.64 | 2210.7133 | 6651.0855 | 413.438
2025-04-20 | 17984 | 38193 | 16007 | 4406.64 | 5068.66 | 6681.7007 | 0
2025-04-27 | 17695 | 38193 | 15071 | 3528.64 | 4146.71 | 6750.0236 | 795.7187
2025-05-04 | 17674 | 38193 | 12799 | 3528.64 | 1716.5233 | 7369.7876 | 333.8625
2025-05-11 | 17523 | 38193 | 14755 | 3536.4 | 3096.4433 | 7693.4137 | 428.924
2025-05-18 | 17814 | 38193 | 13000 | 3536.4 | 2148.5633 | 7023.4654 | 291.4209
2025-05-25 | 17816 | 38193 | 12863 | 3536.4 | 1592.6733 | 7030.5701 | 703.3767
2025-06-01 | 19430 | 38193 | 12197 | 3536.4 | 1592.6733 | 7068.1739 | 0
2025-06-08 | 19813 | 38193 | 12924 | 3587.675 | 1651.0633 | 7685.4049 | 0
2025-06-15 | 21493 | 38193 | 12852 | 3587.675 | 1651.0633 | 7613.6809 | 0
2025-06-22 | 22132 | 38193 | 12812 | 3587.675 | 1651.0633 | 7573.1622 | 0
2025-06-29 | 22622 | 38193 | 12335 | 3587.675 | 1126.0633 | 7621.0174 | 0
2025-07-06 | 22619 | 38193 | 12440 | 3587.675 | 1126.0633 | 7726.6138 | 0
2025-07-13 | 22821 | 38193 | 12512 | 3599.7 | 1220.0033 | 7692.0041 | 0
2025-07-20 | 22872 | 38193 | 12651 | 3599.7 | 1220.0033 | 7831.2155 | 0
2025-07-27 | 22825 | 38193 | 12595 | 3599.7 | 1220.0033 | 7775.5119 | 0
2025-08-03 | 22734 | 38193 | 12800 | 3599.7 | 1220.0033 | 7980.9713 | 0
2025-08-10 | 22695 | 38193 | 12848 | 3645.25 | 1176.1633 | 8026.8747 | 0
2025-08-17 | 22674 | 38193 | 12913 | 3645.25 | 1176.1633 | 8091.5588 | 0
2025-08-24 | 22637 | 38193 | 12960 | 3645.25 | 1176.1633 | 8139.0798 | 0
2025-08-31 | 22722 | 38193 | 12890 | 3645.25 | 1176.1633 | 8068.4028 | 0
2025-09-07 | 22012 | 38193 | 12675 | 3614.1 | 1053.7733 | 8007.405 | 0
2025-09-14 | 22066 | 38193 | 12805 | 3614.1 | 1053.7733 | 8137.7491 | 0
2025-09-21 | 20744 | 38193 | 13296 | 4130.1 | 1053.7733 | 8112.7314 | 0
2025-09-28 | 19148 | 38193 | 14545 | 4918.25 | 1578.7733 | 8048.4932 | 0
2025-10-05 | 18213 | 38193 | 15407 | 4893.95 | 2337.7033 | 8175.7442 | 0
Back to main menu

## Table A9
Back to main menu
Table A9: Firm Scenario - Normal Weather: Ontario Monthly Energy Production by Fuel Type
Month | Year | Nuclear (GWh) | Hydro (GWh) | Gas & Oil (GWh) | Wind (GWh) | Biofuel (GWh) | Other (GWh) | Total (GWh)
Apr | 2024 | 5372.4 | 3150.35 | 954.28 | 1091.96 | 35.46 | 69.04 | 10673.49
May | 2024 | 4963.34 | 3489.2 | 1279.49 | 832.4 | 25.65 | 70.57 | 10660.65
Jun | 2024 | 6134.83 | 3219.46 | 960.63 | 495.87 | 29.18 | 54.59 | 10894.56
Jul | 2024 | 7448.08 | 3019.98 | 1343.74 | 431.72 | 38.35 | 66.22 | 12348.09
Aug | 2024 | 7508.36 | 2769.5 | 1505.59 | 509.31 | 25.46 | 73.62 | 12391.84
Sep | 2024 | 6747.24 | 2611.99 | 1004.24 | 549.96 | 24.26 | 60.47 | 10998.16
Oct | 2024 | 6836.39 | 2766.87 | 530.47 | 861.1 | 24.3 | 50.3 | 11069.43
Nov | 2024 | 6693.94 | 2997.37 | 676.94 | 1017.45 | 23.66 | 34.65 | 11444.01
Dec | 2024 | 6910.91 | 3205.66 | 1186.06 | 1151.51 | 25.53 | 45.99 | 12525.66
Jan | 2025 | 6087.72 | 3262.68 | 2274.89 | 1450.68 | 26.2 | 64.35 | 13166.52
Feb | 2025 | 5210.5 | 3038.05 | 2063.84 | 1267.57 | 23.82 | 65.5 | 11669.28
Mar | 2025 | 5742.71 | 3212.25 | 1753.87 | 1200.3 | 26.16 | 84.57 | 12019.86
Apr | 2025 | 6217.08 | 3157.09 | 479.81 | 866.29 | 22.89 | 47.96 | 10791.12
May | 2025 | 6590.91 | 3479.79 | 337.4 | 340.76 | 22.05 | 24.18 | 10795.09
Jun | 2025 | 6424.76 | 3226.94 | 891.94 | 502.87 | 23.92 | 53.22 | 11123.65
Jul | 2025 | 6910.09 | 3026.61 | 2022.41 | 520.88 | 25.88 | 82.56 | 12588.43
Aug | 2025 | 6908.83 | 2776.83 | 2099.02 | 564.35 | 25.98 | 85.12 | 12460.13
Sep | 2025 | 6325.14 | 2616.63 | 1513.09 | 665.39 | 24.85 | 70.33 | 11215.43
Back to main menu

## Table B1
Back to main menu
Table B1: Transmission Projects
Zone | ID | Transmitter | Description | Proposed I/S Date
Bruce | N/A | Hydro-One | Bruce A 230kV- Replace Breakers & Upgrade Station | 2025-Q2
Bruce | 2019-EX1082 | Hydro-One | Bruce B SS-ABCB replacement | 2025-Q2
East | N/A | Hydro-One | Q3M6, Frontenac TS-Novelis CTS, Tx Line Refurb. | 2024-Q2
Essa | N/A | Hydro-One | Barrie TS DESN Rebuilt | 2024-Q1
Niagara | N/A | Hydro-One | D1A/D3A, Gibson JCT-Thorold TS, Tx Line Refurb. | 2023-Q4 (Completed)
Niagara | 2023-755 | Hydro-One | Beck 2 TS, ABCB Replacement & Yard Upgrade | 2024-Q2
Niagara | N/A | Hydro-One | Thorold TS: T1, MV Switchyard & Component Repl. | 2024-Q3
Northeast | 2020-EX1146 | Hydro-One | A8/9K, Str.141 X Kirkland Lake TS, Tx Ln Ref | 2023-Q3 (Completed)
Northeast | 2019-EX1085 | Hydro-One | HOSSM Echo River New TF and Breaker Removal | 2024-Q2
Northeast | 2023-EX1225 | Hydro-One | K4, Kirkland Lake TS X Matachewan JCT, Tx Line Ref | 2024-Q4
Northeast | N/A | Hydro-One | Echo River: HOSSM Echo River TF Repl/TF Contingency Plan | 2024-Q4
Northeast | N/A | Hydro-One | HOSSM Algoma Steel EAF CTS - 115kV Connection | 2025-Q2
Northwest | N/A | Hydro-One | K1/K2, Krklnd Lk- A. Barrick, Tx Line Refurb (Cu) | 2024-Q3
Northwest | 2021-EX1156 | Hydro-One | Rabbit Lake SS: Component Replacement | 2024-Q4
Northwest | 2016-596 | Hydro-One | Longlac TS: Relocation of line, station and distribution feeders | 2025-Q1
Ottawa | 2016-572 | Hydro-One | M30A/M31A Conductor Upgrade | 2023-Q3 (Completed)
Ottawa | N/A | Hydro-One | NRC TS Connection of 1.25MW DG | 2024-Q1
Ottawa | N/A | Hydro-One | Lincoln Heights TS: T1/T2 & Component Replacement | 2024-Q3
Ottawa | N/A | Hydro-One | Slater TS T2/T3 & Component Replacement | 2024-Q4
Southwest | N/A | Hydro-One | Kenilworth TS: T1, T3, T4 & Switchyard Refurb. | 2023-Q4 (Completed)
Southwest | N/A | Hydro-One | Gage TS: T3,T4,T5,T6, PCT & Switchyard Reconfig. | 2024-Q3
Southwest | 2018-EX1003 | Hydro-One | Orangeville TS: T1, T2, T3, T4 & Component Replace | 2024-Q4
Southwest | N/A | Hydro-One | Wingham TS: T1, T2, PCT & Component Replacement | 2024-Q4
Southwest | 2018-EX980 | Hydro-One | Middleport ABCB Replacement Project | 2025-Q2
Southwest | N/A | Hydro-One | Tx Line Refurb. B7/B8 ¦Burlington TS-Bronte TS | 2025-Q2
Toronto | 2019-EX1083 | Hydro-One | Strachan TS T12/T14; A5-A6 M/C & Comp Replacement | 2023-Q4 (Completed)
Toronto | 2023-744 | Hydro-One | Wilson TS: T1 & Component Replacement | 2024-Q2
Toronto | 2018-EX971 | Hydro-One | Fairbank TS: T1, T2, T3, T4, PCT & LV Yard Replace | 2024-Q4
Toronto | N/A | Hydro-One | John TS Transformer Replacement T5 and T6 | 2025-Q2
Toronto | 2023-EX1253 | Hydro-One | Cherrywood TS 500kV BULK; ABCB Rep Phase 3-1 | 2025-Q2
West | N/A | Hydro-One | Windsor NextStar TS: 230 kV/27.6 kV DESN | 2024-Q3
West | 2020-EX1131 | Hydro-One | Lambton TS: T7/T8, T5/T6, DESN Replacement | 2024-Q3
West | 2019-EX1075 | Hydro-One | Sarnia Scott TS: T5 & Component Replacement | 2024-Q4
West | N/A | Hydro-One | Chatham SS x Lakeshore TS: Stations Work | 2024-Q4
West | N/A | Hydro-One | Keith TS: Replace 6-115 kV Breakers | 2025-Q2

## Table B2
Back to main menu
Table B2: Interface Limits with All Elements in Service
Interface | Limit | Notes
BLIP | 3000
NBLIP | 1800
QFW | 2000
FABCW | 7500 | 2
FETT | 5000 | 3
CLAN | 2000
FIO | 2900
SLW | 1350
FN | 1500 | 3
FS | 1750
P502X South | 1000
EWTE | 325
EWTW | 350
2 FABCW limit varies according to BLIP flow. For each recognized
contingency, separate voltage and stability limit ranges are defined.
Published limit range based on the most restrictive contingency under
optimal Bruce System Conditions in SCO-South Tab1.
3 Fixed boundary condition limit.

## Table B3
Back to main menu
Table B3: Interconnection Flow Limits
Interconnection | Limit - Flows Out of Ontario (MW) |  | Limit - Flows Into Ontario (MW)
Manitoba – Summer* | 210 | 255 | 210 | (3,6)325
Manitoba – Winter* | 300 | (3) | 300 | (3,6)
Minnesota | 150 |  | 100 | (3)
Quebec North (Northeast) – Summer* | 105 |  | 65
D4Z | 0 | (5) | 65
H4Z | 105 | (5) | 0
Quebec North (Northeast)– Winter* | 105 |  | 85
D4Z | 0 |  | 85
H4Z | 105 |  | 0
Quebec South (Ottawa) – Summer* | 1570 |  | 1865
X2Y | 0 |  | 65
Q4C | 120 |  | not of concern
P33C | 0 | 60 | 300
D5A | 200 |  | 250
H9A | 0 |  | 0
HVDC | 1250 |  | 1250
Quebec South (Ottawa) – Winter* | 1590 |  | 1865
X2Y | 0 |  | 65
Q4C | 140 |  | not of concern
P33C | 0 |  | 300
D5A | 200 |  | 250
H9A | 0 |  | 0
HVDC | 1250 |  | 1250
Quebec South (East) – Summer* | 470 |  | 400
B31L + B5D | 470 |  | 400
Quebec South (East) – Winter* | 470 |  | 400
B31L + B5D | 470 |  | 400
New York St. Lawrence – Summer* | 300 |  | 300
New York St. Lawrence – Winter* | 300 |  | 300
New York Niagara – Summer* | 1500 | (1) | 1200 | (1,7)
Emergency Transfer Limit - Summer* | 2160 | (1) | 1860 | (1,7)
New York Niagara – Winter* | 1800 | (1) | 1600 | (1,7)
Emergency Transfer Limit - Winter* | 2200 | (1) | 2200 | (1,7)
Michigan – Summer* | 1650 | (2,3) | 1550 | (2,3)
Emergency Transfer Limit - Summer* | N/A | (2,3) | N/A | (2,3)
Michigan – Winter* | 1650 | (2,3) | 1700 | (2,3)
Emergency Transfer Limit - Winter* | N/A | (2,3) | N/A | (2,3)
* Summer Limits apply from May 1 to October 31. Winter Limits apply from November 1 to April 30.
(1) Flow limits depend on generation dispatch outside Ontario.
(2) Normal limits are based on LT ratings and phase shifters bypassed and Emergency limits are based on
ST ratings and phase shifters regulating. Flow limits vary depending on the generation dispatch
within Ontario.
(3) For real time operation of the interconnection, limits are based on ambient conditions.
(5) Limit based on 0 to 4 km/h wind speed and 30˚C ambient temperature.
(6) Flows into Ontario include flows on circuit SK1.
(7) Flow limits into Ontario are shown without considering QFW transmission constraints within Ontario.
Back to main menu

## Table C1
Back to main menu
Table C1: Bruce Zone
Planned Start | Planned End | Station | Equipment Name | Outage ID | Max Recall | Major Transmission Interface Impacted | Reduction in Limit
2024-04-05 17:00 | 2024-04-12 16:00 | BRUCE A TS, BRUCE JCT, MILTON SS, WILLOW CREEK JCT,BRANTFORD TS, NEWPORT JCT, MIDDLEPORT TS,BECK 2 TS, MID RIVER JCT NIAGARA,MIDDLEPORT TS,CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,CLAIREVILLE TS, ESSA TS,DETWEILER TS, STRATFORD JCT, SEAFORTH TS, STRATFORD TS,LONGWOOD TS | B502M.BAXBJ, B502M.BJXMI, B502M.BJXWJ, 21-B502M, 40-B502M,M32W.NEXBR, M32W.NEXMI, YZ, 25-M32W, 44M32W-19, T4-M32W,BP76.PAXBE, K2L76, L35L76, R76, TL35-BO1,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1,C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,E510V.CLXES, AL510, W3L510, 18-E510V, 51-E510V,B22D.STXDE, B22D.STXST, 26-B22D, 68T1-B22D, 61B22D-26,R5N, T5L45, SS5, T5, R5, T5-H, T5-LT5,25-Q23BM, L23HT6, D2L23, Q23BM-TEMP1 | 1-00239284 Rev. #3,1-00238922 Rev. #11,1-00181622 Rev. #28,1-00220299 Rev. #39,1-00213473 Rev. #37,1-00235682 Rev. #6,1-00237157 Rev. #9,1-00239308 Rev. #10,1-00235814 Rev. #13,1-00246468 Rev. #2 | 8 Hour(s),6 Hour(s),Non-recallable,Non-recallable,Non-recallable,14 Day(s),4 Hour(s),5 Day(s),4 Hour(s),6 Hour(s) | FABCW NBLIP BLIP | 2300 300 300
2024-04-14 16:00 | 2024-04-19 16:00 | CLAIREVILLE TS, ESSA TS,KENT TS, CHATHAM SS, GSPC JCT,DETWEILER TS, STRATFORD JCT, SEAFORTH TS, STRATFORD TS,CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,MIDDLEPORT TS,BECK 2 TS, MID RIVER JCT NIAGARA,BRUCE A TS, BRUCE JCT, MILTON SS, WILLOW CREEK JCT,LONGWOOD TS | E510V.CLXES, AL510, W3L510, 18-E510V, 51-E510V,T1B, T1Y, T4Z, 5-L28C, 86-L28C, T1, T4, T1-L28C, T4L28C, 312L28C-MSO2,B22D.STXDE, B22D.STXST, 26-B22D, 68T1-B22D, 61B22D-26,C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1,BP76.PAXBE, K2L76, L35L76, R76, TL35-BO1,25-Q23BM, L23HT6, D2L23, Q23BM-TEMP1,D1D2, D1L29, D1L27, L33L40, SC22D1, SC22SC, 25-M33W, D1_BUS, SC22, SS2-D, D1L34, D1L33,B502M.BAXBJ, B502M.BJXMI, B502M.BJXWJ, 21-B502M, 40-B502M,R5N, T5L45, SS5, T5, R5, T5-H, T5-LT5 | 1-00235682 Rev. #6,1-00238919 Rev. #6,1-00237157 Rev. #9,1-00213473 Rev. #37,1-00220299 Rev. #39,1-00181622 Rev. #28,1-00246468 Rev. #2,1-00238390 Rev. #3,1-00235814 Rev. #13,1-00239308 Rev. #10 | 14 Day(s),12 Hour(s),4 Hour(s),Non-recallable,Non-recallable,Non-recallable,6 Hour(s),2 Hour(s),4 Hour(s),5 Day(s) | FABCW NBLIP BLIP | 2300 300 300
2024-05-26 07:00 | 2024-05-31 08:00 | ALLANBURG TS, BECK 2 TS, MID RIVER JCT NIAGARA, CROSSLINE JCT, MIDDLEPORT TS, CALEDONIA Q35M JCT,CLAIREVILLE TS,BRUCE B SS, BRUCE JCT, WILLOW CREEK JCT, MILTON SS,LONGWOOD DESN, LAMBTON TS 2, LONGWOOD JCT, LONGWOOD TS,CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,MIDDLEPORT TS,DETWEILER TS, STRATFORD TS, ZURICH JCT | BP76.PAXBE, Q35M.MIXCA, Q35M.QUXAL, D2HT4, H2HT4, K2L76, L26L35, L30TL35, L34L35, L35L76, T4, R76,W3L570, W3L510, T15, T15-HT15, T15-W3, T15-SS2,B501M.BBXBJ, B501M.BJXWJ, B501M.WJXMI, 40-B501M, 29-B501M,L24L.LOXLA, L24L.LOXLD, L24L.LOXLO, AL24, T14Q, T3L24, 27-L24L, T14, T14-L24L, W52-L24L,C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1, 51-C550VP, 52-C550VP, 81-C550VP,26-B23D, 68T2-B23D, 364B23D-MSO1 | 1-00181648 Rev. #9,1-00238525 Rev. #10,1-00237165 Rev. #9,1-00236074 Rev. #16,1-00213473 Rev. #37,1-00220299 Rev. #39,1-00236150 Rev. #5,1-00238602 Rev. #4 | 4 Hour(s),4 Hour(s),4 Hour(s),8 Day(s),Non-recallable,Non-recallable,4 Hour(s),4 Hour(s) | FABCW NBLIP BLIP | 2800 300 300
2024-06-11 16:00 | 2024-06-21 13:00 | DETWEILER TS, STRATFORD TS, ZURICH JCT,LAMBTON TS 2,BRUCE B SS, BRUCE JCT, WILLOW CREEK JCT, MILTON SS,MIDDLEPORT TS,CLAIREVILLE TS | 26-B23D, 68T2-B23D, 364B23D-MSO1,K2L28, L27L28, 27-L28C,B561M.BBXBR, B561M.BRXWI, B561M.WIXMI, 40-B561M, 29-B561M, KL561, L61L71,K1K2, K2L25, SC23K2, SC23SC, T6L31, 25-M31W, K2_BUS, SC23, SS3-K, K2L31, K2L21, TEMPSS6,T14, T14-HT14, T14-SS1, T14-W2,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1 | 1-00238602 Rev. #4,1-00216496 Rev. #13,1-00237189 Rev. #8,1-00237186 Rev. #4,1-00238468 Rev. #3,1-00181626 Rev. #19,1-00220299 Rev. #39 | 4 Hour(s),4 Hour(s),4 Hour(s),2 Day(s),8 Hour(s),4 Hour(s),Non-recallable | FABCW NBLIP BLIP | 2350 300 300
2024-07-08 07:00 | 2024-07-16 12:00 | MIDDLEPORT TS,MILTON SS, TRAFALGAR TS,BRUCE A TS, UNDERWOOD JCT, HANOVER TS, UNDERWOOD WGS,BURLINGTON TS, BURLINGTON JCT, MIDDLEPORT TS, CARLUKE JCT, NEALE JCT, BURLINGTON DESN TS, BECK 2 TS, NIAGARA WEST JCT,GRAND JCT, NANTICOKE TS, HORNING JCT, HORNING TS,LAMBTON TS 2 | T6, T6-LT6, T6-TL581, LT6BUS-TEMP1,M573T.MIXTR, HL573, L502L573, 40-M573T, T15-M573T,B4V.BRXUN, B4V.UNXUN, T4A, 21-B4V, 36B4V-22, 7014B5V-MSO2, 36T4-B4V,Q25BM.BEXNI, Q25BM.BUXBD, Q25BM.BUXBU, Q25BM.MIXCA, Q25BM.NEXBU, 25-Q25BM, 28-Q25BM, 39-Q25BM, T15-Q25BM,59-N5M, 310N5M-LC1,M27B.HOXBU, M27B.HOXHO, M27B.HOXMI, 25-M27B, 39-M27B, 4T4-M27B,K2L28, L27L28, P2L27, 27-L28C, 27-L27V | 1-00220299 Rev. #39,1-00208773 Rev. #10,1-00241125 Rev. #2,1-00238418 Rev. #3,1-00238444 Rev. #7,1-00238499 Rev. #3,1-00216465 Rev. #12 | Non-recallable,14 Day(s),10 Hour(s),6 Hour(s),10 Hour(s),6 Hour(s),4 Hour(s) | FABCW NBLIP BLIP | 550 0 0
2024-08-11 06:00 | 2024-08-16 08:00 | MILTON SS, TRAFALGAR TS,BRUCE A TS, UNDERWOOD JCT, HANOVER TS, UNDERWOOD WGS,BURLINGTON TS, HORNING JCT, HORNING TS, MIDDLEPORT TS,CALEDONIA TS, GRAND JCT,LAMBTON TS 2, ST. CLAIRX TS,MIDDLEPORT TS | M573T.MIXTR, HL573, L502L573, 40-M573T, T15-M573T,B4V.BRXUN, B4V.UNXUN, T4A, 21-B4V, 36B4V-22, 7014B5V-MSO2, 36T4-B4V,M28B.HOXBU, M28B.HOXHO, M28B.HOXMI, 25-M28B, 39-M28B, 4T3-M28B,T2Y, 25-N5M, T2, N27T2-N5M, 310N5M-LC2,L51D.CLXLA, K1L51, L23L51, PS51-2, PS51-1, PS51-S, PS51,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1 | 1-00208773 Rev. #10,1-00241126 Rev. #2,1-00238498 Rev. #3,1-00238512 Rev. #2,1-00235998 Rev. #3,1-00220299 Rev. #39 | 14 Day(s),10 Hour(s),6 Hour(s),10 Hour(s),4 Hour(s),Non-recallable | FABCW NBLIP BLIP | 550 0 0
2024-08-29 17:00 | 2024-09-06 16:00 | BRUCE A TS, BRUCE JCT, WILLOW CREEK JCT, CLAIREVILLE TS, MILTON SS, OWEN SOUND TS,MIDDLEPORT TS, NANTICOKE TS | B560V.BRXBR, B560V.BRXMI, B560V.BRXWI, B560V.MIXCL, DL560, L553L560, 21-B560V, 51-B560V,B27S.BRXOW, T3-B27S, T5-B27S, 21-B27S,M585M.MIXMD, N581M.MDXNA, L81L85, T6L31, 25-M585M, 25-N581M, 40-M585M, 59-N581M, L581_BUS, T6, T6-LT6, T6-TL581, L23HT6,T6, LT6BUS-TEMP1,N581M.MDXNA, AL581, T7L581, T7T12, HT7_BUS | 1-00238565 Rev. #4,1-00241124 Rev. #4,1-00195970 Rev. #14,1-00238566 Rev. #2,1-00238464 Rev. #2,1-00220299 Rev. #39,1-00238492 Rev. #2,1-00238434 Rev. #2,1-00238433 Rev. #2 | 4 Hour(s),4 Hour(s),4 Day(s),4 Hour(s),Non-recallable,Non-recallable,Non-recallable,Non-recallable,Non-recallable | FABCW NBLIP BLIP | 2350 300 300
2024-09-16 08:00 | 2024-09-27 15:00 | MIDDLEPORT TS, NANTICOKE TS,ESSA TS, MILTON SS,BEACH TS, HANNON JCT, DOFASCO KENILWORTH CTS, BECK 2 TS, MIDDLEPORT TS, NEBO JCT, HAMILTON NEBO TS,BRUCE A TS, BRUCE JCT, WILLOW CREEK JCT, CLAIREVILLE TS | N581M.MDXNA, AL581, T7L581, T7T12, 25-N581M, 59-N581M, HT7_BUS,HT4, R4N, HT4L29, HT4_BUS, T4, R4, T4-D, T4-HT4, TSS4,M585M.MIXMD, 25-M585M, 40-M585M,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1, N581M.MDXNA, L81L85, T6L31, L581_BUS, T6, L23HT6,Q24HM.HAXBE, Q24HM.HAXHA, Q24HM.HAXKE, Q24HM.HNXHA, Q24HM.HNXHN, Q24HM.HNXMI, 157T1-Q24HM, 17-Q24HM, 17-Q29HM, 25-Q24HM, 28-Q24HM, T3-Q24HM, 61Q29HM-LC,B560V.BRXBR, B560V.BRXMI, B560V.BRXWI, B560V.MIXCL, 21-B560V, 51-B560V, DL560, L553L560 | 1-00238433 Rev. #2,1-00246166 Rev. #1,1-00238434 Rev. #2,1-00238492 Rev. #2,1-00220299 Rev. #39,1-00238464 Rev. #2,1-00238421 Rev. #2,1-00238566 Rev. #2,1-00195970 Rev. #14 | Non-recallable,4 Hour(s),Non-recallable,Non-recallable,Non-recallable,Non-recallable,10 Hour(s),4 Hour(s),4 Day(s) | FABCW NBLIP BLIP | 2350 300 300
2024-11-04 08:00 | 2024-11-15 17:00 | MIDDLEPORT TS, MILTON SS, NANTICOKE TS,BECK 2 TS,CLAIREVILLE TS, ESSA TS,KENT TS, CHATHAM SS, GSPC JCT,BRUCE A TS, UNDERWOOD JCT, HANOVER TS, UNDERWOOD WGS | M585M.MIXMD, N581M.MDXNA, L81L85, T6L31, 25-M585M, 25-N581M, 40-M585M, 59-N581M, L581_BUS, T6, T6-LT6, T6-TL581, L23HT6,28-PA302, T302, T302-1,N581M.MDXNA, AL581, T7L581, T7T12, HT7_BUS,E511V.CLXES, DL511, W2L511, 18-E511V, 51-E511V,T1B, T1Y, T4Z, 5-L28C, 86-L28C, T1, T4, T1-L28C, T4L28C, 312L28C-MSO2,B4V.BRXUN, B4V.UNXUN, T4A, 21-B4V, 36B4V-22, 36T4-B4V, 161B5V-MSO1, 21-B5V | 1-00238465 Rev. #1,1-00238560 Rev. #1,1-00238433 Rev. #2,1-00238434 Rev. #2,1-00238492 Rev. #2,1-00238538 Rev. #1,1-00240028 Rev. #2,1-00241127 Rev. #1 | 4 Hour(s),8 Hour(s),Non-recallable,Non-recallable,Non-recallable,48 Hour(s),12 Hour(s),10 Hour(s) | FABCW NBLIP BLIP | 1000 0 0
2024-11-17 07:15 | 2024-11-28 17:00 | BRUCE A TS, MAJESTIC JCT, MAJESTIC CTS, WINGHAM JCT, SEAFORTH TS, WINGHAM TS,MIDDLEPORT TS, MILTON SS, NANTICOKE TS,BECK 2 TS,CLAIREVILLE TS, ESSA TS,KENT TS, CHATHAM SS, GSPC JCT | B23D.MJXBR, B23D.MJXMJ, B23D.MJXWI, B23D.WIXSE, B23D.WIXWI, T2-B23D, 21-B23D, 61B23D-21,M585M.MIXMD, N581M.MDXNA, L81L85, T6L31, 25-M585M, 25-N581M, 40-M585M, 59-N581M, L581_BUS, T6, T6-LT6, T6-TL581, L23HT6,N581M.MDXNA, AL581, T7L581, T7T12, HT7_BUS,28-PA302, T302, T302-1,E511V.CLXES, DL511, W2L511, 18-E511V, 51-E511V,T1B, T1Y, T4Z, 5-L28C, 86-L28C, T1, T4, T1-L28C, T4L28C, 312L28C-MSO2 | 1-00241121 Rev. #1,1-00238465 Rev. #1,1-00238433 Rev. #2,1-00238560 Rev. #1,1-00238434 Rev. #2,1-00238492 Rev. #2,1-00238538 Rev. #1,1-00240028 Rev. #2 | 4 Hour(s),4 Hour(s),Non-recallable,8 Hour(s),Non-recallable,Non-recallable,48 Hour(s),12 Hour(s) | FABCW NBLIP BLIP | 800 0 0
2024-12-06 16:00 | 2024-12-12 17:00 | BRUCE A TS, BRUCE JCT, MILTON SS, WILLOW CREEK JCT,MIDDLEPORT TS, NANTICOKE TS | B502M.BAXBJ, B502M.BJXMI, B502M.BJXWJ, 21-B502M, 40-B502M,N581M.MDXNA, AL581, T7L581, T7T12, 25-N581M, 59-N581M, HT7_BUS,M585M.MIXMD, N581M.MDXNA, L81L85, T6L31, 25-M585M, 40-M585M, L581_BUS, T6, T6-LT6, T6-TL581, L23HT6 | 1-00238570 Rev. #1,1-00238433 Rev. #2,1-00238465 Rev. #1 | 4 Hour(s),Non-recallable,4 Hour(s) | FABCW NBLIP BLIP | 2350 300 300
2025-01-20 05:00 | 2025-02-13 18:00 | BRUCE B SS | OLDH5P, OLDH5L563, H5_BUS, H5L563, H5P, H5-H5GIS, H5_GIS_BUS | 1-00220280 Rev. #5 | 6 Hour(s) | FABCW NBLIP BLIP | 50 300 500
2024-04-14 16:00 | 2024-04-19 17:00 | LAMBTON TS 2,KENT TS, CHATHAM SS, GSPC JCT,MIDDLEPORT TS,BRUCE A TS, BRUCE JCT, MILTON SS, WILLOW CREEK JCT | 27-T8, 27T8-L4D, T8,T1B, T1Y, T4Z, 5-L28C, 86-L28C, T1, T4, T1-L28C, T4L28C, 312L28C-MSO2,27-T7, 27-T8, T7, T7-L4D,D1D2, D1L29, D1L27, L33L40, SC22D1, SC22SC, 25-M33W, D1_BUS, SC22, SS2-D, D1L34, D1L33,B502M.BAXBJ, B502M.BJXMI, B502M.BJXWJ, 21-B502M, 40-B502M | 1-00240619 Rev. #5,1-00238919 Rev. #6,1-00231342 Rev. #12,1-00234253 Rev. #9,1-00238390 Rev. #3,1-00235814 Rev. #13 | 14 Day(s),12 Hour(s),4 Hour(s),Non-recallable,2 Hour(s),4 Hour(s) | FABCW NBLIP BLIP | 1750 300 300
2024-04-19 18:00 | 2024-04-27 07:15 | LAMBTON TS 2,BRUCE B SS, BRUCE JCT, WILLOW CREEK JCT, MILTON SS,KENT TS, CHATHAM SS, GSPC JCT | 27-T7, 27-T8, 27T8-L4D, T7, T8, T7-L4D,B501M.BBXBJ, B501M.BJXWJ, B501M.WJXMI, 40-B501M, 29-B501M,27-T8,T1B, T1Y, T4Z, 5-L28C, 86-L28C, T1, T4, T1-L28C, T4L28C, 312L28C-MSO2 | 1-00234253 Rev. #9,1-00237165 Rev. #9,1-00231342 Rev. #12,1-00240619 Rev. #5,1-00238919 Rev. #6 | Non-recallable,4 Hour(s),4 Hour(s),14 Day(s),12 Hour(s) | FABCW NBLIP BLIP | 1750 300 300
2024-05-19 17:00 | 2024-05-31 17:00 | BRUCE B SS, BRUCE JCT, WILLOW CREEK JCT, MILTON SS,LAMBTON TS 2,LONGWOOD DESN, LAMBTON TS 2, LONGWOOD JCT, LONGWOOD TS | B501M.BBXBJ, B501M.BJXWJ, B501M.WJXMI, 40-B501M, 29-B501M,27-T7, 27-T8, 27T8-L4D, T7, T8, T7-L4D,27-T8,L24L.LOXLA, L24L.LOXLD, L24L.LOXLO, AL24, T14Q, T3L24, 27-L24L, T14, T14-L24L, W52-L24L | 1-00237165 Rev. #9,1-00234253 Rev. #9,1-00231342 Rev. #12,1-00236074 Rev. #16,1-00240619 Rev. #5 | 4 Hour(s),Non-recallable,4 Hour(s),8 Day(s),14 Day(s) | FABCW NBLIP BLIP | 1850 300 300
2024-08-26 08:00 | 2024-09-06 16:00 | BRUCE A TS, BRUCE JCT, WILLOW CREEK JCT, CLAIREVILLE TS, MILTON SS | B560V.BRXBR, B560V.BRXMI, B560V.BRXWI, B560V.MIXCL, DL560, L553L560, 21-B560V, 51-B560V | 1-00238565 Rev. #4,1-00195970 Rev. #14,1-00238566 Rev. #2 | 4 Hour(s),4 Day(s),4 Hour(s) | FABCW NBLIP BLIP | 1750 300 300
2024-09-06 16:00 | 2024-09-27 15:00 | BRUCE A TS, BRUCE JCT, WILLOW CREEK JCT, CLAIREVILLE TS, MILTON SS | B560V.BRXBR, B560V.BRXMI, B560V.BRXWI, B560V.MIXCL, DL560, L553L560, 21-B560V, 51-B560V | 1-00195970 Rev. #14,1-00238566 Rev. #2 | 4 Day(s),4 Hour(s) | FABCW NBLIP BLIP | 1750 300 300
2024-10-07 06:00 | 2024-10-18 07:00 | ASHFIELD SS, BRUCE B SS, BRUCE JCT, WILLOW CREEK JCT,KENT TS, CHATHAM SS, GSPC JCT | B563A.BBXBJ, B563A.BJWJ, B563A.WJXAS, OLDH5L563, OLDL501L563, L563L592, L563L565, OLD29-B563A, 322-B563A, L563_BUS, H5L563, L501L563, 29-B563A,T1B, T1Y, T4Z, 5-L28C, 86-L28C, T1, T4, T1-L28C, T4L28C, 312L28C-MSO2 | 1-00241110 Rev. #2,1-00240028 Rev. #2 | 6 Hour(s),12 Hour(s) | FABCW NBLIP BLIP | 250 300 300
2024-12-01 08:00 | 2024-12-12 17:00 | BRUCE A TS, BRUCE JCT, MILTON SS, WILLOW CREEK JCT | B502M.BAXBJ, B502M.BJXMI, B502M.BJXWJ, 21-B502M, 40-B502M | 1-00238570 Rev. #1 | 4 Hour(s) | FABCW NBLIP BLIP | 1750 300 300
2024-06-21 17:00 | 2024-06-27 17:00 | BRUCE B SS, BRUCE JCT, WILLOW CREEK JCT, MILTON SS,PARKWAY TS,CLAIREVILLE TS,CHURCHILL MEADOWS TS, ERINDALE JCT, CHURCHILL MEADOWS JCT, HANLAN JCT, ERINDALE TS, TOMKEN JCT, HURONTARIO SS, JIM YARROW MTS, RICHVIEW TS, TOMKEN TS, TRAFALGAR TS | B561M.BBXBR, B561M.BRXWI, B561M.WIXMI, 40-B561M, 29-B561M, KL561, L61L71,T3, SS1-T3, T3-HT3, T3-LT3,T14, T14-HT14, T14-SS1, T14-W2,R21TH.CHXTR, R21TH.ERXCH, R21TH.ERXER, R21TH.ERXHA, R21TH.HAXHU, R21TH.HAXTO, R21TH.HUXHA, R21TH.HUXJM, R21TH.TOXRI, R21TH.TOXTO, L21L30, 162-R21TH, 240T1-R21TH, 31-R21TH, 5T5-R21TH, 88-R21TH, T4-R21TH | 1-00237189 Rev. #8,1-00237186 Rev. #4,1-00239147 Rev. #3,1-00181626 Rev. #19,1-00238414 Rev. #3 | 4 Hour(s),2 Day(s),3 Hour(s),4 Hour(s),36 Hour(s) | FABCW NBLIP BLIP | 2150 300 300
2024-08-26 07:00 | 2024-09-06 16:00 | BRUCE A TS, BRUCE JCT, WILLOW CREEK JCT, CLAIREVILLE TS, MILTON SS,MIDDLEPORT TS, NANTICOKE TS | B560V.BRXBR, B560V.BRXMI, B560V.BRXWI, B560V.MIXCL, DL560, L553L560, 21-B560V, 51-B560V,N581M.MDXNA, AL581, T7L581, 25-N581M, 59-N581M, T7T12, HT7_BUS,M585M.MIXMD, 25-M585M, 40-M585M, N581M.MDXNA, L81L85, T6L31, L581_BUS, T6, T6-LT6, T6-TL581, L23HT6 | 1-00238565 Rev. #4,1-00238434 Rev. #2,1-00238433 Rev. #2,1-00238492 Rev. #2,1-00238464 Rev. #2,1-00238566 Rev. #2,1-00195970 Rev. #14 | 4 Hour(s),Non-recallable,Non-recallable,Non-recallable,Non-recallable,4 Hour(s),4 Day(s) | FABCW NBLIP BLIP | 2350 300 300
2024-09-06 16:00 | 2024-09-27 15:00 | BRUCE A TS, BRUCE JCT, WILLOW CREEK JCT, CLAIREVILLE TS, MILTON SS,MIDDLEPORT TS, NANTICOKE TS | B560V.BRXBR, B560V.BRXMI, B560V.BRXWI, B560V.MIXCL, DL560, L553L560, 21-B560V, 51-B560V,N581M.MDXNA, AL581, T7L581, 25-N581M, 59-N581M, T7T12, HT7_BUS,M585M.MIXMD, 25-M585M, 40-M585M, N581M.MDXNA, L81L85, T6L31, L581_BUS, T6, T6-LT6, T6-TL581, L23HT6 | 1-00195970 Rev. #14,1-00238434 Rev. #2,1-00238433 Rev. #2,1-00238492 Rev. #2,1-00238464 Rev. #2,1-00238566 Rev. #2 | 4 Day(s),Non-recallable,Non-recallable,Non-recallable,Non-recallable,4 Hour(s) | FABCW NBLIP BLIP | 2350 300 300
2024-10-07 06:00 | 2024-10-15 07:00 | MIDDLEPORT TS, MILTON SS, NANTICOKE TS,ASHFIELD SS, BRUCE B SS, BRUCE JCT, WILLOW CREEK JCT | M585M.MIXMD, N581M.MDXNA, L81L85, T6L31, 25-M585M, 25-N581M, 40-M585M, 59-N581M, L581_BUS, T6, T6-LT6, T6-TL581, L23HT6,N581M.MDXNA, AL581, T7L581, T7T12, HT7_BUS,B563A.BBXBJ, B563A.BJWJ, B563A.WJXAS, OLDH5L563, OLDL501L563, L563L592, L563L565, OLD29-B563A, 322-B563A, L563_BUS, H5L563, L501L563, 29-B563A | 1-00238464 Rev. #2,1-00238492 Rev. #2,1-00238433 Rev. #2,1-00238434 Rev. #2,1-00241110 Rev. #2 | Non-recallable,Non-recallable,Non-recallable,Non-recallable,6 Hour(s) | FABCW NBLIP BLIP | 850 300 300
Back to main menu

## Table C2
Back to main menu
Table C2: East Zone
Planned Start | Planned End | Station | Equipment Name | Outage ID | Max Recall | Major Transmission Interface Impacted | Reduction in Limit
2024-06-09 07:00 | 2024-06-28 17:00 | B5D-B31L SS JCT, ST. LAWRENCE TS | B31L.IPXLA, 49-B31L, B31L-D, B5D-B31L | 1-00245104 Rev. #1 | 4 Hour(s) | FIO BEAU P33C | 250 400 0
2024-03-25 08:00 | 2024-04-05 16:00 | BOWMANVILLE SS | H2A, H2L520, H2_BUS | 1-00244450 Rev. #8 | 6 Hour(s)
2024-10-07 07:00 | 2024-12-19 17:00 | CHATS FALLS TS, HAVELOCK TS, CLARINGTON TS, MARINE JCT | C25H.HAXCF, 2-C25H, 57-C25H, HT3L32, K2L32, 296-T32H, L32_BUS, T32H.HAXMJ, T32H.MJXCL, 57-T32H | 1-00239126 Rev. #4 | 4 Hour(s) | FIO BEAU P33C | 0 0 100
2024-08-06 07:00 | 2024-08-16 17:00 | CATARAQUI TS, WESTBROOK JCT, ODESSA JCT | Q6S.CAXWE, Q6S.WEXOD, 29-Q6S, 59Q6S-2 | 1-00239063 Rev. #2 | 4 Hour(s)
2024-10-14 07:00 | 2024-10-25 17:00 | DALE JCT, SIDNEY TS | P3S.SIXDA, 12-P3S, 65P3S-1 | 1-00239144 Rev. #3 | 4 Hour(s)
2024-09-03 07:00 | 2024-09-08 14:00 | CLARINGTON TS, HAVELOCK TS, MARINE JCT, OTONABEE TS | 128T1-T31H, L23L31, P2L31, 296-T31H, L31_BUS, T31H.HAXMJ, T31H.MJXCL, T31H.MJXOT, 57-T31H | 1-00239080 Rev. #5 | 4 Hour(s)
2024-09-08 14:00 | 2024-09-13 17:00 | CLARINGTON TS, HAVELOCK TS, MARINE JCT, OTONABEE TS,HAWTHORNE TS | 128T1-T31H, L23L31, P2L31, 296-T31H, L31_BUS, T31H.HAXMJ, T31H.MJXCL, T31H.MJXOT, 57-T31H,HT1P1, T2L523, HT2-P2, T2, P1-P2, R2-T2, T2-HT2, T2-LT2 | 1-00239080 Rev. #5,1-00208490 Rev. #7 | 4 Hour(s),6 Hour(s) | FIO BEAU P33C | 1500 0 0
2024-10-07 07:00 | 2024-10-25 09:30 | HAWTHORNE TS,CHATS FALLS TS, HAVELOCK TS, CLARINGTON TS, MARINE JCT | HT1P1, T2L523, HT2-P2, T2, P1-P2, R2-T2, T2-HT2, T2-LT2,C25H.HAXCF, 2-C25H, 57-C25H, HT3L32, K2L32, 296-T32H, L32_BUS, T32H.HAXMJ, T32H.MJXCL, 57-T32H | 1-00208490 Rev. #7,1-00239126 Rev. #4 | 6 Hour(s),4 Hour(s) | FIO BEAU P33C | 1500 0 100
2024-10-25 09:30 | 2024-12-19 17:00 | CHATS FALLS TS, HAVELOCK TS, CLARINGTON TS, MARINE JCT | C25H.HAXCF, 2-C25H, 57-C25H, HT3L32, K2L32, 296-T32H, L32_BUS, T32H.HAXMJ, T32H.MJXCL, 57-T32H | 1-00239126 Rev. #4 | 4 Hour(s) | FIO BEAU P33C | 0 0 100
2024-03-03 17:00 | 2024-04-02 08:00 | LENNOX TS, LAFARGE JCT | DL2, H52L2, 12-X2H, DBUS-TEMP2, H52-TEMP1, NAD3X2H-TEMP1 | 1-00238787 Rev. #17 | Non-recallable
2024-04-02 08:00 | 2024-04-11 16:00 | BROCKVILLE TS, EASTON JCT, EASTON YULE JCT, HINCHINBROOKE SS, SMITHS FALLS TS, ST. LAWRENCE TS,LENNOX TS, LAFARGE JCT | L22H.EAXBR, L22H.EAXEA, L22H.EAXHI, L22H.EAXLA, L22H.EAXSM, 10-L22H, 24T1-L22H, 49-L22H, T3-L22H,DL2, H52L2, 12-X2H, DBUS-TEMP2, H52-TEMP1, NAD3X2H-TEMP1 | 1-00213231 Rev. #25,1-00238787 Rev. #17 | 4 Hour(s),Non-recallable
2024-04-14 14:00 | 2024-04-25 17:00 | BROCKVILLE TS, EASTON JCT, EASTON YULE JCT, HINCHINBROOKE SS, SMITHS FALLS TS, ST. LAWRENCE TS,LENNOX TS, LAFARGE JCT | L22H.EAXBR, L22H.EAXEA, L22H.EAXHI, L22H.EAXLA, L22H.EAXSM, 10-L22H, 24T1-L22H, 49-L22H, T3-L22H,DL2, H52L2, 12-X2H, DBUS-TEMP2, H52-TEMP1, NAD3X2H-TEMP1 | 1-00246060 Rev. #2,1-00238787 Rev. #17 | 4 Hour(s),Non-recallable
2024-04-25 17:00 | 2024-07-02 17:00 | LENNOX TS, LAFARGE JCT | DL2, H52L2, 12-X2H, DBUS-TEMP2, H52-TEMP1, NAD3X2H-TEMP1 | 1-00238787 Rev. #17 | Non-recallable
2024-08-08 07:00 | 2024-08-19 07:00 | LENNOX TS | AL4, H52L4 | 1-00239069 Rev. #2 | Non-recallable
2024-08-19 07:00 | 2024-10-14 07:00 | LENNOX TS,GARDINER STR 44 JCT, WESTBROOK JCT, GARDINER TS, HINCHINBROOKE SS, CATARAQUI TS, LENNOX TS | AL4, H52L4,X4H.HIXCA, X4H.WEXGA, X4H.WEXLE, 10-X4H, 1A-X4H, 1T4-X4H, H1T1-X4H | 1-00239069 Rev. #2,1-00239071 Rev. #3 | Non-recallable,4 Hour(s)
2024-10-14 07:00 | 2024-11-29 17:00 | BROCKVILLE TS, EASTON JCT, EASTON YULE JCT, HINCHINBROOKE SS, SMITHS FALLS TS, ST. LAWRENCE TS,LENNOX TS,GARDINER STR 44 JCT, WESTBROOK JCT, GARDINER TS, CATARAQUI TS, LENNOX TS | L22H.EAXBR, L22H.EAXEA, L22H.EAXHI, L22H.EAXLA, L22H.EAXSM, 10-L22H, 24T1-L22H, 49-L22H, T3-L22H,AL4, H52L4,X4H.HIXCA, X4H.WEXGA, X4H.WEXLE, 10-X4H, 1A-X4H, 1T4-X4H, H1T1-X4H | 1-00239136 Rev. #1,1-00239069 Rev. #2,1-00239071 Rev. #3 | 4 Hour(s),Non-recallable,4 Hour(s)
2024-11-29 17:00 | 2024-12-11 17:00 | LENNOX TS,GARDINER STR 44 JCT, WESTBROOK JCT, GARDINER TS, HINCHINBROOKE SS, CATARAQUI TS, LENNOX TS | AL4, H52L4,X4H.HIXCA, X4H.WEXGA, X4H.WEXLE, 10-X4H, 1A-X4H, 1T4-X4H, H1T1-X4H | 1-00239069 Rev. #2,1-00239071 Rev. #3 | Non-recallable,4 Hour(s)
2024-11-06 07:00 | 2024-11-17 15:00 | ARNPRIOR JCT, BARRETT CHUTE SS, FITZROY JCT, ARNPRIOR TS, CHATS FALLS TS, NQL1 B JCT, LINCOLN HEIGHTS TS, WOODROFFE TS, MANORDALE JCT, MANORDALE MTS, MERIVALE TS, CENTRE POINT JCT | C7BM.ARXAR, C7BM.ARXBA, C7BM.ARXFI, C7BM.CHXFI, C7BM.FIXNQ, C7BM.LIXWO, C7BM.MAXMD, C7BM.NQXMA, C7BM.NQXME, C7BM.WOXCE, 2C7BM, 14-C7BM, 24-C7BM, 53C7BM-14, 6-C7BM, 71-C7BM, C7BM-71, T2-C7BM | 1-00236095 Rev. #2 | 4 Hour(s)
2024-11-17 16:00 | 2024-12-19 17:00 | BELLMAN JCT, CHATS FALLS TS, FITZROY JCT, NQL1 B JCT | C7BM.CHXFI, C7BM.FIXNQ, 2C7BM, 53C7BM-14, L1C7BM-1 | 1-00241758 Rev. #2 | 4 Hour(s)
2024-06-09 07:00 | 2024-06-28 17:00 | B5D-B31L SS JCT, ST. LAWRENCE TS | B31L.IPXLA, 49-B31L, B31L-D, B5D-B31L | 1-00245104 Rev. #1 | 4 Hour(s) | FIO BEAU P33C | 250 400 0
Back to main menu

## Table C3
Back to main menu
Table C3: Essa Zone
Planned Start | Planned End | Station | Equipment Name | Outage ID | Max Recall | Major Transmission Interface Impacted | Reduction in Limit
2024-08-02 07:00 | 2024-08-23 17:00 | CLAIREVILLE TS, HOLLAND JCT, VAUGHAN 4 JCT, HOLLAND TS, VAUGHAN MTS 4, WOODBRIDGE JCT,BLOOR STREET JCT, GERRARD JCT, CECIL TS, DON FLEET JCT, HEARN SS, LEASIDE TS | 51-H83V, L83L89, 153-H83V, H83V.WJXCL, H83V.HJX4J, H83V.4JXWJ, H83V.4JXV4, H83V.HOXHJ,H8LC.BLXLE, H8LC.CEXGE, H8LC.DOXHE, H8LC.GEXBL, H8LC.GEXDO, 22-H8LC-L8-G, 34-H8LC, 49-H8LC, 80H8LC-22, 80H8LC-34, 80H8LC-49 | 1-00238508 Rev. #4,1-00239058 Rev. #4 | 6 Hour(s),8 Hour(s)
2024-09-09 08:00 | 2024-09-20 16:00 | CLAIREVILLE TS, HOLLAND JCT, VAUGHAN 4 JCT, HOLLAND TS, VAUGHAN MTS #4, WOODBRIDGE JCT | H1L82, L76L82, 51-H82V, 153-H82V, H82V.WJXCL, H82V.4JXV4, H82V.4JXWJ, H82V.HJX4J, H82V.HOXHJ | 1-00238534 Rev. #4 | 4 Hour(s)
2024-08-02 07:00 | 2024-08-23 17:00 | CLAIREVILLE TS, HOLLAND JCT, VAUGHAN 4 JCT, HOLLAND TS, VAUGHAN MTS 4, WOODBRIDGE JCT | 51-H83V, L83L89, 153-H83V, H83V.WJXCL, H83V.HJX4J, H83V.4JXWJ, H83V.4JXV4, H83V.HOXHJ | 1-00238508 Rev. #4 | 6 Hour(s)
2024-09-09 08:00 | 2024-09-20 16:00 | CLAIREVILLE TS, HOLLAND JCT, VAUGHAN 4 JCT, HOLLAND TS, VAUGHAN MTS #4, WOODBRIDGE JCT | H1L82, L76L82, 51-H82V, 153-H82V, H82V.WJXCL, H82V.4JXV4, H82V.4JXWJ, H82V.HJX4J, H82V.HOXHJ | 1-00238534 Rev. #4 | 4 Hour(s)
2024-07-03 06:00 | 2024-08-01 17:00 | BEAVER JCT, BROWN HILL TS, BEAVERTON JCT, LINDSAY TS, MINDEN TS, BEAVERTON TS | M81B.BEXBE, M81B.BEXBV, M81B.BSXBE, M81B.BVXLI, M81B.BVXMI, L81L89, 4T1-M81B, 87-M81B, T4-M81B | 1-00238590 Rev. #4 | 4 Hour(s)
2024-09-22 07:00 | 2024-10-25 17:00 | BEAVER JCT, BROWN HILL TS, BEAVERTON JCT, LINDSAY TS, MINDEN TS, BEAVERTON TS | M80B.BEXBE, M80B.BEXBV, M80B.BSXBE, M80B.BVXLI, M80B.BVXMI, L80L88, 4T2-M80B, 87-M80B, T3-M80B | 1-00239109 Rev. #4 | 4 Hour(s)
2024-07-03 06:00 | 2024-08-01 17:00 | BEAVER JCT, BROWN HILL TS, BEAVERTON JCT, LINDSAY TS, MINDEN TS, BEAVERTON TS | M81B.BEXBE, M81B.BEXBV, M81B.BSXBE, M81B.BVXLI, M81B.BVXMI, L81L89, 4T1-M81B, 87-M81B, T4-M81B | 1-00238590 Rev. #4 | 4 Hour(s)
2024-09-22 07:00 | 2024-10-25 17:00 | BEAVER JCT, BROWN HILL TS, BEAVERTON JCT, LINDSAY TS, MINDEN TS, BEAVERTON TS | M80B.BEXBE, M80B.BEXBV, M80B.BSXBE, M80B.BVXLI, M80B.BVXMI, L80L88, 4T2-M80B, 87-M80B, T3-M80B | 1-00239109 Rev. #4 | 4 Hour(s)
2024-02-25 07:00 | 2024-03-27 07:00 | BRACEBRIDGE JCT, COOPERS FALLS JCT, MINDEN TS, ORILLIA TS, ESSA TS, MIDHURST TS, MUSKOKA TS | M7E.BRXMU, M7E.COXBR, M7E.COXMI, M7E.MIXES, M7E.MIXOR, M7E.ORXCO, 18-M7E, 87-M7E, T1-M7E, T2-M7E, T4-M7E | 1-00238814 Rev. #12 | 4 Hour(s)
2024-03-27 07:00 | 2024-04-05 17:00 | BRACEBRIDGE JCT, COOPERS FALLS JCT, MINDEN TS, ORILLIA TS, ESSA TS, MIDHURST TS, MUSKOKA TS,ESSA TS | M7E.BRXMU, M7E.COXBR, M7E.COXMI, M7E.MIXES, M7E.MIXOR, M7E.ORXCO, 18-M7E, 87-M7E, T1-M7E, T2-M7E, T4-M7E,SS2, T2, 18T2-A, 18T2-K | 1-00238814 Rev. #12,1-00242249 Rev. #6 | 4 Hour(s),Non-recallable
2024-03-25 07:00 | 2024-03-31 11:00 | CLAIREVILLE TS, ESSA TS,BRANTFORD TS, NEWPORT JCT, MIDDLEPORT TS,BECK 2 TS, MID RIVER JCT NIAGARA,MIDDLEPORT TS,CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,DETWEILER TS, STRATFORD JCT, SEAFORTH TS, STRATFORD TS | E510V.CLXES, AL510, W3L510, 18-E510V, 51-E510V,M32W.NEXBR, M32W.NEXMI, YZ, 25-M32W, 44M32W-19, T4-M32W,BP76.PAXBE, K2L76, L35L76, R76, TL35-BO1,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1,C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,B22D.STXDE, B22D.STXST, 26-B22D, 68T1-B22D, 61B22D-26,AL510 | 1-00238540 Rev. #3,1-00238922 Rev. #11,1-00181622 Rev. #28,1-00220299 Rev. #39,1-00213473 Rev. #37,1-00235682 Rev. #6,1-00237157 Rev. #9,1-00238545 Rev. #4 | 48 Hour(s),6 Hour(s),Non-recallable,Non-recallable,Non-recallable,14 Day(s),4 Hour(s),5 Day(s) | FS FN P502X CLAN | 0 0 0 700
2024-04-05 17:00 | 2024-04-12 16:00 | BRUCE A TS, BRUCE JCT, MILTON SS, WILLOW CREEK JCT,BRANTFORD TS, NEWPORT JCT, MIDDLEPORT TS,BECK 2 TS, MID RIVER JCT NIAGARA,MIDDLEPORT TS,CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,CLAIREVILLE TS, ESSA TS,DETWEILER TS, STRATFORD JCT, SEAFORTH TS, STRATFORD TS,LONGWOOD TS | B502M.BAXBJ, B502M.BJXMI, B502M.BJXWJ, 21-B502M, 40-B502M,M32W.NEXBR, M32W.NEXMI, YZ, 25-M32W, 44M32W-19, T4-M32W,BP76.PAXBE, K2L76, L35L76, R76, TL35-BO1,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1,C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,E510V.CLXES, AL510, W3L510, 18-E510V, 51-E510V,B22D.STXDE, B22D.STXST, 26-B22D, 68T1-B22D, 61B22D-26,R5N, T5L45, SS5, T5, R5, T5-H, T5-LT5,25-Q23BM, L23HT6, D2L23, Q23BM-TEMP1 | 1-00239284 Rev. #3,1-00238922 Rev. #11,1-00181622 Rev. #28,1-00220299 Rev. #39,1-00213473 Rev. #37,1-00235682 Rev. #6,1-00237157 Rev. #9,1-00239308 Rev. #10,1-00235814 Rev. #13,1-00246468 Rev. #2 | 8 Hour(s),6 Hour(s),Non-recallable,Non-recallable,Non-recallable,14 Day(s),4 Hour(s),5 Day(s),4 Hour(s),6 Hour(s) | FS FN P502X CLAN | 0 0 0 700
2024-04-14 16:00 | 2024-04-19 16:00 | CLAIREVILLE TS, ESSA TS,KENT TS, CHATHAM SS, GSPC JCT,DETWEILER TS, STRATFORD JCT, SEAFORTH TS, STRATFORD TS,CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,MIDDLEPORT TS,BECK 2 TS, MID RIVER JCT NIAGARA,BRUCE A TS, BRUCE JCT, MILTON SS, WILLOW CREEK JCT,LONGWOOD TS | E510V.CLXES, AL510, W3L510, 18-E510V, 51-E510V,T1B, T1Y, T4Z, 5-L28C, 86-L28C, T1, T4, T1-L28C, T4L28C, 312L28C-MSO2,B22D.STXDE, B22D.STXST, 26-B22D, 68T1-B22D, 61B22D-26,C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1,BP76.PAXBE, K2L76, L35L76, R76, TL35-BO1,25-Q23BM, L23HT6, D2L23, Q23BM-TEMP1,D1D2, D1L29, D1L27, L33L40, SC22D1, SC22SC, 25-M33W, D1_BUS, SC22, SS2-D, D1L34, D1L33,B502M.BAXBJ, B502M.BJXMI, B502M.BJXWJ, 21-B502M, 40-B502M,R5N, T5L45, SS5, T5, R5, T5-H, T5-LT5 | 1-00235682 Rev. #6,1-00238919 Rev. #6,1-00237157 Rev. #9,1-00213473 Rev. #37,1-00220299 Rev. #39,1-00181622 Rev. #28,1-00246468 Rev. #2,1-00238390 Rev. #3,1-00235814 Rev. #13,1-00239308 Rev. #10 | 14 Day(s),12 Hour(s),4 Hour(s),Non-recallable,Non-recallable,Non-recallable,6 Hour(s),2 Hour(s),4 Hour(s),5 Day(s) | FS FN P502X CLAN | 0 0 0 700
2024-09-16 08:00 | 2024-09-27 15:00 | MIDDLEPORT TS, NANTICOKE TS,ESSA TS, MILTON SS,BEACH TS, HANNON JCT, DOFASCO KENILWORTH CTS, BECK 2 TS, MIDDLEPORT TS, NEBO JCT, HAMILTON NEBO TS,BRUCE A TS, BRUCE JCT, WILLOW CREEK JCT, CLAIREVILLE TS | N581M.MDXNA, AL581, T7L581, T7T12, 25-N581M, 59-N581M, HT7_BUS,HT4, R4N, HT4L29, HT4_BUS, T4, R4, T4-D, T4-HT4, TSS4,M585M.MIXMD, 25-M585M, 40-M585M,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1, N581M.MDXNA, L81L85, T6L31, L581_BUS, T6, L23HT6,Q24HM.HAXBE, Q24HM.HAXHA, Q24HM.HAXKE, Q24HM.HNXHA, Q24HM.HNXHN, Q24HM.HNXMI, 157T1-Q24HM, 17-Q24HM, 17-Q29HM, 25-Q24HM, 28-Q24HM, T3-Q24HM, 61Q29HM-LC,B560V.BRXBR, B560V.BRXMI, B560V.BRXWI, B560V.MIXCL, 21-B560V, 51-B560V, DL560, L553L560 | 1-00238433 Rev. #2,1-00246166 Rev. #1,1-00238434 Rev. #2,1-00238492 Rev. #2,1-00220299 Rev. #39,1-00238464 Rev. #2,1-00238421 Rev. #2,1-00238566 Rev. #2,1-00195970 Rev. #14 | Non-recallable,4 Hour(s),Non-recallable,Non-recallable,Non-recallable,Non-recallable,10 Hour(s),4 Hour(s),4 Day(s)
2024-11-04 08:00 | 2024-11-15 17:00 | MIDDLEPORT TS, MILTON SS, NANTICOKE TS,BECK 2 TS,CLAIREVILLE TS, ESSA TS,KENT TS, CHATHAM SS, GSPC JCT,BRUCE A TS, UNDERWOOD JCT, HANOVER TS, UNDERWOOD WGS | M585M.MIXMD, N581M.MDXNA, L81L85, T6L31, 25-M585M, 25-N581M, 40-M585M, 59-N581M, L581_BUS, T6, T6-LT6, T6-TL581, L23HT6,28-PA302, T302, T302-1,N581M.MDXNA, AL581, T7L581, T7T12, HT7_BUS,E511V.CLXES, DL511, W2L511, 18-E511V, 51-E511V,T1B, T1Y, T4Z, 5-L28C, 86-L28C, T1, T4, T1-L28C, T4L28C, 312L28C-MSO2,B4V.BRXUN, B4V.UNXUN, T4A, 21-B4V, 36B4V-22, 36T4-B4V, 161B5V-MSO1, 21-B5V | 1-00238465 Rev. #1,1-00238560 Rev. #1,1-00238433 Rev. #2,1-00238434 Rev. #2,1-00238492 Rev. #2,1-00238538 Rev. #1,1-00240028 Rev. #2,1-00241127 Rev. #1 | 4 Hour(s),8 Hour(s),Non-recallable,Non-recallable,Non-recallable,48 Hour(s),12 Hour(s),10 Hour(s) | FS FN P502X CLAN | 0 0 0 700
2024-11-17 07:15 | 2024-11-28 17:00 | BRUCE A TS, MAJESTIC JCT, MAJESTIC CTS, WINGHAM JCT, SEAFORTH TS, WINGHAM TS,MIDDLEPORT TS, MILTON SS, NANTICOKE TS,BECK 2 TS,CLAIREVILLE TS, ESSA TS,KENT TS, CHATHAM SS, GSPC JCT | B23D.MJXBR, B23D.MJXMJ, B23D.MJXWI, B23D.WIXSE, B23D.WIXWI, T2-B23D, 21-B23D, 61B23D-21,M585M.MIXMD, N581M.MDXNA, L81L85, T6L31, 25-M585M, 25-N581M, 40-M585M, 59-N581M, L581_BUS, T6, T6-LT6, T6-TL581, L23HT6,N581M.MDXNA, AL581, T7L581, T7T12, HT7_BUS,28-PA302, T302, T302-1,E511V.CLXES, DL511, W2L511, 18-E511V, 51-E511V,T1B, T1Y, T4Z, 5-L28C, 86-L28C, T1, T4, T1-L28C, T4L28C, 312L28C-MSO2 | 1-00241121 Rev. #1,1-00238465 Rev. #1,1-00238433 Rev. #2,1-00238560 Rev. #1,1-00238434 Rev. #2,1-00238492 Rev. #2,1-00238538 Rev. #1,1-00240028 Rev. #2 | 4 Hour(s),4 Hour(s),Non-recallable,8 Hour(s),Non-recallable,Non-recallable,48 Hour(s),12 Hour(s) | FS FN P502X CLAN | 0 0 0 700
2024-07-03 06:00 | 2024-07-21 07:00 | BEAVER JCT, BROWN HILL TS, BEAVERTON JCT, LINDSAY TS, MINDEN TS, BEAVERTON TS | M81B.BEXBE, M81B.BEXBV, M81B.BSXBE, M81B.BVXLI, M81B.BVXMI, L81L89, 4T1-M81B, 87-M81B, T4-M81B | 1-00238590 Rev. #4 | 4 Hour(s)
2024-07-21 07:00 | 2024-08-01 17:00 | BEAVER JCT, BROWN HILL TS, BEAVERTON JCT, LINDSAY TS, MINDEN TS, BEAVERTON TS,CHURCHILL MEADOWS TS, CHURCHILL MEADOWS JCT, TRAFALGAR TS, ERINDALE JCT, HANLAN JCT, ERINDALE TS, HURONTARIO SS, RICHVIEW TS, TOMKEN JCT, TOMKEN TS | M81B.BEXBE, M81B.BEXBV, M81B.BSXBE, M81B.BVXLI, M81B.BVXMI, L81L89, 4T1-M81B, 87-M81B, T4-M81B,R19TH.CHXTR, R19TH.ERXCH, R19TH.ERXER, R19TH.ERXHA, R19TH.HAXHU, R19TH.TOXRI, R19TH.TOXTO, L19L29, 240T2-R19TH, 31-R19TH, 5T6-R19TH, 88-R19TH, L19L29-L19, T3-R19TH | 1-00238590 Rev. #4,1-00238484 Rev. #4 | 4 Hour(s),36 Hour(s)
2024-09-22 07:00 | 2024-10-15 07:00 | BEAVER JCT, BROWN HILL TS, BEAVERTON JCT, LINDSAY TS, MINDEN TS, BEAVERTON TS | M80B.BEXBE, M80B.BEXBV, M80B.BSXBE, M80B.BVXLI, M80B.BVXMI, L80L88, 4T2-M80B, 87-M80B, T3-M80B | 1-00239109 Rev. #4 | 4 Hour(s)
2024-10-15 07:00 | 2024-10-25 16:00 | CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,BEAVER JCT, BROWN HILL TS, BEAVERTON JCT, LINDSAY TS, MINDEN TS, BEAVERTON TS | C553VP.CHXPJ, C553VP.PJXCL, C553VP.PJXPR, A2L553, L553L560, 51-C553VP, 52-C553VP, 81-C553VP,M80B.BEXBE, M80B.BEXBV, M80B.BSXBE, M80B.BVXLI, M80B.BVXMI, L80L88, 4T2-M80B, 87-M80B, T3-M80B | 1-00238550 Rev. #2,1-00239109 Rev. #4 | 4 Hour(s),4 Hour(s)
2024-03-30 04:30 | 2024-04-05 16:00 | CLAIREVILLE TS,CHURCHILL MEADOWS TS, CHURCHILL MEADOWS JCT, TRAFALGAR TS, ERINDALE JCT, HANLAN JCT, ERINDALE TS, HURONTARIO SS, RICHVIEW TS, TOMKEN JCT, TOMKEN TS, ESSA TS,CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,PALERMO TS, BURLINGTON TS, GLENORCHY JCT, LANTZ JCT, PALERMO TXB JCT, GLENORCHY MTS1 | AL510, W3L510, 51-E510V,R19TH.CHXTR, R19TH.ERXCH, R19TH.ERXER, R19TH.ERXHA, R19TH.HAXHU, R19TH.TOXRI, R19TH.TOXTO, L19L29, 240T2-R19TH, 31-R19TH, 5T6-R19TH, 88-R19TH, L19L29-L19, T3-R19TH,E510V.CLXES, AL510, 18-E510V,C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,T37B.GJXGL, T37B.GJXLA, T37B.PAXBU, T37B.PAXTR, T37B.PJXGJ, T4Y, 31-T37B, 31SC21L-T36B, 31SC21L-T37B, 39-T37B, T4, T4-T37B | 1-00238545 Rev. #4,1-00238480 Rev. #8,1-00235682 Rev. #6,1-00213473 Rev. #37,1-00226775 Rev. #13,1-00238540 Rev. #3 | 5 Day(s),36 Hour(s),14 Day(s),Non-recallable,6 Hour(s),48 Hour(s) | FS FN P502X CLAN | 0 0 0 700
2024-04-12 16:00 | 2024-05-03 17:00 | CLAIREVILLE TS, ESSA TS,CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,CHURCHILL MEADOWS TS, CHURCHILL MEADOWS JCT, TRAFALGAR TS, ERINDALE JCT, HANLAN JCT, ERINDALE TS, HURONTARIO SS, RICHVIEW TS, TOMKEN JCT, TOMKEN TS | E510V.CLXES, AL510, W3L510, 18-E510V, 51-E510V,C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,R19TH.CHXTR, R19TH.ERXCH, R19TH.ERXER, R19TH.ERXHA, R19TH.HAXHU, R19TH.TOXRI, R19TH.TOXTO, L19L29, 240T2-R19TH, 31-R19TH, 5T6-R19TH, 88-R19TH, L19L29-L19, T3-R19TH | 1-00235682 Rev. #6,1-00213473 Rev. #37,1-00238480 Rev. #8 | 14 Day(s),Non-recallable,36 Hour(s) | FS FN P502X CLAN | 0 0 0 700
2024-11-06 17:00 | 2024-11-12 07:00 | MIDDLEPORT TS, MILTON SS, NANTICOKE TS,CLAIREVILLE TS, ESSA TS | M585M.MIXMD, N581M.MDXNA, L81L85, T6L31, 25-M585M, 25-N581M, 40-M585M, 59-N581M, L581_BUS, T6, T6-LT6, T6-TL581, L23HT6,N581M.MDXNA, AL581, T7L581, T7T12, HT7_BUS,E511V.CLXES, DL511, W2L511, 18-E511V, 51-E511V | 1-00238465 Rev. #1,1-00238433 Rev. #2,1-00238434 Rev. #2,1-00238492 Rev. #2,1-00238538 Rev. #1 | 4 Hour(s),Non-recallable,Non-recallable,Non-recallable,48 Hour(s) | FS FN P502X CLAN | 0 0 0 700
2024-11-12 07:00 | 2024-11-29 17:00 | PARKWAY TS,MIDDLEPORT TS, MILTON SS, NANTICOKE TS,CLAIREVILLE TS, ESSA TS | SS4, T4, SS4-T4, T4-HT4, T4-LT4,M585M.MIXMD, N581M.MDXNA, L81L85, T6L31, 25-M585M, 25-N581M, 40-M585M, 59-N581M, L581_BUS, T6, T6-LT6, T6-TL581, L23HT6,N581M.MDXNA, AL581, T7L581, T7T12, HT7_BUS,E511V.CLXES, DL511, W2L511, 18-E511V, 51-E511V | 1-00246738 Rev. #2,1-00238465 Rev. #1,1-00238433 Rev. #2,1-00238434 Rev. #2,1-00238492 Rev. #2,1-00238538 Rev. #1 | 8 Hour(s),4 Hour(s),Non-recallable,Non-recallable,Non-recallable,48 Hour(s) | FS FN P502X CLAN | 0 0 0 700
2024-03-25 07:00 | 2024-04-05 16:00 | CLAIREVILLE TS, ESSA TS | AL510, W3L510, 51-E510V,E510V.CLXES, AL510, 18-E510V | 1-00238545 Rev. #4,1-00235682 Rev. #6,1-00238540 Rev. #3 | 5 Day(s),14 Day(s),48 Hour(s) | FS FN P502X CLAN | 0 0 0 700
2024-04-05 17:00 | 2024-05-03 17:00 | CLAIREVILLE TS, ESSA TS | E510V.CLXES, AL510, W3L510, 18-E510V, 51-E510V | 1-00235682 Rev. #6 | 14 Day(s) | FS FN P502X CLAN | 0 0 0 700
2024-05-21 08:00 | 2024-06-07 16:00 | ESSA TS, HANMER TS | X504E.ESXHA, 18-X504E, 33-X504E | 1-00234064 Rev. #7 | 5 Hour(s) | FS FN P502X CLAN | 990 900 250 0
2024-10-01 07:00 | 2024-10-27 17:00 | ESSA TS, HANMER TS | X503E.ESXHA, 18-X503E, 33-X503E | 1-00234063 Rev. #1 | 5 Hour(s) | FS FN P502X CLAN | 990 900 250 0
2024-10-28 07:00 | 2024-11-03 17:00 | CLAIREVILLE TS, ESSA TS | E511V.CLXES, 18-E511V, 51-E511V, DL511, W2L511 | 1-00241567 Rev. #1,1-00238538 Rev. #1 | 4 Hour(s),48 Hour(s) | FS FN P502X CLAN | 0 0 0 700
2024-11-03 17:00 | 2024-11-29 17:00 | CLAIREVILLE TS, ESSA TS | E511V.CLXES, DL511, W2L511, 18-E511V, 51-E511V | 1-00238538 Rev. #1 | 48 Hour(s) | FS FN P502X CLAN | 0 0 0 700
2024-11-30 07:00 | 2024-12-19 17:00 | DES JOACHIMS TS, OTTO HOLDEN TS | D5H.DEXHO, 5-D5H, 6-D5H | 1-00240190 Rev. #2 | 5 Hour(s) | FS FN P502X CLAN | 25 0 25 0
2024-03-25 07:00 | 2024-04-05 16:00 | CLAIREVILLE TS, ESSA TS | AL510, W3L510, 51-E510V,E510V.CLXES, AL510, 18-E510V | 1-00238545 Rev. #4,1-00235682 Rev. #6,1-00238540 Rev. #3 | 5 Day(s),14 Day(s),48 Hour(s) | FS FN P502X CLAN | 0 0 0 700
2024-04-05 17:00 | 2024-05-03 17:00 | CLAIREVILLE TS, ESSA TS | E510V.CLXES, AL510, W3L510, 18-E510V, 51-E510V | 1-00235682 Rev. #6 | 14 Day(s) | FS FN P502X CLAN | 0 0 0 700
2024-05-21 08:00 | 2024-06-07 16:00 | ESSA TS, HANMER TS | X504E.ESXHA, 18-X504E, 33-X504E | 1-00234064 Rev. #7 | 5 Hour(s) | FS FN P502X CLAN | 990 900 250 0
2024-10-01 07:00 | 2024-10-27 17:00 | ESSA TS, HANMER TS | X503E.ESXHA, 18-X503E, 33-X503E | 1-00234063 Rev. #1 | 5 Hour(s) | FS FN P502X CLAN | 990 900 250 0
2024-10-28 07:00 | 2024-11-03 17:00 | CLAIREVILLE TS, ESSA TS | E511V.CLXES, 18-E511V, 51-E511V, DL511, W2L511 | 1-00241567 Rev. #1,1-00238538 Rev. #1 | 4 Hour(s),48 Hour(s) | FS FN P502X CLAN | 0 0 0 700
2024-11-03 17:00 | 2024-11-29 17:00 | CLAIREVILLE TS, ESSA TS | E511V.CLXES, DL511, W2L511, 18-E511V, 51-E511V | 1-00238538 Rev. #1 | 48 Hour(s) | FS FN P502X CLAN | 0 0 0 700
2024-11-30 07:00 | 2024-12-19 17:00 | DES JOACHIMS TS, OTTO HOLDEN TS | D5H.DEXHO, 5-D5H, 6-D5H | 1-00240190 Rev. #2 | 5 Hour(s) | FS FN P502X CLAN | 25 0 25 0
2024-11-30 07:00 | 2024-12-19 17:00 | DES JOACHIMS TS, OTTO HOLDEN TS | D5H.DEXHO, 5-D5H, 6-D5H | 1-00240190 Rev. #2 | 5 Hour(s) | FS FN P502X CLAN | 25 0 25 0
Back to main menu

## Table C4
``
Table C4: Niagara Zone
Planned Start | Planned End | Station | Equipment Name | Outage ID | Max Recall | Major Transmission Interface Impacted | Reduction in Limit
2024-03-04 08:00 | 2024-03-14 07:15 | CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,MIDDLEPORT TS,BECK 2 TS, MID RIVER JCT NIAGARA | C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1,BP76.PAXBE, K2L76, L35L76, R76, TL35-BO1 | 1-00213473 Rev. #37,1-00220299 Rev. #39,1-00181622 Rev. #28 | Non-recallable,Non-recallable,Non-recallable | NY-W-IMP NY-W-EXP NY-S-EXP NY-S-IMP | 600 500 450 550
2024-03-17 07:00 | 2024-03-24 16:00 | DETWEILER TS, STRATFORD JCT, SEAFORTH TS, STRATFORD TS,CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,MIDDLEPORT TS,BECK 2 TS, MID RIVER JCT NIAGARA,BRANTFORD TS, NEWPORT JCT, MIDDLEPORT TS | B22D.STXDE, B22D.STXST, 26-B22D, 68T1-B22D, 61B22D-26,C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1,BP76.PAXBE, K2L76, L35L76, R76, TL35-BO1,M32W.NEXBR, M32W.NEXMI, YZ, 25-M32W, 44M32W-19, T4-M32W | 1-00237157 Rev. #9,1-00213473 Rev. #37,1-00220299 Rev. #39,1-00181622 Rev. #28,1-00238922 Rev. #11 | 4 Hour(s),Non-recallable,Non-recallable,Non-recallable,6 Hour(s) | NY-W-IMP NY-W-EXP NY-S-EXP NY-S-IMP | 600 500 450 550
2024-03-25 07:00 | 2024-03-31 11:00 | CLAIREVILLE TS, ESSA TS,BRANTFORD TS, NEWPORT JCT, MIDDLEPORT TS,BECK 2 TS, MID RIVER JCT NIAGARA,MIDDLEPORT TS,CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,DETWEILER TS, STRATFORD JCT, SEAFORTH TS, STRATFORD TS | E510V.CLXES, AL510, W3L510, 18-E510V, 51-E510V,M32W.NEXBR, M32W.NEXMI, YZ, 25-M32W, 44M32W-19, T4-M32W,BP76.PAXBE, K2L76, L35L76, R76, TL35-BO1,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1,C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,B22D.STXDE, B22D.STXST, 26-B22D, 68T1-B22D, 61B22D-26,AL510 | 1-00238540 Rev. #3,1-00238922 Rev. #11,1-00181622 Rev. #28,1-00220299 Rev. #39,1-00213473 Rev. #37,1-00235682 Rev. #6,1-00237157 Rev. #9,1-00238545 Rev. #4 | 48 Hour(s),6 Hour(s),Non-recallable,Non-recallable,Non-recallable,14 Day(s),4 Hour(s),5 Day(s) | NY-W-IMP NY-W-EXP NY-S-EXP NY-S-IMP | 600 500 450 550
2024-04-05 17:00 | 2024-04-12 16:00 | BRUCE A TS, BRUCE JCT, MILTON SS, WILLOW CREEK JCT,BRANTFORD TS, NEWPORT JCT, MIDDLEPORT TS,BECK 2 TS, MID RIVER JCT NIAGARA,MIDDLEPORT TS,CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,CLAIREVILLE TS, ESSA TS,DETWEILER TS, STRATFORD JCT, SEAFORTH TS, STRATFORD TS,LONGWOOD TS | B502M.BAXBJ, B502M.BJXMI, B502M.BJXWJ, 21-B502M, 40-B502M,M32W.NEXBR, M32W.NEXMI, YZ, 25-M32W, 44M32W-19, T4-M32W,BP76.PAXBE, K2L76, L35L76, R76, TL35-BO1,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1,C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,E510V.CLXES, AL510, W3L510, 18-E510V, 51-E510V,B22D.STXDE, B22D.STXST, 26-B22D, 68T1-B22D, 61B22D-26,R5N, T5L45, SS5, T5, R5, T5-H, T5-LT5,25-Q23BM, L23HT6, D2L23, Q23BM-TEMP1 | 1-00239284 Rev. #3,1-00238922 Rev. #11,1-00181622 Rev. #28,1-00220299 Rev. #39,1-00213473 Rev. #37,1-00235682 Rev. #6,1-00237157 Rev. #9,1-00239308 Rev. #10,1-00235814 Rev. #13,1-00246468 Rev. #2 | 8 Hour(s),6 Hour(s),Non-recallable,Non-recallable,Non-recallable,14 Day(s),4 Hour(s),5 Day(s),4 Hour(s),6 Hour(s) | NY-W-IMP NY-W-EXP NY-S-EXP NY-S-IMP | 600 500 450 550
2024-04-14 16:00 | 2024-04-19 16:00 | CLAIREVILLE TS, ESSA TS,KENT TS, CHATHAM SS, GSPC JCT,DETWEILER TS, STRATFORD JCT, SEAFORTH TS, STRATFORD TS,CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,MIDDLEPORT TS,BECK 2 TS, MID RIVER JCT NIAGARA,BRUCE A TS, BRUCE JCT, MILTON SS, WILLOW CREEK JCT,LONGWOOD TS | E510V.CLXES, AL510, W3L510, 18-E510V, 51-E510V,T1B, T1Y, T4Z, 5-L28C, 86-L28C, T1, T4, T1-L28C, T4L28C, 312L28C-MSO2,B22D.STXDE, B22D.STXST, 26-B22D, 68T1-B22D, 61B22D-26,C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1,BP76.PAXBE, K2L76, L35L76, R76, TL35-BO1,25-Q23BM, L23HT6, D2L23, Q23BM-TEMP1,D1D2, D1L29, D1L27, L33L40, SC22D1, SC22SC, 25-M33W, D1_BUS, SC22, SS2-D, D1L34, D1L33,B502M.BAXBJ, B502M.BJXMI, B502M.BJXWJ, 21-B502M, 40-B502M,R5N, T5L45, SS5, T5, R5, T5-H, T5-LT5 | 1-00235682 Rev. #6,1-00238919 Rev. #6,1-00237157 Rev. #9,1-00213473 Rev. #37,1-00220299 Rev. #39,1-00181622 Rev. #28,1-00246468 Rev. #2,1-00238390 Rev. #3,1-00235814 Rev. #13,1-00239308 Rev. #10 | 14 Day(s),12 Hour(s),4 Hour(s),Non-recallable,Non-recallable,Non-recallable,6 Hour(s),2 Hour(s),4 Hour(s),5 Day(s) | NY-W-IMP NY-W-EXP NY-S-EXP NY-S-IMP | 600 500 450 550
2024-05-26 07:00 | 2024-05-31 08:00 | ALLANBURG TS, BECK 2 TS, MID RIVER JCT NIAGARA, CROSSLINE JCT, MIDDLEPORT TS, CALEDONIA Q35M JCT,CLAIREVILLE TS,BRUCE B SS, BRUCE JCT, WILLOW CREEK JCT, MILTON SS,LONGWOOD DESN, LAMBTON TS 2, LONGWOOD JCT, LONGWOOD TS,CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,MIDDLEPORT TS,DETWEILER TS, STRATFORD TS, ZURICH JCT | BP76.PAXBE, Q35M.MIXCA, Q35M.QUXAL, D2HT4, H2HT4, K2L76, L26L35, L30TL35, L34L35, L35L76, T4, R76,W3L570, W3L510, T15, T15-HT15, T15-W3, T15-SS2,B501M.BBXBJ, B501M.BJXWJ, B501M.WJXMI, 40-B501M, 29-B501M,L24L.LOXLA, L24L.LOXLD, L24L.LOXLO, AL24, T14Q, T3L24, 27-L24L, T14, T14-L24L, W52-L24L,C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1, 51-C550VP, 52-C550VP, 81-C550VP,26-B23D, 68T2-B23D, 364B23D-MSO1 | 1-00181648 Rev. #9,1-00238525 Rev. #10,1-00237165 Rev. #9,1-00236074 Rev. #16,1-00213473 Rev. #37,1-00220299 Rev. #39,1-00236150 Rev. #5,1-00238602 Rev. #4 | 4 Hour(s),4 Hour(s),4 Hour(s),8 Day(s),Non-recallable,Non-recallable,4 Hour(s),4 Hour(s) | NY-W-IMP NY-W-EXP NY-S-EXP NY-S-IMP | 600 500 450 550
2024-07-08 07:00 | 2024-07-16 12:00 | MIDDLEPORT TS,MILTON SS, TRAFALGAR TS,BRUCE A TS, UNDERWOOD JCT, HANOVER TS, UNDERWOOD WGS,BURLINGTON TS, BURLINGTON JCT, MIDDLEPORT TS, CARLUKE JCT, NEALE JCT, BURLINGTON DESN TS, BECK 2 TS, NIAGARA WEST JCT,GRAND JCT, NANTICOKE TS, HORNING JCT, HORNING TS,LAMBTON TS 2 | T6, T6-LT6, T6-TL581, LT6BUS-TEMP1,M573T.MIXTR, HL573, L502L573, 40-M573T, T15-M573T,B4V.BRXUN, B4V.UNXUN, T4A, 21-B4V, 36B4V-22, 7014B5V-MSO2, 36T4-B4V,Q25BM.BEXNI, Q25BM.BUXBD, Q25BM.BUXBU, Q25BM.MIXCA, Q25BM.NEXBU, 25-Q25BM, 28-Q25BM, 39-Q25BM, T15-Q25BM,59-N5M, 310N5M-LC1,M27B.HOXBU, M27B.HOXHO, M27B.HOXMI, 25-M27B, 39-M27B, 4T4-M27B,K2L28, L27L28, P2L27, 27-L28C, 27-L27V | 1-00220299 Rev. #39,1-00208773 Rev. #10,1-00241125 Rev. #2,1-00238418 Rev. #3,1-00238444 Rev. #7,1-00238499 Rev. #3,1-00216465 Rev. #12 | Non-recallable,14 Day(s),10 Hour(s),6 Hour(s),10 Hour(s),6 Hour(s),4 Hour(s)
2024-07-26 17:00 | 2024-08-01 17:00 | BURLINGTON TS, BURLINGTON JCT, MIDDLEPORT TS, CARLUKE JCT, NEALE JCT, BURLINGTON DESN TS, BECK 2 TS, NIAGARA WEST JCT,LAMBTON TS 2,EAST LAKE ST. CLAIR WF JCT, LAMBTON TS 2,MILTON SS, TRAFALGAR TS,CALEDONIA TS, GRAND JCT, HORNING JCT, HORNING TS,MIDDLEPORT TS | Q25BM.BEXNI, Q25BM.BUXBD, Q25BM.BUXBU, Q25BM.MIXCA, Q25BM.NEXBU, 25-Q25BM, 28-Q25BM, 39-Q25BM, T15-Q25BM,KL25, L25L29, PL29, 27-L25V, 27-L29C, L25V-TEMP1,27-L29C, NA300L29C-2,M573T.MIXTR, HL573, L502L573, 40-M573T, T15-M573T,T2Y, 25-N5M, T2, N27T2-N5M, 310N5M-LC2,M28B.HOXBU, M28B.HOXHO, M28B.HOXMI, 25-M28B, 39-M28B, 4T3-M28B,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1 | 1-00238418 Rev. #3,1-00239852 Rev. #2,1-00239849 Rev. #5,1-00208773 Rev. #10,1-00238512 Rev. #2,1-00238498 Rev. #3,1-00220299 Rev. #39 | 6 Hour(s),4 Hour(s),12 Hour(s),14 Day(s),10 Hour(s),6 Hour(s),Non-recallable
2024-09-16 08:00 | 2024-09-27 15:00 | MIDDLEPORT TS, NANTICOKE TS,ESSA TS, MILTON SS,BEACH TS, HANNON JCT, DOFASCO KENILWORTH CTS, BECK 2 TS, MIDDLEPORT TS, NEBO JCT, HAMILTON NEBO TS,BRUCE A TS, BRUCE JCT, WILLOW CREEK JCT, CLAIREVILLE TS | N581M.MDXNA, AL581, T7L581, T7T12, 25-N581M, 59-N581M, HT7_BUS,HT4, R4N, HT4L29, HT4_BUS, T4, R4, T4-D, T4-HT4, TSS4,M585M.MIXMD, 25-M585M, 40-M585M,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1, N581M.MDXNA, L81L85, T6L31, L581_BUS, T6, L23HT6,Q24HM.HAXBE, Q24HM.HAXHA, Q24HM.HAXKE, Q24HM.HNXHA, Q24HM.HNXHN, Q24HM.HNXMI, 157T1-Q24HM, 17-Q24HM, 17-Q29HM, 25-Q24HM, 28-Q24HM, T3-Q24HM, 61Q29HM-LC,B560V.BRXBR, B560V.BRXMI, B560V.BRXWI, B560V.MIXCL, 21-B560V, 51-B560V, DL560, L553L560 | 1-00238433 Rev. #2,1-00246166 Rev. #1,1-00238434 Rev. #2,1-00238492 Rev. #2,1-00220299 Rev. #39,1-00238464 Rev. #2,1-00238421 Rev. #2,1-00238566 Rev. #2,1-00195970 Rev. #14 | Non-recallable,4 Hour(s),Non-recallable,Non-recallable,Non-recallable,Non-recallable,10 Hour(s),4 Hour(s),4 Day(s)
2024-11-04 08:00 | 2024-11-15 17:00 | MIDDLEPORT TS, MILTON SS, NANTICOKE TS,BECK 2 TS,CLAIREVILLE TS, ESSA TS,KENT TS, CHATHAM SS, GSPC JCT,BRUCE A TS, UNDERWOOD JCT, HANOVER TS, UNDERWOOD WGS | M585M.MIXMD, N581M.MDXNA, L81L85, T6L31, 25-M585M, 25-N581M, 40-M585M, 59-N581M, L581_BUS, T6, T6-LT6, T6-TL581, L23HT6,28-PA302, T302, T302-1,N581M.MDXNA, AL581, T7L581, T7T12, HT7_BUS,E511V.CLXES, DL511, W2L511, 18-E511V, 51-E511V,T1B, T1Y, T4Z, 5-L28C, 86-L28C, T1, T4, T1-L28C, T4L28C, 312L28C-MSO2,B4V.BRXUN, B4V.UNXUN, T4A, 21-B4V, 36B4V-22, 36T4-B4V, 161B5V-MSO1, 21-B5V | 1-00238465 Rev. #1,1-00238560 Rev. #1,1-00238433 Rev. #2,1-00238434 Rev. #2,1-00238492 Rev. #2,1-00238538 Rev. #1,1-00240028 Rev. #2,1-00241127 Rev. #1 | 4 Hour(s),8 Hour(s),Non-recallable,Non-recallable,Non-recallable,48 Hour(s),12 Hour(s),10 Hour(s) | NY-W-IMP NY-W-EXP NY-S-EXP NY-S-IMP | 1100 1050 1050 900
2024-11-17 07:15 | 2024-11-28 17:00 | BRUCE A TS, MAJESTIC JCT, MAJESTIC CTS, WINGHAM JCT, SEAFORTH TS, WINGHAM TS,MIDDLEPORT TS, MILTON SS, NANTICOKE TS,BECK 2 TS,CLAIREVILLE TS, ESSA TS,KENT TS, CHATHAM SS, GSPC JCT | B23D.MJXBR, B23D.MJXMJ, B23D.MJXWI, B23D.WIXSE, B23D.WIXWI, T2-B23D, 21-B23D, 61B23D-21,M585M.MIXMD, N581M.MDXNA, L81L85, T6L31, 25-M585M, 25-N581M, 40-M585M, 59-N581M, L581_BUS, T6, T6-LT6, T6-TL581, L23HT6,N581M.MDXNA, AL581, T7L581, T7T12, HT7_BUS,28-PA302, T302, T302-1,E511V.CLXES, DL511, W2L511, 18-E511V, 51-E511V,T1B, T1Y, T4Z, 5-L28C, 86-L28C, T1, T4, T1-L28C, T4L28C, 312L28C-MSO2 | 1-00241121 Rev. #1,1-00238465 Rev. #1,1-00238433 Rev. #2,1-00238560 Rev. #1,1-00238434 Rev. #2,1-00238492 Rev. #2,1-00238538 Rev. #1,1-00240028 Rev. #2 | 4 Hour(s),4 Hour(s),Non-recallable,8 Hour(s),Non-recallable,Non-recallable,48 Hour(s),12 Hour(s) | NY-W-IMP NY-W-EXP NY-S-EXP NY-S-IMP | 1100 1050 1050 900
2025-09-29 05:00 | 2025-11-26 19:00 | BECK 2 TS, NY NIAGARA 345 KV | PA27.NIXBE, 28R27-PA27, R27-S | 1-00244042 Rev. #3 | Non-recallable | NY-W-IMP NY-W-EXP NY-S-EXP NY-S-IMP | 0 0 50 0
2024-03-04 08:00 | 2024-03-31 18:00 | BECK 2 TS, MID RIVER JCT NIAGARA | BP76.PAXBE, K2L76, L35L76, R76, TL35-BO1 | 1-00181622 Rev. #28 | Non-recallable | NY-W-IMP NY-W-EXP NY-S-EXP NY-S-IMP | 600 500 450 550
2024-03-31 18:00 | 2024-04-21 07:00 | BECK 2 TS, MID RIVER JCT NIAGARA,MIDDLEPORT TS | BP76.PAXBE, K2L76, L35L76, R76, TL35-BO1,25-Q23BM, L23HT6, D2L23, Q23BM-TEMP1 | 1-00181622 Rev. #28,1-00246468 Rev. #2 | Non-recallable,6 Hour(s) | NY-W-IMP NY-W-EXP NY-S-EXP NY-S-IMP | 600 500 450 550
2024-04-28 07:00 | 2024-05-03 17:00 | MIDDLEPORT TS,BECK 2 TS, MID RIVER JCT NIAGARA | D1D2, D1L29, D1L27, L34L35, SC22D1, SC22SC, 25-M34H, D1_BUS, SC22, SS2-D, D1L34, D1L33,BP76.PAXBE, K2L76, L35L76, R76, TL35-BO1 | 1-00238393 Rev. #3,1-00181622 Rev. #28 | 2 Hour(s),Non-recallable | NY-W-IMP NY-W-EXP NY-S-EXP NY-S-IMP | 600 500 450 550
2024-05-05 13:00 | 2024-05-20 08:00 | BECK 2 TS, MID RIVER JCT NIAGARA,CALEDONIA TS, GRAND JCT, MIDDLEPORT TS | BP76.PAXBE, K2L76, L35L76, R76, TL35-BO1,L5L25, L5L32, T2Y, 25-N5M, T2, N27T2-N5M, 310N5M-LC2 | 1-00181622 Rev. #28,1-00246626 Rev. #1 | Non-recallable,4 Hour(s) | NY-W-IMP NY-W-EXP NY-S-EXP NY-S-IMP | 600 500 450 550
2024-05-26 07:00 | 2024-05-31 08:00 | ALLANBURG TS, BECK 2 TS, MID RIVER JCT NIAGARA, CROSSLINE JCT, MIDDLEPORT TS, CALEDONIA Q35M JCT | BP76.PAXBE, Q35M.MIXCA, Q35M.QUXAL, D2HT4, H2HT4, K2L76, L26L35, L30TL35, L34L35, L35L76, T4, R76 | 1-00181648 Rev. #9 | 4 Hour(s) | NY-W-IMP NY-W-EXP NY-S-EXP NY-S-IMP | 600 500 450 550
2024-07-07 07:00 | 2024-07-19 17:00 | BURLINGTON TS, HORNING JCT, HORNING TS, MIDDLEPORT TS, BURLINGTON JCT, CARLUKE JCT, NEALE JCT, BURLINGTON DESN TS, BECK 2 TS, NIAGARA WEST JCT,GRAND JCT, NANTICOKE TS | M27B.HOXBU, M27B.HOXHO, M27B.HOXMI, 25-M27B, 39-M27B, 4T4-M27B,Q25BM.BEXNI, Q25BM.BUXBD, Q25BM.BUXBU, Q25BM.MIXCA, Q25BM.NEXBU, 25-Q25BM, 28-Q25BM, 39-Q25BM, T15-Q25BM,59-N5M, 310N5M-LC1 | 1-00238499 Rev. #3,1-00238418 Rev. #3,1-00238444 Rev. #7 | 6 Hour(s),6 Hour(s),10 Hour(s)
2024-07-21 07:00 | 2024-07-26 07:00 | BURLINGTON TS, BURLINGTON JCT, MIDDLEPORT TS, CARLUKE JCT, NEALE JCT, BURLINGTON DESN TS, BECK 2 TS, NIAGARA WEST JCT, HORNING JCT, HORNING TS,GRAND JCT, NANTICOKE TS | Q25BM.BEXNI, Q25BM.BUXBD, Q25BM.BUXBU, Q25BM.MIXCA, Q25BM.NEXBU, 25-Q25BM, 28-Q25BM, 39-Q25BM, T15-Q25BM,M28B.HOXBU, M28B.HOXHO, M28B.HOXMI, 25-M28B, 39-M28B, 4T3-M28B,59-N5M, 310N5M-LC1 | 1-00238418 Rev. #3,1-00238498 Rev. #3,1-00238444 Rev. #7 | 6 Hour(s),6 Hour(s),10 Hour(s)
2024-07-26 17:00 | 2024-08-01 17:00 | BURLINGTON TS, BURLINGTON JCT, MIDDLEPORT TS, CARLUKE JCT, NEALE JCT, BURLINGTON DESN TS, BECK 2 TS, NIAGARA WEST JCT,CALEDONIA TS, GRAND JCT, HORNING JCT, HORNING TS | Q25BM.BEXNI, Q25BM.BUXBD, Q25BM.BUXBU, Q25BM.MIXCA, Q25BM.NEXBU, 25-Q25BM, 28-Q25BM, 39-Q25BM, T15-Q25BM,T2Y, 25-N5M, T2, N27T2-N5M, 310N5M-LC2,M28B.HOXBU, M28B.HOXHO, M28B.HOXMI, 25-M28B, 39-M28B, 4T3-M28B | 1-00238418 Rev. #3,1-00238512 Rev. #2,1-00238498 Rev. #3 | 6 Hour(s),10 Hour(s),6 Hour(s)
2024-09-08 07:00 | 2024-10-11 17:00 | BEACH TS, HANNON JCT, DOFASCO KENILWORTH CTS, BECK 2 TS, MIDDLEPORT TS, NEBO JCT, HAMILTON NEBO TS | Q24HM.HAXBE, Q24HM.HAXHA, Q24HM.HAXKE, Q24HM.HNXHA, Q24HM.HNXHN, Q24HM.HNXMI, 157T1-Q24HM, 17-Q24HM, 17-Q29HM, 25-Q24HM, 28-Q24HM, T3-Q24HM, 61Q29HM-LC | 1-00238421 Rev. #2 | 10 Hour(s)
2024-11-04 08:00 | 2024-12-06 16:00 | BECK 2 TS | 28-PA302, T302, T302-1 | 1-00238560 Rev. #1 | 8 Hour(s) | NY-W-IMP NY-W-EXP NY-S-EXP NY-S-IMP | 1100 1050 1050 900
2025-09-29 05:00 | 2025-11-26 19:00 | BECK 2 TS, NY NIAGARA 345 KV | PA27.NIXBE, 28R27-PA27, R27-S | 1-00244042 Rev. #3 | Non-recallable | NY-W-IMP NY-W-EXP NY-S-EXP NY-S-IMP | 0 0 50 0
2024-04-19 18:00 | 2024-05-20 08:00 | BECK 2 TS, MID RIVER JCT NIAGARA | BP76.PAXBE, K2L76, L35L76, R76, TL35-BO1 | 1-00181622 Rev. #28 | Non-recallable | NY-W-IMP NY-W-EXP NY-S-EXP NY-S-IMP | 600 500 450 550
2024-05-20 08:00 | 2024-05-31 08:00 | ALLANBURG TS, BECK 2 TS, MID RIVER JCT NIAGARA, CROSSLINE JCT, MIDDLEPORT TS, CALEDONIA Q35M JCT | BP76.PAXBE, Q35M.MIXCA, Q35M.QUXAL, D2HT4, H2HT4, K2L76, L26L35, L30TL35, L34L35, L35L76, T4, R76 | 1-00181648 Rev. #9 | 4 Hour(s) | NY-W-IMP NY-W-EXP NY-S-EXP NY-S-IMP | 600 500 450 550
2024-11-04 08:00 | 2024-12-06 16:00 | BECK 2 TS | 28-PA302, T302, T302-1 | 1-00238560 Rev. #1 | 8 Hour(s) | NY-W-IMP NY-W-EXP NY-S-EXP NY-S-IMP | 1100 1050 1050 900
2025-09-29 05:00 | 2025-11-26 19:00 | BECK 2 TS, NY NIAGARA 345 KV,NYISO CC, NY NIAGARA 230 KV | PA27.NIXBE, 28R27-PA27, R27-S,Misc 1, 2114, 2122 | 1-00244042 Rev. #3,1-00243828 Rev. #1 | Non-recallable,Non-recallable | NY-W-IMP NY-W-EXP NY-S-EXP NY-S-IMP | 0 0 50 0
Back to main menu

## Table C5
Back to main menu
Table C5: Northeast Zone
Planned Start | Planned End | Station | Equipment Name | Outage ID | Max Recall | Major Transmission Interface Impacted | Reduction in Limit
2024-09-10 07:00 | 2024-09-27 17:00 | ANSONVILLE TS, KIDD CREEK MINE JCT, ERG RESOURCES JCT, FALCONBRIDGE KIDD METSITE CTS, PORCUPINE TS | P91G.KIXAN, P91G.KIXKI, P91G.REXKI, P91G.REXPO, H1L91, 30-P91G, H1L91-S | 1-00242378 Rev. #2 | 5 Hour(s)
2024-03-30 04:30 | 2024-04-05 16:00 | CLAIREVILLE TS,CHURCHILL MEADOWS TS, CHURCHILL MEADOWS JCT, TRAFALGAR TS, ERINDALE JCT, HANLAN JCT, ERINDALE TS, HURONTARIO SS, RICHVIEW TS, TOMKEN JCT, TOMKEN TS, ESSA TS,CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,PALERMO TS, BURLINGTON TS, GLENORCHY JCT, LANTZ JCT, PALERMO TXB JCT, GLENORCHY MTS1 | AL510, W3L510, 51-E510V,R19TH.CHXTR, R19TH.ERXCH, R19TH.ERXER, R19TH.ERXHA, R19TH.HAXHU, R19TH.TOXRI, R19TH.TOXTO, L19L29, 240T2-R19TH, 31-R19TH, 5T6-R19TH, 88-R19TH, L19L29-L19, T3-R19TH,E510V.CLXES, AL510, 18-E510V,C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,T37B.GJXGL, T37B.GJXLA, T37B.PAXBU, T37B.PAXTR, T37B.PJXGJ, T4Y, 31-T37B, 31SC21L-T36B, 31SC21L-T37B, 39-T37B, T4, T4-T37B | 1-00238545 Rev. #4,1-00238480 Rev. #8,1-00235682 Rev. #6,1-00213473 Rev. #37,1-00226775 Rev. #13,1-00238540 Rev. #3 | 5 Day(s),36 Hour(s),14 Day(s),Non-recallable,6 Hour(s),48 Hour(s) | FS FN P502X CLAN | 0 0 0 700
2024-05-21 08:00 | 2024-06-07 16:00 | ESSA TS, HANMER TS | X504E.ESXHA, 18-X504E, 33-X504E | 1-00234064 Rev. #7 | 5 Hour(s) | FS FN P502X CLAN | 990 900 250 0
2024-09-10 07:00 | 2024-09-27 17:00 | PORCUPINE TS, ANSONVILLE TS | H1L91, HT7D1, HT8D2, HT7D2, HT8D1, SC21D1, SC22HT8, D2_BUS, HT7_BUS, HT8_BUS, SC21, SC22, SVC1, T7-HT7, T8-HT8 | 1-00234066 Rev. #3 | 12 Hour(s)
2024-10-01 07:00 | 2024-10-27 17:00 | ESSA TS, HANMER TS | X503E.ESXHA, 18-X503E, 33-X503E | 1-00234063 Rev. #1 | 5 Hour(s) | FS FN P502X CLAN | 990 900 250 0
2024-11-30 07:00 | 2024-12-19 17:00 | DES JOACHIMS TS, OTTO HOLDEN TS | D5H.DEXHO, 5-D5H, 6-D5H | 1-00240190 Rev. #2 | 5 Hour(s) | FS FN P502X CLAN | 25 0 25 0
2024-05-21 08:00 | 2024-06-07 16:00 | ESSA TS, HANMER TS | X504E.ESXHA, 18-X504E, 33-X504E | 1-00234064 Rev. #7 | 5 Hour(s) | FS FN P502X CLAN | 990 900 250 0
2024-09-10 07:00 | 2024-09-27 17:00 | PORCUPINE TS, ANSONVILLE TS | H1L91, HT7D1, HT8D2, HT7D2, HT8D1, SC21D1, SC22HT8, D2_BUS, HT7_BUS, HT8_BUS, SC21, SC22, SVC1, T7-HT7, T8-HT8 | 1-00234066 Rev. #3 | 12 Hour(s)
2024-10-01 07:00 | 2024-10-27 17:00 | ESSA TS, HANMER TS | X503E.ESXHA, 18-X503E, 33-X503E | 1-00234063 Rev. #1 | 5 Hour(s) | FS FN P502X CLAN | 990 900 250 0
2024-11-30 07:00 | 2024-12-19 17:00 | DES JOACHIMS TS, OTTO HOLDEN TS | D5H.DEXHO, 5-D5H, 6-D5H | 1-00240190 Rev. #2 | 5 Hour(s) | FS FN P502X CLAN | 25 0 25 0
2024-09-02 07:00 | 2024-09-27 08:00 | HANMER TS, MARTINDALE TS, VALE FROOD STOBIE 2 JCT, VALE COPPER 4 CTS | S21N.FRXIN, S21N.FRXMA, X25S.MAXHA, KL26, KT22, L22L25, 33-X25S, 9-S21N, 9-X25S, K_BUS, T25-K, KL25 | 1-00241700 Rev. #6 | 24 Hour(s)
2024-04-30 18:00 | 2024-05-10 17:00 | HANMER TS, MARTINDALE TS | X25S.MAXHA, 33-X25S, 9-X25S, HL29, 33-X29S | 1-00234077 Rev. #8 | 8 Hour(s)
2024-09-02 07:00 | 2024-09-27 08:00 | HANMER TS, MARTINDALE TS, VALE FROOD STOBIE 2 JCT, VALE COPPER 4 CTS | S21N.FRXIN, S21N.FRXMA, X25S.MAXHA, KL26, KT22, L22L25, 33-X25S, 9-S21N, 9-X25S, K_BUS, T25-K, KL25 | 1-00241700 Rev. #6 | 24 Hour(s)
2024-05-10 07:00 | 2024-05-21 17:00 | WARREN DS, VERNER JCT | 79L1S-39, 939L1S-79 | 1-00244186 Rev. #1 | 5 Hour(s)
2024-07-16 07:00 | 2024-08-09 17:00 | CRYSTAL FALLS TS, PEDLEY JCT, MARTINDALE TS, OTTO HOLDEN TS, WIDDIFIELD TS | H23S.PEXCR, H23S.PEXMA, H23S.PEXWI, H23S.WIXHO, L71L23, 6-H23S, 7T5-H23S, 9-H23S, H23S-9 | 1-00236084 Rev. #2 | 5 Hour(s)
2024-11-16 07:00 | 2024-11-24 17:00 | CRYSTAL FALLS TS, GRANT JCT, A.P. NORTH BAY JCT, MARTINDALE TS, OTTO HOLDEN TS, TROUT LAKE TS, WIDDIFIELD TS | H24S.GRXCR, H24S.GRXMA, H24S.GRXTC, H24S.TCXWI, H24S.WIXHO, H24S.WIXTR, L71L24, 6-H24S, 7T6-H24S, 9-H24S, H24S-9, H24SMSO-9, H24S-6, T4-H24S | 1-00236085 Rev. #1 | 5 Hour(s)
2024-11-30 07:00 | 2024-12-19 17:00 | DES JOACHIMS TS, OTTO HOLDEN TS | D5H.DEXHO, 5-D5H, 6-D5H | 1-00240190 Rev. #2 | 5 Hour(s) | FS FN P502X CLAN | 25 0 25 0
2024-09-10 07:00 | 2024-09-27 17:00 | ANSONVILLE TS, KIDD CREEK MINE JCT, ERG RESOURCES JCT, FALCONBRIDGE KIDD METSITE CTS, PORCUPINE TS,PORCUPINE TS, ANSONVILLE TS | P91G.KIXAN, P91G.KIXKI, P91G.REXKI, P91G.REXPO, H1L91, 30-P91G, H1L91-S,H1L91, HT7D1, HT8D2, HT7D2, HT8D1, SC21D1, SC22HT8, D2_BUS, HT7_BUS, HT8_BUS, SC21, SC22, SVC1, T7-HT7, T8-HT8 | 1-00242378 Rev. #2,1-00234066 Rev. #3 | 5 Hour(s),12 Hour(s)
2024-07-16 07:00 | 2024-08-09 17:00 | CRYSTAL FALLS TS, PEDLEY JCT, MARTINDALE TS, OTTO HOLDEN TS, WIDDIFIELD TS | H23S.PEXCR, H23S.PEXMA, H23S.PEXWI, H23S.WIXHO, L71L23, 6-H23S, 7T5-H23S, 9-H23S, H23S-9 | 1-00236084 Rev. #2 | 5 Hour(s)
2024-11-16 07:00 | 2024-11-24 17:00 | CRYSTAL FALLS TS, GRANT JCT, A.P. NORTH BAY JCT, MARTINDALE TS, OTTO HOLDEN TS, TROUT LAKE TS, WIDDIFIELD TS | H24S.GRXCR, H24S.GRXMA, H24S.GRXTC, H24S.TCXWI, H24S.WIXHO, H24S.WIXTR, L71L24, 6-H24S, 7T6-H24S, 9-H24S, H24S-9, H24SMSO-9, H24S-6, T4-H24S | 1-00236085 Rev. #1 | 5 Hour(s)
2023-06-05 07:00 | 2023-07-04 06:00 | WAWA TS, MARATHON TS,MARATHON TS, WAWA TS | W21M.MAXWA, 14-W21M, 15-W21M | 1-00194140 Rev. #18,1-00191090 Rev. #24 | 500 Day(s),Non-recallable
2023-07-04 06:00 | 2023-11-14 08:30 | MARATHON TS, WAWA TS,WAWA TS, MARATHON TS,GREENWICH WF CGS JCT | W21M.MAXWA, 14-W21M, 15-W21M,15-M23L, 235M23L-MSO2 | 1-00191090 Rev. #24,1-00194140 Rev. #18,1-00229423 Rev. #20 | Non-recallable,500 Day(s),4 Hour(s)
2023-12-31 16:00 | 2024-02-23 12:00 | WAWA TS,MARATHON TS, WAWA TS, MARATHON TS,GREENWICH WF CGS JCT | L21L25, L23L25, NEW14-P25W,W21M.MAXWA, 14-W21M, 15-W21M,15-M23L, 235M23L-MSO2 | 1-00239753 Rev. #11,1-00191090 Rev. #24,1-00194140 Rev. #18,1-00239601 Rev. #13,1-00229423 Rev. #20 | Non-recallable,Non-recallable,500 Day(s),7 Hour(s),4 Hour(s)
2024-03-04 13:00 | 2024-04-05 17:00 | ALEXANDER SS, RESERVE JCT, BIRCH TS, LAKEHEAD TS, PINE PORTAGE SS,GREENWICH WF CGS JCT, MARATHON TS,WAWA TS,MARATHON TS, WAWA TS,RABBIT LAKE SS, VERMILION BAY JCT | A7L.M1XAS, A7L.M1XLA, R1LB.BIXLA, R1LB.LAXPI, 12-A7L, 12-R1LB, 17-R1LB, 26-R1LB, 4-A7L, 57M1-J7,15-M23L, 235M23L-MSO2,W21M.MAXWA, 14-W21M, 15-W21M,L21L25, L23L25, NEW14-P25W,K3D.RAXVE, HL3, L3L4, 15-K3D, L3_BUS, K3D-10 | 1-00239987 Rev. #10,1-00229423 Rev. #20,1-00239601 Rev. #13,1-00194140 Rev. #18,1-00191090 Rev. #24,1-00239753 Rev. #11,1-00201293 Rev. #65,1-00242375 Rev. #19 | 16 Hour(s),4 Hour(s),7 Hour(s),500 Day(s),Non-recallable,Non-recallable,5 Day(s),4 Hour(s)
2024-04-08 07:00 | 2024-04-19 07:00 | WAWA TS,MARATHON TS, WAWA TS, MARATHON TS,GREENWICH WF CGS JCT | L21L25, L23L25, NEW14-P25W,W21M.MAXWA, 14-W21M, 15-W21M,15-M23L, 235M23L-MSO2,HL21, 14-P26W, H_BUS, T2-H, AH | 1-00239753 Rev. #11,1-00191090 Rev. #24,1-00194140 Rev. #18,1-00239601 Rev. #13,1-00235150 Rev. #7,1-00229423 Rev. #20 | Non-recallable,Non-recallable,500 Day(s),7 Hour(s),Non-recallable,4 Hour(s)
2024-04-19 07:00 | 2024-04-28 17:00 | WAWA TS,AUBREY FALLS JCT, MISSISSAGI TS, WAWA TS,MARATHON TS, MARATHON TS,GREENWICH WF CGS JCT | L21L25, L23L25, NEW14-P25W,P26W.AUXMI, P26W.AUXWA, HL21, KL2, KL4, L23L26, L26L74, T2R2, T2SC2, H_BUS, K_BUS, T2, AH,W21M.MAXWA, 14-W21M, 15-W21M,15-M23L, 235M23L-MSO2,HL21, 14-P26W, T2-H | 1-00239753 Rev. #11,1-00182739 Rev. #29,1-00191090 Rev. #24,1-00194140 Rev. #18,1-00239601 Rev. #13,1-00235150 Rev. #7,1-00229423 Rev. #20 | Non-recallable,1 Day(s),Non-recallable,500 Day(s),7 Hour(s),Non-recallable,4 Hour(s)
2024-06-18 07:00 | 2024-06-23 07:00 | RABBIT LAKE SS,MARATHON TS, WAWA TS,WAWA TS, MARATHON TS,KENORA TS, RABBIT LAKE SS | HL7, L2L7, 15-K7K, HL7_BUS, L7_BUS,W21M.MAXWA, 14-W21M, 15-W21M,K7K.RAXKE, 34K7K-15 | 1-00234055 Rev. #8,1-00191090 Rev. #24,1-00194140 Rev. #18,1-00245843 Rev. #2 | 2 Day(s),Non-recallable,500 Day(s),5 Hour(s)
2024-06-23 07:00 | 2024-07-04 07:00 | RABBIT LAKE SS,MACKAY TS, MACKAY JCT, WAWA TS,MARATHON TS,WAWA TS, MARATHON TS,KENORA TS, RABBIT LAKE SS | HL7, L2L7, 15-K7K, HL7_BUS, L7_BUS,W23K.WAXMC, 690, 682, AL23, L23L25, 14-GL4, 14-W23K, L23_BUS, W23K.MKXMK,W21M.MAXWA, 14-W21M, 15-W21M,K7K.RAXKE, 34K7K-15 | 1-00234055 Rev. #8,1-00234129 Rev. #7,1-00191090 Rev. #24,1-00194140 Rev. #18,1-00245843 Rev. #2 | 2 Day(s),24 Hour(s),Non-recallable,500 Day(s),5 Hour(s)
2024-07-08 07:00 | 2024-07-15 07:00 | MACKAY TS, MACKAY JCT, WAWA TS,MARATHON TS,WAWA TS, MARATHON TS,FORT FRANCES TS, MACKENZIE TS | W23K.WAXMC, 690, 682, AL23, L23L25, 14-GL4, 14-W23K, L23_BUS, W23K.MKXMK,W21M.MAXWA, 14-W21M, 15-W21M,F25A.FOXMK, 20-F25A, 22-F25A | 1-00234129 Rev. #7,1-00191090 Rev. #24,1-00194140 Rev. #18,1-00239979 Rev. #2 | 24 Hour(s),Non-recallable,500 Day(s),6 Hour(s)
2024-07-15 07:00 | 2024-07-21 17:00 | MACKAY TS, MACKAY JCT, WAWA TS,ALEXANDER SS, RESERVE JCT, BIRCH TS, LAKEHEAD TS, PINE PORTAGE SS,MARATHON TS,WAWA TS, MARATHON TS,FORT FRANCES TS, MACKENZIE TS | W23K.WAXMC, 690, 682, AL23, L23L25, 14-GL4, 14-W23K, L23_BUS, W23K.MKXMK,A7L.M1XAS, A7L.M1XLA, R1LB.BIXLA, R1LB.LAXPI, 12-A7L, 12-R1LB, 17-R1LB, 26-R1LB, 4-A7L, 57M1-J7,W21M.MAXWA, 14-W21M, 15-W21M,F25A.FOXMK, 20-F25A, 22-F25A | 1-00234129 Rev. #7,1-00239989 Rev. #2,1-00191090 Rev. #24,1-00194140 Rev. #18,1-00239979 Rev. #2 | 24 Hour(s),10 Hour(s),Non-recallable,500 Day(s),6 Hour(s)
2024-07-21 17:00 | 2024-07-26 17:00 | WAWA TS, MARATHON TS,MARATHON TS, WAWA TS,MACKAY TS, MACKAY JCT,ALEXANDER SS, RESERVE JCT, BIRCH TS, LAKEHEAD TS, PINE PORTAGE SS | W21M.MAXWA, 14-W21M, 15-W21M,W23K.WAXMC, 690, 682, AL23, L23L25, 14-GL4, 14-W23K, L23_BUS, W23K.MKXMK,A7L.M1XAS, A7L.M1XLA, R1LB.BIXLA, R1LB.LAXPI, 12-A7L, 12-R1LB, 17-R1LB, 26-R1LB, 4-A7L, 57M1-J7 | 1-00194140 Rev. #18,1-00191090 Rev. #24,1-00234129 Rev. #7,1-00239989 Rev. #2 | 500 Day(s),Non-recallable,24 Hour(s),10 Hour(s)
2024-07-26 17:00 | 2024-07-31 17:00 | ALEXANDER SS, RESERVE JCT, BIRCH TS, LAKEHEAD TS, PINE PORTAGE SS,WAWA TS, MARATHON TS,MARATHON TS, WAWA TS | A7L.M1XAS, A7L.M1XLA, R1LB.BIXLA, R1LB.LAXPI, 12-A7L, 12-R1LB, 17-R1LB, 26-R1LB, 4-A7L, 57M1-J7,W21M.MAXWA, 14-W21M, 15-W21M | 1-00239989 Rev. #2,1-00194140 Rev. #18,1-00191090 Rev. #24 | 10 Hour(s),500 Day(s),Non-recallable
2024-07-31 17:00 | 2024-08-12 07:00 | WAWA TS, MARATHON TS,MARATHON TS, WAWA TS | W21M.MAXWA, 14-W21M, 15-W21M | 1-00194140 Rev. #18,1-00191090 Rev. #24 | 500 Day(s),Non-recallable
2024-08-12 08:00 | 2024-08-18 16:00 | MACKENZIE TS,MARATHON TS, WAWA TS,WAWA TS, MARATHON TS, MOOSE LAKE TS | PL25,W21M.MAXWA, 14-W21M, 15-W21M,A3M.MAXMO, PL22, PL25, T3R3, 20-A3M, 3-A3M, P_BUS, T3, R3, T3-P,T3R3 | 1-00201495 Rev. #21,1-00191090 Rev. #24,1-00194140 Rev. #18,1-00234060 Rev. #2,1-00234972 Rev. #2 | 8 Hour(s),Non-recallable,500 Day(s),24 Hour(s),24 Hour(s)
2024-08-18 17:00 | 2024-09-04 12:00 | MARATHON TS, WAWA TS,WAWA TS, MARATHON TS,MACKENZIE TS | W21M.MAXWA, 14-W21M, 15-W21M,T3R3, 20-A3M, T3, R3, T3-P | 1-00191090 Rev. #24,1-00194140 Rev. #18,1-00234972 Rev. #2 | Non-recallable,500 Day(s),24 Hour(s)
2024-09-23 16:00 | 2024-10-07 07:00 | WAWA TS, MARATHON TS,MARATHON TS, WAWA TS | W21M.MAXWA, 14-W21M, 15-W21M | 1-00194140 Rev. #18,1-00191090 Rev. #24 | 500 Day(s),Non-recallable
2024-10-07 07:00 | 2024-10-15 07:00 | MARATHON TS, WAWA TS,WAWA TS, MARATHON TS,MARGACH DS, MARGACH JCT, RABBIT LAKE SS | W21M.MAXWA, 14-W21M, 15-W21M,K6F.MAXRA, L1L6, HL6, 15-K6F, 24T2-L, HL6_BUS, K6FT1-T2 | 1-00191090 Rev. #24,1-00194140 Rev. #18,1-00242608 Rev. #1 | Non-recallable,500 Day(s),5 Day(s)
2024-10-15 07:00 | 2024-10-21 06:00 | MARGACH DS, MARGACH JCT, RABBIT LAKE SS,WAWA TS, MARATHON TS,ALGOMA TS,MARATHON TS, WAWA TS | K6F.MAXRA, L1L6, HL6, 15-K6F, 24T2-L, HL6_BUS, K6FT1-T2,W21M.MAXWA, 14-W21M, 15-W21M,26-S22A | 1-00242608 Rev. #1,1-00194140 Rev. #18,1-00236087 Rev. #1,1-00191090 Rev. #24 | 5 Day(s),500 Day(s),5 Hour(s),Non-recallable
2024-10-21 06:00 | 2024-10-31 17:00 | MARGACH DS, MARGACH JCT, RABBIT LAKE SS,ALGOMA TS,WAWA TS, MARATHON TS,MARATHON TS, WAWA TS | K6F.MAXRA, L1L6, HL6, 15-K6F, 24T2-L, HL6_BUS, K6FT1-T2,DL22, L22L23, 26-S22A,W21M.MAXWA, 14-W21M, 15-W21M,26-S22A | 1-00242608 Rev. #1,1-00234168 Rev. #1,1-00194140 Rev. #18,1-00236087 Rev. #1,1-00191090 Rev. #24 | 5 Day(s),12 Hour(s),500 Day(s),5 Hour(s),Non-recallable
2024-11-04 06:00 | 2024-11-10 16:00 | WAWA TS, MARATHON TS,ALGOMA TS, MISSISSAGI TS,MARATHON TS, WAWA TS | W21M.MAXWA, 14-W21M, 15-W21M,A23P.MIXAL, KL23, L22L23, 26-A23P, 34-A23P | 1-00194140 Rev. #18,1-00234172 Rev. #1,1-00191090 Rev. #24 | 500 Day(s),12 Hour(s),Non-recallable
2024-11-25 06:00 | 2024-12-06 17:00 | ALGOMA TS, MISSISSAGI TS,GREENWICH WF CGS JCT, GREENWICH LAKE WF CSS, MARATHON TS, LAKEHEAD TS | A24P.MIXAL, DL24, KL24, 26-A24P, 34-A24P,M24L.GJXGS, M24L.GJXMA, M24L.LAXGJ, 12-M24L, 15-M24L | 1-00234175 Rev. #1,1-00236088 Rev. #2 | 12 Hour(s),5 Hour(s)
2024-12-07 06:00 | 2024-12-19 17:00 | ALGOMA TS, HANMER TS,GREENWICH WF CGS JCT, GREENWICH LAKE WF CSS, MARATHON TS, LAKEHEAD TS | X27A.ALXHA, KL23, KL24, 26-X27A, 33-X27A, K_BUS, T8-K,M24L.GJXGS, M24L.GJXMA, M24L.LAXGJ, 12-M24L, 15-M24L | 1-00234062 Rev. #1,1-00236088 Rev. #2 | 12 Hour(s),5 Hour(s)
2024-10-15 07:00 | 2024-10-21 06:00 | ALGOMA TS | 26-S22A | 1-00236087 Rev. #1 | 5 Hour(s)
2024-10-21 06:00 | 2024-11-01 17:00 | ALGOMA TS | DL22, L22L23, 26-S22A,26-S22A | 1-00234168 Rev. #1,1-00236087 Rev. #1 | 12 Hour(s),5 Hour(s)
2024-11-04 06:00 | 2024-11-15 17:00 | ALGOMA TS, MISSISSAGI TS | A23P.MIXAL, KL23, L22L23, 26-A23P, 34-A23P | 1-00234172 Rev. #1 | 12 Hour(s)
2024-11-25 06:00 | 2024-12-06 17:00 | ALGOMA TS, MISSISSAGI TS | A24P.MIXAL, DL24, KL24, 26-A24P, 34-A24P | 1-00234175 Rev. #1 | 12 Hour(s)
2024-12-07 06:00 | 2024-12-19 17:00 | ALGOMA TS, HANMER TS | X27A.ALXHA, KL23, KL24, 26-X27A, 33-X27A, K_BUS, T8-K | 1-00234062 Rev. #1 | 12 Hour(s)
Back to main menu

## Table C6
Back to main menu
Table C6: Northwest Zone
Planned Start | Planned End | Station | Equipment Name | Outage ID | Max Recall | Major Transmission Interface Impacted | Reduction in Limit
2024-02-23 12:00 | 2024-04-07 16:00 | RABBIT LAKE SS, VERMILION BAY JCT | K3D.RAXVE, HL3, L3L4, 15-K3D, L3_BUS, K3D-10 | 1-00242375 Rev. #19,1-00201293 Rev. #65 | 4 Hour(s),5 Day(s)
2024-02-23 12:00 | 2024-04-07 16:00 | RABBIT LAKE SS, VERMILION BAY JCT | K3D.RAXVE, HL3, L3L4, 15-K3D, L3_BUS, K3D-10 | 1-00242375 Rev. #19,1-00201293 Rev. #65 | 4 Hour(s),5 Day(s)
2024-04-10 07:00 | 2024-04-26 17:00 | MINAKI DS, MINAKI JCT, RABBIT LAKE SS | K4W.MIXMI, K4W.RAXMI, L2L4, L3L4, 15-K4W, K4WT1-T2, T1-L | 1-00205586 Rev. #18 | 3 Day(s)
2024-06-09 08:00 | 2024-06-16 17:00 | K6F-10 SW JCT, SIOUX NARROWS DS, SIOUX NARROWS JCT | 27AL-X, 27K6F-172, K6F-10, T1 | 1-00234178 Rev. #6 | 4 Hour(s)
2024-06-18 07:00 | 2024-07-04 07:00 | KENORA TS, RABBIT LAKE SS,RABBIT LAKE SS | K7K.RAXKE, 15-K7K, 34K7K-15,HL7, L2L7, HL7_BUS, L7_BUS | 1-00245843 Rev. #2,1-00234055 Rev. #8 | 5 Hour(s),2 Day(s)
2024-10-07 07:00 | 2024-10-31 17:00 | MARGACH DS, MARGACH JCT, RABBIT LAKE SS | K6F.MAXRA, L1L6, HL6, 15-K6F, 24T2-L, HL6_BUS, K6FT1-T2 | 1-00242608 Rev. #1 | 5 Day(s)
2023-06-05 07:00 | 2023-07-04 06:00 | WAWA TS, MARATHON TS,MARATHON TS, WAWA TS | W21M.MAXWA, 14-W21M, 15-W21M | 1-00194140 Rev. #18,1-00191090 Rev. #24 | 500 Day(s),Non-recallable
2023-07-04 06:00 | 2023-11-14 08:30 | MARATHON TS, WAWA TS,WAWA TS, MARATHON TS,GREENWICH WF CGS JCT | W21M.MAXWA, 14-W21M, 15-W21M,15-M23L, 235M23L-MSO2 | 1-00191090 Rev. #24,1-00194140 Rev. #18,1-00229423 Rev. #20 | Non-recallable,500 Day(s),4 Hour(s)
2023-12-31 16:00 | 2024-02-23 12:00 | WAWA TS,MARATHON TS, WAWA TS, MARATHON TS,GREENWICH WF CGS JCT | L21L25, L23L25, NEW14-P25W,W21M.MAXWA, 14-W21M, 15-W21M,15-M23L, 235M23L-MSO2 | 1-00239753 Rev. #11,1-00191090 Rev. #24,1-00194140 Rev. #18,1-00239601 Rev. #13,1-00229423 Rev. #20 | Non-recallable,Non-recallable,500 Day(s),7 Hour(s),4 Hour(s)
2024-03-04 13:00 | 2024-04-05 17:00 | ALEXANDER SS, RESERVE JCT, BIRCH TS, LAKEHEAD TS, PINE PORTAGE SS,GREENWICH WF CGS JCT, MARATHON TS,WAWA TS,MARATHON TS, WAWA TS,RABBIT LAKE SS, VERMILION BAY JCT | A7L.M1XAS, A7L.M1XLA, R1LB.BIXLA, R1LB.LAXPI, 12-A7L, 12-R1LB, 17-R1LB, 26-R1LB, 4-A7L, 57M1-J7,15-M23L, 235M23L-MSO2,W21M.MAXWA, 14-W21M, 15-W21M,L21L25, L23L25, NEW14-P25W,K3D.RAXVE, HL3, L3L4, 15-K3D, L3_BUS, K3D-10 | 1-00239987 Rev. #10,1-00229423 Rev. #20,1-00239601 Rev. #13,1-00194140 Rev. #18,1-00191090 Rev. #24,1-00239753 Rev. #11,1-00201293 Rev. #65,1-00242375 Rev. #19 | 16 Hour(s),4 Hour(s),7 Hour(s),500 Day(s),Non-recallable,Non-recallable,5 Day(s),4 Hour(s)
2024-04-08 07:00 | 2024-04-19 07:00 | WAWA TS,MARATHON TS, WAWA TS, MARATHON TS,GREENWICH WF CGS JCT | L21L25, L23L25, NEW14-P25W,W21M.MAXWA, 14-W21M, 15-W21M,15-M23L, 235M23L-MSO2,HL21, 14-P26W, H_BUS, T2-H, AH | 1-00239753 Rev. #11,1-00191090 Rev. #24,1-00194140 Rev. #18,1-00239601 Rev. #13,1-00235150 Rev. #7,1-00229423 Rev. #20 | Non-recallable,Non-recallable,500 Day(s),7 Hour(s),Non-recallable,4 Hour(s) | EWTW EWTE | 50 30
2024-04-19 07:00 | 2024-04-28 17:00 | WAWA TS,AUBREY FALLS JCT, MISSISSAGI TS, WAWA TS,MARATHON TS, MARATHON TS,GREENWICH WF CGS JCT | L21L25, L23L25, NEW14-P25W,P26W.AUXMI, P26W.AUXWA, HL21, KL2, KL4, L23L26, L26L74, T2R2, T2SC2, H_BUS, K_BUS, T2, AH,W21M.MAXWA, 14-W21M, 15-W21M,15-M23L, 235M23L-MSO2,HL21, 14-P26W, T2-H | 1-00239753 Rev. #11,1-00182739 Rev. #29,1-00191090 Rev. #24,1-00194140 Rev. #18,1-00239601 Rev. #13,1-00235150 Rev. #7,1-00229423 Rev. #20 | Non-recallable,1 Day(s),Non-recallable,500 Day(s),7 Hour(s),Non-recallable,4 Hour(s) | EWTW EWTE | 50 30
2024-06-18 07:00 | 2024-06-23 07:00 | RABBIT LAKE SS,MARATHON TS, WAWA TS,WAWA TS, MARATHON TS,KENORA TS, RABBIT LAKE SS | HL7, L2L7, 15-K7K, HL7_BUS, L7_BUS,W21M.MAXWA, 14-W21M, 15-W21M,K7K.RAXKE, 34K7K-15 | 1-00234055 Rev. #8,1-00191090 Rev. #24,1-00194140 Rev. #18,1-00245843 Rev. #2 | 2 Day(s),Non-recallable,500 Day(s),5 Hour(s)
2024-06-23 07:00 | 2024-07-04 07:00 | RABBIT LAKE SS,MACKAY TS, MACKAY JCT, WAWA TS,MARATHON TS,WAWA TS, MARATHON TS,KENORA TS, RABBIT LAKE SS | HL7, L2L7, 15-K7K, HL7_BUS, L7_BUS,W23K.WAXMC, 690, 682, AL23, L23L25, 14-GL4, 14-W23K, L23_BUS, W23K.MKXMK,W21M.MAXWA, 14-W21M, 15-W21M,K7K.RAXKE, 34K7K-15 | 1-00234055 Rev. #8,1-00234129 Rev. #7,1-00191090 Rev. #24,1-00194140 Rev. #18,1-00245843 Rev. #2 | 2 Day(s),24 Hour(s),Non-recallable,500 Day(s),5 Hour(s) | EWTW EWTE | 115 40
2024-07-08 07:00 | 2024-07-15 07:00 | MACKAY TS, MACKAY JCT, WAWA TS,MARATHON TS,WAWA TS, MARATHON TS,FORT FRANCES TS, MACKENZIE TS | W23K.WAXMC, 690, 682, AL23, L23L25, 14-GL4, 14-W23K, L23_BUS, W23K.MKXMK,W21M.MAXWA, 14-W21M, 15-W21M,F25A.FOXMK, 20-F25A, 22-F25A | 1-00234129 Rev. #7,1-00191090 Rev. #24,1-00194140 Rev. #18,1-00239979 Rev. #2 | 24 Hour(s),Non-recallable,500 Day(s),6 Hour(s) | EWTW EWTE | 115 40
2024-07-15 07:00 | 2024-07-21 17:00 | MACKAY TS, MACKAY JCT, WAWA TS,ALEXANDER SS, RESERVE JCT, BIRCH TS, LAKEHEAD TS, PINE PORTAGE SS,MARATHON TS,WAWA TS, MARATHON TS,FORT FRANCES TS, MACKENZIE TS | W23K.WAXMC, 690, 682, AL23, L23L25, 14-GL4, 14-W23K, L23_BUS, W23K.MKXMK,A7L.M1XAS, A7L.M1XLA, R1LB.BIXLA, R1LB.LAXPI, 12-A7L, 12-R1LB, 17-R1LB, 26-R1LB, 4-A7L, 57M1-J7,W21M.MAXWA, 14-W21M, 15-W21M,F25A.FOXMK, 20-F25A, 22-F25A | 1-00234129 Rev. #7,1-00239989 Rev. #2,1-00191090 Rev. #24,1-00194140 Rev. #18,1-00239979 Rev. #2 | 24 Hour(s),10 Hour(s),Non-recallable,500 Day(s),6 Hour(s) | EWTW EWTE | 115 40
2024-07-21 17:00 | 2024-07-26 17:00 | WAWA TS, MARATHON TS,MARATHON TS, WAWA TS,MACKAY TS, MACKAY JCT,ALEXANDER SS, RESERVE JCT, BIRCH TS, LAKEHEAD TS, PINE PORTAGE SS | W21M.MAXWA, 14-W21M, 15-W21M,W23K.WAXMC, 690, 682, AL23, L23L25, 14-GL4, 14-W23K, L23_BUS, W23K.MKXMK,A7L.M1XAS, A7L.M1XLA, R1LB.BIXLA, R1LB.LAXPI, 12-A7L, 12-R1LB, 17-R1LB, 26-R1LB, 4-A7L, 57M1-J7 | 1-00194140 Rev. #18,1-00191090 Rev. #24,1-00234129 Rev. #7,1-00239989 Rev. #2 | 500 Day(s),Non-recallable,24 Hour(s),10 Hour(s) | EWTW EWTE | 115 40
2024-07-26 17:00 | 2024-07-31 17:00 | ALEXANDER SS, RESERVE JCT, BIRCH TS, LAKEHEAD TS, PINE PORTAGE SS,WAWA TS, MARATHON TS,MARATHON TS, WAWA TS | A7L.M1XAS, A7L.M1XLA, R1LB.BIXLA, R1LB.LAXPI, 12-A7L, 12-R1LB, 17-R1LB, 26-R1LB, 4-A7L, 57M1-J7,W21M.MAXWA, 14-W21M, 15-W21M | 1-00239989 Rev. #2,1-00194140 Rev. #18,1-00191090 Rev. #24 | 10 Hour(s),500 Day(s),Non-recallable
2024-07-31 17:00 | 2024-08-12 07:00 | WAWA TS, MARATHON TS,MARATHON TS, WAWA TS | W21M.MAXWA, 14-W21M, 15-W21M | 1-00194140 Rev. #18,1-00191090 Rev. #24 | 500 Day(s),Non-recallable
2024-08-12 08:00 | 2024-08-18 16:00 | MACKENZIE TS,MARATHON TS, WAWA TS,WAWA TS, MARATHON TS, MOOSE LAKE TS | PL25,W21M.MAXWA, 14-W21M, 15-W21M,A3M.MAXMO, PL22, PL25, T3R3, 20-A3M, 3-A3M, P_BUS, T3, R3, T3-P,T3R3 | 1-00201495 Rev. #21,1-00191090 Rev. #24,1-00194140 Rev. #18,1-00234060 Rev. #2,1-00234972 Rev. #2 | 8 Hour(s),Non-recallable,500 Day(s),24 Hour(s),24 Hour(s)
2024-08-18 17:00 | 2024-09-04 12:00 | MARATHON TS, WAWA TS,WAWA TS, MARATHON TS,MACKENZIE TS | W21M.MAXWA, 14-W21M, 15-W21M,T3R3, 20-A3M, T3, R3, T3-P | 1-00191090 Rev. #24,1-00194140 Rev. #18,1-00234972 Rev. #2 | Non-recallable,500 Day(s),24 Hour(s)
2024-09-23 16:00 | 2024-10-07 07:00 | WAWA TS, MARATHON TS,MARATHON TS, WAWA TS | W21M.MAXWA, 14-W21M, 15-W21M | 1-00194140 Rev. #18,1-00191090 Rev. #24 | 500 Day(s),Non-recallable
2024-10-07 07:00 | 2024-10-15 07:00 | MARATHON TS, WAWA TS,WAWA TS, MARATHON TS,MARGACH DS, MARGACH JCT, RABBIT LAKE SS | W21M.MAXWA, 14-W21M, 15-W21M,K6F.MAXRA, L1L6, HL6, 15-K6F, 24T2-L, HL6_BUS, K6FT1-T2 | 1-00191090 Rev. #24,1-00194140 Rev. #18,1-00242608 Rev. #1 | Non-recallable,500 Day(s),5 Day(s)
2024-10-15 07:00 | 2024-10-21 06:00 | MARGACH DS, MARGACH JCT, RABBIT LAKE SS,WAWA TS, MARATHON TS,ALGOMA TS,MARATHON TS, WAWA TS | K6F.MAXRA, L1L6, HL6, 15-K6F, 24T2-L, HL6_BUS, K6FT1-T2,W21M.MAXWA, 14-W21M, 15-W21M,26-S22A | 1-00242608 Rev. #1,1-00194140 Rev. #18,1-00236087 Rev. #1,1-00191090 Rev. #24 | 5 Day(s),500 Day(s),5 Hour(s),Non-recallable
2024-10-21 06:00 | 2024-10-31 17:00 | MARGACH DS, MARGACH JCT, RABBIT LAKE SS,ALGOMA TS,WAWA TS, MARATHON TS,MARATHON TS, WAWA TS | K6F.MAXRA, L1L6, HL6, 15-K6F, 24T2-L, HL6_BUS, K6FT1-T2,DL22, L22L23, 26-S22A,W21M.MAXWA, 14-W21M, 15-W21M,26-S22A | 1-00242608 Rev. #1,1-00234168 Rev. #1,1-00194140 Rev. #18,1-00236087 Rev. #1,1-00191090 Rev. #24 | 5 Day(s),12 Hour(s),500 Day(s),5 Hour(s),Non-recallable
2024-11-04 06:00 | 2024-11-10 16:00 | WAWA TS, MARATHON TS,ALGOMA TS, MISSISSAGI TS,MARATHON TS, WAWA TS | W21M.MAXWA, 14-W21M, 15-W21M,A23P.MIXAL, KL23, L22L23, 26-A23P, 34-A23P | 1-00194140 Rev. #18,1-00234172 Rev. #1,1-00191090 Rev. #24 | 500 Day(s),12 Hour(s),Non-recallable
2024-11-15 17:00 | 2024-11-22 16:00 | TERRACE BAY SS,GREENWICH WF CGS JCT, GREENWICH LAKE WF CSS, MARATHON TS, LAKEHEAD TS | 77T1M, 77T1M-82, T1M-S,M24L.GJXGS, M24L.GJXMA, M24L.LAXGJ, 12-M24L, 15-M24L | 1-00225664 Rev. #8,1-00236088 Rev. #2 | 2 Day(s),5 Hour(s)
2024-11-25 06:00 | 2024-12-06 17:00 | ALGOMA TS, MISSISSAGI TS,GREENWICH WF CGS JCT, GREENWICH LAKE WF CSS, MARATHON TS, LAKEHEAD TS | A24P.MIXAL, DL24, KL24, 26-A24P, 34-A24P,M24L.GJXGS, M24L.GJXMA, M24L.LAXGJ, 12-M24L, 15-M24L | 1-00234175 Rev. #1,1-00236088 Rev. #2 | 12 Hour(s),5 Hour(s)
2024-12-07 06:00 | 2024-12-19 17:00 | ALGOMA TS, HANMER TS,GREENWICH WF CGS JCT, GREENWICH LAKE WF CSS, MARATHON TS, LAKEHEAD TS | X27A.ALXHA, KL23, KL24, 26-X27A, 33-X27A, K_BUS, T8-K,M24L.GJXGS, M24L.GJXMA, M24L.LAXGJ, 12-M24L, 15-M24L | 1-00234062 Rev. #1,1-00236088 Rev. #2 | 12 Hour(s),5 Hour(s)
Back to main menu

## Table C7
Back to main menu
Table C7: Ottawa Zone
Planned Start | Planned End | Station | Equipment Name | Outage ID | Max Recall | Major Transmission Interface Impacted | Reduction in Limit
2024-03-24 14:00 | 2024-04-08 06:00 | HAWTHORNE TS | KL5 | 1-00236097 Rev. #12,1-00242728 Rev. #3 | 6 Hour(s),4 Hour(s)
2024-04-12 10:30 | 2024-04-27 10:30 | HAWTHORNE TS | KL5 | 1-00236098 Rev. #13 | Non-recallable
2024-05-12 07:00 | 2024-05-19 16:00 | MERIVALE TS, NEPEAN TS | M32S.NEXME, KL32, L31L32, PL31, 6-M32S, 6-M31A, M32S-1, T4-M32S, L32_BUS | 1-00245563 Rev. #2 | 24 Hour(s) | FIO BEAU P33C | 600 0 150
2024-05-12 07:00 | 2024-05-19 16:00 | MERIVALE TS, NEPEAN TS | M32S.NEXME, KL32, L31L32, PL31, 6-M32S, 6-M31A, M32S-1, T4-M32S, L32_BUS | 1-00245563 Rev. #2 | 24 Hour(s) | FIO BEAU P33C | 600 0 150
2024-09-08 14:00 | 2024-09-13 17:00 | CLARINGTON TS, HAVELOCK TS, MARINE JCT, OTONABEE TS,HAWTHORNE TS | 128T1-T31H, L23L31, P2L31, 296-T31H, L31_BUS, T31H.HAXMJ, T31H.MJXCL, T31H.MJXOT, 57-T31H,HT1P1, T2L523, HT2-P2, T2, P1-P2, R2-T2, T2-HT2, T2-LT2 | 1-00239080 Rev. #5,1-00208490 Rev. #7 | 4 Hour(s),6 Hour(s) | FIO BEAU P33C | 1500 0 0
2024-09-13 17:00 | 2024-10-07 07:00 | HAWTHORNE TS | HT1P1, T2L523, HT2-P2, T2, P1-P2, R2-T2, T2-HT2, T2-LT2 | 1-00208490 Rev. #7 | 6 Hour(s) | FIO BEAU P33C | 1500 0 0
2024-10-07 07:00 | 2024-10-25 09:30 | HAWTHORNE TS,CHATS FALLS TS, HAVELOCK TS, CLARINGTON TS, MARINE JCT | HT1P1, T2L523, HT2-P2, T2, P1-P2, R2-T2, T2-HT2, T2-LT2,C25H.HAXCF, 2-C25H, 57-C25H, HT3L32, K2L32, 296-T32H, L32_BUS, T32H.HAXMJ, T32H.MJXCL, 57-T32H | 1-00208490 Rev. #7,1-00239126 Rev. #4 | 6 Hour(s),4 Hour(s) | FIO BEAU P33C | 1500 0 100
2024-03-24 14:00 | 2024-04-08 06:00 | HAWTHORNE TS | KL5 | 1-00236097 Rev. #12,1-00242728 Rev. #3 | 6 Hour(s),4 Hour(s)
2024-04-12 10:30 | 2024-04-27 10:30 | HAWTHORNE TS | KL5 | 1-00236098 Rev. #13 | Non-recallable
2024-11-06 07:00 | 2024-11-17 15:00 | ARNPRIOR JCT, BARRETT CHUTE SS, FITZROY JCT, ARNPRIOR TS, CHATS FALLS TS, NQL1 B JCT, LINCOLN HEIGHTS TS, WOODROFFE TS, MANORDALE JCT, MANORDALE MTS, MERIVALE TS, CENTRE POINT JCT | C7BM.ARXAR, C7BM.ARXBA, C7BM.ARXFI, C7BM.CHXFI, C7BM.FIXNQ, C7BM.LIXWO, C7BM.MAXMD, C7BM.NQXMA, C7BM.NQXME, C7BM.WOXCE, 2C7BM, 14-C7BM, 24-C7BM, 53C7BM-14, 6-C7BM, 71-C7BM, C7BM-71, T2-C7BM | 1-00236095 Rev. #2 | 4 Hour(s)
2024-11-17 16:00 | 2024-12-19 17:00 | BELLMAN JCT, CHATS FALLS TS, FITZROY JCT, NQL1 B JCT | C7BM.CHXFI, C7BM.FIXNQ, 2C7BM, 53C7BM-14, L1C7BM-1 | 1-00241758 Rev. #2 | 4 Hour(s)
2024-03-24 14:00 | 2024-04-08 06:00 | HAWTHORNE TS | KL5 | 1-00236097 Rev. #12,1-00242728 Rev. #3 | 6 Hour(s),4 Hour(s)
2024-04-12 10:30 | 2024-04-27 10:30 | HAWTHORNE TS | KL5 | 1-00236098 Rev. #13 | Non-recallable
Back to main menu

## Table C8
Back to main menu
Table C8: Southwest Zone
Planned Start | Planned End | Station | Equipment Name | Outage ID | Max Recall | Major Transmission Interface Impacted | Reduction in Limit
2024-06-09 07:00 | 2024-07-05 09:00 | MIDDLEPORT TS | K1K2, K2L25, SC23K2, SC23SC, T6L31, 25-M31W, K2_BUS, SC23, SS3-K, K2L31, K2L21, TEMPSS6 | 1-00238468 Rev. #3 | 8 Hour(s)
2023-11-07 16:00 | 2024-03-04 08:00 | MIDDLEPORT TS,CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS | T6, T6-LT6, T6-TL581, LT6BUS-TEMP1,C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550 | 1-00220299 Rev. #39,1-00213473 Rev. #37 | Non-recallable,Non-recallable | FABCW NBLIP BLIP | 200 0 0
2024-03-04 08:00 | 2024-03-14 07:15 | CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,MIDDLEPORT TS,BECK 2 TS, MID RIVER JCT NIAGARA | C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1,BP76.PAXBE, K2L76, L35L76, R76, TL35-BO1 | 1-00213473 Rev. #37,1-00220299 Rev. #39,1-00181622 Rev. #28 | Non-recallable,Non-recallable,Non-recallable | FABCW NBLIP BLIP | 200 0 0
2024-03-17 07:00 | 2024-03-24 16:00 | DETWEILER TS, STRATFORD JCT, SEAFORTH TS, STRATFORD TS,CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,MIDDLEPORT TS,BECK 2 TS, MID RIVER JCT NIAGARA,BRANTFORD TS, NEWPORT JCT, MIDDLEPORT TS | B22D.STXDE, B22D.STXST, 26-B22D, 68T1-B22D, 61B22D-26,C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1,BP76.PAXBE, K2L76, L35L76, R76, TL35-BO1,M32W.NEXBR, M32W.NEXMI, YZ, 25-M32W, 44M32W-19, T4-M32W | 1-00237157 Rev. #9,1-00213473 Rev. #37,1-00220299 Rev. #39,1-00181622 Rev. #28,1-00238922 Rev. #11 | 4 Hour(s),Non-recallable,Non-recallable,Non-recallable,6 Hour(s) | FABCW NBLIP BLIP | 400 0 0
2024-03-25 07:00 | 2024-03-31 11:00 | CLAIREVILLE TS, ESSA TS,BRANTFORD TS, NEWPORT JCT, MIDDLEPORT TS,BECK 2 TS, MID RIVER JCT NIAGARA,MIDDLEPORT TS,CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,DETWEILER TS, STRATFORD JCT, SEAFORTH TS, STRATFORD TS | E510V.CLXES, AL510, W3L510, 18-E510V, 51-E510V,M32W.NEXBR, M32W.NEXMI, YZ, 25-M32W, 44M32W-19, T4-M32W,BP76.PAXBE, K2L76, L35L76, R76, TL35-BO1,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1,C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,B22D.STXDE, B22D.STXST, 26-B22D, 68T1-B22D, 61B22D-26,AL510 | 1-00238540 Rev. #3,1-00238922 Rev. #11,1-00181622 Rev. #28,1-00220299 Rev. #39,1-00213473 Rev. #37,1-00235682 Rev. #6,1-00237157 Rev. #9,1-00238545 Rev. #4 | 48 Hour(s),6 Hour(s),Non-recallable,Non-recallable,Non-recallable,14 Day(s),4 Hour(s),5 Day(s) | FABCW NBLIP BLIP | 400 0 0
2024-04-05 17:00 | 2024-04-12 16:00 | BRUCE A TS, BRUCE JCT, MILTON SS, WILLOW CREEK JCT,BRANTFORD TS, NEWPORT JCT, MIDDLEPORT TS,BECK 2 TS, MID RIVER JCT NIAGARA,MIDDLEPORT TS,CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,CLAIREVILLE TS, ESSA TS,DETWEILER TS, STRATFORD JCT, SEAFORTH TS, STRATFORD TS,LONGWOOD TS | B502M.BAXBJ, B502M.BJXMI, B502M.BJXWJ, 21-B502M, 40-B502M,M32W.NEXBR, M32W.NEXMI, YZ, 25-M32W, 44M32W-19, T4-M32W,BP76.PAXBE, K2L76, L35L76, R76, TL35-BO1,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1,C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,E510V.CLXES, AL510, W3L510, 18-E510V, 51-E510V,B22D.STXDE, B22D.STXST, 26-B22D, 68T1-B22D, 61B22D-26,R5N, T5L45, SS5, T5, R5, T5-H, T5-LT5,25-Q23BM, L23HT6, D2L23, Q23BM-TEMP1 | 1-00239284 Rev. #3,1-00238922 Rev. #11,1-00181622 Rev. #28,1-00220299 Rev. #39,1-00213473 Rev. #37,1-00235682 Rev. #6,1-00237157 Rev. #9,1-00239308 Rev. #10,1-00235814 Rev. #13,1-00246468 Rev. #2 | 8 Hour(s),6 Hour(s),Non-recallable,Non-recallable,Non-recallable,14 Day(s),4 Hour(s),5 Day(s),4 Hour(s),6 Hour(s) | FABCW NBLIP BLIP | 2300 300 300
2024-04-14 16:00 | 2024-04-19 16:00 | CLAIREVILLE TS, ESSA TS,KENT TS, CHATHAM SS, GSPC JCT,DETWEILER TS, STRATFORD JCT, SEAFORTH TS, STRATFORD TS,CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,MIDDLEPORT TS,BECK 2 TS, MID RIVER JCT NIAGARA,BRUCE A TS, BRUCE JCT, MILTON SS, WILLOW CREEK JCT,LONGWOOD TS | E510V.CLXES, AL510, W3L510, 18-E510V, 51-E510V,T1B, T1Y, T4Z, 5-L28C, 86-L28C, T1, T4, T1-L28C, T4L28C, 312L28C-MSO2,B22D.STXDE, B22D.STXST, 26-B22D, 68T1-B22D, 61B22D-26,C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1,BP76.PAXBE, K2L76, L35L76, R76, TL35-BO1,25-Q23BM, L23HT6, D2L23, Q23BM-TEMP1,D1D2, D1L29, D1L27, L33L40, SC22D1, SC22SC, 25-M33W, D1_BUS, SC22, SS2-D, D1L34, D1L33,B502M.BAXBJ, B502M.BJXMI, B502M.BJXWJ, 21-B502M, 40-B502M,R5N, T5L45, SS5, T5, R5, T5-H, T5-LT5 | 1-00235682 Rev. #6,1-00238919 Rev. #6,1-00237157 Rev. #9,1-00213473 Rev. #37,1-00220299 Rev. #39,1-00181622 Rev. #28,1-00246468 Rev. #2,1-00238390 Rev. #3,1-00235814 Rev. #13,1-00239308 Rev. #10 | 14 Day(s),12 Hour(s),4 Hour(s),Non-recallable,Non-recallable,Non-recallable,6 Hour(s),2 Hour(s),4 Hour(s),5 Day(s) | FABCW NBLIP BLIP | 2300 300 300
2024-05-26 07:00 | 2024-05-31 08:00 | ALLANBURG TS, BECK 2 TS, MID RIVER JCT NIAGARA, CROSSLINE JCT, MIDDLEPORT TS, CALEDONIA Q35M JCT,CLAIREVILLE TS,BRUCE B SS, BRUCE JCT, WILLOW CREEK JCT, MILTON SS,LONGWOOD DESN, LAMBTON TS 2, LONGWOOD JCT, LONGWOOD TS,CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,MIDDLEPORT TS,DETWEILER TS, STRATFORD TS, ZURICH JCT | BP76.PAXBE, Q35M.MIXCA, Q35M.QUXAL, D2HT4, H2HT4, K2L76, L26L35, L30TL35, L34L35, L35L76, T4, R76,W3L570, W3L510, T15, T15-HT15, T15-W3, T15-SS2,B501M.BBXBJ, B501M.BJXWJ, B501M.WJXMI, 40-B501M, 29-B501M,L24L.LOXLA, L24L.LOXLD, L24L.LOXLO, AL24, T14Q, T3L24, 27-L24L, T14, T14-L24L, W52-L24L,C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1, 51-C550VP, 52-C550VP, 81-C550VP,26-B23D, 68T2-B23D, 364B23D-MSO1 | 1-00181648 Rev. #9,1-00238525 Rev. #10,1-00237165 Rev. #9,1-00236074 Rev. #16,1-00213473 Rev. #37,1-00220299 Rev. #39,1-00236150 Rev. #5,1-00238602 Rev. #4 | 4 Hour(s),4 Hour(s),4 Hour(s),8 Day(s),Non-recallable,Non-recallable,4 Hour(s),4 Hour(s) | FABCW NBLIP BLIP | 2800 300 300
2024-06-11 16:00 | 2024-06-21 13:00 | DETWEILER TS, STRATFORD TS, ZURICH JCT,LAMBTON TS 2,BRUCE B SS, BRUCE JCT, WILLOW CREEK JCT, MILTON SS,MIDDLEPORT TS,CLAIREVILLE TS | 26-B23D, 68T2-B23D, 364B23D-MSO1,K2L28, L27L28, 27-L28C,B561M.BBXBR, B561M.BRXWI, B561M.WIXMI, 40-B561M, 29-B561M, KL561, L61L71,K1K2, K2L25, SC23K2, SC23SC, T6L31, 25-M31W, K2_BUS, SC23, SS3-K, K2L31, K2L21, TEMPSS6,T14, T14-HT14, T14-SS1, T14-W2,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1 | 1-00238602 Rev. #4,1-00216496 Rev. #13,1-00237189 Rev. #8,1-00237186 Rev. #4,1-00238468 Rev. #3,1-00181626 Rev. #19,1-00220299 Rev. #39 | 4 Hour(s),4 Hour(s),4 Hour(s),2 Day(s),8 Hour(s),4 Hour(s),Non-recallable | FABCW NBLIP BLIP | 2350 300 300
2024-06-27 17:00 | 2024-07-03 07:00 | MIDDLEPORT TS,LAMBTON TS 2,CLAIREVILLE TS | T6, T6-LT6, T6-TL581, LT6BUS-TEMP1,K2L28, L27L28, P2L27, 27-L28C, 27-L27V,T14, T14-HT14, T14-SS1, T14-W2,K1K2, K2L25, SC23K2, SC23SC, T6L31, 25-M31W, K2_BUS, SC23, SS3-K, K2L31, K2L21, TEMPSS6 | 1-00220299 Rev. #39,1-00216465 Rev. #12,1-00181626 Rev. #19,1-00238468 Rev. #3 | Non-recallable,4 Hour(s),4 Hour(s),8 Hour(s) | FABCW NBLIP BLIP | 250 0 0
2024-07-08 07:00 | 2024-07-16 12:00 | MIDDLEPORT TS,MILTON SS, TRAFALGAR TS,BRUCE A TS, UNDERWOOD JCT, HANOVER TS, UNDERWOOD WGS,BURLINGTON TS, BURLINGTON JCT, MIDDLEPORT TS, CARLUKE JCT, NEALE JCT, BURLINGTON DESN TS, BECK 2 TS, NIAGARA WEST JCT,GRAND JCT, NANTICOKE TS, HORNING JCT, HORNING TS,LAMBTON TS 2 | T6, T6-LT6, T6-TL581, LT6BUS-TEMP1,M573T.MIXTR, HL573, L502L573, 40-M573T, T15-M573T,B4V.BRXUN, B4V.UNXUN, T4A, 21-B4V, 36B4V-22, 7014B5V-MSO2, 36T4-B4V,Q25BM.BEXNI, Q25BM.BUXBD, Q25BM.BUXBU, Q25BM.MIXCA, Q25BM.NEXBU, 25-Q25BM, 28-Q25BM, 39-Q25BM, T15-Q25BM,59-N5M, 310N5M-LC1,M27B.HOXBU, M27B.HOXHO, M27B.HOXMI, 25-M27B, 39-M27B, 4T4-M27B,K2L28, L27L28, P2L27, 27-L28C, 27-L27V | 1-00220299 Rev. #39,1-00208773 Rev. #10,1-00241125 Rev. #2,1-00238418 Rev. #3,1-00238444 Rev. #7,1-00238499 Rev. #3,1-00216465 Rev. #12 | Non-recallable,14 Day(s),10 Hour(s),6 Hour(s),10 Hour(s),6 Hour(s),4 Hour(s) | FABCW NBLIP BLIP | 550 0 0
2024-07-26 17:00 | 2024-08-01 17:00 | BURLINGTON TS, BURLINGTON JCT, MIDDLEPORT TS, CARLUKE JCT, NEALE JCT, BURLINGTON DESN TS, BECK 2 TS, NIAGARA WEST JCT,LAMBTON TS 2,EAST LAKE ST. CLAIR WF JCT, LAMBTON TS 2,MILTON SS, TRAFALGAR TS,CALEDONIA TS, GRAND JCT, HORNING JCT, HORNING TS,MIDDLEPORT TS | Q25BM.BEXNI, Q25BM.BUXBD, Q25BM.BUXBU, Q25BM.MIXCA, Q25BM.NEXBU, 25-Q25BM, 28-Q25BM, 39-Q25BM, T15-Q25BM,KL25, L25L29, PL29, 27-L25V, 27-L29C, L25V-TEMP1,27-L29C, NA300L29C-2,M573T.MIXTR, HL573, L502L573, 40-M573T, T15-M573T,T2Y, 25-N5M, T2, N27T2-N5M, 310N5M-LC2,M28B.HOXBU, M28B.HOXHO, M28B.HOXMI, 25-M28B, 39-M28B, 4T3-M28B,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1 | 1-00238418 Rev. #3,1-00239852 Rev. #2,1-00239849 Rev. #5,1-00208773 Rev. #10,1-00238512 Rev. #2,1-00238498 Rev. #3,1-00220299 Rev. #39 | 6 Hour(s),4 Hour(s),12 Hour(s),14 Day(s),10 Hour(s),6 Hour(s),Non-recallable | FABCW NBLIP BLIP | 150 0 0
2024-08-11 06:00 | 2024-08-16 08:00 | MILTON SS, TRAFALGAR TS,BRUCE A TS, UNDERWOOD JCT, HANOVER TS, UNDERWOOD WGS,BURLINGTON TS, HORNING JCT, HORNING TS, MIDDLEPORT TS,CALEDONIA TS, GRAND JCT,LAMBTON TS 2, ST. CLAIRX TS,MIDDLEPORT TS | M573T.MIXTR, HL573, L502L573, 40-M573T, T15-M573T,B4V.BRXUN, B4V.UNXUN, T4A, 21-B4V, 36B4V-22, 7014B5V-MSO2, 36T4-B4V,M28B.HOXBU, M28B.HOXHO, M28B.HOXMI, 25-M28B, 39-M28B, 4T3-M28B,T2Y, 25-N5M, T2, N27T2-N5M, 310N5M-LC2,L51D.CLXLA, K1L51, L23L51, PS51-2, PS51-1, PS51-S, PS51,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1 | 1-00208773 Rev. #10,1-00241126 Rev. #2,1-00238498 Rev. #3,1-00238512 Rev. #2,1-00235998 Rev. #3,1-00220299 Rev. #39 | 14 Day(s),10 Hour(s),6 Hour(s),10 Hour(s),4 Hour(s),Non-recallable | FABCW NBLIP BLIP | 550 0 0
2024-08-29 17:00 | 2024-09-06 16:00 | BRUCE A TS, BRUCE JCT, WILLOW CREEK JCT, CLAIREVILLE TS, MILTON SS, OWEN SOUND TS,MIDDLEPORT TS, NANTICOKE TS | B560V.BRXBR, B560V.BRXMI, B560V.BRXWI, B560V.MIXCL, DL560, L553L560, 21-B560V, 51-B560V,B27S.BRXOW, T3-B27S, T5-B27S, 21-B27S,M585M.MIXMD, N581M.MDXNA, L81L85, T6L31, 25-M585M, 25-N581M, 40-M585M, 59-N581M, L581_BUS, T6, T6-LT6, T6-TL581, L23HT6,T6, LT6BUS-TEMP1,N581M.MDXNA, AL581, T7L581, T7T12, HT7_BUS | 1-00238565 Rev. #4,1-00241124 Rev. #4,1-00195970 Rev. #14,1-00238566 Rev. #2,1-00238464 Rev. #2,1-00220299 Rev. #39,1-00238492 Rev. #2,1-00238434 Rev. #2,1-00238433 Rev. #2 | 4 Hour(s),4 Hour(s),4 Day(s),4 Hour(s),Non-recallable,Non-recallable,Non-recallable,Non-recallable,Non-recallable | FABCW NBLIP BLIP | 2350 300 300
2024-09-16 08:00 | 2024-09-27 15:00 | MIDDLEPORT TS, NANTICOKE TS,ESSA TS, MILTON SS,BEACH TS, HANNON JCT, DOFASCO KENILWORTH CTS, BECK 2 TS, MIDDLEPORT TS, NEBO JCT, HAMILTON NEBO TS,BRUCE A TS, BRUCE JCT, WILLOW CREEK JCT, CLAIREVILLE TS | N581M.MDXNA, AL581, T7L581, T7T12, 25-N581M, 59-N581M, HT7_BUS,HT4, R4N, HT4L29, HT4_BUS, T4, R4, T4-D, T4-HT4, TSS4,M585M.MIXMD, 25-M585M, 40-M585M,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1, N581M.MDXNA, L81L85, T6L31, L581_BUS, T6, L23HT6,Q24HM.HAXBE, Q24HM.HAXHA, Q24HM.HAXKE, Q24HM.HNXHA, Q24HM.HNXHN, Q24HM.HNXMI, 157T1-Q24HM, 17-Q24HM, 17-Q29HM, 25-Q24HM, 28-Q24HM, T3-Q24HM, 61Q29HM-LC,B560V.BRXBR, B560V.BRXMI, B560V.BRXWI, B560V.MIXCL, 21-B560V, 51-B560V, DL560, L553L560 | 1-00238433 Rev. #2,1-00246166 Rev. #1,1-00238434 Rev. #2,1-00238492 Rev. #2,1-00220299 Rev. #39,1-00238464 Rev. #2,1-00238421 Rev. #2,1-00238566 Rev. #2,1-00195970 Rev. #14 | Non-recallable,4 Hour(s),Non-recallable,Non-recallable,Non-recallable,Non-recallable,10 Hour(s),4 Hour(s),4 Day(s) | FABCW NBLIP BLIP | 2350 300 300
2024-11-04 08:00 | 2024-11-15 17:00 | MIDDLEPORT TS, MILTON SS, NANTICOKE TS,BECK 2 TS,CLAIREVILLE TS, ESSA TS,KENT TS, CHATHAM SS, GSPC JCT,BRUCE A TS, UNDERWOOD JCT, HANOVER TS, UNDERWOOD WGS | M585M.MIXMD, N581M.MDXNA, L81L85, T6L31, 25-M585M, 25-N581M, 40-M585M, 59-N581M, L581_BUS, T6, T6-LT6, T6-TL581, L23HT6,28-PA302, T302, T302-1,N581M.MDXNA, AL581, T7L581, T7T12, HT7_BUS,E511V.CLXES, DL511, W2L511, 18-E511V, 51-E511V,T1B, T1Y, T4Z, 5-L28C, 86-L28C, T1, T4, T1-L28C, T4L28C, 312L28C-MSO2,B4V.BRXUN, B4V.UNXUN, T4A, 21-B4V, 36B4V-22, 36T4-B4V, 161B5V-MSO1, 21-B5V | 1-00238465 Rev. #1,1-00238560 Rev. #1,1-00238433 Rev. #2,1-00238434 Rev. #2,1-00238492 Rev. #2,1-00238538 Rev. #1,1-00240028 Rev. #2,1-00241127 Rev. #1 | 4 Hour(s),8 Hour(s),Non-recallable,Non-recallable,Non-recallable,48 Hour(s),12 Hour(s),10 Hour(s) | FABCW NBLIP BLIP | 1000 0 0
2024-11-17 07:15 | 2024-11-28 17:00 | BRUCE A TS, MAJESTIC JCT, MAJESTIC CTS, WINGHAM JCT, SEAFORTH TS, WINGHAM TS,MIDDLEPORT TS, MILTON SS, NANTICOKE TS,BECK 2 TS,CLAIREVILLE TS, ESSA TS,KENT TS, CHATHAM SS, GSPC JCT | B23D.MJXBR, B23D.MJXMJ, B23D.MJXWI, B23D.WIXSE, B23D.WIXWI, T2-B23D, 21-B23D, 61B23D-21,M585M.MIXMD, N581M.MDXNA, L81L85, T6L31, 25-M585M, 25-N581M, 40-M585M, 59-N581M, L581_BUS, T6, T6-LT6, T6-TL581, L23HT6,N581M.MDXNA, AL581, T7L581, T7T12, HT7_BUS,28-PA302, T302, T302-1,E511V.CLXES, DL511, W2L511, 18-E511V, 51-E511V,T1B, T1Y, T4Z, 5-L28C, 86-L28C, T1, T4, T1-L28C, T4L28C, 312L28C-MSO2 | 1-00241121 Rev. #1,1-00238465 Rev. #1,1-00238433 Rev. #2,1-00238560 Rev. #1,1-00238434 Rev. #2,1-00238492 Rev. #2,1-00238538 Rev. #1,1-00240028 Rev. #2 | 4 Hour(s),4 Hour(s),Non-recallable,8 Hour(s),Non-recallable,Non-recallable,48 Hour(s),12 Hour(s) | FABCW NBLIP BLIP | 800 0 0
2024-12-06 16:00 | 2024-12-12 17:00 | BRUCE A TS, BRUCE JCT, MILTON SS, WILLOW CREEK JCT,MIDDLEPORT TS, NANTICOKE TS | B502M.BAXBJ, B502M.BJXMI, B502M.BJXWJ, 21-B502M, 40-B502M,N581M.MDXNA, AL581, T7L581, T7T12, 25-N581M, 59-N581M, HT7_BUS,M585M.MIXMD, N581M.MDXNA, L81L85, T6L31, 25-M585M, 40-M585M, L581_BUS, T6, T6-LT6, T6-TL581, L23HT6 | 1-00238570 Rev. #1,1-00238433 Rev. #2,1-00238465 Rev. #1 | 4 Hour(s),Non-recallable,4 Hour(s) | FABCW NBLIP BLIP | 2350 300 300
2024-12-12 17:00 | 2024-12-18 17:00 | MIDDLEPORT TS, NANTICOKE TS, MILTON SS | N581M.MDXNA, AL581, T7L581, T7T12, 25-N581M, 59-N581M, HT7_BUS,M585M.MIXMD, N581M.MDXNA, L81L85, T6L31, 25-M585M, 40-M585M, L581_BUS, T6, T6-LT6, T6-TL581, L23HT6 | 1-00238433 Rev. #2,1-00238465 Rev. #1 | Non-recallable,4 Hour(s) | FABCW NBLIP BLIP | 600 0 0
2024-03-30 04:30 | 2024-05-10 17:00 | CHURCHILL MEADOWS TS, CHURCHILL MEADOWS JCT, TRAFALGAR TS, ERINDALE JCT, HANLAN JCT, ERINDALE TS, HURONTARIO SS, RICHVIEW TS, TOMKEN JCT, TOMKEN TS | R19TH.CHXTR, R19TH.ERXCH, R19TH.ERXER, R19TH.ERXHA, R19TH.HAXHU, R19TH.TOXRI, R19TH.TOXTO, L19L29, 240T2-R19TH, 31-R19TH, 5T6-R19TH, 88-R19TH, L19L29-L19, T3-R19TH | 1-00238480 Rev. #8 | 36 Hour(s)
2024-07-21 07:00 | 2024-08-01 17:00 | BEAVER JCT, BROWN HILL TS, BEAVERTON JCT, LINDSAY TS, MINDEN TS, BEAVERTON TS,CHURCHILL MEADOWS TS, CHURCHILL MEADOWS JCT, TRAFALGAR TS, ERINDALE JCT, HANLAN JCT, ERINDALE TS, HURONTARIO SS, RICHVIEW TS, TOMKEN JCT, TOMKEN TS | M81B.BEXBE, M81B.BEXBV, M81B.BSXBE, M81B.BVXLI, M81B.BVXMI, L81L89, 4T1-M81B, 87-M81B, T4-M81B,R19TH.CHXTR, R19TH.ERXCH, R19TH.ERXER, R19TH.ERXHA, R19TH.HAXHU, R19TH.TOXRI, R19TH.TOXTO, L19L29, 240T2-R19TH, 31-R19TH, 5T6-R19TH, 88-R19TH, L19L29-L19, T3-R19TH | 1-00238590 Rev. #4,1-00238484 Rev. #4 | 4 Hour(s),36 Hour(s)
2024-08-01 17:00 | 2024-08-16 17:00 | CHURCHILL MEADOWS TS, CHURCHILL MEADOWS JCT, TRAFALGAR TS, ERINDALE JCT, HANLAN JCT, ERINDALE TS, HURONTARIO SS, RICHVIEW TS, TOMKEN JCT, TOMKEN TS | R19TH.CHXTR, R19TH.ERXCH, R19TH.ERXER, R19TH.ERXHA, R19TH.HAXHU, R19TH.TOXRI, R19TH.TOXTO, L19L29, 240T2-R19TH, 31-R19TH, 5T6-R19TH, 88-R19TH, L19L29-L19, T3-R19TH | 1-00238484 Rev. #4 | 36 Hour(s)
2024-11-17 07:00 | 2024-12-14 17:00 | CHURCHILL MEADOWS JCT, TRAFALGAR TS | 31-R19TH, 31-R21TH, 241R21TH-TEMP10 | 1-00238405 Rev. #1 | 36 Hour(s)
2024-03-31 18:00 | 2024-04-21 07:00 | BECK 2 TS, MID RIVER JCT NIAGARA,MIDDLEPORT TS | BP76.PAXBE, K2L76, L35L76, R76, TL35-BO1,25-Q23BM, L23HT6, D2L23, Q23BM-TEMP1 | 1-00181622 Rev. #28,1-00246468 Rev. #2 | Non-recallable,6 Hour(s)
2024-04-28 07:00 | 2024-05-03 17:00 | MIDDLEPORT TS,BECK 2 TS, MID RIVER JCT NIAGARA | D1D2, D1L29, D1L27, L34L35, SC22D1, SC22SC, 25-M34H, D1_BUS, SC22, SS2-D, D1L34, D1L33,BP76.PAXBE, K2L76, L35L76, R76, TL35-BO1 | 1-00238393 Rev. #3,1-00181622 Rev. #28 | 2 Hour(s),Non-recallable
2024-05-05 13:00 | 2024-05-20 08:00 | BECK 2 TS, MID RIVER JCT NIAGARA,CALEDONIA TS, GRAND JCT, MIDDLEPORT TS | BP76.PAXBE, K2L76, L35L76, R76, TL35-BO1,L5L25, L5L32, T2Y, 25-N5M, T2, N27T2-N5M, 310N5M-LC2 | 1-00181622 Rev. #28,1-00246626 Rev. #1 | Non-recallable,4 Hour(s)
2024-05-26 07:00 | 2024-05-31 08:00 | ALLANBURG TS, BECK 2 TS, MID RIVER JCT NIAGARA, CROSSLINE JCT, MIDDLEPORT TS, CALEDONIA Q35M JCT | BP76.PAXBE, Q35M.MIXCA, Q35M.QUXAL, D2HT4, H2HT4, K2L76, L26L35, L30TL35, L34L35, L35L76, T4, R76 | 1-00181648 Rev. #9 | 4 Hour(s)
2024-07-07 07:00 | 2024-07-19 17:00 | BURLINGTON TS, HORNING JCT, HORNING TS, MIDDLEPORT TS, BURLINGTON JCT, CARLUKE JCT, NEALE JCT, BURLINGTON DESN TS, BECK 2 TS, NIAGARA WEST JCT,GRAND JCT, NANTICOKE TS | M27B.HOXBU, M27B.HOXHO, M27B.HOXMI, 25-M27B, 39-M27B, 4T4-M27B,Q25BM.BEXNI, Q25BM.BUXBD, Q25BM.BUXBU, Q25BM.MIXCA, Q25BM.NEXBU, 25-Q25BM, 28-Q25BM, 39-Q25BM, T15-Q25BM,59-N5M, 310N5M-LC1 | 1-00238499 Rev. #3,1-00238418 Rev. #3,1-00238444 Rev. #7 | 6 Hour(s),6 Hour(s),10 Hour(s)
2024-07-21 07:00 | 2024-07-26 07:00 | BURLINGTON TS, BURLINGTON JCT, MIDDLEPORT TS, CARLUKE JCT, NEALE JCT, BURLINGTON DESN TS, BECK 2 TS, NIAGARA WEST JCT, HORNING JCT, HORNING TS,GRAND JCT, NANTICOKE TS | Q25BM.BEXNI, Q25BM.BUXBD, Q25BM.BUXBU, Q25BM.MIXCA, Q25BM.NEXBU, 25-Q25BM, 28-Q25BM, 39-Q25BM, T15-Q25BM,M28B.HOXBU, M28B.HOXHO, M28B.HOXMI, 25-M28B, 39-M28B, 4T3-M28B,59-N5M, 310N5M-LC1 | 1-00238418 Rev. #3,1-00238498 Rev. #3,1-00238444 Rev. #7 | 6 Hour(s),6 Hour(s),10 Hour(s)
2024-07-26 17:00 | 2024-08-01 17:00 | BURLINGTON TS, BURLINGTON JCT, MIDDLEPORT TS, CARLUKE JCT, NEALE JCT, BURLINGTON DESN TS, BECK 2 TS, NIAGARA WEST JCT,CALEDONIA TS, GRAND JCT, HORNING JCT, HORNING TS | Q25BM.BEXNI, Q25BM.BUXBD, Q25BM.BUXBU, Q25BM.MIXCA, Q25BM.NEXBU, 25-Q25BM, 28-Q25BM, 39-Q25BM, T15-Q25BM,T2Y, 25-N5M, T2, N27T2-N5M, 310N5M-LC2,M28B.HOXBU, M28B.HOXHO, M28B.HOXMI, 25-M28B, 39-M28B, 4T3-M28B | 1-00238418 Rev. #3,1-00238512 Rev. #2,1-00238498 Rev. #3 | 6 Hour(s),10 Hour(s),6 Hour(s)
2024-08-01 17:00 | 2024-08-16 17:00 | BURLINGTON TS, HORNING JCT, HORNING TS, MIDDLEPORT TS,CALEDONIA TS, GRAND JCT | M28B.HOXBU, M28B.HOXHO, M28B.HOXMI, 25-M28B, 39-M28B, 4T3-M28B,T2Y, 25-N5M, T2, N27T2-N5M, 310N5M-LC2 | 1-00238498 Rev. #3,1-00238512 Rev. #2 | 6 Hour(s),10 Hour(s)
2024-08-18 07:00 | 2024-08-29 17:00 | BURLINGTON TS, HORNING JCT, HORNING TS, MIDDLEPORT TS | M27B.HOXBU, M27B.HOXHO, M27B.HOXMI, 25-M27B, 39-M27B, 4T4-M27B | 1-00238500 Rev. #2 | 6 Hour(s)
2024-09-08 07:00 | 2024-10-11 17:00 | BEACH TS, HANNON JCT, DOFASCO KENILWORTH CTS, BECK 2 TS, MIDDLEPORT TS, NEBO JCT, HAMILTON NEBO TS | Q24HM.HAXBE, Q24HM.HAXHA, Q24HM.HAXKE, Q24HM.HNXHA, Q24HM.HNXHN, Q24HM.HNXMI, 157T1-Q24HM, 17-Q24HM, 17-Q29HM, 25-Q24HM, 28-Q24HM, T3-Q24HM, 61Q29HM-LC | 1-00238421 Rev. #2 | 10 Hour(s)
2024-03-17 07:00 | 2024-03-31 11:00 | LAMBTON TS 2,BRANTFORD TS, NEWPORT JCT, MIDDLEPORT TS | 27-T8, 27T8-L4D, T8,27-T7, 27-T8, T7, T7-L4D,M32W.NEXBR, M32W.NEXMI, YZ, 25-M32W, 44M32W-19, T4-M32W | 1-00240619 Rev. #5,1-00231342 Rev. #12,1-00234253 Rev. #9,1-00238922 Rev. #11 | 14 Day(s),4 Hour(s),Non-recallable,6 Hour(s)
2024-04-14 16:00 | 2024-04-19 17:00 | LAMBTON TS 2,KENT TS, CHATHAM SS, GSPC JCT,MIDDLEPORT TS,BRUCE A TS, BRUCE JCT, MILTON SS, WILLOW CREEK JCT | 27-T8, 27T8-L4D, T8,T1B, T1Y, T4Z, 5-L28C, 86-L28C, T1, T4, T1-L28C, T4L28C, 312L28C-MSO2,27-T7, 27-T8, T7, T7-L4D,D1D2, D1L29, D1L27, L33L40, SC22D1, SC22SC, 25-M33W, D1_BUS, SC22, SS2-D, D1L34, D1L33,B502M.BAXBJ, B502M.BJXMI, B502M.BJXWJ, 21-B502M, 40-B502M | 1-00240619 Rev. #5,1-00238919 Rev. #6,1-00231342 Rev. #12,1-00234253 Rev. #9,1-00238390 Rev. #3,1-00235814 Rev. #13 | 14 Day(s),12 Hour(s),4 Hour(s),Non-recallable,2 Hour(s),4 Hour(s) | FABCW NBLIP BLIP | 1750 300 300
2024-06-09 07:00 | 2024-06-25 06:30 | LAMBTON TS 2,MIDDLEPORT TS | 27-T8, 27T8-L4D, T8,K1K2, K2L25, SC23K2, SC23SC, T6L31, 25-M31W, K2_BUS, SC23, SS3-K, K2L31, K2L21, TEMPSS6,27-T7, 27-T8, T7, T7-L4D,K2L28, L27L28, 27-L28C | 1-00240619 Rev. #5,1-00238468 Rev. #3,1-00231342 Rev. #12,1-00234253 Rev. #9,1-00216496 Rev. #13 | 14 Day(s),8 Hour(s),4 Hour(s),Non-recallable,4 Hour(s)
2024-06-25 08:30 | 2024-07-05 09:00 | LAMBTON TS 2,MIDDLEPORT TS | 27-T7, 27-T8, 27T8-L4D, T7, T8, T7-L4D,K2L28, L27L28, P2L27, 27-L28C, 27-L27V,27-T8,K1K2, K2L25, SC23K2, SC23SC, T6L31, 25-M31W, K2_BUS, SC23, SS3-K, K2L31, K2L21, TEMPSS6 | 1-00234253 Rev. #9,1-00216465 Rev. #12,1-00231342 Rev. #12,1-00240619 Rev. #5,1-00238468 Rev. #3 | Non-recallable,4 Hour(s),4 Hour(s),14 Day(s),8 Hour(s)
2024-03-30 04:30 | 2024-04-05 16:00 | CLAIREVILLE TS,CHURCHILL MEADOWS TS, CHURCHILL MEADOWS JCT, TRAFALGAR TS, ERINDALE JCT, HANLAN JCT, ERINDALE TS, HURONTARIO SS, RICHVIEW TS, TOMKEN JCT, TOMKEN TS, ESSA TS,CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,PALERMO TS, BURLINGTON TS, GLENORCHY JCT, LANTZ JCT, PALERMO TXB JCT, GLENORCHY MTS1 | AL510, W3L510, 51-E510V,R19TH.CHXTR, R19TH.ERXCH, R19TH.ERXER, R19TH.ERXHA, R19TH.HAXHU, R19TH.TOXRI, R19TH.TOXTO, L19L29, 240T2-R19TH, 31-R19TH, 5T6-R19TH, 88-R19TH, L19L29-L19, T3-R19TH,E510V.CLXES, AL510, 18-E510V,C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,T37B.GJXGL, T37B.GJXLA, T37B.PAXBU, T37B.PAXTR, T37B.PJXGJ, T4Y, 31-T37B, 31SC21L-T36B, 31SC21L-T37B, 39-T37B, T4, T4-T37B | 1-00238545 Rev. #4,1-00238480 Rev. #8,1-00235682 Rev. #6,1-00213473 Rev. #37,1-00226775 Rev. #13,1-00238540 Rev. #3 | 5 Day(s),36 Hour(s),14 Day(s),Non-recallable,6 Hour(s),48 Hour(s) | FABCW NBLIP BLIP | 200 0 0
2024-04-12 16:00 | 2024-05-03 17:00 | CLAIREVILLE TS, ESSA TS,CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,CHURCHILL MEADOWS TS, CHURCHILL MEADOWS JCT, TRAFALGAR TS, ERINDALE JCT, HANLAN JCT, ERINDALE TS, HURONTARIO SS, RICHVIEW TS, TOMKEN JCT, TOMKEN TS | E510V.CLXES, AL510, W3L510, 18-E510V, 51-E510V,C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,R19TH.CHXTR, R19TH.ERXCH, R19TH.ERXER, R19TH.ERXHA, R19TH.HAXHU, R19TH.TOXRI, R19TH.TOXTO, L19L29, 240T2-R19TH, 31-R19TH, 5T6-R19TH, 88-R19TH, L19L29-L19, T3-R19TH | 1-00235682 Rev. #6,1-00213473 Rev. #37,1-00238480 Rev. #8 | 14 Day(s),Non-recallable,36 Hour(s) | FABCW NBLIP BLIP | 200 0 0
2024-05-05 06:00 | 2024-05-10 17:00 | CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,CHURCHILL MEADOWS TS, CHURCHILL MEADOWS JCT, TRAFALGAR TS, ERINDALE JCT, HANLAN JCT, ERINDALE TS, HURONTARIO SS, RICHVIEW TS, TOMKEN JCT, TOMKEN TS | C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550, 51-C550VP, 52-C550VP, 81-C550VP,R19TH.CHXTR, R19TH.ERXCH, R19TH.ERXER, R19TH.ERXHA, R19TH.HAXHU, R19TH.TOXRI, R19TH.TOXTO, L19L29, 240T2-R19TH, 31-R19TH, 5T6-R19TH, 88-R19TH, L19L29-L19, T3-R19TH | 1-00213473 Rev. #37,1-00236150 Rev. #5,1-00238480 Rev. #8 | Non-recallable,4 Hour(s),36 Hour(s) | FABCW NBLIP BLIP | 200 0 0
2024-06-21 17:00 | 2024-06-27 17:00 | BRUCE B SS, BRUCE JCT, WILLOW CREEK JCT, MILTON SS,PARKWAY TS,CLAIREVILLE TS,CHURCHILL MEADOWS TS, ERINDALE JCT, CHURCHILL MEADOWS JCT, HANLAN JCT, ERINDALE TS, TOMKEN JCT, HURONTARIO SS, JIM YARROW MTS, RICHVIEW TS, TOMKEN TS, TRAFALGAR TS | B561M.BBXBR, B561M.BRXWI, B561M.WIXMI, 40-B561M, 29-B561M, KL561, L61L71,T3, SS1-T3, T3-HT3, T3-LT3,T14, T14-HT14, T14-SS1, T14-W2,R21TH.CHXTR, R21TH.ERXCH, R21TH.ERXER, R21TH.ERXHA, R21TH.HAXHU, R21TH.HAXTO, R21TH.HUXHA, R21TH.HUXJM, R21TH.TOXRI, R21TH.TOXTO, L21L30, 162-R21TH, 240T1-R21TH, 31-R21TH, 5T5-R21TH, 88-R21TH, T4-R21TH | 1-00237189 Rev. #8,1-00237186 Rev. #4,1-00239147 Rev. #3,1-00181626 Rev. #19,1-00238414 Rev. #3 | 4 Hour(s),2 Day(s),3 Hour(s),4 Hour(s),36 Hour(s) | FABCW NBLIP BLIP | 2150 300 300
2024-07-08 07:00 | 2024-07-19 17:00 | CHURCHILL MEADOWS TS, ERINDALE JCT, CHURCHILL MEADOWS JCT, HANLAN JCT, ERINDALE TS, TOMKEN JCT, HURONTARIO SS, JIM YARROW MTS, RICHVIEW TS, TOMKEN TS, TRAFALGAR TS,MILTON SS | R21TH.CHXTR, R21TH.ERXCH, R21TH.ERXER, R21TH.ERXHA, R21TH.HAXHU, R21TH.HAXTO, R21TH.HUXHA, R21TH.HUXJM, R21TH.TOXRI, R21TH.TOXTO, L21L30, 162-R21TH, 240T1-R21TH, 31-R21TH, 5T5-R21TH, 88-R21TH, T4-R21TH,M573T.MIXTR, HL573, L502L573, 40-M573T, T15-M573T | 1-00238414 Rev. #3,1-00208773 Rev. #10 | 36 Hour(s),14 Day(s) | FABCW NBLIP BLIP | 150 0 0
2024-07-21 07:00 | 2024-08-16 08:00 | MILTON SS, TRAFALGAR TS,CHURCHILL MEADOWS TS, CHURCHILL MEADOWS JCT, ERINDALE JCT, HANLAN JCT, ERINDALE TS, HURONTARIO SS, RICHVIEW TS, TOMKEN JCT, TOMKEN TS | M573T.MIXTR, HL573, L502L573, 40-M573T, T15-M573T,R19TH.CHXTR, R19TH.ERXCH, R19TH.ERXER, R19TH.ERXHA, R19TH.HAXHU, R19TH.TOXRI, R19TH.TOXTO, L19L29, 240T2-R19TH, 31-R19TH, 5T6-R19TH, 88-R19TH, L19L29-L19, T3-R19TH | 1-00208773 Rev. #10,1-00238484 Rev. #4 | 14 Day(s),36 Hour(s) | FABCW NBLIP BLIP | 150 0 0
2024-08-26 07:00 | 2024-09-06 16:00 | BRUCE A TS, BRUCE JCT, WILLOW CREEK JCT, CLAIREVILLE TS, MILTON SS,MIDDLEPORT TS, NANTICOKE TS | B560V.BRXBR, B560V.BRXMI, B560V.BRXWI, B560V.MIXCL, DL560, L553L560, 21-B560V, 51-B560V,N581M.MDXNA, AL581, T7L581, 25-N581M, 59-N581M, T7T12, HT7_BUS,M585M.MIXMD, 25-M585M, 40-M585M, N581M.MDXNA, L81L85, T6L31, L581_BUS, T6, T6-LT6, T6-TL581, L23HT6 | 1-00238565 Rev. #4,1-00238434 Rev. #2,1-00238433 Rev. #2,1-00238492 Rev. #2,1-00238464 Rev. #2,1-00238566 Rev. #2,1-00195970 Rev. #14 | 4 Hour(s),Non-recallable,Non-recallable,Non-recallable,Non-recallable,4 Hour(s),4 Day(s) | FABCW NBLIP BLIP | 2350 300 300
2024-09-06 16:00 | 2024-09-27 15:00 | BRUCE A TS, BRUCE JCT, WILLOW CREEK JCT, CLAIREVILLE TS, MILTON SS,MIDDLEPORT TS, NANTICOKE TS | B560V.BRXBR, B560V.BRXMI, B560V.BRXWI, B560V.MIXCL, DL560, L553L560, 21-B560V, 51-B560V,N581M.MDXNA, AL581, T7L581, 25-N581M, 59-N581M, T7T12, HT7_BUS,M585M.MIXMD, 25-M585M, 40-M585M, N581M.MDXNA, L81L85, T6L31, L581_BUS, T6, T6-LT6, T6-TL581, L23HT6 | 1-00195970 Rev. #14,1-00238434 Rev. #2,1-00238433 Rev. #2,1-00238492 Rev. #2,1-00238464 Rev. #2,1-00238566 Rev. #2 | 4 Day(s),Non-recallable,Non-recallable,Non-recallable,Non-recallable,4 Hour(s) | FABCW NBLIP BLIP | 2350 300 300
2024-09-27 17:00 | 2024-10-07 06:00 | MIDDLEPORT TS, NANTICOKE TS, MILTON SS | N581M.MDXNA, AL581, T7L581, 25-N581M, 59-N581M, T7T12, HT7_BUS,M585M.MIXMD, 25-M585M, 40-M585M, N581M.MDXNA, L81L85, T6L31, L581_BUS, T6, T6-LT6, T6-TL581, L23HT6 | 1-00238434 Rev. #2,1-00238433 Rev. #2,1-00238492 Rev. #2,1-00238464 Rev. #2 | Non-recallable,Non-recallable,Non-recallable,Non-recallable | FABCW NBLIP BLIP | 600 0 0
2024-10-07 06:00 | 2024-10-15 07:00 | MIDDLEPORT TS, MILTON SS, NANTICOKE TS,ASHFIELD SS, BRUCE B SS, BRUCE JCT, WILLOW CREEK JCT | M585M.MIXMD, N581M.MDXNA, L81L85, T6L31, 25-M585M, 25-N581M, 40-M585M, 59-N581M, L581_BUS, T6, T6-LT6, T6-TL581, L23HT6,N581M.MDXNA, AL581, T7L581, T7T12, HT7_BUS,B563A.BBXBJ, B563A.BJWJ, B563A.WJXAS, OLDH5L563, OLDL501L563, L563L592, L563L565, OLD29-B563A, 322-B563A, L563_BUS, H5L563, L501L563, 29-B563A | 1-00238464 Rev. #2,1-00238492 Rev. #2,1-00238433 Rev. #2,1-00238434 Rev. #2,1-00241110 Rev. #2 | Non-recallable,Non-recallable,Non-recallable,Non-recallable,6 Hour(s) | FABCW NBLIP BLIP | 850 300 300
2024-10-18 07:00 | 2024-10-25 16:00 | CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,MIDDLEPORT TS, NANTICOKE TS, MILTON SS,PARKWAY TS | C553VP.CHXPJ, C553VP.PJXCL, C553VP.PJXPR, A2L553, L553L560, 51-C553VP, 52-C553VP, 81-C553VP,N581M.MDXNA, AL581, T7L581, 25-N581M, 59-N581M, T7T12, HT7_BUS,M585M.MIXMD, 25-M585M, 40-M585M, N581M.MDXNA, L81L85, T6L31, L581_BUS, T6, T6-LT6, T6-TL581, L23HT6,SS1, T3, SS1-T3, T3-HT3, T3-LT3 | 1-00238550 Rev. #2,1-00238434 Rev. #2,1-00238433 Rev. #2,1-00238492 Rev. #2,1-00238464 Rev. #2,1-00246737 Rev. #3 | 4 Hour(s),Non-recallable,Non-recallable,Non-recallable,Non-recallable,8 Hour(s) | FABCW NBLIP BLIP | 800 0 0
2024-11-06 17:00 | 2024-11-12 07:00 | MIDDLEPORT TS, MILTON SS, NANTICOKE TS,CLAIREVILLE TS, ESSA TS | M585M.MIXMD, N581M.MDXNA, L81L85, T6L31, 25-M585M, 25-N581M, 40-M585M, 59-N581M, L581_BUS, T6, T6-LT6, T6-TL581, L23HT6,N581M.MDXNA, AL581, T7L581, T7T12, HT7_BUS,E511V.CLXES, DL511, W2L511, 18-E511V, 51-E511V | 1-00238465 Rev. #1,1-00238433 Rev. #2,1-00238434 Rev. #2,1-00238492 Rev. #2,1-00238538 Rev. #1 | 4 Hour(s),Non-recallable,Non-recallable,Non-recallable,48 Hour(s) | FABCW NBLIP BLIP | 600 0 0
2024-11-12 07:00 | 2024-11-29 17:00 | PARKWAY TS,MIDDLEPORT TS, MILTON SS, NANTICOKE TS,CLAIREVILLE TS, ESSA TS | SS4, T4, SS4-T4, T4-HT4, T4-LT4,M585M.MIXMD, N581M.MDXNA, L81L85, T6L31, 25-M585M, 25-N581M, 40-M585M, 59-N581M, L581_BUS, T6, T6-LT6, T6-TL581, L23HT6,N581M.MDXNA, AL581, T7L581, T7T12, HT7_BUS,E511V.CLXES, DL511, W2L511, 18-E511V, 51-E511V | 1-00246738 Rev. #2,1-00238465 Rev. #1,1-00238433 Rev. #2,1-00238434 Rev. #2,1-00238492 Rev. #2,1-00238538 Rev. #1 | 8 Hour(s),4 Hour(s),Non-recallable,Non-recallable,Non-recallable,48 Hour(s) | FABCW NBLIP BLIP | 600 0 0
2024-12-01 17:00 | 2024-12-18 17:00 | MIDDLEPORT TS, NANTICOKE TS, MILTON SS | N581M.MDXNA, AL581, T7L581, T7T12, 25-N581M, 59-N581M, HT7_BUS,M585M.MIXMD, N581M.MDXNA, L81L85, T6L31, 25-M585M, 40-M585M, L581_BUS, T6, T6-LT6, T6-TL581, L23HT6 | 1-00238433 Rev. #2,1-00238465 Rev. #1 | Non-recallable,4 Hour(s) | FABCW NBLIP BLIP | 600 0 0
2024-05-20 08:00 | 2024-05-31 08:00 | ALLANBURG TS, BECK 2 TS, MID RIVER JCT NIAGARA, CROSSLINE JCT, MIDDLEPORT TS, CALEDONIA Q35M JCT | BP76.PAXBE, Q35M.MIXCA, Q35M.QUXAL, D2HT4, H2HT4, K2L76, L26L35, L30TL35, L34L35, L35L76, T4, R76 | 1-00181648 Rev. #9 | 4 Hour(s)
2023-09-12 11:30 | 2024-03-17 06:00 | BURLINGTON TS | HT9-T9, T9, T9-H2, SS9-T9, SS9 | 1-00208974 Rev. #66 | Non-recallable
2024-04-10 05:30 | 2024-04-16 07:00 | BURLINGTON TS,SCOTT TS, ST. ANDREWS TS,SEAFORTH TS | HT9-T9, T9, T9-H2, SS9-T9, SS9,HL22, HL23, HL43, KL1, KL2, KL7, T4Q, H_BUS, K_BUS, SS5, T5, T5-H, T5-K, OLDT5-H, OLDT5-K, OLDT5,DTL18 | 1-00208974 Rev. #66,1-00238726 Rev. #13,1-00246196 Rev. #1 | Non-recallable,9 Day(s),8 Hour(s)
2024-04-17 06:00 | 2024-04-25 16:00 | BURLINGTON TS,SCOTT TS, ST. ANDREWS TS | H1H2, H2L18, H2L23, H2L36, H2L40, SC22H2, SC22SC, H2_BUS, HT9-T9, T9, SC22, SC22H2-H2, T9-H2, SS9-T9,HL22, HL23, HL43, KL1, KL2, KL7, T4Q, H_BUS, K_BUS, SS5, T5, T5-H, T5-K, OLDT5-H, OLDT5-K, OLDT5,HT9-T9, SS9 | 1-00238392 Rev. #3,1-00238726 Rev. #13,1-00208974 Rev. #66 | 6 Hour(s),9 Day(s),Non-recallable
2024-04-29 11:30 | 2024-05-05 07:00 | BURLINGTON TS,SEAFORTH TS | HT9-T9, T9, T9-H2, SS9-T9, SS9,DTL18, T2Q | 1-00208974 Rev. #66,1-00239297 Rev. #8 | Non-recallable,8 Day(s)
2024-05-24 17:00 | 2024-06-01 17:00 | BURLINGTON TS,PRESTON TS | HT9-T9, T9, T9-H2, SS9-T9, SS9,T2K, L20-T2, L21-T2, T2 | 1-00208974 Rev. #66,1-00239299 Rev. #3 | Non-recallable,4 Hour(s)
2024-06-02 07:00 | 2024-06-07 16:00 | PRESTON TS,SEAFORTH TS, ST. MARYS TS | T2K, L20-T2, L21-T2, T2,BY, DTL7, T1B | 1-00239299 Rev. #3,1-00239307 Rev. #7 | 4 Hour(s),8 Day(s)
2024-07-08 07:00 | 2024-12-02 15:00 | KITCHENER MTS 5 | T92B, T91B, K5T9-F12C, T9 | 1-00243076 Rev. #2 | 2 Hour(s)
Back to main menu

## Table C9
Back to main menu
Table C9: Toronto Zone
Planned Start | Planned End | Station | Equipment Name | Outage ID | Max Recall | Major Transmission Interface Impacted | Reduction in Limit
2024-05-10 16:00 | 2024-05-16 17:00 | BASIN TS, BASIN JCT, HEARN SS | H1L.BAXBA, H1L.BAXHE, 22-H1L-L1-G, 4-H1L, H1L-CA | 1-00238978 Rev. #3 | 4 Hour(s)
2024-06-13 07:00 | 2024-07-09 07:00 | BLOOR STREET JCT, GERRARD JCT, CECIL TS, DON FLEET JCT, HEARN SS, LEASIDE TS | H6LC.BLXLE, H6LC.CEXGE, H6LC.DOXHE, H6LC.GEXBL, H6LC.GEXDO, 22-H6LC-L6-G, 34-H6LC, 49-H6LC, 80H6LC-34, 80H6LC-22, 80H6LC-49 | 1-00239028 Rev. #6 | 8 Hour(s)
2024-07-09 07:00 | 2024-07-19 17:00 | BLOOR STREET JCT, GERRARD JCT, CECIL TS, DON FLEET JCT, HEARN SS, LEASIDE TS | H6LC.BLXLE, H6LC.CEXGE, H6LC.DOXHE, H6LC.GEXBL, H6LC.GEXDO, 22-H6LC-L6-G, 34-H6LC, 49-H6LC, 80H6LC-34, 80H6LC-22, 80H6LC-49, H1L6, L5L6, L6L13, PL6 | 1-00239028 Rev. #6,1-00239048 Rev. #2 | 8 Hour(s),6 Hour(s)
2024-07-21 16:00 | 2024-07-26 17:00 | BLOOR STREET JCT, GERRARD JCT, CECIL TS, DON FLEET JCT, HEARN SS, LEASIDE TS | H6LC.BLXLE, H6LC.CEXGE, H6LC.DOXHE, H6LC.GEXBL, H6LC.GEXDO, H1L6, L5L6, L6L13, PL6, 22-H6LC-L6-G, 34-H6LC, 49-H6LC, 80H6LC-34, 80H6LC-22, 80H6LC-49,H8LC.BLXLE, H8LC.CEXGE, H8LC.DOXHE, H8LC.GEXBL, H8LC.GEXDO, 22-H8LC-L8-G, 34-H8LC, 49-H8LC, 80H8LC-22, 80H8LC-34, 80H8LC-49 | 1-00239048 Rev. #2,1-00239058 Rev. #4 | 6 Hour(s),8 Hour(s)
2024-07-26 17:00 | 2024-08-02 07:00 | BLOOR STREET JCT, GERRARD JCT, CECIL TS, DON FLEET JCT, HEARN SS, LEASIDE TS | H8LC.BLXLE, H8LC.CEXGE, H8LC.DOXHE, H8LC.GEXBL, H8LC.GEXDO, 22-H8LC-L8-G, 34-H8LC, 49-H8LC, 80H8LC-22, 80H8LC-34, 80H8LC-49 | 1-00239058 Rev. #4 | 8 Hour(s)
2024-08-02 07:00 | 2024-08-23 17:00 | CLAIREVILLE TS, HOLLAND JCT, VAUGHAN 4 JCT, HOLLAND TS, VAUGHAN MTS 4, WOODBRIDGE JCT,BLOOR STREET JCT, GERRARD JCT, CECIL TS, DON FLEET JCT, HEARN SS, LEASIDE TS | 51-H83V, L83L89, 153-H83V, H83V.WJXCL, H83V.HJX4J, H83V.4JXWJ, H83V.4JXV4, H83V.HOXHJ,H8LC.BLXLE, H8LC.CEXGE, H8LC.DOXHE, H8LC.GEXBL, H8LC.GEXDO, 22-H8LC-L8-G, 34-H8LC, 49-H8LC, 80H8LC-22, 80H8LC-34, 80H8LC-49 | 1-00238508 Rev. #4,1-00239058 Rev. #4 | 6 Hour(s),8 Hour(s)
2024-08-23 17:00 | 2024-08-30 17:00 | BLOOR STREET JCT, GERRARD JCT, CECIL TS, DON FLEET JCT, HEARN SS, LEASIDE TS | H8LC.BLXLE, H8LC.CEXGE, H8LC.DOXHE, H8LC.GEXBL, H8LC.GEXDO, 22-H8LC-L8-G, 34-H8LC, 49-H8LC, 80H8LC-22, 80H8LC-34, 80H8LC-49 | 1-00239058 Rev. #4 | 8 Hour(s)
2024-09-09 08:00 | 2024-09-20 16:00 | CLAIREVILLE TS, HOLLAND JCT, VAUGHAN 4 JCT, HOLLAND TS, VAUGHAN MTS #4, WOODBRIDGE JCT | H1L82, L76L82, 51-H82V, 153-H82V, H82V.WJXCL, H82V.4JXV4, H82V.4JXWJ, H82V.HJX4J, H82V.HOXHJ | 1-00238534 Rev. #4 | 4 Hour(s)
2024-10-08 08:00 | 2024-10-15 07:00 | BASIN TS, BASIN JCT, HEARN SS | H3L.BAXBA, H3L.BAXHE, H2L3, LT2L3, LT2L11, 22-H3L-L3-G, 4-H3L, H3L-CA | 1-00239128 Rev. #1 | 6 Hour(s)
2024-10-15 16:00 | 2024-10-25 16:00 | CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS | C553VP.CHXPJ, C553VP.PJXCL, C553VP.PJXPR, A2L553, L553L560, 51-C553VP, 52-C553VP, 81-C553VP | 1-00238550 Rev. #2 | 4 Hour(s) | FABCW | 200
2024-11-18 04:30 | 2025-02-20 09:00 | CHERRYWOOD TS | PL543, PL553, P_BUS, T17-P, T17-HT17, D4HT17, HT17L28, SS17 | 1-00194246 Rev. #2 | Non-recallable
2024-10-07 07:00 | 2024-12-19 17:00 | CHATS FALLS TS, HAVELOCK TS, CLARINGTON TS, MARINE JCT | C25H.HAXCF, 2-C25H, 57-C25H, HT3L32, K2L32, 296-T32H, L32_BUS, T32H.HAXMJ, T32H.MJXCL, 57-T32H | 1-00239126 Rev. #4 | 4 Hour(s)
2024-04-08 07:00 | 2024-04-19 16:00 | CLAIREVILLE TS, WOODBRIDGE JCT, KLEINBURG TS, VAUGHAN 3 JCT, WOODBRIDGE TS | V44.CLXWJ, V44.KLXV3, V44.V3XWJ, V44.WJXWO, 45T1-V44, 51-V44, D6T5-V44 | 1-00208875 Rev. #9 | 4 Hour(s)
2024-08-02 07:00 | 2024-08-23 17:00 | CLAIREVILLE TS, HOLLAND JCT, VAUGHAN 4 JCT, HOLLAND TS, VAUGHAN MTS 4, WOODBRIDGE JCT | 51-H83V, L83L89, 153-H83V, H83V.WJXCL, H83V.HJX4J, H83V.4JXWJ, H83V.4JXV4, H83V.HOXHJ | 1-00238508 Rev. #4 | 6 Hour(s)
2024-09-09 08:00 | 2024-09-20 16:00 | CLAIREVILLE TS, HOLLAND JCT, VAUGHAN 4 JCT, HOLLAND TS, VAUGHAN MTS #4, WOODBRIDGE JCT | H1L82, L76L82, 51-H82V, 153-H82V, H82V.WJXCL, H82V.4JXV4, H82V.4JXWJ, H82V.HJX4J, H82V.HOXHJ | 1-00238534 Rev. #4 | 4 Hour(s)
2023-11-07 16:00 | 2024-03-04 08:00 | MIDDLEPORT TS,CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS | T6, T6-LT6, T6-TL581, LT6BUS-TEMP1,C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550 | 1-00220299 Rev. #39,1-00213473 Rev. #37 | Non-recallable,Non-recallable | FABCW | 200
2024-03-04 08:00 | 2024-03-14 07:15 | CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,MIDDLEPORT TS,BECK 2 TS, MID RIVER JCT NIAGARA | C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1,BP76.PAXBE, K2L76, L35L76, R76, TL35-BO1 | 1-00213473 Rev. #37,1-00220299 Rev. #39,1-00181622 Rev. #28 | Non-recallable,Non-recallable,Non-recallable | FABCW | 200
2024-03-17 07:00 | 2024-03-24 16:00 | DETWEILER TS, STRATFORD JCT, SEAFORTH TS, STRATFORD TS,CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,MIDDLEPORT TS,BECK 2 TS, MID RIVER JCT NIAGARA,BRANTFORD TS, NEWPORT JCT, MIDDLEPORT TS | B22D.STXDE, B22D.STXST, 26-B22D, 68T1-B22D, 61B22D-26,C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1,BP76.PAXBE, K2L76, L35L76, R76, TL35-BO1,M32W.NEXBR, M32W.NEXMI, YZ, 25-M32W, 44M32W-19, T4-M32W | 1-00237157 Rev. #9,1-00213473 Rev. #37,1-00220299 Rev. #39,1-00181622 Rev. #28,1-00238922 Rev. #11 | 4 Hour(s),Non-recallable,Non-recallable,Non-recallable,6 Hour(s) | FABCW | 400
2024-03-25 07:00 | 2024-03-31 11:00 | CLAIREVILLE TS, ESSA TS,BRANTFORD TS, NEWPORT JCT, MIDDLEPORT TS,BECK 2 TS, MID RIVER JCT NIAGARA,MIDDLEPORT TS,CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,DETWEILER TS, STRATFORD JCT, SEAFORTH TS, STRATFORD TS | E510V.CLXES, AL510, W3L510, 18-E510V, 51-E510V,M32W.NEXBR, M32W.NEXMI, YZ, 25-M32W, 44M32W-19, T4-M32W,BP76.PAXBE, K2L76, L35L76, R76, TL35-BO1,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1,C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,B22D.STXDE, B22D.STXST, 26-B22D, 68T1-B22D, 61B22D-26,AL510 | 1-00238540 Rev. #3,1-00238922 Rev. #11,1-00181622 Rev. #28,1-00220299 Rev. #39,1-00213473 Rev. #37,1-00235682 Rev. #6,1-00237157 Rev. #9,1-00238545 Rev. #4 | 48 Hour(s),6 Hour(s),Non-recallable,Non-recallable,Non-recallable,14 Day(s),4 Hour(s),5 Day(s) | FABCW | 400
2024-04-05 17:00 | 2024-04-12 16:00 | BRUCE A TS, BRUCE JCT, MILTON SS, WILLOW CREEK JCT,BRANTFORD TS, NEWPORT JCT, MIDDLEPORT TS,BECK 2 TS, MID RIVER JCT NIAGARA,MIDDLEPORT TS,CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,CLAIREVILLE TS, ESSA TS,DETWEILER TS, STRATFORD JCT, SEAFORTH TS, STRATFORD TS,LONGWOOD TS | B502M.BAXBJ, B502M.BJXMI, B502M.BJXWJ, 21-B502M, 40-B502M,M32W.NEXBR, M32W.NEXMI, YZ, 25-M32W, 44M32W-19, T4-M32W,BP76.PAXBE, K2L76, L35L76, R76, TL35-BO1,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1,C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,E510V.CLXES, AL510, W3L510, 18-E510V, 51-E510V,B22D.STXDE, B22D.STXST, 26-B22D, 68T1-B22D, 61B22D-26,R5N, T5L45, SS5, T5, R5, T5-H, T5-LT5,25-Q23BM, L23HT6, D2L23, Q23BM-TEMP1 | 1-00239284 Rev. #3,1-00238922 Rev. #11,1-00181622 Rev. #28,1-00220299 Rev. #39,1-00213473 Rev. #37,1-00235682 Rev. #6,1-00237157 Rev. #9,1-00239308 Rev. #10,1-00235814 Rev. #13,1-00246468 Rev. #2 | 8 Hour(s),6 Hour(s),Non-recallable,Non-recallable,Non-recallable,14 Day(s),4 Hour(s),5 Day(s),4 Hour(s),6 Hour(s) | FABCW | 2300
2024-04-14 16:00 | 2024-04-19 16:00 | CLAIREVILLE TS, ESSA TS,KENT TS, CHATHAM SS, GSPC JCT,DETWEILER TS, STRATFORD JCT, SEAFORTH TS, STRATFORD TS,CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,MIDDLEPORT TS,BECK 2 TS, MID RIVER JCT NIAGARA,BRUCE A TS, BRUCE JCT, MILTON SS, WILLOW CREEK JCT,LONGWOOD TS | E510V.CLXES, AL510, W3L510, 18-E510V, 51-E510V,T1B, T1Y, T4Z, 5-L28C, 86-L28C, T1, T4, T1-L28C, T4L28C, 312L28C-MSO2,B22D.STXDE, B22D.STXST, 26-B22D, 68T1-B22D, 61B22D-26,C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1,BP76.PAXBE, K2L76, L35L76, R76, TL35-BO1,25-Q23BM, L23HT6, D2L23, Q23BM-TEMP1,D1D2, D1L29, D1L27, L33L40, SC22D1, SC22SC, 25-M33W, D1_BUS, SC22, SS2-D, D1L34, D1L33,B502M.BAXBJ, B502M.BJXMI, B502M.BJXWJ, 21-B502M, 40-B502M,R5N, T5L45, SS5, T5, R5, T5-H, T5-LT5 | 1-00235682 Rev. #6,1-00238919 Rev. #6,1-00237157 Rev. #9,1-00213473 Rev. #37,1-00220299 Rev. #39,1-00181622 Rev. #28,1-00246468 Rev. #2,1-00238390 Rev. #3,1-00235814 Rev. #13,1-00239308 Rev. #10 | 14 Day(s),12 Hour(s),4 Hour(s),Non-recallable,Non-recallable,Non-recallable,6 Hour(s),2 Hour(s),4 Hour(s),5 Day(s) | FABCW | 2300
2024-05-26 07:00 | 2024-05-31 08:00 | ALLANBURG TS, BECK 2 TS, MID RIVER JCT NIAGARA, CROSSLINE JCT, MIDDLEPORT TS, CALEDONIA Q35M JCT,CLAIREVILLE TS,BRUCE B SS, BRUCE JCT, WILLOW CREEK JCT, MILTON SS,LONGWOOD DESN, LAMBTON TS 2, LONGWOOD JCT, LONGWOOD TS,CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,MIDDLEPORT TS,DETWEILER TS, STRATFORD TS, ZURICH JCT | BP76.PAXBE, Q35M.MIXCA, Q35M.QUXAL, D2HT4, H2HT4, K2L76, L26L35, L30TL35, L34L35, L35L76, T4, R76,W3L570, W3L510, T15, T15-HT15, T15-W3, T15-SS2,B501M.BBXBJ, B501M.BJXWJ, B501M.WJXMI, 40-B501M, 29-B501M,L24L.LOXLA, L24L.LOXLD, L24L.LOXLO, AL24, T14Q, T3L24, 27-L24L, T14, T14-L24L, W52-L24L,C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1, 51-C550VP, 52-C550VP, 81-C550VP,26-B23D, 68T2-B23D, 364B23D-MSO1 | 1-00181648 Rev. #9,1-00238525 Rev. #10,1-00237165 Rev. #9,1-00236074 Rev. #16,1-00213473 Rev. #37,1-00220299 Rev. #39,1-00236150 Rev. #5,1-00238602 Rev. #4 | 4 Hour(s),4 Hour(s),4 Hour(s),8 Day(s),Non-recallable,Non-recallable,4 Hour(s),4 Hour(s) | FABCW | 2800
2024-06-11 16:00 | 2024-06-21 13:00 | DETWEILER TS, STRATFORD TS, ZURICH JCT,LAMBTON TS 2,BRUCE B SS, BRUCE JCT, WILLOW CREEK JCT, MILTON SS,MIDDLEPORT TS,CLAIREVILLE TS | 26-B23D, 68T2-B23D, 364B23D-MSO1,K2L28, L27L28, 27-L28C,B561M.BBXBR, B561M.BRXWI, B561M.WIXMI, 40-B561M, 29-B561M, KL561, L61L71,K1K2, K2L25, SC23K2, SC23SC, T6L31, 25-M31W, K2_BUS, SC23, SS3-K, K2L31, K2L21, TEMPSS6,T14, T14-HT14, T14-SS1, T14-W2,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1 | 1-00238602 Rev. #4,1-00216496 Rev. #13,1-00237189 Rev. #8,1-00237186 Rev. #4,1-00238468 Rev. #3,1-00181626 Rev. #19,1-00220299 Rev. #39 | 4 Hour(s),4 Hour(s),4 Hour(s),2 Day(s),8 Hour(s),4 Hour(s),Non-recallable | FABCW | 2350
2024-06-27 17:00 | 2024-07-03 07:00 | MIDDLEPORT TS,LAMBTON TS 2,CLAIREVILLE TS | T6, T6-LT6, T6-TL581, LT6BUS-TEMP1,K2L28, L27L28, P2L27, 27-L28C, 27-L27V,T14, T14-HT14, T14-SS1, T14-W2,K1K2, K2L25, SC23K2, SC23SC, T6L31, 25-M31W, K2_BUS, SC23, SS3-K, K2L31, K2L21, TEMPSS6 | 1-00220299 Rev. #39,1-00216465 Rev. #12,1-00181626 Rev. #19,1-00238468 Rev. #3 | Non-recallable,4 Hour(s),4 Hour(s),8 Hour(s) | FABCW | 250
2024-07-08 07:00 | 2024-07-16 12:00 | MIDDLEPORT TS,MILTON SS, TRAFALGAR TS,BRUCE A TS, UNDERWOOD JCT, HANOVER TS, UNDERWOOD WGS,BURLINGTON TS, BURLINGTON JCT, MIDDLEPORT TS, CARLUKE JCT, NEALE JCT, BURLINGTON DESN TS, BECK 2 TS, NIAGARA WEST JCT,GRAND JCT, NANTICOKE TS, HORNING JCT, HORNING TS,LAMBTON TS 2 | T6, T6-LT6, T6-TL581, LT6BUS-TEMP1,M573T.MIXTR, HL573, L502L573, 40-M573T, T15-M573T,B4V.BRXUN, B4V.UNXUN, T4A, 21-B4V, 36B4V-22, 7014B5V-MSO2, 36T4-B4V,Q25BM.BEXNI, Q25BM.BUXBD, Q25BM.BUXBU, Q25BM.MIXCA, Q25BM.NEXBU, 25-Q25BM, 28-Q25BM, 39-Q25BM, T15-Q25BM,59-N5M, 310N5M-LC1,M27B.HOXBU, M27B.HOXHO, M27B.HOXMI, 25-M27B, 39-M27B, 4T4-M27B,K2L28, L27L28, P2L27, 27-L28C, 27-L27V | 1-00220299 Rev. #39,1-00208773 Rev. #10,1-00241125 Rev. #2,1-00238418 Rev. #3,1-00238444 Rev. #7,1-00238499 Rev. #3,1-00216465 Rev. #12 | Non-recallable,14 Day(s),10 Hour(s),6 Hour(s),10 Hour(s),6 Hour(s),4 Hour(s) | FABCW | 550
2024-07-26 17:00 | 2024-08-01 17:00 | BURLINGTON TS, BURLINGTON JCT, MIDDLEPORT TS, CARLUKE JCT, NEALE JCT, BURLINGTON DESN TS, BECK 2 TS, NIAGARA WEST JCT,LAMBTON TS 2,EAST LAKE ST. CLAIR WF JCT, LAMBTON TS 2,MILTON SS, TRAFALGAR TS,CALEDONIA TS, GRAND JCT, HORNING JCT, HORNING TS,MIDDLEPORT TS | Q25BM.BEXNI, Q25BM.BUXBD, Q25BM.BUXBU, Q25BM.MIXCA, Q25BM.NEXBU, 25-Q25BM, 28-Q25BM, 39-Q25BM, T15-Q25BM,KL25, L25L29, PL29, 27-L25V, 27-L29C, L25V-TEMP1,27-L29C, NA300L29C-2,M573T.MIXTR, HL573, L502L573, 40-M573T, T15-M573T,T2Y, 25-N5M, T2, N27T2-N5M, 310N5M-LC2,M28B.HOXBU, M28B.HOXHO, M28B.HOXMI, 25-M28B, 39-M28B, 4T3-M28B,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1 | 1-00238418 Rev. #3,1-00239852 Rev. #2,1-00239849 Rev. #5,1-00208773 Rev. #10,1-00238512 Rev. #2,1-00238498 Rev. #3,1-00220299 Rev. #39 | 6 Hour(s),4 Hour(s),12 Hour(s),14 Day(s),10 Hour(s),6 Hour(s),Non-recallable | FABCW | 150
2024-08-11 06:00 | 2024-08-16 08:00 | MILTON SS, TRAFALGAR TS,BRUCE A TS, UNDERWOOD JCT, HANOVER TS, UNDERWOOD WGS,BURLINGTON TS, HORNING JCT, HORNING TS, MIDDLEPORT TS,CALEDONIA TS, GRAND JCT,LAMBTON TS 2, ST. CLAIRX TS,MIDDLEPORT TS | M573T.MIXTR, HL573, L502L573, 40-M573T, T15-M573T,B4V.BRXUN, B4V.UNXUN, T4A, 21-B4V, 36B4V-22, 7014B5V-MSO2, 36T4-B4V,M28B.HOXBU, M28B.HOXHO, M28B.HOXMI, 25-M28B, 39-M28B, 4T3-M28B,T2Y, 25-N5M, T2, N27T2-N5M, 310N5M-LC2,L51D.CLXLA, K1L51, L23L51, PS51-2, PS51-1, PS51-S, PS51,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1 | 1-00208773 Rev. #10,1-00241126 Rev. #2,1-00238498 Rev. #3,1-00238512 Rev. #2,1-00235998 Rev. #3,1-00220299 Rev. #39 | 14 Day(s),10 Hour(s),6 Hour(s),10 Hour(s),4 Hour(s),Non-recallable | FABCW | 550
2024-08-29 17:00 | 2024-09-06 16:00 | BRUCE A TS, BRUCE JCT, WILLOW CREEK JCT, CLAIREVILLE TS, MILTON SS, OWEN SOUND TS,MIDDLEPORT TS, NANTICOKE TS | B560V.BRXBR, B560V.BRXMI, B560V.BRXWI, B560V.MIXCL, DL560, L553L560, 21-B560V, 51-B560V,B27S.BRXOW, T3-B27S, T5-B27S, 21-B27S,M585M.MIXMD, N581M.MDXNA, L81L85, T6L31, 25-M585M, 25-N581M, 40-M585M, 59-N581M, L581_BUS, T6, T6-LT6, T6-TL581, L23HT6,T6, LT6BUS-TEMP1,N581M.MDXNA, AL581, T7L581, T7T12, HT7_BUS | 1-00238565 Rev. #4,1-00241124 Rev. #4,1-00195970 Rev. #14,1-00238566 Rev. #2,1-00238464 Rev. #2,1-00220299 Rev. #39,1-00238492 Rev. #2,1-00238434 Rev. #2,1-00238433 Rev. #2 | 4 Hour(s),4 Hour(s),4 Day(s),4 Hour(s),Non-recallable,Non-recallable,Non-recallable,Non-recallable,Non-recallable | FABCW | 2350
2024-09-16 08:00 | 2024-09-27 15:00 | MIDDLEPORT TS, NANTICOKE TS,ESSA TS, MILTON SS,BEACH TS, HANNON JCT, DOFASCO KENILWORTH CTS, BECK 2 TS, MIDDLEPORT TS, NEBO JCT, HAMILTON NEBO TS,BRUCE A TS, BRUCE JCT, WILLOW CREEK JCT, CLAIREVILLE TS | N581M.MDXNA, AL581, T7L581, T7T12, 25-N581M, 59-N581M, HT7_BUS,HT4, R4N, HT4L29, HT4_BUS, T4, R4, T4-D, T4-HT4, TSS4,M585M.MIXMD, 25-M585M, 40-M585M,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1, N581M.MDXNA, L81L85, T6L31, L581_BUS, T6, L23HT6,Q24HM.HAXBE, Q24HM.HAXHA, Q24HM.HAXKE, Q24HM.HNXHA, Q24HM.HNXHN, Q24HM.HNXMI, 157T1-Q24HM, 17-Q24HM, 17-Q29HM, 25-Q24HM, 28-Q24HM, T3-Q24HM, 61Q29HM-LC,B560V.BRXBR, B560V.BRXMI, B560V.BRXWI, B560V.MIXCL, 21-B560V, 51-B560V, DL560, L553L560 | 1-00238433 Rev. #2,1-00246166 Rev. #1,1-00238434 Rev. #2,1-00238492 Rev. #2,1-00220299 Rev. #39,1-00238464 Rev. #2,1-00238421 Rev. #2,1-00238566 Rev. #2,1-00195970 Rev. #14 | Non-recallable,4 Hour(s),Non-recallable,Non-recallable,Non-recallable,Non-recallable,10 Hour(s),4 Hour(s),4 Day(s) | FABCW | 2350
2024-11-04 08:00 | 2024-11-15 17:00 | MIDDLEPORT TS, MILTON SS, NANTICOKE TS,BECK 2 TS,CLAIREVILLE TS, ESSA TS,KENT TS, CHATHAM SS, GSPC JCT,BRUCE A TS, UNDERWOOD JCT, HANOVER TS, UNDERWOOD WGS | M585M.MIXMD, N581M.MDXNA, L81L85, T6L31, 25-M585M, 25-N581M, 40-M585M, 59-N581M, L581_BUS, T6, T6-LT6, T6-TL581, L23HT6,28-PA302, T302, T302-1,N581M.MDXNA, AL581, T7L581, T7T12, HT7_BUS,E511V.CLXES, DL511, W2L511, 18-E511V, 51-E511V,T1B, T1Y, T4Z, 5-L28C, 86-L28C, T1, T4, T1-L28C, T4L28C, 312L28C-MSO2,B4V.BRXUN, B4V.UNXUN, T4A, 21-B4V, 36B4V-22, 36T4-B4V, 161B5V-MSO1, 21-B5V | 1-00238465 Rev. #1,1-00238560 Rev. #1,1-00238433 Rev. #2,1-00238434 Rev. #2,1-00238492 Rev. #2,1-00238538 Rev. #1,1-00240028 Rev. #2,1-00241127 Rev. #1 | 4 Hour(s),8 Hour(s),Non-recallable,Non-recallable,Non-recallable,48 Hour(s),12 Hour(s),10 Hour(s) | FABCW | 1000
2024-11-17 07:15 | 2024-11-28 17:00 | BRUCE A TS, MAJESTIC JCT, MAJESTIC CTS, WINGHAM JCT, SEAFORTH TS, WINGHAM TS,MIDDLEPORT TS, MILTON SS, NANTICOKE TS,BECK 2 TS,CLAIREVILLE TS, ESSA TS,KENT TS, CHATHAM SS, GSPC JCT | B23D.MJXBR, B23D.MJXMJ, B23D.MJXWI, B23D.WIXSE, B23D.WIXWI, T2-B23D, 21-B23D, 61B23D-21,M585M.MIXMD, N581M.MDXNA, L81L85, T6L31, 25-M585M, 25-N581M, 40-M585M, 59-N581M, L581_BUS, T6, T6-LT6, T6-TL581, L23HT6,N581M.MDXNA, AL581, T7L581, T7T12, HT7_BUS,28-PA302, T302, T302-1,E511V.CLXES, DL511, W2L511, 18-E511V, 51-E511V,T1B, T1Y, T4Z, 5-L28C, 86-L28C, T1, T4, T1-L28C, T4L28C, 312L28C-MSO2 | 1-00241121 Rev. #1,1-00238465 Rev. #1,1-00238433 Rev. #2,1-00238560 Rev. #1,1-00238434 Rev. #2,1-00238492 Rev. #2,1-00238538 Rev. #1,1-00240028 Rev. #2 | 4 Hour(s),4 Hour(s),Non-recallable,8 Hour(s),Non-recallable,Non-recallable,48 Hour(s),12 Hour(s) | FABCW | 800
2024-12-06 16:00 | 2024-12-12 17:00 | BRUCE A TS, BRUCE JCT, MILTON SS, WILLOW CREEK JCT,MIDDLEPORT TS, NANTICOKE TS | B502M.BAXBJ, B502M.BJXMI, B502M.BJXWJ, 21-B502M, 40-B502M,N581M.MDXNA, AL581, T7L581, T7T12, 25-N581M, 59-N581M, HT7_BUS,M585M.MIXMD, N581M.MDXNA, L81L85, T6L31, 25-M585M, 40-M585M, L581_BUS, T6, T6-LT6, T6-TL581, L23HT6 | 1-00238570 Rev. #1,1-00238433 Rev. #2,1-00238465 Rev. #1 | 4 Hour(s),Non-recallable,4 Hour(s) | FABCW | 2350
2024-12-12 17:00 | 2024-12-18 17:00 | MIDDLEPORT TS, NANTICOKE TS, MILTON SS | N581M.MDXNA, AL581, T7L581, T7T12, 25-N581M, 59-N581M, HT7_BUS,M585M.MIXMD, N581M.MDXNA, L81L85, T6L31, 25-M585M, 40-M585M, L581_BUS, T6, T6-LT6, T6-TL581, L23HT6 | 1-00238433 Rev. #2,1-00238465 Rev. #1 | Non-recallable,4 Hour(s) | FABCW | 600
2024-03-30 04:30 | 2024-05-10 17:00 | CHURCHILL MEADOWS TS, CHURCHILL MEADOWS JCT, TRAFALGAR TS, ERINDALE JCT, HANLAN JCT, ERINDALE TS, HURONTARIO SS, RICHVIEW TS, TOMKEN JCT, TOMKEN TS | R19TH.CHXTR, R19TH.ERXCH, R19TH.ERXER, R19TH.ERXHA, R19TH.HAXHU, R19TH.TOXRI, R19TH.TOXTO, L19L29, 240T2-R19TH, 31-R19TH, 5T6-R19TH, 88-R19TH, L19L29-L19, T3-R19TH | 1-00238480 Rev. #8 | 36 Hour(s)
2024-07-21 07:00 | 2024-08-01 17:00 | BEAVER JCT, BROWN HILL TS, BEAVERTON JCT, LINDSAY TS, MINDEN TS, BEAVERTON TS,CHURCHILL MEADOWS TS, CHURCHILL MEADOWS JCT, TRAFALGAR TS, ERINDALE JCT, HANLAN JCT, ERINDALE TS, HURONTARIO SS, RICHVIEW TS, TOMKEN JCT, TOMKEN TS | M81B.BEXBE, M81B.BEXBV, M81B.BSXBE, M81B.BVXLI, M81B.BVXMI, L81L89, 4T1-M81B, 87-M81B, T4-M81B,R19TH.CHXTR, R19TH.ERXCH, R19TH.ERXER, R19TH.ERXHA, R19TH.HAXHU, R19TH.TOXRI, R19TH.TOXTO, L19L29, 240T2-R19TH, 31-R19TH, 5T6-R19TH, 88-R19TH, L19L29-L19, T3-R19TH | 1-00238590 Rev. #4,1-00238484 Rev. #4 | 4 Hour(s),36 Hour(s)
2024-08-01 17:00 | 2024-08-16 17:00 | CHURCHILL MEADOWS TS, CHURCHILL MEADOWS JCT, TRAFALGAR TS, ERINDALE JCT, HANLAN JCT, ERINDALE TS, HURONTARIO SS, RICHVIEW TS, TOMKEN JCT, TOMKEN TS | R19TH.CHXTR, R19TH.ERXCH, R19TH.ERXER, R19TH.ERXHA, R19TH.HAXHU, R19TH.TOXRI, R19TH.TOXTO, L19L29, 240T2-R19TH, 31-R19TH, 5T6-R19TH, 88-R19TH, L19L29-L19, T3-R19TH | 1-00238484 Rev. #4 | 36 Hour(s)
2024-10-15 07:00 | 2024-10-25 16:00 | CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,BEAVER JCT, BROWN HILL TS, BEAVERTON JCT, LINDSAY TS, MINDEN TS, BEAVERTON TS | C553VP.CHXPJ, C553VP.PJXCL, C553VP.PJXPR, A2L553, L553L560, 51-C553VP, 52-C553VP, 81-C553VP,M80B.BEXBE, M80B.BEXBV, M80B.BSXBE, M80B.BVXLI, M80B.BVXMI, L80L88, 4T2-M80B, 87-M80B, T3-M80B | 1-00238550 Rev. #2,1-00239109 Rev. #4 | 4 Hour(s),4 Hour(s) | FABCW | 200
2024-11-17 07:00 | 2024-12-14 17:00 | CHURCHILL MEADOWS JCT, TRAFALGAR TS | 31-R19TH, 31-R21TH, 241R21TH-TEMP10 | 1-00238405 Rev. #1 | 36 Hour(s)
2024-04-14 16:00 | 2024-04-19 17:00 | LAMBTON TS 2,KENT TS, CHATHAM SS, GSPC JCT,MIDDLEPORT TS,BRUCE A TS, BRUCE JCT, MILTON SS, WILLOW CREEK JCT | 27-T8, 27T8-L4D, T8,T1B, T1Y, T4Z, 5-L28C, 86-L28C, T1, T4, T1-L28C, T4L28C, 312L28C-MSO2,27-T7, 27-T8, T7, T7-L4D,D1D2, D1L29, D1L27, L33L40, SC22D1, SC22SC, 25-M33W, D1_BUS, SC22, SS2-D, D1L34, D1L33,B502M.BAXBJ, B502M.BJXMI, B502M.BJXWJ, 21-B502M, 40-B502M | 1-00240619 Rev. #5,1-00238919 Rev. #6,1-00231342 Rev. #12,1-00234253 Rev. #9,1-00238390 Rev. #3,1-00235814 Rev. #13 | 14 Day(s),12 Hour(s),4 Hour(s),Non-recallable,2 Hour(s),4 Hour(s) | FABCW | 1750
2024-04-19 18:00 | 2024-04-27 07:15 | LAMBTON TS 2,BRUCE B SS, BRUCE JCT, WILLOW CREEK JCT, MILTON SS,KENT TS, CHATHAM SS, GSPC JCT | 27-T7, 27-T8, 27T8-L4D, T7, T8, T7-L4D,B501M.BBXBJ, B501M.BJXWJ, B501M.WJXMI, 40-B501M, 29-B501M,27-T8,T1B, T1Y, T4Z, 5-L28C, 86-L28C, T1, T4, T1-L28C, T4L28C, 312L28C-MSO2 | 1-00234253 Rev. #9,1-00237165 Rev. #9,1-00231342 Rev. #12,1-00240619 Rev. #5,1-00238919 Rev. #6 | Non-recallable,4 Hour(s),4 Hour(s),14 Day(s),12 Hour(s) | FABCW | 1750
2024-05-19 17:00 | 2024-05-31 17:00 | BRUCE B SS, BRUCE JCT, WILLOW CREEK JCT, MILTON SS,LAMBTON TS 2,LONGWOOD DESN, LAMBTON TS 2, LONGWOOD JCT, LONGWOOD TS | B501M.BBXBJ, B501M.BJXWJ, B501M.WJXMI, 40-B501M, 29-B501M,27-T7, 27-T8, 27T8-L4D, T7, T8, T7-L4D,27-T8,L24L.LOXLA, L24L.LOXLD, L24L.LOXLO, AL24, T14Q, T3L24, 27-L24L, T14, T14-L24L, W52-L24L | 1-00237165 Rev. #9,1-00234253 Rev. #9,1-00231342 Rev. #12,1-00236074 Rev. #16,1-00240619 Rev. #5 | 4 Hour(s),Non-recallable,4 Hour(s),8 Day(s),14 Day(s) | FABCW | 1850
2024-08-26 08:00 | 2024-09-06 16:00 | BRUCE A TS, BRUCE JCT, WILLOW CREEK JCT, CLAIREVILLE TS, MILTON SS | B560V.BRXBR, B560V.BRXMI, B560V.BRXWI, B560V.MIXCL, DL560, L553L560, 21-B560V, 51-B560V | 1-00238565 Rev. #4,1-00195970 Rev. #14,1-00238566 Rev. #2 | 4 Hour(s),4 Day(s),4 Hour(s) | FABCW | 1750
2024-09-06 16:00 | 2024-09-27 15:00 | BRUCE A TS, BRUCE JCT, WILLOW CREEK JCT, CLAIREVILLE TS, MILTON SS | B560V.BRXBR, B560V.BRXMI, B560V.BRXWI, B560V.MIXCL, DL560, L553L560, 21-B560V, 51-B560V | 1-00195970 Rev. #14,1-00238566 Rev. #2 | 4 Day(s),4 Hour(s) | FABCW | 1750
2024-12-01 08:00 | 2024-12-12 17:00 | BRUCE A TS, BRUCE JCT, MILTON SS, WILLOW CREEK JCT | B502M.BAXBJ, B502M.BJXMI, B502M.BJXWJ, 21-B502M, 40-B502M | 1-00238570 Rev. #1 | 4 Hour(s) | FABCW | 1750
2023-11-07 16:00 | 2024-03-24 16:00 | CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS | C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550 | 1-00213473 Rev. #37 | Non-recallable | FABCW | 200
2024-03-30 04:30 | 2024-04-05 16:00 | CLAIREVILLE TS,CHURCHILL MEADOWS TS, CHURCHILL MEADOWS JCT, TRAFALGAR TS, ERINDALE JCT, HANLAN JCT, ERINDALE TS, HURONTARIO SS, RICHVIEW TS, TOMKEN JCT, TOMKEN TS, ESSA TS,CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,PALERMO TS, BURLINGTON TS, GLENORCHY JCT, LANTZ JCT, PALERMO TXB JCT, GLENORCHY MTS1 | AL510, W3L510, 51-E510V,R19TH.CHXTR, R19TH.ERXCH, R19TH.ERXER, R19TH.ERXHA, R19TH.HAXHU, R19TH.TOXRI, R19TH.TOXTO, L19L29, 240T2-R19TH, 31-R19TH, 5T6-R19TH, 88-R19TH, L19L29-L19, T3-R19TH,E510V.CLXES, AL510, 18-E510V,C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,T37B.GJXGL, T37B.GJXLA, T37B.PAXBU, T37B.PAXTR, T37B.PJXGJ, T4Y, 31-T37B, 31SC21L-T36B, 31SC21L-T37B, 39-T37B, T4, T4-T37B | 1-00238545 Rev. #4,1-00238480 Rev. #8,1-00235682 Rev. #6,1-00213473 Rev. #37,1-00226775 Rev. #13,1-00238540 Rev. #3 | 5 Day(s),36 Hour(s),14 Day(s),Non-recallable,6 Hour(s),48 Hour(s) | FABCW | 200
2024-04-12 16:00 | 2024-05-03 17:00 | CLAIREVILLE TS, ESSA TS,CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,CHURCHILL MEADOWS TS, CHURCHILL MEADOWS JCT, TRAFALGAR TS, ERINDALE JCT, HANLAN JCT, ERINDALE TS, HURONTARIO SS, RICHVIEW TS, TOMKEN JCT, TOMKEN TS | E510V.CLXES, AL510, W3L510, 18-E510V, 51-E510V,C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,R19TH.CHXTR, R19TH.ERXCH, R19TH.ERXER, R19TH.ERXHA, R19TH.HAXHU, R19TH.TOXRI, R19TH.TOXTO, L19L29, 240T2-R19TH, 31-R19TH, 5T6-R19TH, 88-R19TH, L19L29-L19, T3-R19TH | 1-00235682 Rev. #6,1-00213473 Rev. #37,1-00238480 Rev. #8 | 14 Day(s),Non-recallable,36 Hour(s) | FABCW | 200
2024-05-05 06:00 | 2024-05-10 17:00 | CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,CHURCHILL MEADOWS TS, CHURCHILL MEADOWS JCT, TRAFALGAR TS, ERINDALE JCT, HANLAN JCT, ERINDALE TS, HURONTARIO SS, RICHVIEW TS, TOMKEN JCT, TOMKEN TS | C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550, 51-C550VP, 52-C550VP, 81-C550VP,R19TH.CHXTR, R19TH.ERXCH, R19TH.ERXER, R19TH.ERXHA, R19TH.HAXHU, R19TH.TOXRI, R19TH.TOXTO, L19L29, 240T2-R19TH, 31-R19TH, 5T6-R19TH, 88-R19TH, L19L29-L19, T3-R19TH | 1-00213473 Rev. #37,1-00236150 Rev. #5,1-00238480 Rev. #8 | Non-recallable,4 Hour(s),36 Hour(s) | FABCW | 200
2024-06-21 17:00 | 2024-06-27 17:00 | BRUCE B SS, BRUCE JCT, WILLOW CREEK JCT, MILTON SS,PARKWAY TS,CLAIREVILLE TS,CHURCHILL MEADOWS TS, ERINDALE JCT, CHURCHILL MEADOWS JCT, HANLAN JCT, ERINDALE TS, TOMKEN JCT, HURONTARIO SS, JIM YARROW MTS, RICHVIEW TS, TOMKEN TS, TRAFALGAR TS | B561M.BBXBR, B561M.BRXWI, B561M.WIXMI, 40-B561M, 29-B561M, KL561, L61L71,T3, SS1-T3, T3-HT3, T3-LT3,T14, T14-HT14, T14-SS1, T14-W2,R21TH.CHXTR, R21TH.ERXCH, R21TH.ERXER, R21TH.ERXHA, R21TH.HAXHU, R21TH.HAXTO, R21TH.HUXHA, R21TH.HUXJM, R21TH.TOXRI, R21TH.TOXTO, L21L30, 162-R21TH, 240T1-R21TH, 31-R21TH, 5T5-R21TH, 88-R21TH, T4-R21TH | 1-00237189 Rev. #8,1-00237186 Rev. #4,1-00239147 Rev. #3,1-00181626 Rev. #19,1-00238414 Rev. #3 | 4 Hour(s),2 Day(s),3 Hour(s),4 Hour(s),36 Hour(s) | FABCW | 2150
2024-07-08 07:00 | 2024-07-19 17:00 | CHURCHILL MEADOWS TS, ERINDALE JCT, CHURCHILL MEADOWS JCT, HANLAN JCT, ERINDALE TS, TOMKEN JCT, HURONTARIO SS, JIM YARROW MTS, RICHVIEW TS, TOMKEN TS, TRAFALGAR TS,MILTON SS | R21TH.CHXTR, R21TH.ERXCH, R21TH.ERXER, R21TH.ERXHA, R21TH.HAXHU, R21TH.HAXTO, R21TH.HUXHA, R21TH.HUXJM, R21TH.TOXRI, R21TH.TOXTO, L21L30, 162-R21TH, 240T1-R21TH, 31-R21TH, 5T5-R21TH, 88-R21TH, T4-R21TH,M573T.MIXTR, HL573, L502L573, 40-M573T, T15-M573T | 1-00238414 Rev. #3,1-00208773 Rev. #10 | 36 Hour(s),14 Day(s) | FABCW | 150
2024-07-21 07:00 | 2024-08-16 08:00 | MILTON SS, TRAFALGAR TS,CHURCHILL MEADOWS TS, CHURCHILL MEADOWS JCT, ERINDALE JCT, HANLAN JCT, ERINDALE TS, HURONTARIO SS, RICHVIEW TS, TOMKEN JCT, TOMKEN TS | M573T.MIXTR, HL573, L502L573, 40-M573T, T15-M573T,R19TH.CHXTR, R19TH.ERXCH, R19TH.ERXER, R19TH.ERXHA, R19TH.HAXHU, R19TH.TOXRI, R19TH.TOXTO, L19L29, 240T2-R19TH, 31-R19TH, 5T6-R19TH, 88-R19TH, L19L29-L19, T3-R19TH | 1-00208773 Rev. #10,1-00238484 Rev. #4 | 14 Day(s),36 Hour(s) | FABCW | 150
2024-08-26 07:00 | 2024-09-06 16:00 | BRUCE A TS, BRUCE JCT, WILLOW CREEK JCT, CLAIREVILLE TS, MILTON SS,MIDDLEPORT TS, NANTICOKE TS | B560V.BRXBR, B560V.BRXMI, B560V.BRXWI, B560V.MIXCL, DL560, L553L560, 21-B560V, 51-B560V,N581M.MDXNA, AL581, T7L581, 25-N581M, 59-N581M, T7T12, HT7_BUS,M585M.MIXMD, 25-M585M, 40-M585M, N581M.MDXNA, L81L85, T6L31, L581_BUS, T6, T6-LT6, T6-TL581, L23HT6 | 1-00238565 Rev. #4,1-00238434 Rev. #2,1-00238433 Rev. #2,1-00238492 Rev. #2,1-00238464 Rev. #2,1-00238566 Rev. #2,1-00195970 Rev. #14 | 4 Hour(s),Non-recallable,Non-recallable,Non-recallable,Non-recallable,4 Hour(s),4 Day(s) | FABCW | 2350
2024-09-06 16:00 | 2024-09-27 15:00 | BRUCE A TS, BRUCE JCT, WILLOW CREEK JCT, CLAIREVILLE TS, MILTON SS,MIDDLEPORT TS, NANTICOKE TS | B560V.BRXBR, B560V.BRXMI, B560V.BRXWI, B560V.MIXCL, DL560, L553L560, 21-B560V, 51-B560V,N581M.MDXNA, AL581, T7L581, 25-N581M, 59-N581M, T7T12, HT7_BUS,M585M.MIXMD, 25-M585M, 40-M585M, N581M.MDXNA, L81L85, T6L31, L581_BUS, T6, T6-LT6, T6-TL581, L23HT6 | 1-00195970 Rev. #14,1-00238434 Rev. #2,1-00238433 Rev. #2,1-00238492 Rev. #2,1-00238464 Rev. #2,1-00238566 Rev. #2 | 4 Day(s),Non-recallable,Non-recallable,Non-recallable,Non-recallable,4 Hour(s) | FABCW | 2350
2024-09-27 17:00 | 2024-10-07 06:00 | MIDDLEPORT TS, NANTICOKE TS, MILTON SS | N581M.MDXNA, AL581, T7L581, 25-N581M, 59-N581M, T7T12, HT7_BUS,M585M.MIXMD, 25-M585M, 40-M585M, N581M.MDXNA, L81L85, T6L31, L581_BUS, T6, T6-LT6, T6-TL581, L23HT6 | 1-00238434 Rev. #2,1-00238433 Rev. #2,1-00238492 Rev. #2,1-00238464 Rev. #2 | Non-recallable,Non-recallable,Non-recallable,Non-recallable | FABCW | 600
2024-10-07 06:00 | 2024-10-15 07:00 | MIDDLEPORT TS, MILTON SS, NANTICOKE TS,ASHFIELD SS, BRUCE B SS, BRUCE JCT, WILLOW CREEK JCT | M585M.MIXMD, N581M.MDXNA, L81L85, T6L31, 25-M585M, 25-N581M, 40-M585M, 59-N581M, L581_BUS, T6, T6-LT6, T6-TL581, L23HT6,N581M.MDXNA, AL581, T7L581, T7T12, HT7_BUS,B563A.BBXBJ, B563A.BJWJ, B563A.WJXAS, OLDH5L563, OLDL501L563, L563L592, L563L565, OLD29-B563A, 322-B563A, L563_BUS, H5L563, L501L563, 29-B563A | 1-00238464 Rev. #2,1-00238492 Rev. #2,1-00238433 Rev. #2,1-00238434 Rev. #2,1-00241110 Rev. #2 | Non-recallable,Non-recallable,Non-recallable,Non-recallable,6 Hour(s) | FABCW | 850
2024-10-18 07:00 | 2024-10-25 16:00 | CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,MIDDLEPORT TS, NANTICOKE TS, MILTON SS,PARKWAY TS | C553VP.CHXPJ, C553VP.PJXCL, C553VP.PJXPR, A2L553, L553L560, 51-C553VP, 52-C553VP, 81-C553VP,N581M.MDXNA, AL581, T7L581, 25-N581M, 59-N581M, T7T12, HT7_BUS,M585M.MIXMD, 25-M585M, 40-M585M, N581M.MDXNA, L81L85, T6L31, L581_BUS, T6, T6-LT6, T6-TL581, L23HT6,SS1, T3, SS1-T3, T3-HT3, T3-LT3 | 1-00238550 Rev. #2,1-00238434 Rev. #2,1-00238433 Rev. #2,1-00238492 Rev. #2,1-00238464 Rev. #2,1-00246737 Rev. #3 | 4 Hour(s),Non-recallable,Non-recallable,Non-recallable,Non-recallable,8 Hour(s) | FABCW | 800
2024-11-06 17:00 | 2024-11-12 07:00 | MIDDLEPORT TS, MILTON SS, NANTICOKE TS,CLAIREVILLE TS, ESSA TS | M585M.MIXMD, N581M.MDXNA, L81L85, T6L31, 25-M585M, 25-N581M, 40-M585M, 59-N581M, L581_BUS, T6, T6-LT6, T6-TL581, L23HT6,N581M.MDXNA, AL581, T7L581, T7T12, HT7_BUS,E511V.CLXES, DL511, W2L511, 18-E511V, 51-E511V | 1-00238465 Rev. #1,1-00238433 Rev. #2,1-00238434 Rev. #2,1-00238492 Rev. #2,1-00238538 Rev. #1 | 4 Hour(s),Non-recallable,Non-recallable,Non-recallable,48 Hour(s) | FABCW | 600
2024-11-12 07:00 | 2024-11-29 17:00 | PARKWAY TS,MIDDLEPORT TS, MILTON SS, NANTICOKE TS,CLAIREVILLE TS, ESSA TS | SS4, T4, SS4-T4, T4-HT4, T4-LT4,M585M.MIXMD, N581M.MDXNA, L81L85, T6L31, 25-M585M, 25-N581M, 40-M585M, 59-N581M, L581_BUS, T6, T6-LT6, T6-TL581, L23HT6,N581M.MDXNA, AL581, T7L581, T7T12, HT7_BUS,E511V.CLXES, DL511, W2L511, 18-E511V, 51-E511V | 1-00246738 Rev. #2,1-00238465 Rev. #1,1-00238433 Rev. #2,1-00238434 Rev. #2,1-00238492 Rev. #2,1-00238538 Rev. #1 | 8 Hour(s),4 Hour(s),Non-recallable,Non-recallable,Non-recallable,48 Hour(s) | FABCW | 600
2024-12-01 17:00 | 2024-12-18 17:00 | MIDDLEPORT TS, NANTICOKE TS, MILTON SS | N581M.MDXNA, AL581, T7L581, T7T12, 25-N581M, 59-N581M, HT7_BUS,M585M.MIXMD, N581M.MDXNA, L81L85, T6L31, 25-M585M, 40-M585M, L581_BUS, T6, T6-LT6, T6-TL581, L23HT6 | 1-00238433 Rev. #2,1-00238465 Rev. #1 | Non-recallable,4 Hour(s) | FABCW | 600
2024-09-03 07:00 | 2024-09-08 14:00 | CLARINGTON TS, HAVELOCK TS, MARINE JCT, OTONABEE TS | 128T1-T31H, L23L31, P2L31, 296-T31H, L31_BUS, T31H.HAXMJ, T31H.MJXCL, T31H.MJXOT, 57-T31H | 1-00239080 Rev. #5 | 4 Hour(s)
2024-09-08 14:00 | 2024-09-13 17:00 | CLARINGTON TS, HAVELOCK TS, MARINE JCT, OTONABEE TS,HAWTHORNE TS | 128T1-T31H, L23L31, P2L31, 296-T31H, L31_BUS, T31H.HAXMJ, T31H.MJXCL, T31H.MJXOT, 57-T31H,HT1P1, T2L523, HT2-P2, T2, P1-P2, R2-T2, T2-HT2, T2-LT2 | 1-00239080 Rev. #5,1-00208490 Rev. #7 | 4 Hour(s),6 Hour(s)
2024-10-07 07:00 | 2024-10-25 09:30 | HAWTHORNE TS,CHATS FALLS TS, HAVELOCK TS, CLARINGTON TS, MARINE JCT | HT1P1, T2L523, HT2-P2, T2, P1-P2, R2-T2, T2-HT2, T2-LT2,C25H.HAXCF, 2-C25H, 57-C25H, HT3L32, K2L32, 296-T32H, L32_BUS, T32H.HAXMJ, T32H.MJXCL, 57-T32H | 1-00208490 Rev. #7,1-00239126 Rev. #4 | 6 Hour(s),4 Hour(s)
2024-10-25 09:30 | 2024-12-19 17:00 | CHATS FALLS TS, HAVELOCK TS, CLARINGTON TS, MARINE JCT | C25H.HAXCF, 2-C25H, 57-C25H, HT3L32, K2L32, 296-T32H, L32_BUS, T32H.HAXMJ, T32H.MJXCL, 57-T32H | 1-00239126 Rev. #4 | 4 Hour(s)
2024-03-25 07:00 | 2024-04-05 16:00 | CLAIREVILLE TS, ESSA TS | AL510, W3L510, 51-E510V,E510V.CLXES, AL510, 18-E510V | 1-00238545 Rev. #4,1-00235682 Rev. #6,1-00238540 Rev. #3 | 5 Day(s),14 Day(s),48 Hour(s)
2024-04-05 17:00 | 2024-05-03 17:00 | CLAIREVILLE TS, ESSA TS | E510V.CLXES, AL510, W3L510, 18-E510V, 51-E510V | 1-00235682 Rev. #6 | 14 Day(s)
2024-10-28 07:00 | 2024-11-03 17:00 | CLAIREVILLE TS, ESSA TS | E511V.CLXES, 18-E511V, 51-E511V, DL511, W2L511 | 1-00241567 Rev. #1,1-00238538 Rev. #1 | 4 Hour(s),48 Hour(s)
2024-11-03 17:00 | 2024-11-29 17:00 | CLAIREVILLE TS, ESSA TS | E511V.CLXES, DL511, W2L511, 18-E511V, 51-E511V | 1-00238538 Rev. #1 | 48 Hour(s)
2024-03-25 07:00 | 2024-04-05 16:00 | CLAIREVILLE TS, ESSA TS | AL510, W3L510, 51-E510V,E510V.CLXES, AL510, 18-E510V | 1-00238545 Rev. #4,1-00235682 Rev. #6,1-00238540 Rev. #3 | 5 Day(s),14 Day(s),48 Hour(s)
2024-04-05 17:00 | 2024-05-03 17:00 | CLAIREVILLE TS, ESSA TS | E510V.CLXES, AL510, W3L510, 18-E510V, 51-E510V | 1-00235682 Rev. #6 | 14 Day(s)
2024-10-28 07:00 | 2024-11-03 17:00 | CLAIREVILLE TS, ESSA TS | E511V.CLXES, 18-E511V, 51-E511V, DL511, W2L511 | 1-00241567 Rev. #1,1-00238538 Rev. #1 | 4 Hour(s),48 Hour(s)
2024-11-03 17:00 | 2024-11-29 17:00 | CLAIREVILLE TS, ESSA TS | E511V.CLXES, DL511, W2L511, 18-E511V, 51-E511V | 1-00238538 Rev. #1 | 48 Hour(s)
Back to main menu

## Table C10
Back to main menu
Table C10: West Zone
Planned Start | Planned End | Station | Equipment Name | Outage ID | Max Recall | Major Transmission Interface Impacted | Reduction in Limit
2024-04-05 17:00 | 2024-04-12 16:00 | BRUCE A TS, BRUCE JCT, MILTON SS, WILLOW CREEK JCT,BRANTFORD TS, NEWPORT JCT, MIDDLEPORT TS,BECK 2 TS, MID RIVER JCT NIAGARA,MIDDLEPORT TS,CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,CLAIREVILLE TS, ESSA TS,DETWEILER TS, STRATFORD JCT, SEAFORTH TS, STRATFORD TS,LONGWOOD TS | B502M.BAXBJ, B502M.BJXMI, B502M.BJXWJ, 21-B502M, 40-B502M,M32W.NEXBR, M32W.NEXMI, YZ, 25-M32W, 44M32W-19, T4-M32W,BP76.PAXBE, K2L76, L35L76, R76, TL35-BO1,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1,C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,E510V.CLXES, AL510, W3L510, 18-E510V, 51-E510V,B22D.STXDE, B22D.STXST, 26-B22D, 68T1-B22D, 61B22D-26,R5N, T5L45, SS5, T5, R5, T5-H, T5-LT5,25-Q23BM, L23HT6, D2L23, Q23BM-TEMP1 | 1-00239284 Rev. #3,1-00238922 Rev. #11,1-00181622 Rev. #28,1-00220299 Rev. #39,1-00213473 Rev. #37,1-00235682 Rev. #6,1-00237157 Rev. #9,1-00239308 Rev. #10,1-00235814 Rev. #13,1-00246468 Rev. #2 | 8 Hour(s),6 Hour(s),Non-recallable,Non-recallable,Non-recallable,14 Day(s),4 Hour(s),5 Day(s),4 Hour(s),6 Hour(s)
2024-04-14 16:00 | 2024-04-19 16:00 | CLAIREVILLE TS, ESSA TS,KENT TS, CHATHAM SS, GSPC JCT,DETWEILER TS, STRATFORD JCT, SEAFORTH TS, STRATFORD TS,CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,MIDDLEPORT TS,BECK 2 TS, MID RIVER JCT NIAGARA,BRUCE A TS, BRUCE JCT, MILTON SS, WILLOW CREEK JCT,LONGWOOD TS | E510V.CLXES, AL510, W3L510, 18-E510V, 51-E510V,T1B, T1Y, T4Z, 5-L28C, 86-L28C, T1, T4, T1-L28C, T4L28C, 312L28C-MSO2,B22D.STXDE, B22D.STXST, 26-B22D, 68T1-B22D, 61B22D-26,C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1,BP76.PAXBE, K2L76, L35L76, R76, TL35-BO1,25-Q23BM, L23HT6, D2L23, Q23BM-TEMP1,D1D2, D1L29, D1L27, L33L40, SC22D1, SC22SC, 25-M33W, D1_BUS, SC22, SS2-D, D1L34, D1L33,B502M.BAXBJ, B502M.BJXMI, B502M.BJXWJ, 21-B502M, 40-B502M,R5N, T5L45, SS5, T5, R5, T5-H, T5-LT5 | 1-00235682 Rev. #6,1-00238919 Rev. #6,1-00237157 Rev. #9,1-00213473 Rev. #37,1-00220299 Rev. #39,1-00181622 Rev. #28,1-00246468 Rev. #2,1-00238390 Rev. #3,1-00235814 Rev. #13,1-00239308 Rev. #10 | 14 Day(s),12 Hour(s),4 Hour(s),Non-recallable,Non-recallable,Non-recallable,6 Hour(s),2 Hour(s),4 Hour(s),5 Day(s)
2024-05-26 07:00 | 2024-05-31 08:00 | ALLANBURG TS, BECK 2 TS, MID RIVER JCT NIAGARA, CROSSLINE JCT, MIDDLEPORT TS, CALEDONIA Q35M JCT,CLAIREVILLE TS,BRUCE B SS, BRUCE JCT, WILLOW CREEK JCT, MILTON SS,LONGWOOD DESN, LAMBTON TS 2, LONGWOOD JCT, LONGWOOD TS,CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,MIDDLEPORT TS,DETWEILER TS, STRATFORD TS, ZURICH JCT | BP76.PAXBE, Q35M.MIXCA, Q35M.QUXAL, D2HT4, H2HT4, K2L76, L26L35, L30TL35, L34L35, L35L76, T4, R76,W3L570, W3L510, T15, T15-HT15, T15-W3, T15-SS2,B501M.BBXBJ, B501M.BJXWJ, B501M.WJXMI, 40-B501M, 29-B501M,L24L.LOXLA, L24L.LOXLD, L24L.LOXLO, AL24, T14Q, T3L24, 27-L24L, T14, T14-L24L, W52-L24L,C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1, 51-C550VP, 52-C550VP, 81-C550VP,26-B23D, 68T2-B23D, 364B23D-MSO1 | 1-00181648 Rev. #9,1-00238525 Rev. #10,1-00237165 Rev. #9,1-00236074 Rev. #16,1-00213473 Rev. #37,1-00220299 Rev. #39,1-00236150 Rev. #5,1-00238602 Rev. #4 | 4 Hour(s),4 Hour(s),4 Hour(s),8 Day(s),Non-recallable,Non-recallable,4 Hour(s),4 Hour(s) | MICH-W-IMP MICH-W-EXP MICH-S-EXP MICH-S-IMP | 300 350 300 200
2024-06-11 16:00 | 2024-06-21 13:00 | DETWEILER TS, STRATFORD TS, ZURICH JCT,LAMBTON TS 2,BRUCE B SS, BRUCE JCT, WILLOW CREEK JCT, MILTON SS,MIDDLEPORT TS,CLAIREVILLE TS | 26-B23D, 68T2-B23D, 364B23D-MSO1,K2L28, L27L28, 27-L28C,B561M.BBXBR, B561M.BRXWI, B561M.WIXMI, 40-B561M, 29-B561M, KL561, L61L71,K1K2, K2L25, SC23K2, SC23SC, T6L31, 25-M31W, K2_BUS, SC23, SS3-K, K2L31, K2L21, TEMPSS6,T14, T14-HT14, T14-SS1, T14-W2,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1 | 1-00238602 Rev. #4,1-00216496 Rev. #13,1-00237189 Rev. #8,1-00237186 Rev. #4,1-00238468 Rev. #3,1-00181626 Rev. #19,1-00220299 Rev. #39 | 4 Hour(s),4 Hour(s),4 Hour(s),2 Day(s),8 Hour(s),4 Hour(s),Non-recallable | MICH-W-IMP MICH-W-EXP MICH-S-EXP MICH-S-IMP | 300 350 300 200
2024-06-27 17:00 | 2024-07-03 07:00 | MIDDLEPORT TS,LAMBTON TS 2,CLAIREVILLE TS | T6, T6-LT6, T6-TL581, LT6BUS-TEMP1,K2L28, L27L28, P2L27, 27-L28C, 27-L27V,T14, T14-HT14, T14-SS1, T14-W2,K1K2, K2L25, SC23K2, SC23SC, T6L31, 25-M31W, K2_BUS, SC23, SS3-K, K2L31, K2L21, TEMPSS6 | 1-00220299 Rev. #39,1-00216465 Rev. #12,1-00181626 Rev. #19,1-00238468 Rev. #3 | Non-recallable,4 Hour(s),4 Hour(s),8 Hour(s) | MICH-W-IMP MICH-W-EXP MICH-S-EXP MICH-S-IMP | 300 350 300 200
2024-07-08 07:00 | 2024-07-16 12:00 | MIDDLEPORT TS,MILTON SS, TRAFALGAR TS,BRUCE A TS, UNDERWOOD JCT, HANOVER TS, UNDERWOOD WGS,BURLINGTON TS, BURLINGTON JCT, MIDDLEPORT TS, CARLUKE JCT, NEALE JCT, BURLINGTON DESN TS, BECK 2 TS, NIAGARA WEST JCT,GRAND JCT, NANTICOKE TS, HORNING JCT, HORNING TS,LAMBTON TS 2 | T6, T6-LT6, T6-TL581, LT6BUS-TEMP1,M573T.MIXTR, HL573, L502L573, 40-M573T, T15-M573T,B4V.BRXUN, B4V.UNXUN, T4A, 21-B4V, 36B4V-22, 7014B5V-MSO2, 36T4-B4V,Q25BM.BEXNI, Q25BM.BUXBD, Q25BM.BUXBU, Q25BM.MIXCA, Q25BM.NEXBU, 25-Q25BM, 28-Q25BM, 39-Q25BM, T15-Q25BM,59-N5M, 310N5M-LC1,M27B.HOXBU, M27B.HOXHO, M27B.HOXMI, 25-M27B, 39-M27B, 4T4-M27B,K2L28, L27L28, P2L27, 27-L28C, 27-L27V | 1-00220299 Rev. #39,1-00208773 Rev. #10,1-00241125 Rev. #2,1-00238418 Rev. #3,1-00238444 Rev. #7,1-00238499 Rev. #3,1-00216465 Rev. #12 | Non-recallable,14 Day(s),10 Hour(s),6 Hour(s),10 Hour(s),6 Hour(s),4 Hour(s) | MICH-W-IMP MICH-W-EXP MICH-S-EXP MICH-S-IMP | 300 350 300 200
2024-07-26 17:00 | 2024-08-01 17:00 | BURLINGTON TS, BURLINGTON JCT, MIDDLEPORT TS, CARLUKE JCT, NEALE JCT, BURLINGTON DESN TS, BECK 2 TS, NIAGARA WEST JCT,LAMBTON TS 2,EAST LAKE ST. CLAIR WF JCT, LAMBTON TS 2,MILTON SS, TRAFALGAR TS,CALEDONIA TS, GRAND JCT, HORNING JCT, HORNING TS,MIDDLEPORT TS | Q25BM.BEXNI, Q25BM.BUXBD, Q25BM.BUXBU, Q25BM.MIXCA, Q25BM.NEXBU, 25-Q25BM, 28-Q25BM, 39-Q25BM, T15-Q25BM,KL25, L25L29, PL29, 27-L25V, 27-L29C, L25V-TEMP1,27-L29C, NA300L29C-2,M573T.MIXTR, HL573, L502L573, 40-M573T, T15-M573T,T2Y, 25-N5M, T2, N27T2-N5M, 310N5M-LC2,M28B.HOXBU, M28B.HOXHO, M28B.HOXMI, 25-M28B, 39-M28B, 4T3-M28B,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1 | 1-00238418 Rev. #3,1-00239852 Rev. #2,1-00239849 Rev. #5,1-00208773 Rev. #10,1-00238512 Rev. #2,1-00238498 Rev. #3,1-00220299 Rev. #39 | 6 Hour(s),4 Hour(s),12 Hour(s),14 Day(s),10 Hour(s),6 Hour(s),Non-recallable | MICH-W-IMP MICH-W-EXP MICH-S-EXP MICH-S-IMP | 300 350 300 200
2024-08-11 06:00 | 2024-08-16 08:00 | MILTON SS, TRAFALGAR TS,BRUCE A TS, UNDERWOOD JCT, HANOVER TS, UNDERWOOD WGS,BURLINGTON TS, HORNING JCT, HORNING TS, MIDDLEPORT TS,CALEDONIA TS, GRAND JCT,LAMBTON TS 2, ST. CLAIRX TS,MIDDLEPORT TS | M573T.MIXTR, HL573, L502L573, 40-M573T, T15-M573T,B4V.BRXUN, B4V.UNXUN, T4A, 21-B4V, 36B4V-22, 7014B5V-MSO2, 36T4-B4V,M28B.HOXBU, M28B.HOXHO, M28B.HOXMI, 25-M28B, 39-M28B, 4T3-M28B,T2Y, 25-N5M, T2, N27T2-N5M, 310N5M-LC2,L51D.CLXLA, K1L51, L23L51, PS51-2, PS51-1, PS51-S, PS51,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1 | 1-00208773 Rev. #10,1-00241126 Rev. #2,1-00238498 Rev. #3,1-00238512 Rev. #2,1-00235998 Rev. #3,1-00220299 Rev. #39 | 14 Day(s),10 Hour(s),6 Hour(s),10 Hour(s),4 Hour(s),Non-recallable | MICH-W-IMP MICH-W-EXP MICH-S-EXP MICH-S-IMP | 500 600 550 450
2024-11-04 08:00 | 2024-11-15 17:00 | MIDDLEPORT TS, MILTON SS, NANTICOKE TS,BECK 2 TS,CLAIREVILLE TS, ESSA TS,KENT TS, CHATHAM SS, GSPC JCT,BRUCE A TS, UNDERWOOD JCT, HANOVER TS, UNDERWOOD WGS | M585M.MIXMD, N581M.MDXNA, L81L85, T6L31, 25-M585M, 25-N581M, 40-M585M, 59-N581M, L581_BUS, T6, T6-LT6, T6-TL581, L23HT6,28-PA302, T302, T302-1,N581M.MDXNA, AL581, T7L581, T7T12, HT7_BUS,E511V.CLXES, DL511, W2L511, 18-E511V, 51-E511V,T1B, T1Y, T4Z, 5-L28C, 86-L28C, T1, T4, T1-L28C, T4L28C, 312L28C-MSO2,B4V.BRXUN, B4V.UNXUN, T4A, 21-B4V, 36B4V-22, 36T4-B4V, 161B5V-MSO1, 21-B5V | 1-00238465 Rev. #1,1-00238560 Rev. #1,1-00238433 Rev. #2,1-00238434 Rev. #2,1-00238492 Rev. #2,1-00238538 Rev. #1,1-00240028 Rev. #2,1-00241127 Rev. #1 | 4 Hour(s),8 Hour(s),Non-recallable,Non-recallable,Non-recallable,48 Hour(s),12 Hour(s),10 Hour(s)
2024-11-17 07:15 | 2024-11-28 17:00 | BRUCE A TS, MAJESTIC JCT, MAJESTIC CTS, WINGHAM JCT, SEAFORTH TS, WINGHAM TS,MIDDLEPORT TS, MILTON SS, NANTICOKE TS,BECK 2 TS,CLAIREVILLE TS, ESSA TS,KENT TS, CHATHAM SS, GSPC JCT | B23D.MJXBR, B23D.MJXMJ, B23D.MJXWI, B23D.WIXSE, B23D.WIXWI, T2-B23D, 21-B23D, 61B23D-21,M585M.MIXMD, N581M.MDXNA, L81L85, T6L31, 25-M585M, 25-N581M, 40-M585M, 59-N581M, L581_BUS, T6, T6-LT6, T6-TL581, L23HT6,N581M.MDXNA, AL581, T7L581, T7T12, HT7_BUS,28-PA302, T302, T302-1,E511V.CLXES, DL511, W2L511, 18-E511V, 51-E511V,T1B, T1Y, T4Z, 5-L28C, 86-L28C, T1, T4, T1-L28C, T4L28C, 312L28C-MSO2 | 1-00241121 Rev. #1,1-00238465 Rev. #1,1-00238433 Rev. #2,1-00238560 Rev. #1,1-00238434 Rev. #2,1-00238492 Rev. #2,1-00238538 Rev. #1,1-00240028 Rev. #2 | 4 Hour(s),4 Hour(s),Non-recallable,8 Hour(s),Non-recallable,Non-recallable,48 Hour(s),12 Hour(s)
2023-08-08 06:00 | 2023-08-29 09:30 | LAMBTON TS 2 | 27-T8, 27T8-L4D, T8 | 1-00231342 Rev. #12 | 4 Hour(s) | MICH-W-IMP MICH-W-EXP MICH-S-EXP MICH-S-IMP | 500 600 550 450
2023-08-29 09:30 | 2023-11-16 08:00 | LAMBTON TS 2 | 27-T8, 27T8-L4D, T8,27-T7, 27-T8, T7, T7-L4D | 1-00231342 Rev. #12,1-00234253 Rev. #9 | 4 Hour(s),Non-recallable | MICH-W-IMP MICH-W-EXP MICH-S-EXP MICH-S-IMP | 500 600 550 450
2023-11-16 08:00 | 2024-03-17 07:00 | LAMBTON TS 2 | 27-T7, 27-T8, 27T8-L4D, T7, T8, T7-L4D,27-T8 | 1-00234253 Rev. #9,1-00231342 Rev. #12,1-00240619 Rev. #5 | Non-recallable,4 Hour(s),14 Day(s) | MICH-W-IMP MICH-W-EXP MICH-S-EXP MICH-S-IMP | 500 600 550 450
2024-03-17 07:00 | 2024-03-31 11:00 | LAMBTON TS 2,BRANTFORD TS, NEWPORT JCT, MIDDLEPORT TS | 27-T8, 27T8-L4D, T8,27-T7, 27-T8, T7, T7-L4D,M32W.NEXBR, M32W.NEXMI, YZ, 25-M32W, 44M32W-19, T4-M32W | 1-00240619 Rev. #5,1-00231342 Rev. #12,1-00234253 Rev. #9,1-00238922 Rev. #11 | 14 Day(s),4 Hour(s),Non-recallable,6 Hour(s) | MICH-W-IMP MICH-W-EXP MICH-S-EXP MICH-S-IMP | 500 600 550 450
2024-04-14 16:00 | 2024-04-19 17:00 | LAMBTON TS 2,KENT TS, CHATHAM SS, GSPC JCT,MIDDLEPORT TS,BRUCE A TS, BRUCE JCT, MILTON SS, WILLOW CREEK JCT | 27-T8, 27T8-L4D, T8,T1B, T1Y, T4Z, 5-L28C, 86-L28C, T1, T4, T1-L28C, T4L28C, 312L28C-MSO2,27-T7, 27-T8, T7, T7-L4D,D1D2, D1L29, D1L27, L33L40, SC22D1, SC22SC, 25-M33W, D1_BUS, SC22, SS2-D, D1L34, D1L33,B502M.BAXBJ, B502M.BJXMI, B502M.BJXWJ, 21-B502M, 40-B502M | 1-00240619 Rev. #5,1-00238919 Rev. #6,1-00231342 Rev. #12,1-00234253 Rev. #9,1-00238390 Rev. #3,1-00235814 Rev. #13 | 14 Day(s),12 Hour(s),4 Hour(s),Non-recallable,2 Hour(s),4 Hour(s) | MICH-W-IMP MICH-W-EXP MICH-S-EXP MICH-S-IMP | 500 600 550 450
2024-04-19 18:00 | 2024-04-27 07:15 | LAMBTON TS 2,BRUCE B SS, BRUCE JCT, WILLOW CREEK JCT, MILTON SS,KENT TS, CHATHAM SS, GSPC JCT | 27-T7, 27-T8, 27T8-L4D, T7, T8, T7-L4D,B501M.BBXBJ, B501M.BJXWJ, B501M.WJXMI, 40-B501M, 29-B501M,27-T8,T1B, T1Y, T4Z, 5-L28C, 86-L28C, T1, T4, T1-L28C, T4L28C, 312L28C-MSO2 | 1-00234253 Rev. #9,1-00237165 Rev. #9,1-00231342 Rev. #12,1-00240619 Rev. #5,1-00238919 Rev. #6 | Non-recallable,4 Hour(s),4 Hour(s),14 Day(s),12 Hour(s) | MICH-W-IMP MICH-W-EXP MICH-S-EXP MICH-S-IMP | 500 600 550 450
2024-05-19 17:00 | 2024-05-31 17:00 | BRUCE B SS, BRUCE JCT, WILLOW CREEK JCT, MILTON SS,LAMBTON TS 2,LONGWOOD DESN, LAMBTON TS 2, LONGWOOD JCT, LONGWOOD TS | B501M.BBXBJ, B501M.BJXWJ, B501M.WJXMI, 40-B501M, 29-B501M,27-T7, 27-T8, 27T8-L4D, T7, T8, T7-L4D,27-T8,L24L.LOXLA, L24L.LOXLD, L24L.LOXLO, AL24, T14Q, T3L24, 27-L24L, T14, T14-L24L, W52-L24L | 1-00237165 Rev. #9,1-00234253 Rev. #9,1-00231342 Rev. #12,1-00236074 Rev. #16,1-00240619 Rev. #5 | 4 Hour(s),Non-recallable,4 Hour(s),8 Day(s),14 Day(s) | MICH-W-IMP MICH-W-EXP MICH-S-EXP MICH-S-IMP | 500 600 550 450
2024-06-09 07:00 | 2024-06-25 06:30 | LAMBTON TS 2,MIDDLEPORT TS | 27-T8, 27T8-L4D, T8,K1K2, K2L25, SC23K2, SC23SC, T6L31, 25-M31W, K2_BUS, SC23, SS3-K, K2L31, K2L21, TEMPSS6,27-T7, 27-T8, T7, T7-L4D,K2L28, L27L28, 27-L28C | 1-00240619 Rev. #5,1-00238468 Rev. #3,1-00231342 Rev. #12,1-00234253 Rev. #9,1-00216496 Rev. #13 | 14 Day(s),8 Hour(s),4 Hour(s),Non-recallable,4 Hour(s) | MICH-W-IMP MICH-W-EXP MICH-S-EXP MICH-S-IMP | 500 600 550 450
2024-06-25 08:30 | 2024-07-05 09:00 | LAMBTON TS 2,MIDDLEPORT TS | 27-T7, 27-T8, 27T8-L4D, T7, T8, T7-L4D,K2L28, L27L28, P2L27, 27-L28C, 27-L27V,27-T8,K1K2, K2L25, SC23K2, SC23SC, T6L31, 25-M31W, K2_BUS, SC23, SS3-K, K2L31, K2L21, TEMPSS6 | 1-00234253 Rev. #9,1-00216465 Rev. #12,1-00231342 Rev. #12,1-00240619 Rev. #5,1-00238468 Rev. #3 | Non-recallable,4 Hour(s),4 Hour(s),14 Day(s),8 Hour(s) | MICH-W-IMP MICH-W-EXP MICH-S-EXP MICH-S-IMP | 500 600 550 450
2024-07-05 09:00 | 2024-07-16 12:00 | LAMBTON TS 2 | K2L28, L27L28, P2L27, 27-L28C, 27-L27V,27-T7, 27-T8, 27T8-L4D, T7, T8, T7-L4D,27-T8 | 1-00216465 Rev. #12,1-00234253 Rev. #9,1-00231342 Rev. #12,1-00240619 Rev. #5 | 4 Hour(s),Non-recallable,4 Hour(s),14 Day(s) | MICH-W-IMP MICH-W-EXP MICH-S-EXP MICH-S-IMP | 500 600 550 450
2024-07-17 18:00 | 2024-08-02 11:00 | LAMBTON TS 2,EAST LAKE ST. CLAIR WF JCT, LAMBTON TS 2 | 27-T8, 27T8-L4D, T8,27-L29C, NA300L29C-2,27-T7, 27-T8, T7, T7-L4D,KL25, L25L29, PL29, 27-L25V, 27-L29C, L25V-TEMP1 | 1-00240619 Rev. #5,1-00239849 Rev. #5,1-00231342 Rev. #12,1-00234253 Rev. #9,1-00239852 Rev. #2 | 14 Day(s),12 Hour(s),4 Hour(s),Non-recallable,4 Hour(s) | MICH-W-IMP MICH-W-EXP MICH-S-EXP MICH-S-IMP | 500 600 550 450
2024-08-07 07:00 | 2024-08-20 16:00 | LAMBTON TS 2, ST. CLAIRX TS | 27-T7, 27-T8, 27T8-L4D, T7, T8, T7-L4D,L51D.CLXLA, K1L51, L23L51, PS51-2, PS51-1, PS51-S, PS51,27-T8 | 1-00234253 Rev. #9,1-00235998 Rev. #3,1-00231342 Rev. #12,1-00240619 Rev. #5 | Non-recallable,4 Hour(s),4 Hour(s),14 Day(s) | MICH-W-IMP MICH-W-EXP MICH-S-EXP MICH-S-IMP | 1000 1200 1100 900
2024-10-07 06:00 | 2024-10-18 07:00 | ASHFIELD SS, BRUCE B SS, BRUCE JCT, WILLOW CREEK JCT,KENT TS, CHATHAM SS, GSPC JCT | B563A.BBXBJ, B563A.BJWJ, B563A.WJXAS, OLDH5L563, OLDL501L563, L563L592, L563L565, OLD29-B563A, 322-B563A, L563_BUS, H5L563, L501L563, 29-B563A,T1B, T1Y, T4Z, 5-L28C, 86-L28C, T1, T4, T1-L28C, T4L28C, 312L28C-MSO2 | 1-00241110 Rev. #2,1-00240028 Rev. #2 | 6 Hour(s),12 Hour(s)
2023-08-08 06:00 | 2023-08-29 09:30 | LAMBTON TS 2 | 27-T8, 27T8-L4D, T8 | 1-00231342 Rev. #12 | 4 Hour(s) | MICH-W-IMP MICH-W-EXP MICH-S-EXP MICH-S-IMP | 500 600 550 450
2023-08-29 09:30 | 2023-11-16 08:00 | LAMBTON TS 2 | 27-T8, 27T8-L4D, T8,27-T7, 27-T8, T7, T7-L4D | 1-00231342 Rev. #12,1-00234253 Rev. #9 | 4 Hour(s),Non-recallable | MICH-W-IMP MICH-W-EXP MICH-S-EXP MICH-S-IMP | 500 600 550 450
2023-11-16 08:00 | 2024-04-14 16:00 | LAMBTON TS 2 | 27-T7, 27-T8, 27T8-L4D, T7, T8, T7-L4D,27-T8 | 1-00234253 Rev. #9,1-00231342 Rev. #12,1-00240619 Rev. #5 | Non-recallable,4 Hour(s),14 Day(s) | MICH-W-IMP MICH-W-EXP MICH-S-EXP MICH-S-IMP | 500 600 550 450
2024-05-01 06:15 | 2024-05-26 07:00 | LAMBTON TS 2,LONGWOOD DESN, LAMBTON TS 2, LONGWOOD JCT, LONGWOOD TS | 27-T7, 27-T8, 27T8-L4D, T7, T8, T7-L4D,27-T8,L24L.LOXLA, L24L.LOXLD, L24L.LOXLO, AL24, T14Q, T3L24, 27-L24L, T14, T14-L24L, W52-L24L | 1-00234253 Rev. #9,1-00231342 Rev. #12,1-00240619 Rev. #5,1-00236074 Rev. #16 | Non-recallable,4 Hour(s),14 Day(s),8 Day(s) | MICH-W-IMP MICH-W-EXP MICH-S-EXP MICH-S-IMP | 500 600 550 450
2024-06-05 12:00 | 2024-06-25 06:30 | LAMBTON TS 2 | K2L28, L27L28, 27-L28C,27-T7, 27-T8, 27T8-L4D, T7, T8, T7-L4D,27-T8 | 1-00216496 Rev. #13,1-00234253 Rev. #9,1-00231342 Rev. #12,1-00240619 Rev. #5 | 4 Hour(s),Non-recallable,4 Hour(s),14 Day(s) | MICH-W-IMP MICH-W-EXP MICH-S-EXP MICH-S-IMP | 500 600 550 450
2024-06-25 08:30 | 2024-07-16 12:00 | LAMBTON TS 2 | K2L28, L27L28, P2L27, 27-L28C, 27-L27V,27-T7, 27-T8, 27T8-L4D, T7, T8, T7-L4D,27-T8 | 1-00216465 Rev. #12,1-00234253 Rev. #9,1-00231342 Rev. #12,1-00240619 Rev. #5 | 4 Hour(s),Non-recallable,4 Hour(s),14 Day(s) | MICH-W-IMP MICH-W-EXP MICH-S-EXP MICH-S-IMP | 500 600 550 450
2024-07-17 18:00 | 2024-08-02 11:00 | LAMBTON TS 2,EAST LAKE ST. CLAIR WF JCT, LAMBTON TS 2 | 27-T7, 27-T8, 27T8-L4D, T7, T8, T7-L4D,27-L29C, NA300L29C-2,27-T8,KL25, L25L29, PL29, 27-L25V, 27-L29C, L25V-TEMP1 | 1-00234253 Rev. #9,1-00239849 Rev. #5,1-00231342 Rev. #12,1-00240619 Rev. #5,1-00239852 Rev. #2 | Non-recallable,12 Hour(s),4 Hour(s),14 Day(s),4 Hour(s) | MICH-W-IMP MICH-W-EXP MICH-S-EXP MICH-S-IMP | 500 600 550 450
2024-08-07 07:00 | 2024-08-20 16:00 | LAMBTON TS 2, ST. CLAIRX TS | 27-T8, 27T8-L4D, T8,L51D.CLXLA, K1L51, L23L51, PS51-2, PS51-1, PS51-S, PS51,27-T7, 27-T8, T7, T7-L4D | 1-00240619 Rev. #5,1-00235998 Rev. #3,1-00231342 Rev. #12,1-00234253 Rev. #9 | 14 Day(s),4 Hour(s),4 Hour(s),Non-recallable | MICH-W-IMP MICH-W-EXP MICH-S-EXP MICH-S-IMP | 1000 1200 1100 900
2024-04-10 05:30 | 2024-04-16 07:00 | BURLINGTON TS,SCOTT TS, ST. ANDREWS TS,SEAFORTH TS | HT9-T9, T9, T9-H2, SS9-T9, SS9,HL22, HL23, HL43, KL1, KL2, KL7, T4Q, H_BUS, K_BUS, SS5, T5, T5-H, T5-K, OLDT5-H, OLDT5-K, OLDT5,DTL18 | 1-00208974 Rev. #66,1-00238726 Rev. #13,1-00246196 Rev. #1 | Non-recallable,9 Day(s),8 Hour(s)
2024-04-17 06:00 | 2024-04-25 16:00 | BURLINGTON TS,SCOTT TS, ST. ANDREWS TS | H1H2, H2L18, H2L23, H2L36, H2L40, SC22H2, SC22SC, H2_BUS, HT9-T9, T9, SC22, SC22H2-H2, T9-H2, SS9-T9,HL22, HL23, HL43, KL1, KL2, KL7, T4Q, H_BUS, K_BUS, SS5, T5, T5-H, T5-K, OLDT5-H, OLDT5-K, OLDT5,HT9-T9, SS9 | 1-00238392 Rev. #3,1-00238726 Rev. #13,1-00208974 Rev. #66 | 6 Hour(s),9 Day(s),Non-recallable
2024-06-10 16:00 | 2024-08-11 17:00 | KEITH TS | HT12K | 1-00240265 Rev. #5 | Non-recallable
2024-08-17 14:00 | 2024-10-11 07:00 | KEITH TS | HT11K | 1-00240272 Rev. #4 | Non-recallable
Back to main menu

## Table C11
Back to main menu
Table C11: External Interties
Planned Start | Planned End | Station | Equipment Name | Outage ID | Max Recall | Major Transmission Interface Impacted | Reduction in Limit
2024-04-05 17:00 | 2024-04-12 16:00 | BRUCE A TS, BRUCE JCT, MILTON SS, WILLOW CREEK JCT,BRANTFORD TS, NEWPORT JCT, MIDDLEPORT TS,BECK 2 TS, MID RIVER JCT NIAGARA,MIDDLEPORT TS,CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,CLAIREVILLE TS, ESSA TS,DETWEILER TS, STRATFORD JCT, SEAFORTH TS, STRATFORD TS,LONGWOOD TS | B502M.BAXBJ, B502M.BJXMI, B502M.BJXWJ, 21-B502M, 40-B502M,M32W.NEXBR, M32W.NEXMI, YZ, 25-M32W, 44M32W-19, T4-M32W,BP76.PAXBE, K2L76, L35L76, R76, TL35-BO1,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1,C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,E510V.CLXES, AL510, W3L510, 18-E510V, 51-E510V,B22D.STXDE, B22D.STXST, 26-B22D, 68T1-B22D, 61B22D-26,R5N, T5L45, SS5, T5, R5, T5-H, T5-LT5,25-Q23BM, L23HT6, D2L23, Q23BM-TEMP1 | 1-00239284 Rev. #3,1-00238922 Rev. #11,1-00181622 Rev. #28,1-00220299 Rev. #39,1-00213473 Rev. #37,1-00235682 Rev. #6,1-00237157 Rev. #9,1-00239308 Rev. #10,1-00235814 Rev. #13,1-00246468 Rev. #2 | 8 Hour(s),6 Hour(s),Non-recallable,Non-recallable,Non-recallable,14 Day(s),4 Hour(s),5 Day(s),4 Hour(s),6 Hour(s) | FABCW NBLIP BLIP | 2300 300 300
2024-06-09 07:00 | 2024-06-28 17:00 | B5D-B31L SS JCT, ST. LAWRENCE TS | B31L.IPXLA, 49-B31L, B31L-D, B5D-B31L | 1-00245104 Rev. #1 | 4 Hour(s) | FIO BEAU P33C | 250 400 0
2024-04-14 16:00 | 2024-04-19 16:00 | CLAIREVILLE TS, ESSA TS,KENT TS, CHATHAM SS, GSPC JCT,DETWEILER TS, STRATFORD JCT, SEAFORTH TS, STRATFORD TS,CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,MIDDLEPORT TS,BECK 2 TS, MID RIVER JCT NIAGARA,BRUCE A TS, BRUCE JCT, MILTON SS, WILLOW CREEK JCT,LONGWOOD TS | E510V.CLXES, AL510, W3L510, 18-E510V, 51-E510V,T1B, T1Y, T4Z, 5-L28C, 86-L28C, T1, T4, T1-L28C, T4L28C, 312L28C-MSO2,B22D.STXDE, B22D.STXST, 26-B22D, 68T1-B22D, 61B22D-26,C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1,BP76.PAXBE, K2L76, L35L76, R76, TL35-BO1,25-Q23BM, L23HT6, D2L23, Q23BM-TEMP1,D1D2, D1L29, D1L27, L33L40, SC22D1, SC22SC, 25-M33W, D1_BUS, SC22, SS2-D, D1L34, D1L33,B502M.BAXBJ, B502M.BJXMI, B502M.BJXWJ, 21-B502M, 40-B502M,R5N, T5L45, SS5, T5, R5, T5-H, T5-LT5 | 1-00235682 Rev. #6,1-00238919 Rev. #6,1-00237157 Rev. #9,1-00213473 Rev. #37,1-00220299 Rev. #39,1-00181622 Rev. #28,1-00246468 Rev. #2,1-00238390 Rev. #3,1-00235814 Rev. #13,1-00239308 Rev. #10 | 14 Day(s),12 Hour(s),4 Hour(s),Non-recallable,Non-recallable,Non-recallable,6 Hour(s),2 Hour(s),4 Hour(s),5 Day(s) | FABCW NBLIP BLIP | 2300 300 300
2024-05-26 07:00 | 2024-05-31 08:00 | ALLANBURG TS, BECK 2 TS, MID RIVER JCT NIAGARA, CROSSLINE JCT, MIDDLEPORT TS, CALEDONIA Q35M JCT,CLAIREVILLE TS,BRUCE B SS, BRUCE JCT, WILLOW CREEK JCT, MILTON SS,LONGWOOD DESN, LAMBTON TS 2, LONGWOOD JCT, LONGWOOD TS,CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,MIDDLEPORT TS,DETWEILER TS, STRATFORD TS, ZURICH JCT | BP76.PAXBE, Q35M.MIXCA, Q35M.QUXAL, D2HT4, H2HT4, K2L76, L26L35, L30TL35, L34L35, L35L76, T4, R76,W3L570, W3L510, T15, T15-HT15, T15-W3, T15-SS2,B501M.BBXBJ, B501M.BJXWJ, B501M.WJXMI, 40-B501M, 29-B501M,L24L.LOXLA, L24L.LOXLD, L24L.LOXLO, AL24, T14Q, T3L24, 27-L24L, T14, T14-L24L, W52-L24L,C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1, 51-C550VP, 52-C550VP, 81-C550VP,26-B23D, 68T2-B23D, 364B23D-MSO1 | 1-00181648 Rev. #9,1-00238525 Rev. #10,1-00237165 Rev. #9,1-00236074 Rev. #16,1-00213473 Rev. #37,1-00220299 Rev. #39,1-00236150 Rev. #5,1-00238602 Rev. #4 | 4 Hour(s),4 Hour(s),4 Hour(s),8 Day(s),Non-recallable,Non-recallable,4 Hour(s),4 Hour(s) | FABCW NBLIP BLIP | 2800 300 300
2024-08-11 06:00 | 2024-08-16 08:00 | MILTON SS, TRAFALGAR TS,BRUCE A TS, UNDERWOOD JCT, HANOVER TS, UNDERWOOD WGS,BURLINGTON TS, HORNING JCT, HORNING TS, MIDDLEPORT TS,CALEDONIA TS, GRAND JCT,LAMBTON TS 2, ST. CLAIRX TS,MIDDLEPORT TS | M573T.MIXTR, HL573, L502L573, 40-M573T, T15-M573T,B4V.BRXUN, B4V.UNXUN, T4A, 21-B4V, 36B4V-22, 7014B5V-MSO2, 36T4-B4V,M28B.HOXBU, M28B.HOXHO, M28B.HOXMI, 25-M28B, 39-M28B, 4T3-M28B,T2Y, 25-N5M, T2, N27T2-N5M, 310N5M-LC2,L51D.CLXLA, K1L51, L23L51, PS51-2, PS51-1, PS51-S, PS51,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1 | 1-00208773 Rev. #10,1-00241126 Rev. #2,1-00238498 Rev. #3,1-00238512 Rev. #2,1-00235998 Rev. #3,1-00220299 Rev. #39 | 14 Day(s),10 Hour(s),6 Hour(s),10 Hour(s),4 Hour(s),Non-recallable | FABCW NBLIP BLIP | 550 0 0
2024-11-04 08:00 | 2024-11-15 17:00 | MIDDLEPORT TS, MILTON SS, NANTICOKE TS,BECK 2 TS,CLAIREVILLE TS, ESSA TS,KENT TS, CHATHAM SS, GSPC JCT,BRUCE A TS, UNDERWOOD JCT, HANOVER TS, UNDERWOOD WGS | M585M.MIXMD, N581M.MDXNA, L81L85, T6L31, 25-M585M, 25-N581M, 40-M585M, 59-N581M, L581_BUS, T6, T6-LT6, T6-TL581, L23HT6,28-PA302, T302, T302-1,N581M.MDXNA, AL581, T7L581, T7T12, HT7_BUS,E511V.CLXES, DL511, W2L511, 18-E511V, 51-E511V,T1B, T1Y, T4Z, 5-L28C, 86-L28C, T1, T4, T1-L28C, T4L28C, 312L28C-MSO2,B4V.BRXUN, B4V.UNXUN, T4A, 21-B4V, 36B4V-22, 36T4-B4V, 161B5V-MSO1, 21-B5V | 1-00238465 Rev. #1,1-00238560 Rev. #1,1-00238433 Rev. #2,1-00238434 Rev. #2,1-00238492 Rev. #2,1-00238538 Rev. #1,1-00240028 Rev. #2,1-00241127 Rev. #1 | 4 Hour(s),8 Hour(s),Non-recallable,Non-recallable,Non-recallable,48 Hour(s),12 Hour(s),10 Hour(s) | FABCW NBLIP BLIP | 1000 0 0
2024-11-17 07:15 | 2024-11-28 17:00 | BRUCE A TS, MAJESTIC JCT, MAJESTIC CTS, WINGHAM JCT, SEAFORTH TS, WINGHAM TS,MIDDLEPORT TS, MILTON SS, NANTICOKE TS,BECK 2 TS,CLAIREVILLE TS, ESSA TS,KENT TS, CHATHAM SS, GSPC JCT | B23D.MJXBR, B23D.MJXMJ, B23D.MJXWI, B23D.WIXSE, B23D.WIXWI, T2-B23D, 21-B23D, 61B23D-21,M585M.MIXMD, N581M.MDXNA, L81L85, T6L31, 25-M585M, 25-N581M, 40-M585M, 59-N581M, L581_BUS, T6, T6-LT6, T6-TL581, L23HT6,N581M.MDXNA, AL581, T7L581, T7T12, HT7_BUS,28-PA302, T302, T302-1,E511V.CLXES, DL511, W2L511, 18-E511V, 51-E511V,T1B, T1Y, T4Z, 5-L28C, 86-L28C, T1, T4, T1-L28C, T4L28C, 312L28C-MSO2 | 1-00241121 Rev. #1,1-00238465 Rev. #1,1-00238433 Rev. #2,1-00238560 Rev. #1,1-00238434 Rev. #2,1-00238492 Rev. #2,1-00238538 Rev. #1,1-00240028 Rev. #2 | 4 Hour(s),4 Hour(s),Non-recallable,8 Hour(s),Non-recallable,Non-recallable,48 Hour(s),12 Hour(s) | FABCW NBLIP BLIP | 800 0 0
2024-04-14 16:00 | 2024-04-19 17:00 | LAMBTON TS 2,KENT TS, CHATHAM SS, GSPC JCT,MIDDLEPORT TS,BRUCE A TS, BRUCE JCT, MILTON SS, WILLOW CREEK JCT | 27-T8, 27T8-L4D, T8,T1B, T1Y, T4Z, 5-L28C, 86-L28C, T1, T4, T1-L28C, T4L28C, 312L28C-MSO2,27-T7, 27-T8, T7, T7-L4D,D1D2, D1L29, D1L27, L33L40, SC22D1, SC22SC, 25-M33W, D1_BUS, SC22, SS2-D, D1L34, D1L33,B502M.BAXBJ, B502M.BJXMI, B502M.BJXWJ, 21-B502M, 40-B502M | 1-00240619 Rev. #5,1-00238919 Rev. #6,1-00231342 Rev. #12,1-00234253 Rev. #9,1-00238390 Rev. #3,1-00235814 Rev. #13 | 14 Day(s),12 Hour(s),4 Hour(s),Non-recallable,2 Hour(s),4 Hour(s) | FABCW NBLIP BLIP | 1750 300 300
2024-04-19 18:00 | 2024-04-27 07:15 | LAMBTON TS 2,BRUCE B SS, BRUCE JCT, WILLOW CREEK JCT, MILTON SS,KENT TS, CHATHAM SS, GSPC JCT | 27-T7, 27-T8, 27T8-L4D, T7, T8, T7-L4D,B501M.BBXBJ, B501M.BJXWJ, B501M.WJXMI, 40-B501M, 29-B501M,27-T8,T1B, T1Y, T4Z, 5-L28C, 86-L28C, T1, T4, T1-L28C, T4L28C, 312L28C-MSO2 | 1-00234253 Rev. #9,1-00237165 Rev. #9,1-00231342 Rev. #12,1-00240619 Rev. #5,1-00238919 Rev. #6 | Non-recallable,4 Hour(s),4 Hour(s),14 Day(s),12 Hour(s) | FABCW NBLIP BLIP | 1750 300 300
2024-05-19 17:00 | 2024-05-31 17:00 | BRUCE B SS, BRUCE JCT, WILLOW CREEK JCT, MILTON SS,LAMBTON TS 2,LONGWOOD DESN, LAMBTON TS 2, LONGWOOD JCT, LONGWOOD TS | B501M.BBXBJ, B501M.BJXWJ, B501M.WJXMI, 40-B501M, 29-B501M,27-T7, 27-T8, 27T8-L4D, T7, T8, T7-L4D,27-T8,L24L.LOXLA, L24L.LOXLD, L24L.LOXLO, AL24, T14Q, T3L24, 27-L24L, T14, T14-L24L, W52-L24L | 1-00237165 Rev. #9,1-00234253 Rev. #9,1-00231342 Rev. #12,1-00236074 Rev. #16,1-00240619 Rev. #5 | 4 Hour(s),Non-recallable,4 Hour(s),8 Day(s),14 Day(s) | FABCW NBLIP BLIP | 1850 300 300
2024-03-25 07:00 | 2024-03-31 11:00 | CLAIREVILLE TS, ESSA TS,BRANTFORD TS, NEWPORT JCT, MIDDLEPORT TS,BECK 2 TS, MID RIVER JCT NIAGARA,MIDDLEPORT TS,CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,DETWEILER TS, STRATFORD JCT, SEAFORTH TS, STRATFORD TS | E510V.CLXES, AL510, W3L510, 18-E510V, 51-E510V,M32W.NEXBR, M32W.NEXMI, YZ, 25-M32W, 44M32W-19, T4-M32W,BP76.PAXBE, K2L76, L35L76, R76, TL35-BO1,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1,C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,B22D.STXDE, B22D.STXST, 26-B22D, 68T1-B22D, 61B22D-26,AL510 | 1-00238540 Rev. #3,1-00238922 Rev. #11,1-00181622 Rev. #28,1-00220299 Rev. #39,1-00213473 Rev. #37,1-00235682 Rev. #6,1-00237157 Rev. #9,1-00238545 Rev. #4 | 48 Hour(s),6 Hour(s),Non-recallable,Non-recallable,Non-recallable,14 Day(s),4 Hour(s),5 Day(s) | FS FN P502X CLAN | 0 0 0 700
2024-03-04 08:00 | 2024-03-14 07:15 | CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,MIDDLEPORT TS,BECK 2 TS, MID RIVER JCT NIAGARA | C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1,BP76.PAXBE, K2L76, L35L76, R76, TL35-BO1 | 1-00213473 Rev. #37,1-00220299 Rev. #39,1-00181622 Rev. #28 | Non-recallable,Non-recallable,Non-recallable | NY-W-IMP NY-W-EXP NY-S-EXP NY-S-IMP | 600 500 450 550
2024-04-05 17:00 | 2024-04-12 16:00 | BRUCE A TS, BRUCE JCT, MILTON SS, WILLOW CREEK JCT,BRANTFORD TS, NEWPORT JCT, MIDDLEPORT TS,BECK 2 TS, MID RIVER JCT NIAGARA,MIDDLEPORT TS,CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,CLAIREVILLE TS, ESSA TS,DETWEILER TS, STRATFORD JCT, SEAFORTH TS, STRATFORD TS,LONGWOOD TS | B502M.BAXBJ, B502M.BJXMI, B502M.BJXWJ, 21-B502M, 40-B502M,M32W.NEXBR, M32W.NEXMI, YZ, 25-M32W, 44M32W-19, T4-M32W,BP76.PAXBE, K2L76, L35L76, R76, TL35-BO1,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1,C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,E510V.CLXES, AL510, W3L510, 18-E510V, 51-E510V,B22D.STXDE, B22D.STXST, 26-B22D, 68T1-B22D, 61B22D-26,R5N, T5L45, SS5, T5, R5, T5-H, T5-LT5,25-Q23BM, L23HT6, D2L23, Q23BM-TEMP1 | 1-00239284 Rev. #3,1-00238922 Rev. #11,1-00181622 Rev. #28,1-00220299 Rev. #39,1-00213473 Rev. #37,1-00235682 Rev. #6,1-00237157 Rev. #9,1-00239308 Rev. #10,1-00235814 Rev. #13,1-00246468 Rev. #2 | 8 Hour(s),6 Hour(s),Non-recallable,Non-recallable,Non-recallable,14 Day(s),4 Hour(s),5 Day(s),4 Hour(s),6 Hour(s) | FS FN P502X CLAN | 0 0 0 700
2024-04-14 16:00 | 2024-04-19 16:00 | CLAIREVILLE TS, ESSA TS,KENT TS, CHATHAM SS, GSPC JCT,DETWEILER TS, STRATFORD JCT, SEAFORTH TS, STRATFORD TS,CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,MIDDLEPORT TS,BECK 2 TS, MID RIVER JCT NIAGARA,BRUCE A TS, BRUCE JCT, MILTON SS, WILLOW CREEK JCT,LONGWOOD TS | E510V.CLXES, AL510, W3L510, 18-E510V, 51-E510V,T1B, T1Y, T4Z, 5-L28C, 86-L28C, T1, T4, T1-L28C, T4L28C, 312L28C-MSO2,B22D.STXDE, B22D.STXST, 26-B22D, 68T1-B22D, 61B22D-26,C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1,BP76.PAXBE, K2L76, L35L76, R76, TL35-BO1,25-Q23BM, L23HT6, D2L23, Q23BM-TEMP1,D1D2, D1L29, D1L27, L33L40, SC22D1, SC22SC, 25-M33W, D1_BUS, SC22, SS2-D, D1L34, D1L33,B502M.BAXBJ, B502M.BJXMI, B502M.BJXWJ, 21-B502M, 40-B502M,R5N, T5L45, SS5, T5, R5, T5-H, T5-LT5 | 1-00235682 Rev. #6,1-00238919 Rev. #6,1-00237157 Rev. #9,1-00213473 Rev. #37,1-00220299 Rev. #39,1-00181622 Rev. #28,1-00246468 Rev. #2,1-00238390 Rev. #3,1-00235814 Rev. #13,1-00239308 Rev. #10 | 14 Day(s),12 Hour(s),4 Hour(s),Non-recallable,Non-recallable,Non-recallable,6 Hour(s),2 Hour(s),4 Hour(s),5 Day(s) | FS FN P502X CLAN | 0 0 0 700
2024-11-04 08:00 | 2024-11-15 17:00 | MIDDLEPORT TS, MILTON SS, NANTICOKE TS,BECK 2 TS,CLAIREVILLE TS, ESSA TS,KENT TS, CHATHAM SS, GSPC JCT,BRUCE A TS, UNDERWOOD JCT, HANOVER TS, UNDERWOOD WGS | M585M.MIXMD, N581M.MDXNA, L81L85, T6L31, 25-M585M, 25-N581M, 40-M585M, 59-N581M, L581_BUS, T6, T6-LT6, T6-TL581, L23HT6,28-PA302, T302, T302-1,N581M.MDXNA, AL581, T7L581, T7T12, HT7_BUS,E511V.CLXES, DL511, W2L511, 18-E511V, 51-E511V,T1B, T1Y, T4Z, 5-L28C, 86-L28C, T1, T4, T1-L28C, T4L28C, 312L28C-MSO2,B4V.BRXUN, B4V.UNXUN, T4A, 21-B4V, 36B4V-22, 36T4-B4V, 161B5V-MSO1, 21-B5V | 1-00238465 Rev. #1,1-00238560 Rev. #1,1-00238433 Rev. #2,1-00238434 Rev. #2,1-00238492 Rev. #2,1-00238538 Rev. #1,1-00240028 Rev. #2,1-00241127 Rev. #1 | 4 Hour(s),8 Hour(s),Non-recallable,Non-recallable,Non-recallable,48 Hour(s),12 Hour(s),10 Hour(s) | FS FN P502X CLAN | 0 0 0 700
2024-11-17 07:15 | 2024-11-28 17:00 | BRUCE A TS, MAJESTIC JCT, MAJESTIC CTS, WINGHAM JCT, SEAFORTH TS, WINGHAM TS,MIDDLEPORT TS, MILTON SS, NANTICOKE TS,BECK 2 TS,CLAIREVILLE TS, ESSA TS,KENT TS, CHATHAM SS, GSPC JCT | B23D.MJXBR, B23D.MJXMJ, B23D.MJXWI, B23D.WIXSE, B23D.WIXWI, T2-B23D, 21-B23D, 61B23D-21,M585M.MIXMD, N581M.MDXNA, L81L85, T6L31, 25-M585M, 25-N581M, 40-M585M, 59-N581M, L581_BUS, T6, T6-LT6, T6-TL581, L23HT6,N581M.MDXNA, AL581, T7L581, T7T12, HT7_BUS,28-PA302, T302, T302-1,E511V.CLXES, DL511, W2L511, 18-E511V, 51-E511V,T1B, T1Y, T4Z, 5-L28C, 86-L28C, T1, T4, T1-L28C, T4L28C, 312L28C-MSO2 | 1-00241121 Rev. #1,1-00238465 Rev. #1,1-00238433 Rev. #2,1-00238560 Rev. #1,1-00238434 Rev. #2,1-00238492 Rev. #2,1-00238538 Rev. #1,1-00240028 Rev. #2 | 4 Hour(s),4 Hour(s),Non-recallable,8 Hour(s),Non-recallable,Non-recallable,48 Hour(s),12 Hour(s) | FS FN P502X CLAN | 0 0 0 700
2024-03-04 08:00 | 2024-03-14 07:15 | CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,MIDDLEPORT TS,BECK 2 TS, MID RIVER JCT NIAGARA | C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1,BP76.PAXBE, K2L76, L35L76, R76, TL35-BO1 | 1-00213473 Rev. #37,1-00220299 Rev. #39,1-00181622 Rev. #28 | Non-recallable,Non-recallable,Non-recallable | FABCW NBLIP BLIP | 200 0 0
2024-03-04 08:00 | 2024-03-14 07:15 | CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,MIDDLEPORT TS,BECK 2 TS, MID RIVER JCT NIAGARA | C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1,BP76.PAXBE, K2L76, L35L76, R76, TL35-BO1 | 1-00213473 Rev. #37,1-00220299 Rev. #39,1-00181622 Rev. #28 | Non-recallable,Non-recallable,Non-recallable | FABCW | 200
2024-03-31 18:00 | 2024-04-21 07:00 | BECK 2 TS, MID RIVER JCT NIAGARA,MIDDLEPORT TS | BP76.PAXBE, K2L76, L35L76, R76, TL35-BO1,25-Q23BM, L23HT6, D2L23, Q23BM-TEMP1 | 1-00181622 Rev. #28,1-00246468 Rev. #2 | Non-recallable,6 Hour(s)
2024-04-28 07:00 | 2024-05-03 17:00 | MIDDLEPORT TS,BECK 2 TS, MID RIVER JCT NIAGARA | D1D2, D1L29, D1L27, L34L35, SC22D1, SC22SC, 25-M34H, D1_BUS, SC22, SS2-D, D1L34, D1L33,BP76.PAXBE, K2L76, L35L76, R76, TL35-BO1 | 1-00238393 Rev. #3,1-00181622 Rev. #28 | 2 Hour(s),Non-recallable
2024-05-05 13:00 | 2024-05-20 08:00 | BECK 2 TS, MID RIVER JCT NIAGARA,CALEDONIA TS, GRAND JCT, MIDDLEPORT TS | BP76.PAXBE, K2L76, L35L76, R76, TL35-BO1,L5L25, L5L32, T2Y, 25-N5M, T2, N27T2-N5M, 310N5M-LC2 | 1-00181622 Rev. #28,1-00246626 Rev. #1 | Non-recallable,4 Hour(s)
2024-05-26 07:00 | 2024-05-31 08:00 | ALLANBURG TS, BECK 2 TS, MID RIVER JCT NIAGARA, CROSSLINE JCT, MIDDLEPORT TS, CALEDONIA Q35M JCT | BP76.PAXBE, Q35M.MIXCA, Q35M.QUXAL, D2HT4, H2HT4, K2L76, L26L35, L30TL35, L34L35, L35L76, T4, R76 | 1-00181648 Rev. #9 | 4 Hour(s)
2024-03-17 07:00 | 2024-03-31 11:00 | LAMBTON TS 2,BRANTFORD TS, NEWPORT JCT, MIDDLEPORT TS | 27-T8, 27T8-L4D, T8,27-T7, 27-T8, T7, T7-L4D,M32W.NEXBR, M32W.NEXMI, YZ, 25-M32W, 44M32W-19, T4-M32W | 1-00240619 Rev. #5,1-00231342 Rev. #12,1-00234253 Rev. #9,1-00238922 Rev. #11 | 14 Day(s),4 Hour(s),Non-recallable,6 Hour(s)
2024-06-09 07:00 | 2024-06-25 06:30 | LAMBTON TS 2,MIDDLEPORT TS | 27-T8, 27T8-L4D, T8,K1K2, K2L25, SC23K2, SC23SC, T6L31, 25-M31W, K2_BUS, SC23, SS3-K, K2L31, K2L21, TEMPSS6,27-T7, 27-T8, T7, T7-L4D,K2L28, L27L28, 27-L28C | 1-00240619 Rev. #5,1-00238468 Rev. #3,1-00231342 Rev. #12,1-00234253 Rev. #9,1-00216496 Rev. #13 | 14 Day(s),8 Hour(s),4 Hour(s),Non-recallable,4 Hour(s)
2024-06-25 08:30 | 2024-07-05 09:00 | LAMBTON TS 2,MIDDLEPORT TS | 27-T7, 27-T8, 27T8-L4D, T7, T8, T7-L4D,K2L28, L27L28, P2L27, 27-L28C, 27-L27V,27-T8,K1K2, K2L25, SC23K2, SC23SC, T6L31, 25-M31W, K2_BUS, SC23, SS3-K, K2L31, K2L21, TEMPSS6 | 1-00234253 Rev. #9,1-00216465 Rev. #12,1-00231342 Rev. #12,1-00240619 Rev. #5,1-00238468 Rev. #3 | Non-recallable,4 Hour(s),4 Hour(s),14 Day(s),8 Hour(s)
2024-05-20 08:00 | 2024-05-31 08:00 | ALLANBURG TS, BECK 2 TS, MID RIVER JCT NIAGARA, CROSSLINE JCT, MIDDLEPORT TS, CALEDONIA Q35M JCT | BP76.PAXBE, Q35M.MIXCA, Q35M.QUXAL, D2HT4, H2HT4, K2L76, L26L35, L30TL35, L34L35, L35L76, T4, R76 | 1-00181648 Rev. #9 | 4 Hour(s)
2024-04-05 17:00 | 2024-04-12 16:00 | BRUCE A TS, BRUCE JCT, MILTON SS, WILLOW CREEK JCT,BRANTFORD TS, NEWPORT JCT, MIDDLEPORT TS,BECK 2 TS, MID RIVER JCT NIAGARA,MIDDLEPORT TS,CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,CLAIREVILLE TS, ESSA TS,DETWEILER TS, STRATFORD JCT, SEAFORTH TS, STRATFORD TS,LONGWOOD TS | B502M.BAXBJ, B502M.BJXMI, B502M.BJXWJ, 21-B502M, 40-B502M,M32W.NEXBR, M32W.NEXMI, YZ, 25-M32W, 44M32W-19, T4-M32W,BP76.PAXBE, K2L76, L35L76, R76, TL35-BO1,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1,C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,E510V.CLXES, AL510, W3L510, 18-E510V, 51-E510V,B22D.STXDE, B22D.STXST, 26-B22D, 68T1-B22D, 61B22D-26,R5N, T5L45, SS5, T5, R5, T5-H, T5-LT5,25-Q23BM, L23HT6, D2L23, Q23BM-TEMP1 | 1-00239284 Rev. #3,1-00238922 Rev. #11,1-00181622 Rev. #28,1-00220299 Rev. #39,1-00213473 Rev. #37,1-00235682 Rev. #6,1-00237157 Rev. #9,1-00239308 Rev. #10,1-00235814 Rev. #13,1-00246468 Rev. #2 | 8 Hour(s),6 Hour(s),Non-recallable,Non-recallable,Non-recallable,14 Day(s),4 Hour(s),5 Day(s),4 Hour(s),6 Hour(s)
2024-03-17 07:00 | 2024-03-24 16:00 | DETWEILER TS, STRATFORD JCT, SEAFORTH TS, STRATFORD TS,CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,MIDDLEPORT TS,BECK 2 TS, MID RIVER JCT NIAGARA,BRANTFORD TS, NEWPORT JCT, MIDDLEPORT TS | B22D.STXDE, B22D.STXST, 26-B22D, 68T1-B22D, 61B22D-26,C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1,BP76.PAXBE, K2L76, L35L76, R76, TL35-BO1,M32W.NEXBR, M32W.NEXMI, YZ, 25-M32W, 44M32W-19, T4-M32W | 1-00237157 Rev. #9,1-00213473 Rev. #37,1-00220299 Rev. #39,1-00181622 Rev. #28,1-00238922 Rev. #11 | 4 Hour(s),Non-recallable,Non-recallable,Non-recallable,6 Hour(s) | FABCW | 400
2024-03-25 07:00 | 2024-03-31 11:00 | CLAIREVILLE TS, ESSA TS,BRANTFORD TS, NEWPORT JCT, MIDDLEPORT TS,BECK 2 TS, MID RIVER JCT NIAGARA,MIDDLEPORT TS,CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,DETWEILER TS, STRATFORD JCT, SEAFORTH TS, STRATFORD TS | E510V.CLXES, AL510, W3L510, 18-E510V, 51-E510V,M32W.NEXBR, M32W.NEXMI, YZ, 25-M32W, 44M32W-19, T4-M32W,BP76.PAXBE, K2L76, L35L76, R76, TL35-BO1,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1,C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,B22D.STXDE, B22D.STXST, 26-B22D, 68T1-B22D, 61B22D-26,AL510 | 1-00238540 Rev. #3,1-00238922 Rev. #11,1-00181622 Rev. #28,1-00220299 Rev. #39,1-00213473 Rev. #37,1-00235682 Rev. #6,1-00237157 Rev. #9,1-00238545 Rev. #4 | 48 Hour(s),6 Hour(s),Non-recallable,Non-recallable,Non-recallable,14 Day(s),4 Hour(s),5 Day(s) | FABCW | 400
2024-04-05 17:00 | 2024-04-12 16:00 | BRUCE A TS, BRUCE JCT, MILTON SS, WILLOW CREEK JCT,BRANTFORD TS, NEWPORT JCT, MIDDLEPORT TS,BECK 2 TS, MID RIVER JCT NIAGARA,MIDDLEPORT TS,CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,CLAIREVILLE TS, ESSA TS,DETWEILER TS, STRATFORD JCT, SEAFORTH TS, STRATFORD TS,LONGWOOD TS | B502M.BAXBJ, B502M.BJXMI, B502M.BJXWJ, 21-B502M, 40-B502M,M32W.NEXBR, M32W.NEXMI, YZ, 25-M32W, 44M32W-19, T4-M32W,BP76.PAXBE, K2L76, L35L76, R76, TL35-BO1,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1,C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,E510V.CLXES, AL510, W3L510, 18-E510V, 51-E510V,B22D.STXDE, B22D.STXST, 26-B22D, 68T1-B22D, 61B22D-26,R5N, T5L45, SS5, T5, R5, T5-H, T5-LT5,25-Q23BM, L23HT6, D2L23, Q23BM-TEMP1 | 1-00239284 Rev. #3,1-00238922 Rev. #11,1-00181622 Rev. #28,1-00220299 Rev. #39,1-00213473 Rev. #37,1-00235682 Rev. #6,1-00237157 Rev. #9,1-00239308 Rev. #10,1-00235814 Rev. #13,1-00246468 Rev. #2 | 8 Hour(s),6 Hour(s),Non-recallable,Non-recallable,Non-recallable,14 Day(s),4 Hour(s),5 Day(s),4 Hour(s),6 Hour(s) | FABCW | 2300
2024-04-14 16:00 | 2024-04-19 16:00 | CLAIREVILLE TS, ESSA TS,KENT TS, CHATHAM SS, GSPC JCT,DETWEILER TS, STRATFORD JCT, SEAFORTH TS, STRATFORD TS,CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,MIDDLEPORT TS,BECK 2 TS, MID RIVER JCT NIAGARA,BRUCE A TS, BRUCE JCT, MILTON SS, WILLOW CREEK JCT,LONGWOOD TS | E510V.CLXES, AL510, W3L510, 18-E510V, 51-E510V,T1B, T1Y, T4Z, 5-L28C, 86-L28C, T1, T4, T1-L28C, T4L28C, 312L28C-MSO2,B22D.STXDE, B22D.STXST, 26-B22D, 68T1-B22D, 61B22D-26,C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1,BP76.PAXBE, K2L76, L35L76, R76, TL35-BO1,25-Q23BM, L23HT6, D2L23, Q23BM-TEMP1,D1D2, D1L29, D1L27, L33L40, SC22D1, SC22SC, 25-M33W, D1_BUS, SC22, SS2-D, D1L34, D1L33,B502M.BAXBJ, B502M.BJXMI, B502M.BJXWJ, 21-B502M, 40-B502M,R5N, T5L45, SS5, T5, R5, T5-H, T5-LT5 | 1-00235682 Rev. #6,1-00238919 Rev. #6,1-00237157 Rev. #9,1-00213473 Rev. #37,1-00220299 Rev. #39,1-00181622 Rev. #28,1-00246468 Rev. #2,1-00238390 Rev. #3,1-00235814 Rev. #13,1-00239308 Rev. #10 | 14 Day(s),12 Hour(s),4 Hour(s),Non-recallable,Non-recallable,Non-recallable,6 Hour(s),2 Hour(s),4 Hour(s),5 Day(s) | FABCW | 2300
2024-05-26 07:00 | 2024-05-31 08:00 | ALLANBURG TS, BECK 2 TS, MID RIVER JCT NIAGARA, CROSSLINE JCT, MIDDLEPORT TS, CALEDONIA Q35M JCT,CLAIREVILLE TS,BRUCE B SS, BRUCE JCT, WILLOW CREEK JCT, MILTON SS,LONGWOOD DESN, LAMBTON TS 2, LONGWOOD JCT, LONGWOOD TS,CHERRYWOOD TS, PARKWAY JCT, CLAIREVILLE TS, PARKWAY TS,MIDDLEPORT TS,DETWEILER TS, STRATFORD TS, ZURICH JCT | BP76.PAXBE, Q35M.MIXCA, Q35M.QUXAL, D2HT4, H2HT4, K2L76, L26L35, L30TL35, L34L35, L35L76, T4, R76,W3L570, W3L510, T15, T15-HT15, T15-W3, T15-SS2,B501M.BBXBJ, B501M.BJXWJ, B501M.WJXMI, 40-B501M, 29-B501M,L24L.LOXLA, L24L.LOXLD, L24L.LOXLO, AL24, T14Q, T3L24, 27-L24L, T14, T14-L24L, W52-L24L,C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, HT4L550, JL550, W2L550, W3L550,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1, 51-C550VP, 52-C550VP, 81-C550VP,26-B23D, 68T2-B23D, 364B23D-MSO1 | 1-00181648 Rev. #9,1-00238525 Rev. #10,1-00237165 Rev. #9,1-00236074 Rev. #16,1-00213473 Rev. #37,1-00220299 Rev. #39,1-00236150 Rev. #5,1-00238602 Rev. #4 | 4 Hour(s),4 Hour(s),4 Hour(s),8 Day(s),Non-recallable,Non-recallable,4 Hour(s),4 Hour(s) | FABCW | 2800
2024-08-11 06:00 | 2024-08-16 08:00 | MILTON SS, TRAFALGAR TS,BRUCE A TS, UNDERWOOD JCT, HANOVER TS, UNDERWOOD WGS,BURLINGTON TS, HORNING JCT, HORNING TS, MIDDLEPORT TS,CALEDONIA TS, GRAND JCT,LAMBTON TS 2, ST. CLAIRX TS,MIDDLEPORT TS | M573T.MIXTR, HL573, L502L573, 40-M573T, T15-M573T,B4V.BRXUN, B4V.UNXUN, T4A, 21-B4V, 36B4V-22, 7014B5V-MSO2, 36T4-B4V,M28B.HOXBU, M28B.HOXHO, M28B.HOXMI, 25-M28B, 39-M28B, 4T3-M28B,T2Y, 25-N5M, T2, N27T2-N5M, 310N5M-LC2,L51D.CLXLA, K1L51, L23L51, PS51-2, PS51-1, PS51-S, PS51,T6, T6-LT6, T6-TL581, LT6BUS-TEMP1 | 1-00208773 Rev. #10,1-00241126 Rev. #2,1-00238498 Rev. #3,1-00238512 Rev. #2,1-00235998 Rev. #3,1-00220299 Rev. #39 | 14 Day(s),10 Hour(s),6 Hour(s),10 Hour(s),4 Hour(s),Non-recallable | FABCW | 550
2024-11-04 08:00 | 2024-11-15 17:00 | MIDDLEPORT TS, MILTON SS, NANTICOKE TS,BECK 2 TS,CLAIREVILLE TS, ESSA TS,KENT TS, CHATHAM SS, GSPC JCT,BRUCE A TS, UNDERWOOD JCT, HANOVER TS, UNDERWOOD WGS | M585M.MIXMD, N581M.MDXNA, L81L85, T6L31, 25-M585M, 25-N581M, 40-M585M, 59-N581M, L581_BUS, T6, T6-LT6, T6-TL581, L23HT6,28-PA302, T302, T302-1,N581M.MDXNA, AL581, T7L581, T7T12, HT7_BUS,E511V.CLXES, DL511, W2L511, 18-E511V, 51-E511V,T1B, T1Y, T4Z, 5-L28C, 86-L28C, T1, T4, T1-L28C, T4L28C, 312L28C-MSO2,B4V.BRXUN, B4V.UNXUN, T4A, 21-B4V, 36B4V-22, 36T4-B4V, 161B5V-MSO1, 21-B5V | 1-00238465 Rev. #1,1-00238560 Rev. #1,1-00238433 Rev. #2,1-00238434 Rev. #2,1-00238492 Rev. #2,1-00238538 Rev. #1,1-00240028 Rev. #2,1-00241127 Rev. #1 | 4 Hour(s),8 Hour(s),Non-recallable,Non-recallable,Non-recallable,48 Hour(s),12 Hour(s),10 Hour(s) | FABCW | 1000
2024-11-17 07:15 | 2024-11-28 17:00 | BRUCE A TS, MAJESTIC JCT, MAJESTIC CTS, WINGHAM JCT, SEAFORTH TS, WINGHAM TS,MIDDLEPORT TS, MILTON SS, NANTICOKE TS,BECK 2 TS,CLAIREVILLE TS, ESSA TS,KENT TS, CHATHAM SS, GSPC JCT | B23D.MJXBR, B23D.MJXMJ, B23D.MJXWI, B23D.WIXSE, B23D.WIXWI, T2-B23D, 21-B23D, 61B23D-21,M585M.MIXMD, N581M.MDXNA, L81L85, T6L31, 25-M585M, 25-N581M, 40-M585M, 59-N581M, L581_BUS, T6, T6-LT6, T6-TL581, L23HT6,N581M.MDXNA, AL581, T7L581, T7T12, HT7_BUS,28-PA302, T302, T302-1,E511V.CLXES, DL511, W2L511, 18-E511V, 51-E511V,T1B, T1Y, T4Z, 5-L28C, 86-L28C, T1, T4, T1-L28C, T4L28C, 312L28C-MSO2 | 1-00241121 Rev. #1,1-00238465 Rev. #1,1-00238433 Rev. #2,1-00238560 Rev. #1,1-00238434 Rev. #2,1-00238492 Rev. #2,1-00238538 Rev. #1,1-00240028 Rev. #2 | 4 Hour(s),4 Hour(s),Non-recallable,8 Hour(s),Non-recallable,Non-recallable,48 Hour(s),12 Hour(s) | FABCW | 800
Back to main menu