## Motor Eligible Measures List
IAP - Retrofit Program - Motors Eligible Measures Worksheet - May 1, 2017
Motors must operate a minimum of 2,000 hours per year to be eligible for Participant Incentives. Only 3-phase motors meeting or exceeding the Efficiency Levels of the Nameplate NEMA Full Load Nominal Efficiency as listed in CEE Motors List (January 2012) below are eligible. Note: New construction or major renovation projects which are eligible under the IAP High Performance New Construction Program are not eligible under the IAP RETROFIT Program. INSTRUCTIONS: In order to calculate the Participant Incentive amount, enter the number of motors to be installed in the 'Quantity' row. Based on the type (ODP/TEFC), size (HP), speed (RPM), and efficiency of the motor, determine the Participant Incentive per motor and enter this amount in the 'Participant Incentive ($/Motor)' row. The 'Total Participant Incentive' row will automatically populate based on this information. The 'Required Information' must also be completed for each unit. The sum of the 'Total Participant Incentive' amounts will be automatically populated in the 'TOTAL PARTICIPANT INCENTIVE REQUESTED' field at the bottom of the worksheet. For more than five motor types, please use an additional copy of this worksheet. In order to receive your Participant Incentive payment, invoices showing proof of payment must be submitted to the IESO. It is recommended that you provide manufacturer technical specification sheets demonstrating that the equipment meets the program requirements including the applicable NEMA rated efficiency. You may be required to provide additional information in connection with your Project in order for your Application to be approved.
OPEN DRIP-PROOF (ODP) MOTORS
| Motor Size (HP) | Assumed Base Case | Nameplate NEMA Full Load Minimum Nominal Efficiency | Assumed Base Case | Nameplate NEMA Full Load Minimum Nominal Efficiency | Assumed Base Case | Nameplate NEMA Full Load Minimum Nominal Efficiency | Participant Incentive ($/Motor)
|  | Speed: 1200 RPM |  | Speed: 1800 RPM |  | Speed: 3600 RPM
| 1 | 82.5% | 83.5% | 85.5% | 86.5% | 77% | 78% | 5
| 1.5 | 86.5% | 87.5% | 86.5% | 87.5% | 84% | 85% | 5
| 2 | 87.5% | 88.5% | 86.5% | 87.5% | 85.5% | 86.5% | 7
| 3 | 88.5% | 89.5% | 89.5% | 90.5% | 85.5% | 86.5% | 10
| 5 | 89.5% | 90.5% | 89.5% | 90.5% | 86.5% | 87.5% | 15
| 7.5 | 90.2% | 91.2% | 91% | 92% | 88.5% | 89.5% | 25
| 10 | 91.7% | 92.7% | 91.7% | 92.7% | 89.5% | 90.5% | 30
| 15 | 91.7% | 92.7% | 93% | 94% | 90.2% | 91.2% | 45
| 20 | 92.4% | 93.4% | 93% | 94% | 91% | 92% | 65
| 25 | 93% | 94% | 93.6% | 94.6% | 91.7% | 92.7% | 80
| 30 | 93.6% | 94.6% | 94.1% | 95.1% | 91.7% | 92.7% | 95
| 40 | 94.1% | 95.1% | 94.1% | 95.1% | 92.4% | 93.4% | 125
| 50 | 94.1% | 95.1% | 94.5% | 95.5% | 93% | 94% | 155
| 60 | 94.5% | 95.5% | 95% | 96% | 93.6% | 94.6% | 180
| 75 | 94.5% | 95.5% | 95% | 96% | 93.6% | 94.6% | 230
| 100 | 95% | 96% | 95.4% | 96.4% | 93.6% | 94.6% | 300
| 125 | 95% | 96% | 95.4% | 96.4% | 94.1% | 95.1% | 375
| 150 | 95.4% | 96.4% | 95.8% | 96.8% | 94.1% | 95.1% | 450
| 200 | 95.4% | 96.4% | 95.8% | 96.8% | 95% | 96% | 595
TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS
| Motor Size (HP) | Assumed Base Case | Nameplate NEMA Full Load Minimum Nominal Efficiency | Assumed Base Case | Nameplate NEMA Full Load Minimum Nominal Efficiency | Assumed Base Case | Nameplate NEMA Full Load Minimum Nominal Efficiency | Participant Incentive ($/Motor)
|  | Speed: 1200 RPM |  | Speed: 1800 RPM |  | Speed: 3600 RPM
| 1 | 82.5% | 83.5% | 85.5% | 86.5% | 77% | 78% | 5
| 1.5 | 87.5% | 88.5% | 86.5% | 87.5% | 84% | 85% | 5
| 2 | 88.5% | 89.5% | 86.5% | 87.5% | 85.5% | 86.5% | 7
| 3 | 89.5% | 90.5% | 89.5% | 90.5% | 86.5% | 87.5% | 10
| 5 | 89.5% | 90.5% | 89.5% | 90.5% | 88.5% | 89.5% | 15
| 7.5 | 91% | 92% | 91.7% | 92.7% | 89.5% | 90.5% | 25
| 10 | 91% | 92% | 91.7% | 92.7% | 90.2% | 91.2% | 30
| 15 | 91.7% | 92.7% | 92.4% | 93.4% | 91% | 92% | 45
| 20 | 91.7% | 92.7% | 93% | 94% | 91% | 92% | 65
| 25 | 93% | 94% | 93.6% | 94.6% | 91.7% | 92.7% | 80
| 30 | 93% | 94% | 93.6% | 94.6% | 91.7% | 92.7% | 95
| 40 | 94.1% | 95.1% | 94.1% | 95.1% | 92.4% | 93.4% | 125
| 50 | 94.1% | 95.1% | 94.5% | 95.5% | 93% | 94% | 155
| 60 | 94.5% | 95.5% | 95% | 96% | 93.6% | 94.6% | 180
| 75 | 94.5% | 95.5% | 95.4% | 96.4% | 93.6% | 94.6% | 230
| 100 | 95% | 96% | 95.4% | 96.4% | 94.1% | 95.1% | 300
| 125 | 95% | 96% | 95.4% | 96.4% | 95% | 96% | 375
| 150 | 95.8% | 96.8% | 95.8% | 96.8% | 95% | 96% | 450
| 200 | 95.8% | 96.8% | 96.2% | 97.2% | 95.4% | 96.4% | 595
IAP - Retrofit Program - Motors Eligible Measures Worksheet - May 1, 2017
Required Information |  |  | Example |  | #1 | #2 | #3 | #4 | #5
Reason: “N”=New or “F”=Failed |  |  | N
Location: Building and Room |  |  | North Pump
Function: Fan, Pump, Process, Other |  |  | Pump
Manufacturer |  |  | ABC
Model Number |  |  | GH553
“ODP” or “TEFC” |  |  | TEFC
Size in Horsepower |  |  | 30
Speed in RPM |  |  | 1800
Nameplate NEMA Full Load Nominal Efficiency |  |  | 94.5%
Annual Run Hours (actual) |  |  | 5000
Quantity |  |  | 5
Participant Incentive ($/Motor) |  |  | 95
Total Participant Incentive |  |  | 475 |  | 0 | 0 | 0 | 0 | 0
Note: The Eligible Measures Lists and Eligible Measures Worksheets are based on assumptions and are subject to change and the incentive amounts do not include HST or other applicable taxes.
[5 empty] | TOTAL PARTICIPANT INCENTIVE REQUESTED: |  |  |  | 0
Name of Applicant:
Company Name:
Building Address:

## Version Control (hidden)
Version Number | 6
Month | May
Day | 1
Year | 2017
Make sure to update the version number on the footer as there is no Excel function that can currently do this automatically

## Revision History (hidden)
Version Number | Date | Revision Type | Tab | Details
5 | 2013-12-19 | Formatting | Motor Eligible Measures List | Blank columns and rows (far right and bottom) were hidden
5 | 2013-12-19 | Formatting | Version Control | Version control updated. Version: 5.0 Date: January 31, 2014
5 | 2013-12-31 | Clarification | Motor Eligible Measures List | Assumed Base Case columns were added (Columns C,F and G)
5 | 2014-01-01 | Revison No. | Motor Eligible Measures List | Footer Revision No. was changed from V4.0 to V5.0
5 | 2014-12-05 | Revison No. | Motor Eligible Measures List | Footer Revision No. was changed from V4.0 to V5.0