## General Instructions
General Instructions:
The workbook covers the project specifications and testing procedures for the DER test cases.
1. The 'Project Specifications' worksheet includes the list of attributes of the DER resources to be completed.
1a. The project specifications are to be completed for each aggregated resources and each individual resource that is not part of an aggregate.
1b. The specifications table has been set up for a default of three aggregated and/or individual resources. If more there are more than three resources, please expand the table as needed by copying and pasting the values columns for each additional resource.
1c. The value for power capacity of the resource that is to be provided is the simultaneous aggregated resource peak value (an example is provided below).
2. The 'Outline' worksheet includes a description of the test and test values that are to be filled out.
2a. The test values (expected and measured) are to be completed for each aggregated resources and each individual resource that is not part of an aggregate.
2b. The tables have been set up for a default of four instances of a test. If more there are more than four instances, please expand the tables as needed by copying and pasting the values columns for each additional test instance
2c. The tables have been set up for a default of three aggregated and/or individual resources. If there are more than three resources, please expand the tables as needed by copying and pasting the table for each additional resource.
3. The 'Procedure' worksheet includes a high level description of the steps involved in the test case.
Notes:
For individual resource or aggregation time series data, including metering data, the data shall be recorded and made available to the IESO for the time and duration indicated in the test plan document.
Any data (before, during, and after testing) that can inhibit a resource’s performance when providing the desired sevices should be captured and disclosed in the test case.
Simultaneous Aggregated Resource Peak Example:
Simultaneous aggregated resource peak = the maximum energy demand or output for an aggregation of DERs as constrained by the lesser of local system or resource limits.
The following example shows the difference between the total peak value and the simultaneous aggregated resource peak (considering resource and/or system limitations), value of the project:
Project Description:
A project consists of 6 six electric vehicles (EVs) on a feeder, with a maximum charging power 10 kW for each EV. The maximum number of EVs that will charge simultaneously is 4, due to a limitation of the distribution station transformer.
The total max capacity (i.e. the total peak value) of the project is 60 kW (6 EVs x 10 kW).
The power capacity of the resource (i.e. Simultaneous aggregated resource peak) of the project is 40 kW (4 EVs x 10 kW).
Note: In some projects, the total max capacity equals the power capacity of the resource.
Project Resources - Relationship Types
The diagram below illustrates the relationship types between the project, the aggregate resources and the individual resources and also provide examples of attributes that are required.

## Project Specifications
Test Case Project Specifications - Demand Response and Transactive Energy
Step 1 of 2: For the project, please complete the following table.
Project | Value
Project Name
Business Name and Address of Commercial Participant(s) (Note: names and addresses of residential Participants or residences are excluded)
Project Testing Duration (a date range)
Program Funding Sources
Step 2 of 2: For each aggregated resource or each individual resource not part of an aggregate, please complete the following table.
Specifications | Unit | Resource #1 Value | Resource #2 Value | Resource #3 Value
Description of Resources (if aggregated, include a description of the resources that make up the aggregation). | N/A
Individual Resource (i.e. not part of an aggregation) (Y/N) | Y or N
Aggregated Resource (Y/N) | Y or N
Aggregated Resource - Number of individual resources that make up the aggregation | N/A
Local Distribution Company ("LDC") | N/A
LDC Wholesale Market Delivery Point ID(s) | N/A
Delivery Point ID (deemed commercial point of delivery as determined by the LDC) | N/A
Substation(s) at connection point to IESO-Controlled Grid | N/A
Location (Address in Ontario)1 | N/A
Technology Type(s) | N/A
Power Capacity of a Resource That Cannot Store Energy2 | kW
Maximum Discharging Rate of the Resource* (if applicable) | kW
Maximum Charging Rate of the Resource2 (if applicable) | kW
Energy Storage Capacity of the Resource2 (if applicable) | kWh
Operating (Ambient) Temperature Range Certified by Equipment Manufacturer | deg. C
Resource ID1 | N/A
1Not to be collected from a residential Participant.
2If aggregated, enter the simultaneous aggregated resource peak value of the resources that make up the aggregation (see example in General Instructions).

## Outline
Test Case Outline - Demand Response and Transactive Energy
Demand Response
This Test Case assesses the ability of the DER to respond to future events based on programmed rules or a signal at least several hours in advance of the required activity.
The system should automatically respond at the correct time and carry out the desired task.
This includes charge management activities for scheduling if applicable (i.e. if the task requires full charge at a certain time, the system should automatically manage the capacity).
Resources completing DR testing should familiarize themselves with IESO Market Manual 12.0 Section 5.3.3 for full testing procedures of capacity auction resources including success criteria.
Description
This test will simulate having a kW-day obligation from the IESO Demand Response Auction for the summer and/or winter period.
The DR must be offered during 'availability periods' (summer months is 12:00-21:00, winter is 16:00-21:00), or the provider would face penalties.
The DR is scheduled during the 'availability periods'- with a maximum of four hours called.
Note:
DR is not called during every availability period; it is based on a 'standby' notice (typically issued day ahead) indicating it may be called, then an activation 'pre-dispatch reports' which schedules
DR for 2.5 hours ahead
This test will start at a pre-determined time, without prior knowledge of the state of charge. The participant will receive an activation notice approximately 2.5 hours in advance of activation.
The participant will be required to provide full capacity for the entire availability period. The test may be repeated more than once. The data points must be recorded and time-stamped.
Notes:
1. Project operators are required to manage the state of charge (if applicable).
2. Prior to test case implementation, please consult with the IESO regarding any additional test timing conditions to satisfy contract requirements.
Step 1 of 1: For each aggregated resource or each individual resource not part of an aggregate, please complete the following table.
Notes:
1. All blank cells are to be completed by the participant, including the Test Observation Notes field (as needed).
2. For the Measured Value cells, please enter the data in the cell if the data is a single value. If the data is made up multiple values (e.g. time series data), please enter the reference data file name in the cell and attach the necessary corresponding file when reporting.
3. The sampling period for the Measured Values should be between 4 seconds and 5-minutes. The IESO's preference is for a faster sampling period, if possible.
DER Resource #1
Category | Specifications | Notes | Unit | Test Observation Notes | Test Cycle #1 Expected Value | Test Cycle #1 Measured Value | Test Cycle #2 Expected Value | Test Cycle #2 Measured Value | Test Cycle #3 Expected Value | Test Cycle #3 Measured Value | Test Cycle #4 Expected Value | Test Cycle #4 Measured Value
Resource ID | Resource ID | N/A | N/A |  | N/A |  | N/A |  | N/A |  | N/A
Test Date | Day | The date of the test (may be a range). | Date |  | N/A |  | N/A |  | N/A |  | N/A
Test Time | Time | The time of the test (may be a range). | Time |  | N/A |  | N/A |  | N/A |  | N/A
Expected and Measured Values | Offered DR Power Capacity | The target/offered amount of Demand Response Capacity being tested for this test case | kW
Expected and Measured Values | Offered DR Ramp Rate - Ramp down rate | The target/offered amount of Demand Response Ramp Rate being tested for this test case | kW/min
Expected and Measured Values | Offered DR Ramp Rate - Ramp up rate | The target/offered amount of Demand Response Ramp Rate being tested for this test case | kW/min
Expected and Measured Values | Instantaneous Accuracy | Minimum acceptable value: 15% as measured by: [Power output/input (AC) - Offered DR Capacity] ÷ Offered DR Capacity The IESO DR auction has a compliance deadband of +15%. | +/- X%
Expected and Measured Values | Maximum Sampling Rate | The maximum rate at which the each kW based data point can be sampled | Samples per Second
Measured Values Only | Measured Power output/input (AC) - delivery point level | Record the AC power entering or exiting each delivery point to the distribution system. | kW |  | N/A |  | N/A |  | N/A |  | N/A
Measured Values Only | System Temperature | Measure the system temperature, monitoring for overheating (if applicable). Maximum sampling period is 10 minutes. | deg. C |  | N/A |  | N/A |  | N/A |  | N/A
Measured Values Only | Ambient Temperature | Measure the ambient temperature. Maximum sampling period is 10 minutes. | deg. C |  | N/A |  | N/A |  | N/A |  | N/A
Measured Values Only | Grid voltage | Observed grid voltage at or near each tested delivery point. | V |  | N/A |  | N/A |  | N/A |  | N/A
DER Resource #2
Category | Specifications | Notes | Unit | Test Observation Notes | Test Cycle #1 Expected Value | Test Cycle #1 Measured Value | Test Cycle #2 Expected Value | Test Cycle #2 Measured Value | Test Cycle #3 Expected Value | Test Cycle #3 Measured Value | Test Cycle #4 Expected Value | Test Cycle #4 Measured Value
Resource ID | Resource ID | N/A | N/A |  | N/A |  | N/A |  | N/A |  | N/A
Test Date | Day | The date of the test (may be a range). | Date |  | N/A |  | N/A |  | N/A |  | N/A
Test Time | Time | The time of the test (may be a range). | Time |  | N/A |  | N/A |  | N/A |  | N/A
Expected and Measured Values | Offered DR Power Capacity | The target/offered amount of Demand Response Capacity being tested for this test case | kW
Expected and Measured Values | Offered DR Ramp Rate - Ramp down rate | The target/offered amount of Demand Response Ramp Rate being tested for this test case | kW/min
Expected and Measured Values | Offered DR Ramp Rate - Ramp up rate | The target/offered amount of Demand Response Ramp Rate being tested for this test case | kW/min
Expected and Measured Values | Instantaneous Accuracy | Minimum acceptable value: 15% as measured by: [Power output/input (AC) - Offered DR Capacity] ÷ Offered DR Capacity The IESO DR auction has a compliance deadband of +15%. | +/- X%
Expected and Measured Values | Maximum Sampling Rate | The maximum rate at which the each kW based data point can be sampled | Samples per Second
Measured Values Only | Measured Power output/input (AC) - delivery point level | Record the AC power entering or exiting each delivery point to the distribution system. | kW |  | N/A |  | N/A |  | N/A |  | N/A
Measured Values Only | System Temperature | Measure the system temperature, monitoring for overheating (if applicable). Maximum sampling period is 10 minutes. | deg. C |  | N/A |  | N/A |  | N/A |  | N/A
Measured Values Only | Ambient Temperature | Measure the ambient temperature. Maximum sampling period is 10 minutes. | deg. C |  | N/A |  | N/A |  | N/A |  | N/A
Measured Values Only | Grid voltage | Observed grid voltage at or near each tested delivery point. | V |  | N/A |  | N/A |  | N/A |  | N/A
DER Resource #3
Category | Specifications | Notes | Unit | Test Observation Notes | Test Cycle #1 Expected Value | Test Cycle #1 Measured Value | Test Cycle #2 Expected Value | Test Cycle #2 Measured Value | Test Cycle #3 Expected Value | Test Cycle #3 Measured Value | Test Cycle #4 Expected Value | Test Cycle #4 Measured Value
Resource ID | Resource ID | N/A | N/A |  | N/A |  | N/A |  | N/A |  | N/A
Test Date | Day | The date of the test (may be a range). | Date |  | N/A |  | N/A |  | N/A |  | N/A
Test Time | Time | The time of the test (may be a range). | Time |  | N/A |  | N/A |  | N/A |  | N/A
Expected and Measured Values | Offered DR Power Capacity | The target/offered amount of Demand Response Capacity being tested for this test case | kW
Expected and Measured Values | Offered DR Ramp Rate - Ramp down rate | The target/offered amount of Demand Response Ramp Rate being tested for this test case | kW/min
Expected and Measured Values | Offered DR Ramp Rate - Ramp up rate | The target/offered amount of Demand Response Ramp Rate being tested for this test case | kW/min
Expected and Measured Values | Instantaneous Accuracy | Minimum acceptable value: 15% as measured by: [Power output/input (AC) - Offered DR Capacity] ÷ Offered DR Capacity The IESO DR auction has a compliance deadband of +15%. | +/- X%
Expected and Measured Values | Maximum Sampling Rate | The maximum rate at which the each kW based data point can be sampled | Samples per Second
Measured Values Only | Measured Power output/input (AC) - delivery point level | Record the AC power entering or exiting each delivery point to the distribution system. | kW |  | N/A |  | N/A |  | N/A |  | N/A
Measured Values Only | System Temperature | Measure the system temperature, monitoring for overheating (if applicable). Maximum sampling period is 10 minutes. | deg. C |  | N/A |  | N/A |  | N/A |  | N/A
Measured Values Only | Ambient Temperature | Measure the ambient temperature. Maximum sampling period is 10 minutes. | deg. C |  | N/A |  | N/A |  | N/A |  | N/A
Measured Values Only | Grid voltage | Observed grid voltage at or near each tested delivery point. | V |  | N/A |  | N/A |  | N/A |  | N/A

## Procedure
Test Case Procedure - Demand Response and Transactive Energy
Section | Step # | Description
Initialize Test | 1 | Determine offered DR kW. Note: DR is scheduled from 12:00-21:00 during the summer and 16:00-21:00 during the winter - with a maximum of four hours called.
Initialize Test | 2 | Final review of system to ensure its prepared for test.
Test | 3 | Ensure DR capacity will be available (e.g., charge batteries) for the dispatch at 13:00 (summer) or 17:00 (winter).
Test | 4 | Verify the system has started to output the correct amount of DR.
Test | 5 | The system should be outputting power steadily, acting as a DR resource, as programmed. Periodically confirm temperature/other factors are as expected. Also, verify the DER has sufficient capacity to complete the test.
Test | 6 | Confirm DR stops after the four hour dispatch period is completed.
Ending | 7 | Return the overall system to normal operation.
Ending | 8 | Confirm the appropriate data points were gathered. Note any unexpected behavior in test log.
Self-Assesment | 9 | A successful test can be determined if a DER is able to appropriately reduce consumption or curtail load in response to the activation notice.