## General Instructions
General Instructions:
The workbook covers the project specifications and testing procedures for the DER test cases.
1. The 'Project Specifications' worksheet includes the list of attributes of the DER resources to be completed.
1a. The project specifications are to be completed for each aggregated resources and each individual resource that is not part of an aggregate.
1b. The specifications table has been set up for a default of three aggregated and/or individual resources. If more there are more than three resources, please expand the table as needed by copying and pasting the values columns for each additional resource.
1c. The value for power capacity of the resource that is to be provided is the simultaneous aggregated resource peak value (an example is provided below).
2. The 'Outline' worksheet includes a description of the test and test values that are to be filled out.
2a. The test values (expected and measured) are to be completed for each aggregated resources and each individual resource that is not part of an aggregate.
2b. The tables have been set up for a default of four instances of a test. If more there are more than four instances, please expand the tables as needed by copying and pasting the values columns for each additional test instance
2c. The tables have been set up for a default of three aggregated and/or individual resources. If there are more than three resources, please expand the tables as needed by copying and pasting the table for each additional resource.
3. The 'Procedure' worksheet includes a high level description of the steps involved in the test case.
Notes:
For individual resource or aggregation time series data, including metering data, the data shall be recorded and made available to the IESO for the time and duration indicated in the test plan document.
Any data (before, during, and after testing) that can inhibit a resource’s performance when providing the desired sevices should be captured and disclosed in the test case.
Simultaneous Aggregated Resource Peak Example:
Simultaneous aggregated resource peak = the maximum energy demand or output for an aggregation of DERs as constrained by the lesser of local system or resource limits.
The following example shows the difference between the total peak value and the simultaneous aggregated resource peak (considering resource and/or system limitations), value of the project:
Project Description:
A project consists of 6 six electric vehicles (EVs) on a feeder, with a maximum charging power 10 kW for each EV. The maximum number of EVs that will charge simultaneously is 4, due to a limitation of the distribution station transformer.
The total max capacity (i.e. the total peak value) of the project is 60 kW (6 EVs x 10 kW).
The power capacity of the resource (i.e. Simultaneous aggregated resource peak) of the project is 40 kW (4 EVs x 10 kW).
Note: In some projects, the total max capacity equals the power capacity of the resource.
Project Resources - Relationship Types
The diagram below illustrates the relationship types between the project, the aggregate resources and the individual resources and also provide examples of attributes that are required.

## Project Specifications
Test Case Project Specifications - Operating Reserve
Step 1 of 2: For the project, please complete the following table.
Project | Value
Project Name
Business Name and Address of Commercial Participant(s) (Note: names and addresses of residential Participants or residences are excluded)
Project Testing Duration (a date range)
Program Funding Sources
Step 2 of 2: For each aggregated resource or each individual resource not part of an aggregate, please complete the following table.
Specifications | Unit | Resource #1 Value | Resource #2 Value | Resource #3 Value
Description of Resources (if aggregated, include a description of the resources that make up the aggregation). | N/A
Individual Resource (i.e. not part of an aggregation) (Y/N) | Y or N
Aggregated Resource (Y/N) | Y or N
Aggregated Resource - Number of individual resources that make up the aggregation | N/A
Local Distribution Company ("LDC") | N/A
LDC Wholesale Market Delivery Point ID(s) | N/A
Delivery Point ID (deemed commercial point of delivery as determined by the LDC) | N/A
Substation(s) at connection point to IESO-Controlled Grid | N/A
Location (Address in Ontario)1 | N/A
Technology Type(s) | N/A
Power Capacity of a Resource That Cannot Store Energy2 | kW
Maximum Discharging Rate of the Resource* (if applicable) | kW
Maximum Charging Rate of the Resource2 (if applicable) | kW
Energy Storage Capacity of the Resource2 (if applicable) | kWh
Operating (Ambient) Temperature Range Certified by Equipment Manufacturer | deg. C
Resource ID1 | N/A
1Not to be collected from a residential Participant.
2If aggregated, enter the simultaneous aggregated resource peak value of the resources that make up the aggregation (see example in General Instructions).

## Outline
Test Case Outline - Operating Reserve
Operating Reserve
This test case will involve multiple test cycles to assess the ability of each Resource to provide 10-minute spinning operating reserve and/or 30-minute operative reserve.
In each test cycle, the resource shall reach its target level of energy injection or withdrawal within 10 minutes (or 30 minutes) of activation and sustain that target level for a minimum of 60 minutes.
Evaluations will consider availability, consistency and repeatability over a time period specified by the IESO.
Resources completing Operating Reserve (O.R.) testing should familiarize themselves with IESO Performance Standards for O.R. found in the IESO Market Rules Appendix 5.1 - Section 1.2
Description
This test will simulate or trigger O.R. Activations as per agreed protocol with the IESO.
There will be no advance notice or preparation prior to each O.R. test. The O.R. Activations shall be for a minimum of 60 minutes.
The results of the test will be evaluated on the basis of each of the individual DERs or DER aggregation defined in the Project Specifications tab in this spreadsheet.
The test may be repeated more than once. The data points must be recorded and time-stamped.
Notes:
1. Project operators are required to manage the state of charge (if applicable).
2. Prior to test case implementation, please consult with the IESO regarding any additional test timing conditions to satisfy contract requirements.
Step 1 of 1: For each aggregated resource or each individual resource not part of an aggregate, please complete the following table.
Notes:
1. All blank cells are to be completed by the participant, including the Test Observation Notes field (as needed).
2. For the Measured Value cells, please enter the data in the cell if the data is a single value. If the data is made up multiple values (e.g. time series data), please enter the reference data file name in the cell and attach the necessary corresponding file when reporting.
3. The sampling period for the Measured Values should be between 4 seconds and 5-minutes. The IESO's preference is for a faster sampling period, if possible.
DER Resource #1
Category | Specifications | Notes | Unit | Test Observation Notes | Test Cycle #1 Expected Value | Test Cycle #1 Measured Value | Test Cycle #2 Expected Value | Test Cycle #2 Measured Value | Test Cycle #3 Expected Value | Test Cycle #3 Measured Value | Test Cycle #4 Expected Value | Test Cycle #4 Measured Value
Resource ID | Resource ID | N/A | N/A |  | N/A |  | N/A |  | N/A |  | N/A
Test Date | Day | The date of the test (may be a range). | Date |  | N/A |  | N/A |  | N/A |  | N/A
Test Time | Time | The time of the test (may be a range). | Time |  | N/A |  | N/A |  | N/A |  | N/A
Test Time | Operating Reserve Activation Call | Time stamp of O.R. Activation Call | Time |  | N/A |  | N/A
Expected and Measured Values | Average Power Output | Based on a 1 hour of operation and must account for losses as well as capacity limits | kW
Expected and Measured Values | Ramp Rate | The OR bid must be accompanied with the submission of a ramp rate. First test the fastest ramp rate then later try with slower rates. | kW/min
Expected and Measured Values | Ramp Rate Accuracy | How closely does the facility follow the submitted ramp rate. | +/- X%
Expected and Measured Values | Instantaneous Accuracy | Always remain within the acceptable range of power output, with the exception of ramp up and ramp down periods | +/- X%
Expected and Measured Values | O.R. dispatch quantity | Target Power output/input (AC) - delivery point level for O.R. Activation call | kW
Measured Values Only | Measured Power output/input (AC) - delivery point level at O.R. Call | Record the AC power entering or exiting each delivery point to the distribution system at the timestamp of the O.R. call | kW |  | N/A |  | N/A |  | N/A |  | N/A
Measured Values Only | Measured Power output/input (AC) - delivery point level - O.R. target time | Record the AC power entering or exiting each delivery point to the distribution system at 10 minutes or 30 minutes after or O.R. activation call - depending on class of O.R. being tested | kW
Measured Values Only | System Load | The system load of the facility to view how its operation effects grid operations | kW
Measured Values Only | System Temperature | Measure the system temperature, monitoring for overheating (if applicable). Maximum sampling period is 10 minutes. | deg. C |  | N/A |  | N/A |  | N/A |  | N/A
Measured Values Only | Ambient Temperature | Measure the ambient temperature. Maximum sampling period is 10 minutes. | deg. C |  | N/A |  | N/A |  | N/A |  | N/A
Measured Values Only | Grid voltage | Observed grid voltage at or near each tested delivery point. | V |  | N/A |  | N/A |  | N/A |  | N/A
DER Resource #2
Category | Specifications | Notes | Unit | Test Observation Notes | Test Cycle #1 Expected Value | Test Cycle #1 Measured Value | Test Cycle #2 Expected Value | Test Cycle #2 Measured Value | Test Cycle #3 Expected Value | Test Cycle #3 Measured Value | Test Cycle #4 Expected Value | Test Cycle #4 Measured Value
Resource ID | Resource ID | N/A | N/A |  | N/A |  | N/A |  | N/A |  | N/A
Test Date | Day | The date of the test (may be a range). | Date |  | N/A |  | N/A |  | N/A |  | N/A
Test Time | Time | The time of the test (may be a range). | Time |  | N/A |  | N/A |  | N/A |  | N/A
Test Time | Operating Reserve Activation Call | Time stamp of O.R. Activation Call | Time |  | N/A |  | N/A
Expected and Measured Values | Average Power Output | Based on a 1 hour of operation and must account for losses as well as capacity limits | kW
Expected and Measured Values | Ramp Rate | The OR bid must be accompanied with the submission of a ramp rate. First test the fastest ramp rate then later try with slower rates. | kW/min
Expected and Measured Values | Ramp Rate Accuracy | How closely does the facility follow the submitted ramp rate. | +/- X%
Expected and Measured Values | Instantaneous Accuracy | Always remain within the acceptable range of power output, with the exception of ramp up and ramp down periods | +/- X%
Expected and Measured Values | O.R. dispatch quantity | Target Power output/input (AC) - delivery point level for O.R. Activation call | kW
Measured Values Only | Measured Power output/input (AC) - delivery point level at O.R. Call | Record the AC power entering or exiting each delivery point to the distribution system at the timestamp of the O.R. call | kW |  | N/A |  | N/A |  | N/A |  | N/A
Measured Values Only | Measured Power output/input (AC) - delivery point level - O.R. target time | Record the AC power entering or exiting each delivery point to the distribution system at 10 minutes or 30 minutes after or O.R. activation call - depending on class of O.R. being tested | kW
Measured Values Only | System Load | The system load of the facility to view how its operation effects grid operations | kW
Measured Values Only | System Temperature | Measure the system temperature, monitoring for overheating (if applicable). Maximum sampling period is 10 minutes. | deg. C |  | N/A |  | N/A |  | N/A |  | N/A
Measured Values Only | Ambient Temperature | Measure the ambient temperature. Maximum sampling period is 10 minutes. | deg. C |  | N/A |  | N/A |  | N/A |  | N/A
Measured Values Only | Grid voltage | Observed grid voltage at or near each tested delivery point. | V |  | N/A |  | N/A |  | N/A |  | N/A
DER Resource #3
Category | Specifications | Notes | Unit | Test Observation Notes | Test Cycle #1 Expected Value | Test Cycle #1 Measured Value | Test Cycle #2 Expected Value | Test Cycle #2 Measured Value | Test Cycle #3 Expected Value | Test Cycle #3 Measured Value | Test Cycle #4 Expected Value | Test Cycle #4 Measured Value
Resource ID | Resource ID | N/A | N/A |  | N/A |  | N/A |  | N/A |  | N/A
Test Date | Day | The date of the test (may be a range). | Date |  | N/A |  | N/A |  | N/A |  | N/A
Test Time | Time | The time of the test (may be a range). | Time |  | N/A |  | N/A |  | N/A |  | N/A
Test Time | Operating Reserve Activation Call | Time stamp of O.R. Activation Call | Time |  | N/A |  | N/A
Expected and Measured Values | Average Power Output | Based on a 1 hour of operation and must account for losses as well as capacity limits | kW
Expected and Measured Values | Ramp Rate | The OR bid must be accompanied with the submission of a ramp rate. First test the fastest ramp rate then later try with slower rates. | kW/min
Expected and Measured Values | Ramp Rate Accuracy | How closely does the facility follow the submitted ramp rate. | +/- X%
Expected and Measured Values | Instantaneous Accuracy | Always remain within the acceptable range of power output, with the exception of ramp up and ramp down periods | +/- X%
Expected and Measured Values | O.R. dispatch quantity | Target Power output/input (AC) - delivery point level for O.R. Activation call | kW
Measured Values Only | Measured Power output/input (AC) - delivery point level at O.R. Call | Record the AC power entering or exiting each delivery point to the distribution system at the timestamp of the O.R. call | kW |  | N/A |  | N/A |  | N/A |  | N/A
Measured Values Only | Measured Power output/input (AC) - delivery point level - O.R. target time | Record the AC power entering or exiting each delivery point to the distribution system at 10 minutes or 30 minutes after or O.R. activation call - depending on class of O.R. being tested | kW
Measured Values Only | System Load | The system load of the facility to view how its operation effects grid operations | kW
Measured Values Only | System Temperature | Measure the system temperature, monitoring for overheating (if applicable). Maximum sampling period is 10 minutes. | deg. C |  | N/A |  | N/A |  | N/A |  | N/A
Measured Values Only | Ambient Temperature | Measure the ambient temperature. Maximum sampling period is 10 minutes. | deg. C |  | N/A |  | N/A |  | N/A |  | N/A
Measured Values Only | Grid voltage | Observed grid voltage at or near each tested delivery point. | V |  | N/A |  | N/A |  | N/A |  | N/A

## Procedure
Test Case Procedure - Operating Reserve
Section | Step # | Description
Pretest (in any order) | 1 | Prepare the functionality that will simulate the autonomous activation of the Operative Reserve (O.R.) service.
Pretest (in any order) | 2 | Prepare to perform any pretest scheduling that needs to occur before being activated.
Pretest (in any order) | 3 | Ensure the system can sample data during the ramp period
Pretest (in any order) | 4 | Determine the ramp rate of the DER.
Initialize Test | 5 | Determine whether generating O.R., load O.R. or both services are going to be provided for the days testing.
Initialize Test | 6 | Simulate the accepted status of a bid.
Initialize Test | 7 | Load O.R.: discharge DER to the lower limit. (for energy storage resources) Generating O.R.: charge DER storage to upper limit. (for energy storage resources)
Initialize Test | 8 | Final review of system and increase sampling rate to prepare for ramping.
Test | 9 | The operating reserve signal/notification will be sent, after which the facility will handle the trigger autonomously to carry out the function.
Test | 10a | Record system injection/withdrawal at the timestamp of the O.R. activation call and at 10 minutes or 30 minutes from the call.
Test | 10b | Record system injection/withdrawal at 5 minute intervals for the duration of the O.R. activation call
Test | 11 | Analyze system output temperature to ensure nothing is overheating and responding appropriately to the signal
Test | 12 | Observe the ramp down is completed correctly
Ending | 13 | Return the overall system to normal operation.
Ending | 14 | Confirm the appropriate data points were gathered. Note any unexpected behaviour in test log.
Self-Assesment | 15 | A successful test can be determined when a DER meets its O.R. notification within the prescribed time depending on the O.R. category (10 minute or 30 minute reserve)