## General
| Moratorium Modelling | Moratorium Update | Pathways Modelling | Pathways update
Study Period | 2024 - 2035 | confirmed | 2024 - 2050 | confirmed
Year(s) of Focus | 2035 |  | 2035 and 2050
Objective and Further Opportunity | Replacement of 2021 Annual Planning Outlook proxy resources with incremental non-emitting resources based on availability, reliability and cost, with existing natural gas assumed to be available through the study period | confirmed | Develop an expansion and replacement resource mix with incremental non-emitting resources based on availability, reliability and cost, with existing natural gas available if retrofitted with carbon capture and storage or to operate on low-carbon fuels | confirmed
| Evaluate opportunity to replace 2021 Annual Planning Outlook existing natural gas with incremental non-emitting resources based on availability, reliability and cost | confirmed | Evaluate policy opportunities to enable net zero emissions by 2050 or earlier timeframe | confirmed
Policy | Moratorium Modelling |  | Pathways Modelling
Carbon Prices | • $50/tonne CO2e in 2022 • rising $15/tonne CO2e/year in 2023-2030 • $170/tonne CO2e in 2030-2035 | confirmed | • $50/tonne CO2e in 2022 • rising $15/tonne CO2e/year in 2023-2030 • $170/tonne CO2e in 2030 • rising $15/tonne CO2e/year in 2031-2050 • $470/tonne CO2e in 2050 | The IESO recommends that the carbon price should be inflation adjusted to the end of the study period so there are no real cost declines. The approach we propose is $15/tonne increases to 2035 and increasing with inflation thereafter
Carbon Border Adjustment | No | confirmed | Yes | confirmed
Emissions Performance Standards (EPS) Natural Gas fired Electricity Generation Allowance Benchmark | • 370 tonne CO2e/GWh for 2024 - 2035 | confirmed | • 370 tonne CO2e/GWh until 2030 • tapering to 0 tonne CO2e/GWh by 2035 | confirmed
Offshore Wind | Not Considered | Part of Potential Resource Options | Part of Potential Resource Options | confirmed
Carbon Capture, Utilization and Storage (CCUS) | Not Considered | confirmed | Part of Potential Resource Options | Not Considered
Demand Scenario | Moratorium Modelling |  | Pathways Modelling
Demand Forecast | • 2021 Annual Planning Outlook Reference Scenario Demand Forecast | confirmed | • Pathways Scenario demand forecast to be developed in 2022 Q1-Q2 ○ Consistent with societal decarbonization goals ○ Step changes in technology adoption curves based on known, flagged and potential policy ○ Primarily driven by widespread fuel switching ■ From fossil fueled equipment ■ To electric supplied equipment, high efficiency case if available | confirmed
Conservation Programs | • Consistent with 2021 Annual Planning Outlook Reference Scenario Demand Forecast ○ Includes assumption of continued delivery of conservation programs through the end of the outlook period at budget and savings levels consistent with the current 2021-2024 CDM Framework • Incremental electricity conservation program savings potential exists up to the level of savings as identified in the 2019 IESO and Ontario Energy Board Integrated Ontario Electricity and Natural Gas Conservation Achievable Potential Study, maximum potential Scenario "B" ○ This incremental savings will be considered as an option that competes with other Potential Resource Options https://www.ieso.ca/en/Sector-Participants/Planning-and-Forecasting/Annual-Planning-Outlook | confirmed | • The level of Conservation Program savings included in the Pathways Scenario demand forecast will be consistent with the maximum potential scenario identified in the latest available electricity conservation and demand management acheivable potential study. The IESO is currently updating the 2019 study and will use new findings if available | The Pathways Demand Scenario will include levels of Conservation Program savings consistent with the level of savings as identified in the 2019 IESO and Ontario Energy Board Integrated Ontario Electricity and Natural Gas Conservation Achievable Potential Study (2019 CDM APS), maximum potential Scenario "B". As the 2019 CDM APS has a study period up to the end of 2038, the Pathways Demand Scenario will include an assumption that the level of annual electricity conservation savings in the 2039-2050 period of the Pathways Demand Scenario will be consistent with average levels identified in the 2019 CDM APS.
Distributed Energy Resources (DERs) | • Consistent with 2021 Annual Planning Outlook Reference Scenario ○ Based on current identified levels of distributed energy resources, assumed to have continued availability post contract, through the end of the outlook period • Incremental distributed energy resources can potentially exist up to levels to be identified in the IESO 2022 Distributed Energy Resource Achievable Potential Study ○ This incremental energy resource potential will be considered as an option that competes with other Potential Resource Options | confirmed | • Incremental distributed energy resources can potentially exist up to levels to be identified in the IESO's 2022 Distributed Energy Resource Achievable Potential Study ○ This incremental energy resource potential will be considered as an option that competes with other Potential Resource Options https://www.ieso.ca/en/Sector-Participants/Engagement-Initiatives/Engagements/DER-Potential-Study | confirmed
Resources | Moratorium Modelling |  | Pathways Modelling
| Demand response |  | Demand response
| Solar |  | Solar
| Wind |  | Wind
| Storage |  | Storage
| Hydro |  | Hydro
| SMR |  | SMR
| Large Nuclear - likely not built due to time frame |  | Large Nuclear
| Clean Hydrogen for Thermal - Blue |  | Clean Hydrogen for Thermal - Blue and Green

## Resource Sheet_Detailed
All Costs in 2021 USD
Renewable Generation | Zone | Max Capacity (MW) | 2020 Max Capacity Factor (%) | 2030 Max Capacity Factor (%) | 2040 Max Capacity Factor (%) | 2020 Build Cost ($/kW) | 2030 Build Cost ($/kW) | 2040 Build Cost ($/kW) | 2020 FO&M Charge ($/kW/year) | 2030 FO&M Charge ($/kW/year) | 2040 FO&M Charge ($/kW/year) | VO&M/Fuel Charge ($/MWh) | Transmission Cost ($/kW) | Economic Life (years) | 2020 Summer UCAP (%) | 2030 Summer UCAP (%) | 2040 Summer UCAP (%) | 2020 Winter UCAP (%) | 2030 Winter UCAP (%) | 2040 Winter UCAP (%) | Build Lead Time (years) | Resource Category Annual Build Limit (MW)
New Onshore Wind | Northeast | 1 x 100 MW | 51% | 52% | 52% | 1175 | 980 | 877 | 43 | 40 | 38 | 0 | 80 | 30 | 46% | 47% | 48% | 31% | 33% | 33% | 5 | 1000
| Northeast | 5 x 100 MW | 48% | 49% | 50% | 1175 | 980 | 877 | 43 | 40 | 38 | 0 | 96 | 30 | 26% | 28% | 28% | 54% | 56% | 56% | 5 | 1000
| Northeast | 6 x 100 MW | 39% | 40% | 41% | 1175 | 980 | 877 | 43 | 40 | 38 | 0 | 133.33 | 30 | 15% | 17% | 17% | 40% | 42% | 43% | 5 | 1000
| Northwest | 2 x 100 MW | 51% | 52% | 52% | 1175 | 980 | 877 | 43 | 40 | 38 | 0 | 40 | 30 | 30% | 32% | 32% | 57% | 58% | 59% | 5 | 1000
| Northwest | 3 x 100 MW | 49% | 50% | 50% | 1175 | 980 | 877 | 43 | 40 | 38 | 0 | 693.33 | 30 | 41% | 42% | 43% | 46% | 47% | 47% | 5 | 1000
| Northwest | 6 x 100 MW | 46% | 48% | 48% | 1175 | 980 | 877 | 43 | 40 | 38 | 0 | 186.67 | 30 | 34% | 36% | 37% | 46% | 48% | 48% | 5 | 1000
| Northwest | 2 x 100 MW | 40% | 42% | 43% | 1175 | 980 | 877 | 43 | 40 | 38 | 0 | 120 | 30 | 28% | 29% | 30% | 35% | 36% | 37% | 5 | 1000
| Southwest/Bruce/Niagara | 2 x 100 MW | 43% | 44% | 45% | 1175 | 980 | 877 | 43 | 40 | 38 | 0 | 40 | 30 | 16% | 18% | 18% | 58% | 60% | 61% | 5 | 1000
| Southwest/Bruce/Niagara | 26 x 100 MW | 36% | 37% | 38% | 1175 | 980 | 877 | 43 | 40 | 38 | 0 | 323.08 | 30 | 13% | 15% | 15% | 47% | 48% | 49% | 5 | 1000
| Toronto/Essa/East/Ottawa | 3 x 100 MW | 44% | 45% | 46% | 1175 | 980 | 877 | 43 | 40 | 38 | 0 | 80 | 30 | 17% | 18% | 19% | 60% | 61% | 62% | 5 | 1000
| Toronto/Essa/East/Ottawa | 21 x 100 MW | 35% | 36% | 37% | 1175 | 980 | 877 | 43 | 40 | 38 | 0 | 91.43 | 30 | 13% | 15% | 15% | 49% | 50% | 51% | 5 | 1000
| West | 3 x 100 MW | 46% | 47% | 48% | 1175 | 980 | 877 | 43 | 40 | 38 | 0 | 53.33 | 30 | 19% | 20% | 21% | 55% | 56% | 57% | 5 | 1000
| West | 11 x 100 MW | 38% | 40% | 41% | 1175 | 980 | 877 | 43 | 40 | 38 | 0 | 283.64 | 30 | 12% | 13% | 14% | 47% | 48% | 49% | 5 | 1000
New Offshore Wind | East/Southwest | No limit, 100 MW sites | 45% | 47% | 47% | 3379 | 2625 | 2325 | 106 | 91 | 82 | 0 | 820 | 30 | 18% | 19% | 20% | 60% | 61% | 62% | 10 | 1000
| Northeast | No limit, 100 MW sites | 53% | 53% | 54% | 3379 | 2625 | 2325 | 106 | 91 | 82 | 0 | 820 | 30 | 50% | 50% | 51% | 35% | 36% | 36% | 10 | 1000
| Northwest | No limit, 100 MW sites | 50% | 51% | 52% | 3379 | 2625 | 2325 | 106 | 91 | 82 | 0 | 820 | 30 | 30% | 32% | 32% | 57% | 58% | 59% | 10 | 1000
New Solar | Northeast | No limit, 100 MW sites | 20% | 22% | 22% | 1167 | 804 | 729 | 22 | 17 | 16 | 0 | N/A | 25 | 34% | 35% | 35% | 1% | 1% | 1% | 4 | 600
| Northwest | No limit, 100 MW sites | 21% | 22% | 23% | 1167 | 804 | 729 | 22 | 17 | 16 | 0 | N/A | 25 | 40% | 40% | 41% | 2% | 2% | 2% | 4 | 600
| Southwest/West/Bruce/Niagara | No limit, 100 MW sites | 20% | 22% | 23% | 1167 | 804 | 729 | 22 | 17 | 16 | 0 | N/A | 25 | 37% | 38% | 38% | 1% | 1% | 1% | 4 | 600
| Toronto/Essa/East/Ottawa | No limit, 100 MW sites | 21% | 22% | 23% | 1167 | 804 | 729 | 22 | 17 | 16 | 0 | N/A | 25 | 35% | 36% | 36% | 0% | 0% | 0% | 4 | 600
New Hydro | Northeast | 35 x 10 MW | 67% | 67% | 67% | 10759 | 10759 | 10759 | 63 | 63 | 63 | GRC | N/A | 75 | 85% | 85% | 85% | 82% | 82% | 82% | 10 | 1000
| Northeast | 7 x 50 MW | 47% | 47% | 47% | 11541 | 11541 | 11541 | 43 | 43 | 43 | GRC | N/A | 75 | 57% | 57% | 57% | 57% | 57% | 57% | 10 | 1000
| Northeast | 6 x 375 MW | 35% | 35% | 35% | 11355 | 11355 | 11355 | 31 | 31 | 31 | GRC | N/A | 75 | 39% | 39% | 39% | 53% | 53% | 53% | 10 | 1000
| Northeast | 5 x 180 MW | 27% | 27% | 27% | 11488 | 11488 | 11488 | 36 | 36 | 36 | GRC | N/A | 75 | 39% | 39% | 39% | 25% | 25% | 25% | 10 | 1000
| Northwest | 15 x 10 MW | 61% | 61% | 61% | 11596 | 11596 | 11596 | 65 | 65 | 65 | GRC | N/A | 75 | 91% | 91% | 91% | 91% | 91% | 91% | 10 | 1000
| Northwest | 10 x 20 MW | 50% | 50% | 50% | 11579 | 11579 | 11579 | 53 | 53 | 53 | GRC | N/A | 75 | 34% | 34% | 34% | 31% | 31% | 31% | 10 | 1000
| Northwest | 5 x 55 MW | 35% | 35% | 35% | 11518 | 11518 | 11518 | 40 | 40 | 40 | GRC | N/A | 75 | 55% | 55% | 55% | 70% | 70% | 70% | 10 | 1000
| Northwest | 1 x 12 MW | 27% | 27% | 27% | 11602 | 11602 | 11602 | 67 | 67 | 67 | GRC | N/A | 75 | 32% | 32% | 32% | 61% | 61% | 61% | 10 | 1000
| South | 8 x 4 MW | 65% | 65% | 65% | 6498 | 6498 | 6498 | 83 | 83 | 83 | GRC | N/A | 75 | 18% | 18% | 18% | 32% | 32% | 32% | 10 | 1000
Nuclear Generation | Zone | Max Capacity (MW) | Max Capacity Factor (%) | 2020 Build Cost ($/kW) | 2030 Build Cost ($/kW) | 2040 Build Cost ($/kW) | FO&M Charge ($/kW/year) | VO&M Charge ($/MWh) | Fuel Cost ($/MWh) | Economic Life (years) | Summer UCAP (%) | Winter UCAP (%) | Build Lead Time (years) | Resource Category Annual Build Limit (MW)
New Large Nuclear | East/Southwest | No limit, 600 MW units | 93% | 7699 | 7194 | 6693 | 157 | 2 | 0.85 | 60 | 93% | 93% | 15 | 3000
New Small Modular Nuclear | N/A | No limit, 200 MW units | 93% | 9219 | 9219 | 9219 | 148 | 2 | 0.85 | 60 | 93% | 93% | 8 | 1000
Storage | Duration | Max Capacity (MW) | 2020 Build Cost ($/kW) | 2030 Build Cost ($/kW) | 2040 Build Cost ($/kW) | 2020 FO&M Charge ($/kW/year) | 2030 FO&M Charge ($/kW/year) | 2040 FO&M Charge ($/kW/year) | VO&M Charge ($/MWh) | Economic Life (cycles/years) | Roundtrip Efficiency | Summer UCAP (%) | Winter UCAP (%) | Build Lead Time (years) | Resource Category Annual Build Limit (MW)
New Battery Storage (NREL, moderate) | 4 Hr | 1000 MW | 1479 | 851 | 744 | 37 | 22 | 18 | 0 | 3500 cycles | 85% | 95% | 95% | 3 | 500
New Battery Storage (NREL, moderate) | 6 Hr | 1000 MW | 2080 | 1170 | 1014 | 52 | 29 | 25 | 0 | 3500 cycles | 85% | 95% | 95% | 3 | 500
New Battery Storage (NREL, moderate) | 8 Hr | 1000 MW | 2680 | 1487 | 1284 | 67 | 37 | 33 | 0 | 3500 cycles | 85% | 95% | 95% | 3 | 500
New Battery Storage (NREL, moderate) | 10 Hr | 2000 MW | 3280 | 1806 | 1553 | 82 | 46 | 39 | 0 | 3500 cycles | 85% | 95% | 95% | 3 | 500
Marmora PGS | 5 Hr | 400 MW | Confidential | [6 empty] | 75 | Confidential | 95% | 95% | 10 | 1000
Meaford PGS | 8 Hr | 1000 MW | [7 empty] | 75 |  | 95% | 95% | 10 | 1000
Oxford/Schreiber PGS | 12 Hr | 600 MW | [7 empty] | 75 |  | 95% | 95% | 10 | 1000
Load Participation | 2020 Upper Limit (MW) | 2030 Upper Limit (MW) | 2040 Upper Limit (MW) | Capacity Cost ($/MW-yr) | Activation Cost ($/MWh) | Summer UCAP (%) | Winter UCAP (%) | Acceptable Number of Activations (#/yr) | Min Hours of Delivery per Activation (hrs) | Max Hours of Delivery per Activation (hrs)
Hourly Demand Response (HDR) - Industrial (process-based) | 998.6 | 1261.2 | 1501 | 104076 | 1999 | 69% | 78% | 5 | 1 | 4
HDR - Commercial & Institutional (lighting/HVAC/other-based) | 1288.4 | 1693.5 | 2112 | 104076 | 1500 | 69% | 78% | 25 | 1 | 4
HDR - Residential (smart thermostat/EV/other-based) | 2518.6 | 3856.2 | 5208 | 104076 | 1500 | 69% | 78% | 15 | 1 | 4
5-min Dispatchable Load - process-based (incl.<1 MW resources) | 1054 | 1331.2 | 1585 | 104076 | 1650 | 69% | 78% | N/A | N/A | 4
Firm Imports | Max Capacity (MW) | Intertie Build Cost ($) | Capacity Cost ($/MW-yr) | Energy Cost ($/MWh) | Summer UCAP (%) | Winter UCAP (%) | Agreement Length (years) | Build Lead Time (years)
Quebec - Current Interties | 4 x 450 MW | N/A | Confidential |  | 100% | 100% | 20 | 5
Quebec - New Intertie | 2000 | 1400000000 |  |  | 100% | 100% | 25 | 10
Combustion Generation | Fuel | Fuel Cost Conservative ($/MMBtu) | Fuel Cost Advanced ($/MMBtu) | Emissions (kg CO2/kg H2) | Max Capacity (MW) | 2020 Build Cost ($/KW) | 2030 Build Cost ($/KW) | 2040 Build Cost ($/KW) | FO&M Charge ($/KW/year) | VO&M Charge ($MWh) | Economic Life (year) | Heat Rate (MMBtu/MWh) | Summer UCAP (%) | Winter UCAP (%) | Build Lead Time (years) | Resource Category Annual Build Limit (MW)
New Hydrogen SCGT | Blue Hydrogen | 20.68 | 9 | 0.445 | No limit, 250 MW units | N/A | 1050 | 990 | 28.76 | 6.8 | 30 | 8.78 | 95% | 95% | 5 | 1000
For Moratorium Case Only
Combustion Generation | Fuel | Fuel Forecast | Capital Injection ($/MW) | FO&M Charge ($/kW/year) | VO&M Charge ($/MWh) | Economic Life (years) | Technical Characteristics
Repowering of Natural Gas Facilities Post Contract Termination | Natural Gas | 2021 APO | 20% of new build cost | Escalated portion of current NRR (~20%) | Same as current facility | 10 | Same as facility to be repowered
For Pathways Case Only
Combustion Generation | Fuel | Fuel Cost Conservative ($/MMBtu) | Fuel Cost Advanced ($/MMBtu) | Emissions (kg CO2/kg H2) | 2020 Retrofit Cost ($/KW) | 2030 Retrofit Cost ($/KW) | 2040 Retrofit Cost ($/KW) | FO&M Charge ($/KW/year) | VO&M ($/MWh) | Economic Life (year) | Technical Characteristics
Retrofit - Hydrogen SCGT | Blue Hydrogen | 20.68 | 9 | 0.445 | N/A | 284.8 | 272 | Existing NG FO&M * 1.24 | Existing NG VO&M * 1.24 | 30 | Same as facility to be retrofitted
Retrofit - Hydrogen SCGT | Green Hydrogen | 72.024 | 27.008 | 0 | N/A | 284.8 | 272 | Existing NG FO&M * 1.24 | Existing NG VO&M * 1.24 | 30 | Same as facility to be retrofitted

## Demand Scenario
Sector | End Use / Sub-Sectors | Case | Assumption | Assumptions Update
Residential | Space Heating | New buildings, new equipment | • Expected regulation: space heating equipment in new construction of residential sector buildings to be zero emissions from 2030 ○ Substitution of natural gas, propane or heating oil fuelled space heating equipment to a mix of electric powered air source heat pumps, ground source heat pumps and resistive heating technology | • Substitution of natural gas, propane or heating oil fuelled and electric resistance type space heating equipment to a mix of electric powered air source heat pumps and ground source heat pumps • Assumption of air source heat pump technological improvement over the outlook period to enable: ○ operation in potential coldest weather ○ maintance of coefficient of performance in potential coldest weather • Assumption is phased in: ○ over a 9 year transition period; ○ incremental 1/9 (11%) per year increase over baseline; ○ 100% effect by target year; • Assumptions is 100% applied in: ○ Toronto IESO Zone by year 2030; ○ All other IESO Zones by year 2035;
Residential | Space Heating | Existing buildings, replacement of expired equipment | • Expected regulation: 100% of sales of new space heating equipment for residential buildings to be zero emissions by 2035 ○ For replacement of installed equipment in existing buildings ○ Substitution of natural gas, propane or heating oil fuelled water heating equipment to a mix of electric powered heat pumps and resistive heating technology | • Substitution of natural gas, propane or heating oil fuelled and electric resistance type space heating equipment to a mix of electric powered air source heat pumps and ground source heat pumps • Assumption of air source heat pump technological improvement over the outlook period to enable: ○ operation in potential coldest weather ○ maintance of coefficient of performance in potential coldest weather • Assumption is phased in: ○ over a 9 year transition period; ○ incremental 1/9 (11%) per year increase over baseline; ○ 100% effect by target year;
Residential | Water Heating | New buildings, new equipment | • Expected regulation: water heating equipment in new construction of residential sector buildings to be zero emissions from 2030 ○ Substitution of natural gas, propane or heating oil fuelled water heating equipment to a mix of electric powered heat pumps and resistive heating technology | • Substitution of natural gas, propane or heating oil fuelled and electric resistance type water heating equipment to electric powered heat pumps • Assumption of air source heat pump technological improvement over the outlook period to enable: ○ operation in potential coldest weather ○ maintance of coefficient of performance in potential coldest weather • Assumption is phased in: ○ over a 9 year transition period; ○ incremental 1/9 (11%) per year increase over baseline; ○ 100% effect by target year; • Assumptions is 100% applied in: ○ Toronto IESO Zone by year 2030; ○ All other IESO Zones by year 2035;
Residential | Water Heating | Existing buildings, replacement of expired equipment | • Expected regulation: 100% of sales of new water heating equipment for residential buildings to be zero emissions by 2035 ○ For replacement of installed equipment in existing buildings ○ Substitution of natural gas, propane or heating oil fuelled water heating equipment to a mix of electric powered heat pumps and resistive heating technology | • Substitution of natural gas, propane or heating oil fuelled and electric resistance type water heating equipment to electric powered heat pumps • Assumption of air source heat pump technological improvement over the outlook period to enable: ○ operation in potential coldest weather ○ maintance of coefficient of performance in potential coldest weather • Assumption is phased in: ○ over a 9 year transition period; ○ incremental 1/9 (11%) per year increase over baseline; ○ 100% effect by target year;
Residential | Cooking | New buildings, new equipment | • not included in original input assumptions table | • Expected regulation: cooking equipment in new construction of residential sector buildings to be zero emissions from 2030: ○ Substitution of natural gas fuelled cooking equipment to electric powered resistive heating technology • Assumption is phased in: ○ over a 9 year transition period; ○ incremental 1/9 (11%) per year increase over baseline; ○ 100% effect by target year; • Assumptions is 100% applied in: ○ Toronto IESO Zone by year 2030; ○ All other IESO Zones by year 2035;
Residential | Cooking | Existing buildings, replacement of expired equipment | • not included in original input assumptions table | • Expected regulation: 100% of sales of new cooking equipment for residential buildings to be zero emissions by 2035: ○ For replacement of installed equipment in existing buildings ○ Substitution of natural gas fuelled cooking equipment to electric powered resistive heating technology • Assumption is phased in: ○ over a 9 year transition period; ○ incremental 1/9 (11%) per year increase over baseline; ○ 100% effect by target year;
Residential | Clothes Drying | New buildings, new equipment | • Expected regulation: clothes drying equipment in new construction of residential sector buildings to be zero emissions from 2030 ○ Substitution of natural gas fuelled clothes drying equipment to electric powered resistive heating technology | • Substitution of natural gas fuelled and electric resistive clothes drying equipment to electric powered condensing clothes dryers and electric heat pump clothes dryers • Assumption is phased in: ○ over a 9 year transition period; ○ incremental 1/9 (11%) per year increase over baseline; ○ 100% effect by target year; • Assumptions is 100% applied in: ○ Toronto IESO Zone by year 2030; ○ All other IESO Zones by year 2035;
Residential | Clothes Drying | Existing buildings, replacement of expired equipment | • Expected regulation: 100% of sales of new clothes drying equipment for residential buildings to be zero emissions by 2035 ○ For replacement of installed equipment in existing buildings ○ Substitution of natural gas fuelled clothes drying equipment to electric powered resistive heating technology | • Substitution of natural gas fuelled and electric resistive clothes drying equipment to electric powered condensing clothes dryers and electric heat pump clothes dryers • Assumption is phased in: ○ over a 9 year transition period; ○ incremental 1/9 (11%) per year increase over baseline; ○ 100% effect by target year;
Commercial | Space Heating | New buildings, new equipment | • Expected regulation: space heating equipment in new construction of commercial sector buildings to be zero emissions in 2030 and thereafter ○ Substitution of natural gas, propane or heating oil fuelled space heating equipment to a mix of electric powered air source heat pumps, ground source heat pumps and resistive heating technology | • Substitution of natural gas, propane or heating oil fuelled and electric resistance type space heating equipment to a mix of electric powered air source heat pumps and ground source heat pumps • Assumption of air source heat pump technological improvement over the outlook period to enable: ○ operation in potential coldest weather ○ maintance of coefficient of performance in potential coldest weather • Assumption is phased in: ○ over a 9 year transition period; ○ incremental 1/9 (11%) per year increase over baseline; ○ 100% effect by target year; • Assumptions is 100% applied in: ○ Toronto IESO Zone by year 2030; ○ All other IESO Zones by year 2035;
Commercial | Space Heating | Existing buildings, replacement of expired equipment | • Expected regulation: 100% of sales of new space heating equipment for commercial buildings to be zero emissions by 2035 ○ For replacement of installed equipment in existing buildings ○ Substitution of natural gas, propane or heating oil fuelled water heating equipment to a mix of electric powered heat pumps and resistive heating technology | • Substitution of natural gas, propane or heating oil fuelled and electric resistance type space heating equipment to a mix of electric powered air source heat pumps and ground source heat pumps • Assumption of air source heat pump technological improvement over the outlook period to enable: ○ operation in potential coldest weather ○ maintance of coefficient of performance in potential coldest weather • Assumption is phased in: ○ over a 9 year transition period; ○ incremental 1/9 (11%) per year increase over baseline; ○ 100% effect by target year;
Commercial | Water Heating | New buildings, new equipment | • Expected regulation: water heating equipment in new construction of commercial sector buildings to be zero emissions in 2030 and thereafter ○ Substitution of natural gas, propane or heating oil fuelled water heating equipment to a mix of electric powered heat pumps and resistive heating technology | • Substitution of natural gas, propane or heating oil fuelled and electric resistance type water heating equipment to electric powered heat pumps • Assumption of air source heat pump technological improvement over the outlook period to enable: ○ operation in potential coldest weather ○ maintance of coefficient of performance in potential coldest weather • Assumption is phased in: ○ over a 9 year transition period; ○ incremental 1/9 (11%) per year increase over baseline; ○ 100% effect by target year; • Assumptions is 100% applied in: ○ Toronto IESO Zone by year 2030; ○ All other IESO Zones by year 2035;
Commercial | Water Heating | Existing buildings, replacement of expired equipment | • Expected regulation: 100% of sales of new water heating equipment for commercial buildings to be zero emissions by 2035 ○ For replacement of installed equipment in existing buildings ○ Substitution of natural gas, propane or heating oil fuelled water heating equipment to a mix of electric powered heat pumps and resistive heating technology | • Substitution of natural gas, propane or heating oil fuelled and electric resistance type water heating equipment to electric powered heat pumps • Assumption of air source heat pump technological improvement over the outlook period to enable: ○ operation in potential coldest weather ○ maintance of coefficient of performance in potential coldest weather • Assumption is phased in: ○ over a 9 year transition period; ○ incremental 1/9 (11%) per year increase over baseline; ○ 100% effect by target year;
Commercial | Cooking | New buildings, new equipment | • not included in original input assumptions table | • Expected regulation: cooking equipment in new construction of commercial sector buildings to be zero emissions from 2030: ○ Substitution of natural gas fuelled cooking equipment to electric powered resistive heating technology • Assumption is phased in: ○ over a 9 year transition period; ○ incremental 1/9 (11%) per year increase over baseline; ○ 100% effect by target year; • Assumptions is 100% applied in: ○ Toronto IESO Zone by year 2030; ○ All other IESO Zones by year 2035;
Commercial | Cooking | Existing buildings, replacement of expired equipment | • not included in original input assumptions table | • Expected regulation: 100% of sales of new cooking equipment for commercial buildings to be zero emissions by 2035: ○ For replacement of installed equipment in existing buildings ○ Substitution of natural gas fuelled cooking equipment to electric powered resistive heating technology • Assumption is phased in: ○ over a 9 year transition period; ○ incremental 1/9 (11%) per year increase over baseline; ○ 100% effect by target year;
Industrial | Mining |  | • Continued sub-sector development, supported by Ontario Critical Minerals Strategy, to produce raw materials required to enable societal electrification infrastructure ○ Including continued development of Ontario Ring of Fire region mineral deposits and electrification of transportation infrastructure | • Incremental Northwest Ontario Ring of Fire mining project development: ○ materializing beginning in year 2030, growing through early 2040s, flattening by late 2040s ○ electricity demand grows to roughly 50% of year 2022 total Ontario levels by year 2050 • Inclusion of additional Northeast Ontario prospective mining project developments
| Other Manufacturing |  | • Continued fossil fuel to electricity substitution for industrial processes over the outlook period, similar to approach taken in previous IESO outlook demand forecast ○ For Pathways Scenario, beginning in year 6, an incremental 1% per year of existing fossil fuel consumption is converted to electricity over the outlook period ■ For example, based on 2019 Ontario Industrial fossil fuel energy consumption equating to approximately 90 TWh / year: □ by year 5, 2028: 0% fuel switching □ by year 6, 2029: 1% fuel switching of 2019 levels results in approximately +1 TWh/year; □ by year 10, 2033: 5% fuel switching of 2019 levels results in approximately +5 TWh/year; □ by year 20, 2043: 15% fuel switching of 2019 levels results in approximately +14 TWh/year; □ by year 27, 2050: 22% fuel switching of 2019 levels results in approximately +20 TWh/year; | • Included ○ subsitution of natural gas for energy purposes to electricity for energy purposes ○ does not consider total sector fossil fuel consumption since a portion of industrial sector fossil fuel consumption is for chemical inputs of production processes rather than energy supply purposes • Electrification assume to begin in year 2030, due to: ○ complexity of industrial processes ○ difficulty to identify fuel switching opportunities ○ difficulty to implement fuel swithcing technologies • Final levels of increased industrial sector electricity demand will be simliar to original assumption
Agricultural | Greenhouse Space and Water Heating | all | • not included in original input assumptions table | • Assumes transition to electric heat pump powered space and water heating from year 2030 to year 2040.
Transportation Electrification | Light Duty Vehicles |  | • Light Duty Vehicles ○ Consistent with federal government policy targets: ■ Mandatory target of 100% of new sales of light-duty vehicles in 2035 and thereafter to be zero-emission (announced June 29, 2021) ■ Interim target of at least 50% of new sales of light-duty vehicles in 2030 and thereafter to be zero-emission (announced December 17, 2021) | • Light Duty Battery Electric Vehicles: ○ Consistent with federal government policy targets: ■ Mandatory target of 100% of new sales of light-duty vehicles in 2035 and thereafter to be zero-emission (announced June 29, 2021) ■ Interim target of 60% of new sales of light-duty vehicles in 2030 and thereafter to be zero-emission
Transportation Electrification | Heavy Duty Vehicles |  | • Heavy Duty Vehicles ○ Consideration of 100% of municipal transit commission buses to be electrified by 2040 | • Medium and Heavy Duty Battery Electric Vehicles: ○ Consideration of 100% of municipal transit commission buses to be electrified by 2040 ○ Increased bus fleet, and electrical charging demand, of 10% higher than baseline forecasts ○ Other electric mobility electrical charging demand increased to be equivalent of 5% of light duty battery electric vehicles • Majority of freight vehicles to be hydrogen fuel cell powered, rather than battery electric powered
Transportation Electrification | Rail Transit |  | • Steady expansion across the province over the outlook period | • Rail transportation as a whole, electricity demand to be 20% higher than base line forecasts
Transportation Electrification | Rail Shipping |  | • Emerging electrification over the 2030s, advancement in the 2040s

## Resource Description
Table | Column | Description
Renewables | NREL Resource Class | NREL's in-house classification of the strength of the underlying fuel availability (i.e. wind, solar irradiance etc.) https://data.openei.org/submissions/4129
| Capacity Factor (%) | Capacity factor is the measure of how often a power plant runs for a specific period of time. It's expressed as a percentage and calculated by dividing the actual unit electricity output by the maximum possible output.
| Summer Capacity Value (UCAP%) | A measure of the total MW that can be relied upon to contribute towards Resource Adequacy during the Summer Delivery Period in % of ICAP MW
| Winter Capacity Value (UCAP%) | A measure of the total MW that can be relied upon to contribute towards Resource Adequacy during the Winter Delivery Period in % of ICAP MW
| CAPEX ($2021CAD/kW) | Estimate of capital expenditure required to build new MWs
| OM&A ($2021CAD/kw-yr) | The fixed annual Operations, Maintenance and Administration costs
| Technology Readiness Level (TRL) - 2022 | See TRL-CRI Definitions Tab
| Construction Lead-Time (years) | Number of years required to build the new MWs
| Project Life (years) | Number of years the project is anticipated to be in service
Incremental Categories In Thermal | Outage Rate (EFORd %) | A measure of the probability that an electric power generating unit will not be available due to a forced outage or forced derating when there is a demand on the unit to generate
| Start-Up Time (hrs) | The amount of time required for the unit to reach its Minimum Loading Point (MLP)
| Minimum Run Time (hrs) | The minimum amount of time that the unit must remain at or above its MLP
| Minimum Down-Time (hrs) | The minimum amount of time between when the unit is shut-down and when it can be re-started
| Minimum Loading Point (MW) | The minimum generation output level that must be maintained while the unit is online
| Variable OM&A ($/MWh) | A measure of the variable operations, maintenance and administration costs
| Fixed OM&A ($/kw-year) | A measure of the fixed operations, maintenance and administration costs
| Fuel Cost ($/MWh) | The cost of the input fuel (e.g. Renewable Natural Gas, Uranium, Hydrogen)
| Commercial Readiness - 2022 | See TRL-CRI Definitions Tab
| Earliest In-service Date | This is to capture that some resource types will not be mature enough for commercial operation until later in the study horizon
Incremental Categories In Storage | Representative Technologies | This category provides example technologies that would be able to provide the storage durations defined. Pumped Hydro storage will be limited to the 3 facilities identified in the November 10, 2021 Minister's letter
| Upper Limit on MW in Category (UCAP MW) | This is the upper cap on total installation of each storage duration category. The concept is to try and capture the diminishing returns (or increasing reservoir size need) as more storage is adopted on the system
| Roundtrip Efficiency (%) | A measure of how much energy can be re-injected into the grid after it has been stored in the storage unit. A percentage of how much energy can be re-injected from total energy consumed to charge the unit
Incremental Categories In Load Participation | Max Number of Activations (#/yr) | A measure of how many times per year the DR unit can be called upon to delivery energy
| Max Hours of Delivery per Activation (Hrs) | A measure of the maximum number of hours that the DR unit can deliver energy per activation
| Annual Capacity Cost ($/MW-yr) | A measure of how much it is expected to cost to secure DR capacity
| Activation Cost ($/MWh) | A measure of how much it is expected to cost to activate a DR unit to deliver energy
Incremental Categories In Imports | Maximum Capacity Being Considered (MW) | This is the maximum amount of capacity that IESO anticipates could be made available from the neighbouring jurisdiction. The limits will be based on capacity and internal transmission limits identified in the neighbouring jurisdictions; Ontario transmission considerations will be incorporated into our capacity cost curves
| Energy Cost ($/MWh) | This is the expected average cost of the energy being delivered from the neighbouring jurisdiction

## TRL-CRI Definitions
Level | Technology Readiness Level
Level 1 | Basic principles of concept are observed and reported
Level 2 | Technology concept and/or application formulated
Level 3 | Analytical and experimental critical function and/or proof of concept
Level 4 | Component and/or validation in a laboratory environment
Level 5 | Component and/or validation in a simulated environment
Level 6 | System/subsystem model or prototype demonstration in a simulated environment
Level 7 | Prototype ready for demonstration in an appropriate operational environment
Level 8 | Actual technology completed and qualified through tests and demonstrations
Level 9 | Actual technology proven through successful deployment in an operational setting
Australian Renewable Energy Agency, ARENA 2014 - Commercial Readiness Index for Renewable Energy Sectors
Source: | https://arena.gov.au/assets/2014/02/Commercial-Readiness-Index.pdf
Status Summary Level | Commercial Readiness Index
6 | "Bankable" grade asset class driven by same criteria as other mature energy technologies. Considered as a "Bankable” grade asset class with known standards and performance expectations. Market and technology risks not driving investment decisions. Proponent capability, pricing and other typical market forces driving uptake.
5 | Market competition driving widespread deployment in context of long-term policy settings. Competition emerging across all areas of supply chain with commoditisation of key components and financial products occurring.
4 | Multiple commercial applications becoming evident locally although still subsidised. Verifiable data on technical and financial performance in the public domain driving interest from variety of debt and equity sources however still requiring government support. Regulatory challenges being addressed in multiple jurisdictions.
3 | Commercial scale up occurring driven by specific policy and emerging debt finance. Commercial proposition being driven by technology proponents and market segment participants – publically discoverable data driving emerging interest from finance and regulatory sectors.
2 | Commercial trial: Small scale, first of a kind project funded by equity and government project support. Commercial proposition backed by evidence of verifiable data typically not in the public domain.
1 | Hypothetical commercial proposition: Technically ready – commercially untested and unproven. Commercial proposition driven by technology advocates with little or no evidence of verifiable technical or financial data to substantiate claims