## IESO Change History
Date of Change | Version | Change
2024-01-29 | 35 | Updated to remove IESO specific information
2024-02-20 | 36 | Updated EOP-011-1 and EOP-011-2 statuses
2024-05-01 | 37 | The milestones report has been reconcilied to update existing NERC requirements and NPCC directories. In addition, all current and future effective NERC requirements and NPCC directories have been added.

## NERC Standards List
Standard Number | Standard Group | Standard Number Without Version | Document Title | NERC BOT Adoption Date | USA Approval Status | OEB Start Date | OEB End Date | Review Status in Ontario | Mandatory Enforcement Date in Ontario | Inactive Date in Ontario | Status In Ontario | External Link
As Of 2024/05/01
BAL-001-0 | BAL | BAL-001 | Real Power Balancing Control Performance | 2005-02-08 | Approved |  | 1900-04-01 | Not Initiated | 2007-06-18 | 2008-08-26 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/BAL-001-0.pdf
BAL-001-0.1a | BAL | BAL-001 | Real Power Balancing Control Performance | 2008-10-29 | Approved | 2009-05-15 | 2009-09-12 | Not Initiated | 2009-09-13 | 2014-06-30 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/BAL-001-0_1a.pdf
BAL-001-0a | BAL | BAL-001 | Real Power Balancing Control Performance | 2007-10-23 | Approved |  |  | Not Initiated | 2008-08-27 | 2009-05-12 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/BAL-001-0a.pdf
BAL-001-1 | BAL | BAL-001 | Real Power Balancing Control Performance | 2012-12-19 | Approved | 2013-09-26 | 2014-01-24 | Not Initiated | 2014-07-01 | 2016-06-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/BAL-001-1.pdf
BAL-001-2 | BAL | BAL-001 | Real Power Balancing Control Performance | 2013-08-15 | Approved | 2014-04-07 | 2014-08-15 | Not Initiated | 2016-07-01 |  | Effective | http://www.nerc.com/pa/Stand/Reliability Standards/BAL-001-2.pdf
BAL-002-0 | BAL | BAL-002 | Disturbance Control Performance | 2005-02-08 | Approved |  |  | Not Initiated | 2005-02-08 | 2012-09-30 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/BAL-002-0.pdf
BAL-002-1 | BAL | BAL-002 | Disturbance Control Performance | 2010-08-05 | Approved | 2011-03-10 | 2011-07-08 | Not Initiated | 2012-10-01 | 2017-12-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/BAL-002-1.pdf
BAL-002-1a | BAL | BAL-002 | Disturbance Control Performance | 2012-11-07 | Approved | 2013-04-02 | 2013-07-31 | Not Initiated | 2013-04-02 | 2017-02-17 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/BAL-002-1a.pdf
BAL-002-2 | BAL | BAL-002 | Disturbance Control Standard – Contingency Reserve for Recovery from a Balancing Contingency Event | 2015-11-05 | Approved | 2016-02-05 | 2016-06-04 | Not Initiated | 2016-02-05 | 2017-12-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/BAL-002-2.pdf
BAL-002-2(i) | BAL | BAL-002 | Disturbance Control Standard – Contingency Reserve for Recovery from a Balancing Contingency Event | 2015-11-05 | Approved | 2016-02-05 | 2016-06-04 | Not Initiated | 2018-01-01 | 2019-06-30 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/BAL-002-2(i).pdf
BAL-002-3 | BAL | BAL-002 | Disturbance Control Standard – Contingency Reserve for Recovery from a Balancing Contingency Event | 2018-08-16 | Approved | 2018-08-21 | 2018-12-19 | Not Initiated | 2019-07-01 |  | Effective | https://www.nerc.com/pa/Stand/Reliability%20Standards/BAL-002-3.pdf
BAL-003-0 | BAL | BAL-003 | Frequency Response and Bias | 2005-02-08 | Approved |  |  | Not Initiated | 2007-06-18 | 2008-08-26 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/BAL-003-0.pdf
BAL-003-0.1a | BAL | BAL-003 | Frequency Response and Bias | 2008-10-29 | Approved |  |  | Not Initiated | 2009-05-13 | 2009-06-28 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/BAL-003-0_1a.pdf
BAL-003-0.1b | BAL | BAL-003 | Frequency Response and Bias | 2008-10-29 | Approved | 2009-05-15 | 2009-09-12 | Not Initiated | 2009-09-13 | 2015-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/BAL-003-0_1b.pdf
BAL-003-0a | BAL | BAL-003 | Frequency Response and Bias | 2007-10-23 | Approved |  |  | Not Initiated | 2008-08-27 | 2009-05-12 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/BAL-003-0a.pdf
BAL-003-0b | BAL | BAL-003 | Frequency Response and Bias | 2008-02-12 | Approved |  |  | Not Initiated | 2009-05-14 | 2009-06-28 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/BAL-003-0b.pdf
BAL-003-1 | BAL | BAL-003 | Frequency Response and Frequency Bias Setting | 2013-02-07 | Approved | 2013-04-04 | 2013-08-02 | Not Initiated | 2015-04-01 | 2015-11-12 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/BAL-003-1.pdf
BAL-003-1.1 | BAL | BAL-003 | Frequency Response and Frequency Bias Setting | 2013-02-07 | Approved | 2013-04-04 | 2013-08-02 | Not Initiated | 2015-11-13 | 2020-12-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/BAL-003-1.1.pdf
BAL-003-2 | BAL | BAL-003 | Frequency Response and Frequency Bias Setting | 2019-12-19 | Approved | 2020-01-10 | 2020-04-18 | Not Initiated | 2021-01-01 |  | Effective | https://www.nerc.com/pa/Stand/Reliability%20Standards/BAL-003-2.pdf
BAL-004-0 | BAL | BAL-004 | Time Error Correction | 2005-02-08 | Approved | 2011-07-08 | 2011-07-08 | Not Initiated | 2011-07-08 | 2017-04-01 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/BAL-004-0.pdf
BAL-004-1 | BAL | BAL-004 | Time Error Correction | 2008-03-26 | Not Approved |  |  | Not Initiated | 2008-03-26 | 2011-07-07 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/BAL-004-1.pdf
BAL-005-0 | BAL | BAL-005 | Automatic Generation Control | 2005-02-08 | Approved |  |  | Not Initiated | 2007-06-18 | 2008-08-26 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/BAL-005-0.pdf
BAL-005-0.1b | BAL | BAL-005 | Automatic Generation Control | 2008-10-29 | Approved | 2009-05-15 | 2009-09-12 | Not Initiated | 2009-09-13 | 2012-10-09 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/BAL-005-0_1b.pdf
BAL-005-0.2b | BAL | BAL-005 | Automatic Generation Control | 2012-03-08 | Approved | 2012-06-11 | 2012-10-09 | Not Initiated | 2012-10-10 | 2018-12-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/BAL-005-0_2b.pdf
BAL-005-0a | BAL | BAL-005 | Automatic Generation Control | 2007-05-02 | Not Approved |  |  | Not Initiated |  | 2008-04-15 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/BAL-005-0a.pdf
BAL-005-0b | BAL | BAL-005 | Automatic Generation Control | 2008-02-12 | Approved |  |  | Not Initiated | 2008-08-27 | 2009-05-12 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/BAL-005-0b.pdf
BAL-005-1 | BAL | BAL-005 | Balancing Authority Control | 2016-02-11 | Approved | 2016-04-26 | 2016-08-24 | Not Initiated | 2019-01-01 |  | Effective | http://www.nerc.com/pa/Stand/Reliability Standards/BAL-005-1.pdf
BAL-006-0 | BAL | BAL-006 | Inadvertent Interchange | 2005-02-08 | Not Approved |  |  | Not Initiated |  | 2006-05-01 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/BAL-006-0.pdf
BAL-006-1 | BAL | BAL-006 | Inadvertent Interchange | 2006-05-02 | Approved |  |  | Not Initiated | 2007-06-18 | 2009-05-12 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/BAL-006-1.pdf
BAL-006-1.1 | BAL | BAL-006 | Inadvertent Interchange | 2008-10-29 | Approved | 2009-05-15 | 2009-09-12 | Not Initiated | 2009-09-13 | 2010-06-30 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/BAL-006-1_1.pdf
BAL-006-2 | BAL | BAL-006 | Inadvertent Interchange | 2009-11-05 | Approved | 2009-12-11 | 2010-04-10 | Not Initiated | 2011-04-01 | 2018-12-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/BAL-006-2.pdf
CIP-001-0 | CIP | CIP-001 | Sabotage Reporting | 2005-02-08 | Not Approved |  |  | Not Initiated |  | 2007-01-01 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-001-0.pdf
CIP-001-1 | CIP | CIP-001 | Sabotage Reporting | 2006-11-01 | Approved |  |  | Not Initiated | 2006-11-01 | 2010-09-08 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-001-1.pdf
CIP-001-1a | CIP | CIP-001 | Sabotage Reporting | 2010-02-16 | Approved | 2010-05-11 | 2010-09-08 | Not Initiated | 2010-09-09 | 2012-05-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-001-1a.pdf
CIP-001-2a | CIP | CIP-001 | Sabotage Reporting | 2011-02-17 | Approved | 2012-02-01 | 2012-05-31 | Not Initiated | 2012-06-01 | 2013-12-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-001-2a.pdf
CIP-002-1 | CIP | CIP-002 | Cyber Security — Critical Cyber Asset Identification | 2006-05-02 | Approved |  |  | Not Initiated | 2006-05-02 | 2010-03-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-002-1.pdf
CIP-002-2 | CIP | CIP-002 | Cyber Security — Critical Cyber Asset Identification | 2009-05-06 | Approved | 2009-06-03 | 2009-10-01 | Not Initiated | 2010-04-01 | 2010-12-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-002-2.pdf
CIP-002-3 | CIP | CIP-002 | Cyber Security - Critical Cyber Asset Identification | 2009-12-16 | Approved | 2010-01-26 | 2010-05-26 | Not Initiated | 2011-01-01 | 2016-06-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-002-3.pdf
CIP-002-3(i) | CIP | CIP-002 | Cyber Security - Critical Cyber Asset Identification | 2014-11-13 | Not Approved | 2015-02-10 | 2015-06-10 | Not Initiated |  | 2014-11-13 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-002-3(i).pdf
CIP-002-3(i)b | CIP | CIP-002 | Cyber Security - Critical Cyber Asset Identification | 2014-11-13 | Not Approved | 2015-02-10 | 2015-06-10 | Not Initiated |  | 2014-11-13 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-002-3(i)b.pdf
CIP-002-3a | CIP | CIP-002 | Cyber Security - Critical Cyber Asset Identification | 2012-05-09 | Not Approved | 2012-09-06 | 2013-01-04 | Not Initiated |  | 2013-03-21 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-002-3a.pdf
CIP-002-3b | CIP | CIP-002 | Cyber Security - Critical Cyber Asset Identification | 2013-02-07 | Not Approved | 2016-06-30 | 2016-06-30 | Not Initiated |  | 2016-06-30 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-002-3b.pdf
CIP-002-4 | CIP | CIP-002 | Cyber Security — Critical Cyber Asset Identification | 2011-01-24 | Approved | 2011-06-14 | 2011-10-12 | Not Initiated | 2014-10-01 | 2014-02-03 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-002-4.pdf
CIP-002-4a | CIP | CIP-002 | Cyber Security — Critical Cyber Asset Identification | 2012-05-09 | Not Approved | 2012-08-03 | 2012-12-01 | Not Initiated |  | 2013-03-21 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-002-4a.pdf
CIP-002-5 | CIP | CIP-002 | Cyber Security — BES Cyber System Categorization | 2012-11-26 | Not Approved | 2013-02-05 | 2013-06-05 | Not Initiated |  | 2014-02-03 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-002-5.pdf
CIP-002-5.1 | CIP | CIP-002 | Cyber Security — BES Cyber System Categorization | 2013-09-27 | Approved | 2013-10-01 | 2014-01-29 | Not Initiated | 2016-07-01 | 2016-12-26 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-002-5_1.pdf
CIP-002-5.1a | CIP | CIP-002 | Cyber Security — BES Cyber System Categorization | 2016-12-14 | Approved | 1899-12-31 | 1900-01-01 | Not Initiated | 2016-12-27 |  | Effective | http://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-002-5.1a.pdf
CIP-002-6 | CIP | CIP-002 | Cyber Security – BES Cyber System Categorization | 2020-05-14 | Not Approved | 2020-06-12 | 2020-10-10 | Not Initiated |  | 2021-02-04 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-002-6.pdf
CIP-003-1 | CIP | CIP-003 | Cyber Security — Security Management Controls | 2006-05-02 | Approved |  |  | Not Initiated | 2006-05-02 | 2010-06-30 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-003-1.pdf
CIP-003-2 | CIP | CIP-003 | Cyber Security — Security Management Controls | 2009-05-06 | Approved | 2009-06-03 | 2009-10-01 | Not Initiated | 2010-07-01 | 2010-12-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-003-2.pdf
CIP-003-3 | CIP | CIP-003 | Cyber Security - Security Management Controls | 2009-12-16 | Approved | 2010-01-26 | 2010-05-26 | Not Initiated | 2011-01-01 | 2016-06-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-003-3.pdf
CIP-003-3a | CIP | CIP-003 | Cyber Security - Security Management Controls | 2013-11-07 | Not Approved | 1899-12-31 | 1900-01-01 | Not Initiated |  | 2016-06-30 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-003-3a.pdf
CIP-003-4 | CIP | CIP-003 | Cyber Security — Security Management Controls | 2011-01-24 | Approved | 2011-06-14 | 2011-10-12 | Not Initiated | 2014-10-01 | 2014-02-03 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-003-4.pdf
CIP-003-4a | CIP | CIP-003 | Cyber Security — Security Management Controls | 2013-11-07 | Not Approved |  |  | Not Initiated |  | 2014-02-03 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-003-4a.pdf
CIP-003-5 | CIP | CIP-003 | Cyber Security — Security Management Controls | 2012-11-26 | Approved | 2013-02-05 | 2013-06-05 | Not Initiated | 2016-04-01 | 2016-06-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-003-5.pdf
CIP-003-6 | CIP | CIP-003 | Cyber Security — Security Management Controls | 2014-11-13 | Approved | 2015-02-26 | 2015-06-26 | Not Initiated | 2016-07-01 | 2019-12-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-003-6.pdf
CIP-003-7 | CIP | CIP-003 | Cyber Security — Security Management Controls | 2017-02-09 | Approved | 2017-03-20 | 2017-07-18 | Not Initiated | 2020-01-01 | 2020-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-003-7.pdf
CIP-003-8 | CIP | CIP-003 | Cyber Security — Security Management Controls | 2019-05-08 | Approved | 2019-06-14 | 2019-09-19 | Not Initiated | 2020-04-01 | 2026-06-30 | Effective | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-003-8.pdf
CIP-003-9 | CIP | CIP-003 | Cyber Security — Security Management Controls | 2022-11-16 | Approved | 2023-01-05 | 2023-05-05 | Not Initiated | 2026-07-01 |  | Future Effective | https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-003-9.pdf
CIP-004-1 | CIP | CIP-004 | Cyber Security — Personnel & Training | 2006-05-02 | Approved |  |  | Not Initiated | 2006-05-02 | 2010-06-30 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-004-1.pdf
CIP-004-2 | CIP | CIP-004 | Cyber Security — Personnel & Training | 2009-05-06 | Approved | 2009-06-03 | 2009-10-01 | Not Initiated | 2010-07-01 | 2010-12-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-004-2.pdf
CIP-004-3 | CIP | CIP-004 | Cyber Security — Personnel & Training | 2009-12-16 | Approved | 2010-01-26 | 2010-05-26 | Not Initiated | 2011-01-01 | 2013-09-17 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-004-3.pdf
CIP-004-3a | CIP | CIP-004 | Cyber Security - Personnel & Training | 2012-05-24 | Approved | 2013-07-19 | 2013-09-18 | Not Initiated | 2013-09-18 | 2016-06-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-004-3a.pdf
CIP-004-4 | CIP | CIP-004 | Cyber Security — Personnel & Training | 2011-01-24 | Approved | 2011-06-14 | 2011-10-12 | Not Initiated | 2012-12-13 | 2012-12-11 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-004-4.pdf
CIP-004-4a | CIP | CIP-004 | Cyber Security — Personnel & Training | 2012-05-24 | Approved | 2012-09-06 | 2013-01-04 | Not Initiated | 2014-10-01 | 2014-02-03 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-004-4a.pdf
CIP-004-5 | CIP | CIP-004 | Cyber Security — Personnel & Training | 2012-11-26 | Not Approved | 2013-02-05 | 2013-06-05 | Not Initiated |  | 2013-09-30 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-004-5.pdf
CIP-004-5.1 | CIP | CIP-004 | Cyber Security — Personnel & Training | 2013-09-27 | Approved | 2013-10-01 | 2014-01-29 | Not Initiated | 2016-04-01 | 2016-06-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-004-5_1.pdf
CIP-004-6 | CIP | CIP-004 | Cyber Security — Personnel & Training | 2014-11-13 | Approved | 2015-02-26 | 2015-06-26 | Not Initiated | 2016-07-01 | 2023-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-004-6.pdf
CIP-004-7 | CIP | CIP-004 | Cyber Security — Personnel & Training | 2021-08-12 | Approved | 2021-09-21 | 2022-01-19 | Not Initiated | 2024-04-01 |  | Effective | https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-004-7.pdf
CIP-005-1 | CIP | CIP-005 | Cyber Security — Electronic Security Perimeter(s) | 2006-05-02 | Approved |  |  | Not Initiated | 2006-05-02 | 2010-02-15 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-005-1.pdf
CIP-005-1a | CIP | CIP-005 | Cyber Security — Electronic Security Perimeter(s) | 2010-02-16 | Not Approved |  |  | Not Initiated | 2010-02-16 | 2010-06-30 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-005-1a.pdf
CIP-005-2 | CIP | CIP-005 | Cyber Security — Electronic Security Perimeter(s) | 2009-05-06 | Approved | 2009-10-01 | 2010-06-03 | Not Initiated | 2010-07-01 | 2010-09-30 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-005-2.pdf
CIP-005-2a | CIP | CIP-005 | Cyber Security — Electronic Security Perimeter(s) | 2010-02-16 | Approved |  |  | Not Initiated | 2010-10-01 | 2010-12-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-005-2a.pdf
CIP-005-3 | CIP | CIP-005 | Cyber Security — Electronic Security Perimeter(s) | 2009-12-16 | Approved | 2010-01-26 | 2010-05-26 | Not Initiated | 2011-01-01 | 2011-03-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-005-3.pdf
CIP-005-3a | CIP | CIP-005 | Cyber Security — Electronic Security Perimeter(s) | 2010-02-16 | Approved | 2010-05-11 | 2010-09-08 | Not Initiated | 2011-04-01 | 2016-06-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-005-3a.pdf
CIP-005-4a | CIP | CIP-005 | Cyber Security — Electronic Security Perimeter(s) | 2011-01-24 | Approved | 2012-02-01 | 2012-05-31 | Not Initiated | 2014-10-01 | 2014-02-03 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-005-4a.pdf
CIP-005-5 | CIP | CIP-005 | Cyber Security — Electronic Security Perimeter(s) | 2012-11-26 | Approved | 2013-02-05 | 2013-06-05 | Not Initiated | 2016-07-01 | 2020-06-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-005-5.pdf
CIP-005-6 | CIP | CIP-005 | Cyber Security — Electronic Security Perimeter(s) | 2017-08-10 | Approved | 2017-10-10 | 2018-02-07 | Not Initiated | 2020-10-01 | 2022-09-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-005-6.pdf
CIP-005-7 | CIP | CIP-005 | Cyber Security – Electronic Security Perimeter(s) | 2020-12-21 | Approved | 2021-01-19 | 2021-04-28 | Not Initiated | 2022-10-01 |  | Effective | https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-005-7.pdf
CIP-006-1 | CIP | CIP-006 | Cyber Security — Physical Security of Critical Cyber Assets | 2006-05-02 | Approved |  |  | Not Initiated | 2006-05-02 | 2009-08-04 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-006-1.pdf
CIP-006-1a | CIP | CIP-006 | Cyber Security — Physical Security of Critical Cyber Assets | 2008-02-12 | Not Approved |  |  | Not Initiated |  | 2009-12-22 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-006-1a.pdf
CIP-006-1b | CIP | CIP-006 | Cyber Security — Physical Security of Critical Cyber Assets | 2009-08-05 | Not Approved |  |  | Not Initiated | 2009-08-05 | 2010-02-15 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-006-1b.pdf
CIP-006-1c | CIP | CIP-006 | Cyber Security — Physical Security of Critical Cyber Assets | 2010-02-16 | Not Approved |  |  | Not Initiated | 2010-02-16 | 2010-03-31 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-006-1c.pdf
CIP-006-2 | CIP | CIP-006 | Cyber Security — Physical Security of Critical Cyber Assets | 2009-05-06 | Approved | 2009-06-03 | 2009-10-01 | Not Initiated | 2010-04-01 | 2010-12-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-006-2.pdf
CIP-006-2a | CIP | CIP-006 | Cyber Security — Physical Security of Critical Cyber Assets | 2009-05-06 | Approved |  |  | Not Initiated | 2010-07-15 | 2010-09-30 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-006-2a.pdf
CIP-006-2b | CIP | CIP-006 | Cyber Security — Physical Security of Critical Cyber Assets | 2009-08-05 | Approved |  |  | Not Initiated | 2010-07-16 | 2010-07-14 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-006-2b.pdf
CIP-006-2c | CIP | CIP-006 | Cyber Security — Physical Security of Critical Cyber Assets | 2010-02-16 | Approved | 2010-01-26 | 2010-05-26 | Not Initiated | 2011-01-01 | 2011-03-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-006-2c.pdf
CIP-006-3 | CIP | CIP-006 | Cyber Security — Physical Security of Critical Cyber Assets | 2009-12-16 | Approved |  |  | Not Initiated | 2009-12-16 | 2010-09-30 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-006-3.pdf
CIP-006-3a | CIP | CIP-006 | Cyber Security — Physical Security of Critical Cyber Assets | 2009-12-16 | Approved |  |  | Not Initiated | 2010-10-01 | 2011-05-18 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-006-3a.pdf
CIP-006-3c | CIP | CIP-006 | Cyber Security — Physical Security of Critical Cyber Assets | 2010-02-16 | Approved | 2010-05-11 | 2010-09-08 | Not Initiated | 2011-04-01 | 2016-06-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-006-3c.pdf
CIP-006-3d | CIP | CIP-006 | Cyber Security — Physical Security of Critical Cyber Assets | 2012-02-09 | Not Approved | 2012-07-16 | 2012-11-13 | Not Initiated |  | 2013-03-21 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-006-3d.pdf
CIP-006-4c | CIP | CIP-006 | Cyber Security — Physical Security of Critical Cyber Assets | 2011-01-24 | Approved | 2011-06-14 | 2011-10-12 | Not Initiated | 2014-10-01 | 2014-02-03 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-006-4c.pdf
CIP-006-4d | CIP | CIP-006 | Cyber Security — Physical Security of Critical Cyber Assets | 2012-02-09 | Not Approved | 2012-07-16 | 2012-11-13 | Not Initiated |  | 2013-03-21 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-006-4d.pdf
CIP-006-5 | CIP | CIP-006 | Cyber Security — Physical Security of BES Cyber Systems | 2012-11-26 | Approved | 2013-02-05 | 2013-06-05 | Not Initiated | 2016-04-01 | 2016-06-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-006-5.pdf
CIP-006-6 | CIP | CIP-006 | Cyber Security — Physical Security of BES Cyber Systems | 2014-11-13 | Approved | 2015-02-26 | 2015-06-26 | Not Initiated | 2016-07-01 |  | Effective | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-006-6.pdf
CIP-007-1 | CIP | CIP-007 | Cyber Security — Systems Security Management | 2006-05-02 | Approved |  |  | Not Initiated | 2006-05-02 | 2010-04-10 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-007-1.pdf
CIP-007-2 | CIP | CIP-007 | Cyber Security — Systems Security Management | 2009-05-06 | Approved |  |  | Not Initiated | 2010-03-17 | 2010-03-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-007-2.pdf
CIP-007-2a | CIP | CIP-007 | Cyber Security — Systems Security Management | 2009-11-05 | Approved | 2009-12-11 | 2010-04-10 | Not Initiated | 2010-04-11 | 2010-12-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-007-2a.pdf
CIP-007-3 | CIP | CIP-007 | Cyber Security — Systems Security Management | 2009-12-16 | Pending Approval |  |  | Not Initiated |  |  | Pending Approval In The USA | https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-007-3.pdf
CIP-007-3a | CIP | CIP-007 | Cyber Security - Systems Security Management | 2009-12-16 | Approved | 2010-01-26 | 2010-05-26 | Not Initiated | 2011-01-01 | 2016-06-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-007-3a.pdf
CIP-007-3b | CIP | CIP-007 | Cyber Security - Systems Security Management | 2013-11-07 | Not Approved | 1899-12-31 | 1900-01-01 | Not Initiated |  | 2016-06-30 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-007-3b.pdf
CIP-007-4a | CIP | CIP-007 | Cyber Security — Systems Security Management | 2011-01-24 | Approved | 2011-06-14 | 2011-10-12 | Not Initiated | 2014-10-01 | 2014-02-03 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-007-4a.pdf
CIP-007-4b | CIP | CIP-007 | Cyber Security — Systems Security Management | 2013-11-07 | Not Approved |  |  | Not Initiated |  | 2014-02-03 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-007-4b.pdf
CIP-007-5 | CIP | CIP-007 | Cyber Security — Systems Security Management | 2012-11-26 | Approved | 2013-02-05 | 2013-06-05 | Not Initiated | 2016-04-01 | 2016-06-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-007-5.pdf
CIP-007-6 | CIP | CIP-007 | Cyber Security — Systems Security Management | 2014-11-13 | Approved | 2015-02-26 | 2015-06-26 | Not Initiated | 2016-07-01 |  | Effective | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-007-6.pdf
CIP-008-1 | CIP | CIP-008 | Cyber Security — Incident Reporting and Response Planning | 2006-05-02 | Approved |  |  | Not Initiated | 2006-05-02 | 2010-06-30 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-008-1.pdf
CIP-008-2 | CIP | CIP-008 | Cyber Security — Incident Reporting and Response Planning | 2009-05-06 | Approved | 2009-06-03 | 2009-10-01 | Not Initiated | 2010-07-01 | 2010-12-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-008-2.pdf
CIP-008-3 | CIP | CIP-008 | Cyber Security - Incident Reporting and Response Planning | 2009-12-16 | Approved | 2010-01-26 | 2010-05-26 | Not Initiated | 2011-01-01 | 2016-06-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-008-3.pdf
CIP-008-4 | CIP | CIP-008 | Cyber Security — Incident Reporting and Response Planning | 2011-01-24 | Approved | 2011-06-14 | 2011-10-12 | Not Initiated | 2014-10-01 | 2014-02-03 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-008-4.pdf
CIP-008-5 | CIP | CIP-008 | Cyber Security — Incident Reporting and Response Planning | 2012-11-26 | Approved | 2013-02-05 | 2013-06-05 | Not Initiated | 2016-07-01 | 2021-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-008-5.pdf
CIP-008-6 | CIP | CIP-008 | Cyber Security — Incident Reporting and Response Planning | 2019-02-07 | Approved | 2019-04-01 | 2019-07-01 | Not Initiated | 2021-04-01 |  | Effective | https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-008-6.pdf
CIP-009-1 | CIP | CIP-009 | Cyber Security — Recovery Plans for Critical Cyber Assets | 2006-05-02 | Approved |  |  | Not Initiated | 2006-05-02 | 2010-06-30 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-009-1.pdf
CIP-009-2 | CIP | CIP-009 | Cyber Security — Recovery Plans for Critical Cyber Assets | 2009-05-06 | Approved | 2009-06-03 | 2009-10-01 | Not Initiated | 2010-07-01 | 2010-12-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-009-2.pdf
CIP-009-3 | CIP | CIP-009 | Cyber Security - Recovery Plans for Critical Cyber Assets | 2009-12-16 | Approved | 2010-01-26 | 2010-05-26 | Not Initiated | 2011-01-01 | 2016-06-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-009-3.pdf
CIP-009-4 | CIP | CIP-009 | Cyber Security — Recovery Plans for Critical Cyber Assets | 2011-01-24 | Approved | 2011-06-14 | 2011-10-12 | Not Initiated | 2014-10-01 | 2014-02-03 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-009-4.pdf
CIP-009-5 | CIP | CIP-009 | Cyber Security — Recovery Plans for BES Cyber Systems | 2012-11-26 | Approved | 2013-02-05 | 2013-06-05 | Not Initiated | 2016-04-01 | 2016-06-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-009-5.pdf
CIP-009-6 | CIP | CIP-009 | Cyber Security — Recovery Plans for BES Cyber Systems | 2014-11-13 | Approved | 2015-02-26 | 2015-06-26 | Not Initiated | 2016-07-01 |  | Effective | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-009-6.pdf
CIP-010-1 | CIP | CIP-010 | Cyber Security — Configuration Change Management and Vulnerability Assessments | 2012-11-26 | Approved | 2013-02-05 | 2013-06-05 | Not Initiated | 2016-04-01 | 2016-06-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-010-1.pdf
CIP-010-2 | CIP | CIP-010 | Cyber Security — Configuration Change Management and Vulnerability Assessments | 2014-11-13 | Approved | 2015-02-26 | 2015-06-26 | Not Initiated | 2016-07-01 | 2020-06-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-010-2.pdf
CIP-010-3 | CIP | CIP-010 | Cyber Security — Configuration Change Management and Vulnerability Assessments | 2017-08-10 | Approved | 2017-10-10 | 2017-10-31 | Not Initiated | 2020-10-01 | 2022-09-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-010-3.pdf
CIP-010-4 | CIP | CIP-010 | – Cyber Security — Configuration Change Management and Vulnerability Assessments | 2020-06-12 | Approved | 2021-01-19 | 2021-04-28 | Not Initiated | 2022-10-01 |  | Effective | https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-010-4.pdf
CIP-011-1 | CIP | CIP-011 | Cyber Security Information Protection | 2012-11-26 | Not Approved | 2013-02-05 | 2013-06-05 | Not Initiated | 2016-04-01 | 2016-06-30 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-011-1.pdf
CIP-011-2 | CIP | CIP-011 | Cyber Security Information Protection | 2014-11-13 | Approved | 2015-02-26 | 2015-06-26 | Not Initiated | 2016-07-01 | 2024-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-011-2.pdf
CIP-011-3 | CIP | CIP-011 | Cyber Security — Information Protection | 2021-08-12 | Approved | 2021-09-21 | 2022-01-19 | Not Initiated | 2024-04-01 |  | Effective | https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-011-3.pdf
CIP-012-1 | CIP | CIP-012 | Cyber Security – Control Center Communication Networks | 2018-08-16 | Approved | 2018-09-21 | 2019-01-19 | Not Initiated | 2022-07-01 |  | Effective | https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-012-1.pdf
CIP-012-2 | CIP | CIP-012 | Cyber Security – Communications between Control Centers | 2023-12-12 | Pending Approval | 2024-03-21 | 2024-07-19 | Not Initiated |  |  | Under OEB Review | https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-012-2.pdf
CIP-013-1 | CIP | CIP-013 | Cyber Security - Supply Chain Risk Management | 2017-08-10 | Approved | 2017-10-10 | 2018-02-07 | Not Initiated | 2020-10-01 | 2022-09-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-013-1.pdf
CIP-013-2 | CIP | CIP-013 | Cyber Security - Supply Chain Risk Management | 2020-12-12 | Approved | 2021-01-19 | 2021-04-28 | Not Initiated | 2022-10-01 |  | Effective | https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-013-2.pdf
CIP-014-1 | CIP | CIP-014 | Physical Security | 2014-05-13 | Approved | 2014-05-30 | 2014-09-27 | Not Initiated | 2015-10-01 | 2015-10-01 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-014-1.pdf
CIP-014-2 | CIP | CIP-014 | Physical Security | 2015-05-07 | Approved | 2015-05-22 | 2015-09-18 | Not Initiated | 2015-10-02 | 2022-06-16 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/CIP-014-2.pdf
CIP-014-3 | CIP | CIP-014 | Physical Security | 2022-02-11 | Approved |  |  | Not Initiated | 2022-06-16 |  | Effective | https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-014-3.pdf
COM-001-0 | COM | COM-001 | Telecommunications | 2005-02-08 | Not Approved |  | 1900-04-01 | Not Initiated |  | 2007-01-01 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/COM-001-0.pdf
COM-001-1 | COM | COM-001 | Telecommunications | 2006-11-01 | Approved |  | 1900-04-01 | Not Initiated | 2007-06-18 | 2009-05-12 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/COM-001-1.pdf
COM-001-1.1 | COM | COM-001 | Telecommunications | 2008-10-29 | Approved | 2009-05-15 | 2009-09-12 | Not Initiated | 2009-09-13 | 2016-06-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/COM-001-1_1.pdf
COM-001-2 | COM | COM-001 | Communications | 2012-11-07 | Approved | 2014-05-21 | 2014-09-11 | Not Initiated | 2015-10-01 | 2015-11-12 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/COM-001-2.pdf
COM-001-2.1 | COM | COM-001 | Communications | 2012-11-07 | Approved | 1899-12-31 | 1900-01-01 | Not Initiated | 2015-11-13 | 2017-09-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/COM-001-2.1.pdf
COM-001-3 | COM | COM-001 | Communications | 2016-08-11 | Approved | 2016-08-17 | 2016-12-15 | Not Initiated | 2017-10-01 |  | Effective | http://www.nerc.com/pa/Stand/Project 201507 Internal Communications Capabilitie/COM-001-3_Clean_060116.pdf
COM-002-0 | COM | COM-002 | Communication and Coordination | 2005-02-08 | Not Approved |  | 1900-04-01 | Not Initiated |  | 2006-11-01 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/COM-002-0.pdf
COM-002-1 | COM | COM-002 | Communication and Coordination | 2006-02-07 | Not Approved |  | 1900-04-01 | Not Initiated |  | 2007-01-01 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/COM-002-1.pdf
COM-002-2 | COM | COM-002 | Communications and Coordination | 2006-11-01 | Approved | 1899-12-31 | 1900-01-01 | Not Initiated | 2006-11-01 | 2016-06-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/COM-002-2.pdf
COM-002-2a | COM | COM-002 | Communications and Coordination | 2012-02-09 | Not Approved | 1899-12-31 | 1900-01-01 | Not Initiated |  | 2016-06-30 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/COM-002-2a.pdf
COM-002-3 | COM | COM-002 | Communications and Coordination | 2012-11-07 | Not Approved | 1899-12-31 | 1900-01-01 | Not Initiated |  | 2016-06-30 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/COM-002-3.pdf
COM-002-4 | COM | COM-002 | Operating Personnel Communications Protocols | 2014-05-06 | Approved | 2014-05-21 | 2014-09-11 | Not Initiated | 2016-07-01 |  | Effective | http://www.nerc.com/pa/Stand/Reliability Standards/COM-002-4.pdf
EOP-001-0 | EOP | EOP-001 | Emergency Operations Planning | 2005-02-08 | Approved |  | 1900-04-01 | Not Initiated | 2005-02-08 | 2012-01-26 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/EOP-001-0.pdf
EOP-001-0.1b | EOP | EOP-001 | Emergency Operations Planning | 2012-03-08 | Approved | 2012-06-11 | 2012-10-09 | Not Initiated | 2012-10-10 | 2013-06-30 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/EOP-001-0_1b.pdf
EOP-001-0b | EOP | EOP-001 | Emergency Operations Planning | 2010-11-04 | Approved | 2011-09-28 | 2012-01-26 | Not Initiated | 2012-01-27 | 2012-10-09 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/EOP-001-0b.pdf
EOP-001-1 | EOP | EOP-001 | Emergency Operations Planning | 2008-10-17 | Not Approved | 2010-01-26 | 2010-05-26 | Not Initiated |  | 2011-05-23 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/EOP-001-1.pdf
EOP-001-2 | EOP | EOP-001 | Emergency Operations Planning | 2009-08-05 | Approved | 2010-01-26 | 2010-05-26 | Not Initiated | 2012-09-14 | 2011-12-14 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/EOP-001-2.pdf
EOP-001-2.1b | EOP | EOP-001 | Emergency Operations Planning | 2012-03-08 | Approved | 2012-06-11 | 2012-10-09 | Not Initiated | 2013-07-01 | 2017-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/EOP-001-2_1b.pdf
EOP-001-2b | EOP | EOP-001 | Emergency Operations Planning | 2010-11-04 | Approved | 2011-09-28 | 2012-01-26 | Not Initiated | 2012-09-14 | 2012-09-12 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/EOP-001-2b.pdf
EOP-002-0 | EOP | EOP-002 | Capacity and Energy Emergencies | 2005-02-08 | Not Approved |  | 1900-04-01 | Not Initiated |  | 2006-11-01 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/EOP-002-0.pdf
EOP-002-1 | EOP | EOP-002 | Capacity and Energy Emergencies | 2006-02-07 | Not Approved |  | 1900-04-01 | Not Initiated |  | 2007-01-01 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/EOP-002-1.pdf
EOP-002-2 | EOP | EOP-002 | Capacity and Energy Emergencies | 2006-11-01 | Approved |  | 1900-04-01 | Not Initiated | 2006-11-01 | 2009-09-12 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/EOP-002-2.pdf
EOP-002-2.1 | EOP | EOP-002 | Capacity and Energy Emergencies | 2008-10-29 | Approved | 2009-05-15 | 2009-09-12 | Not Initiated | 2009-09-13 | 2012-03-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/EOP-002-2_1.pdf
EOP-002-3 | EOP | EOP-002 | Capacity and Energy Emergencies | 2010-08-05 | Approved | 2011-03-10 | 2011-07-08 | Not Initiated | 2012-04-01 | 2012-10-09 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/EOP-002-3.pdf
EOP-002-3.1 | EOP | EOP-002 | Capacity and Energy Emergencies | 2012-03-08 | Approved | 2012-06-11 | 2012-10-09 | Not Initiated | 2012-10-10 | 2017-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/EOP-002-3_1.pdf
EOP-003-0 | EOP | EOP-003 | Load Shedding Plans | 2005-02-08 | Not Approved |  | 1900-04-01 | Not Initiated |  | 2007-01-01 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/EOP-003-0.pdf
EOP-003-1 | EOP | EOP-003 | Load Shedding Plans | 2006-11-01 | Approved |  | 1900-04-01 | Not Initiated | 2006-11-01 | 2013-09-30 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/EOP-003-1.pdf
EOP-003-2 | EOP | EOP-003 | Load Shedding Plans | 2010-11-04 | Approved | 2011-04-20 | 2011-08-18 | Not Initiated | 2013-10-01 | 2017-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/EOP-003-2.pdf
EOP-004-1 | EOP | EOP-004 | Disturbance Reporting | 2006-11-01 | Approved |  | 1900-04-01 | Not Initiated | 2006-11-01 | 2013-12-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/EOP-004-1.pdf
EOP-004-2 | EOP | EOP-004 | Event Reporting | 2012-11-07 | Approved | 2013-01-10 | 2013-05-10 | Not Initiated | 2014-01-01 | 2017-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/EOP-004-2.pdf
EOP-004-3 | EOP | EOP-004 | Event Reporting | 2014-11-13 | Approved | 2015-02-10 | 2015-06-10 | Not Initiated | 2017-04-01 | 2019-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/EOP-004-3.pdf
EOP-004-4 | EOP | EOP-004 | Event Reporting | 2017-02-09 | Approved | 2017-03-31 | 2017-07-29 | Not Initiated | 2019-04-01 |  | Effective | http://www.nerc.com/pa/Stand/Reliability Standards/EOP-004-4.pdf
EOP-005-0 | EOP | EOP-005 | System Restoration Plans | 2005-02-08 | Not Approved |  | 1900-04-01 | Not Initiated |  | 2007-05-02 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/EOP-005-0.pdf
EOP-005-1 | EOP | EOP-005 | System Restoration Plans | 2006-05-02 | Approved |  | 1900-04-01 | Not Initiated | 2007-05-02 | 2013-06-30 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/EOP-005-1.pdf
EOP-005-2 | EOP | EOP-005 | System Restoration from Blackstart Resources | 2009-08-05 | Approved | 2010-01-26 | 2010-05-26 | Not Initiated | 2013-07-01 | 2019-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/EOP-005-2.pdf
EOP-005-3 | EOP | EOP-005 | System Restoration from Blackstart Resources | 2017-02-09 | Approved | 2017-03-31 | 2017-07-29 | Not Initiated | 2019-04-01 |  | Effective | http://www.nerc.com/pa/Stand/Reliability Standards/EOP-005-3.pdf
EOP-006-0 | EOP | EOP-006 | Reliability Coordination – System Restoration | 2005-02-08 | Not Approved |  | 1900-04-01 | Not Initiated |  | 2007-01-01 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/EOP-006-0.pdf
EOP-006-1 | EOP | EOP-006 | Reliability Coordination – System Restoration | 2006-11-01 | Approved |  | 1900-04-01 | Not Initiated | 2006-11-01 | 2013-06-30 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/EOP-006-1.pdf
EOP-006-2 | EOP | EOP-006 | System Restoration Coordination | 2009-08-05 | Approved | 2010-01-26 | 2010-05-26 | Not Initiated | 2013-07-01 | 2019-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/EOP-006-2.pdf
EOP-006-3 | EOP | EOP-006 | System Restoration Coordination | 2017-02-09 | Approved | 2017-03-31 | 2017-07-29 | Not Initiated | 2019-04-01 |  | Effective | http://www.nerc.com/pa/Stand/Reliability Standards/EOP-006-3.pdf
EOP-007-0 | EOP | EOP-007 | Establish, Maintain, and Document a Regional Blackstart Capability Plan | 2005-02-08 | Not Approved |  | 1900-04-01 | Not Initiated | 2005-02-08 | 2011-05-23 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/EOP-007-0.pdf
EOP-008-0 | EOP | EOP-008 | Plans for Loss of Control Center Functionality | 2005-02-08 | Approved |  | 1900-04-01 | Not Initiated | 2005-02-08 | 2013-09-30 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/EOP-008-0.pdf
EOP-008-1 | EOP | EOP-008 | Loss of Control Center Functionality | 2010-08-05 | Approved | 2011-03-10 | 2011-07-08 | Not Initiated | 2013-10-01 | 2019-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/EOP-008-1.pdf
EOP-008-2 | EOP | EOP-008 | Loss of Control Center Functionality | 2017-02-09 | Approved | 2017-03-31 | 2017-07-29 | Not Initiated | 2019-04-01 |  | Effective | http://www.nerc.com/pa/Stand/Reliability Standards/EOP-008-2.pdf
EOP-009-0 | EOP | EOP-009 | Documentation of Blackstart Generating Unit Test Results | 2005-02-08 | Approved |  | 1900-04-01 | Not Initiated | 2005-02-08 | 2013-06-30 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/EOP-009-0.pdf
EOP-010-1 | EOP | EOP-010 | Geomagnetic Disturbance Operations | 2013-11-07 | Approved | 2013-11-15 | 2014-03-15 | Not Initiated | 2015-04-01 |  | Effective | http://www.nerc.com/pa/Stand/Reliability Standards/EOP-010-1.pdf
EOP-011-1 | EOP | EOP-011 | Emergency Operations | 2014-11-13 | Approved | 2015-01-07 | 2015-05-08 | Not Initiated | 2017-04-01 | 2023-09-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/EOP-011-1.pdf
EOP-011-2 | EOP | EOP-011 | Emergency Preparedness and Operations | 2021-06-11 | Approved | 2021-06-11 | 2021-10-09 | Not Initiated | 2023-10-01 |  | Effective | https://www.nerc.com/pa/Stand/Project%20201906%20Cold%20Weather%20DL/2019-06_EOP-011-2_Clean_05182021.pdf
EOP-011-3 | EOP | EOP-011 | Emergency Operations | 2022-02-16 | Pending Approval | 2022-12-09 | 2023-04-08 | Not Initiated |  |  | Pending Approval In The USA | https://www.nerc.com/pa/Stand/Reliability%20Standards/EOP-011-3.pdf
EOP-011-4 | EOP | EOP-011 | Emergency Operations | 2023-10-23 | Pending Approval | 2023-11-15 | 2024-03-14 | Not Initiated |  |  | Pending Approval In The USA | https://www.nerc.com/pa/Stand/Reliability%20Standards/EOP-011-4.pdf
EOP-012-1 | EOP | EOP-012 | Extreme Cold Weather Preparedness and Operations | 2022-02-16 | Approved | 2022-12-09 | 2023-04-08 | Not Initiated | 2025-01-01 |  | Future Effective | https://www.nerc.com/pa/Stand/Reliability%20Standards/EOP-012-1.pdf
EOP-012-2 | EOP | EOP-012 | Extreme Cold Weather Preparedness and Operations | 2024-02-15 | Pending Approval | 2024-03-04 | 2024-07-02 | Not Initiated |  |  | Under OEB Review | https://www.nerc.com/pa/Stand/Reliability%20Standards/EOP-012-2.pdf
FAC-001-0 | FAC | FAC-001 | Facility Connection Requirements | 2005-02-08 | Approved |  | 1900-04-01 | Not Initiated | 2005-02-08 | 2014-12-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/FAC-001-0.pdf
FAC-001-1 | FAC | FAC-001 | Facility Connection Requirements | 2012-02-09 | Approved | 2012-09-06 | 2013-01-04 | Not Initiated | 2013-11-25 | 2015-12-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/FAC-001-1.pdf
FAC-001-2 | FAC | FAC-001 | Facility Interconnection Requirements | 2014-08-14 | Approved | 2014-08-29 | 2014-12-27 | Not Initiated | 2016-01-01 | 2018-12-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/FAC-001-2.pdf
FAC-001-3 | FAC | FAC-001 | Facility Interconnection Requirements | 2016-02-11 | Approved | 2016-04-26 | 2016-08-24 | Not Initiated | 2019-01-01 | 2023-12-31 | Retired | http://www.nerc.com/pa/Stand/Project 20101421 Phase 2 DL/FAC-001-3_Draft_Standard_Clean_01272016.pdf
FAC-001-4 | FAC | FAC-001 | Facility Interconnection Requirements | 2022-05-12 | Approved | 2022-06-21 | 2022-10-19 | Not Initiated | 2024-01-01 |  | Effective | https://www.nerc.com/pa/Stand/Reliability%20Standards/FAC-001-4.pdf
FAC-002-0 | FAC | FAC-002 | Coordination of Plans For New Generation, Transmission, and End-User Facilities | 2005-02-08 | Approved |  | 1900-04-01 | Not Initiated | 2005-02-08 | 2012-03-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/FAC-002-0.pdf
FAC-002-1 | FAC | FAC-002 | Coordination of Plans For New Generation, Transmission, and End-User Facilities | 2010-08-05 | Approved | 2011-03-10 | 2011-07-08 | Not Initiated | 2012-04-01 | 2015-12-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/FAC-002-1.pdf
FAC-002-2 | FAC | FAC-002 | Facility Interconnection Studies | 2014-08-14 | Approved | 2014-08-29 | 2014-12-27 | Not Initiated | 2016-01-01 | 2021-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/FAC-002-2.pdf
FAC-002-3 | FAC | FAC-002 | Facility Interconnection Studies | 2020-01-23 | Approved | 2020-02-26 | 2000-06-25 | Not Initiated | 2021-04-01 | 2023-12-31 | Retired | https://www.nerc.com/pa/Stand/Project201707StandardsAlignmentwithRegistration/FAC-002-3%20Project%202017%2007%20%20Clean_January2020.pdf
FAC-002-4 | FAC | FAC-002 | Facility Interconnection Studies | 2022-05-12 | Approved | 2022-06-21 | 2022-10-19 | Not Initiated | 2024-01-01 |  | Effective | https://www.nerc.com/pa/Stand/Reliability%20Standards/FAC-002-4.pdf
FAC-003-0 | FAC | FAC-003 | Vegetation Management Program | 2005-02-08 | Not Approved |  | 1900-04-01 | Not Initiated |  | 2006-04-07 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/FAC-003-0.pdf
FAC-003-1 | FAC | FAC-003 | Transmission Vegetation Management Program | 2006-02-07 | Approved |  | 1900-04-01 | Not Initiated | 2006-02-14 | 2014-06-30 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/FAC-003-1.pdf
FAC-003-2 | FAC | FAC-003 | Transmission Vegetation Management | 2011-11-03 | Approved | 2012-02-03 | 2012-06-02 | Not Initiated | 2014-07-01 | 2013-11-25 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/FAC-003-2.pdf
FAC-003-3 | FAC | FAC-003 | Transmission Vegetation Management | 2012-05-09 | Approved | 2012-09-06 | 2013-01-04 | Not Initiated | 2014-07-01 | 2016-09-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/FAC-003-3.pdf
FAC-003-4 | FAC | FAC-003 | Transmission Vegetation Management | 2016-02-11 | Approved | 2016-03-22 | 2016-06-18 | Not Initiated | 2016-10-01 | 2024-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/FAC-003-4.pdf
FAC-003-5 | FAC | FAC-003 | Transmission Vegetation Management | 2021-05-13 | Approved | 2021-07-07 | 2021-11-04 | Not Initiated | 2024-04-01 |  | Effective | https://www.nerc.com/pa/Stand/Reliability%20Standards/FAC-003-5.pdf
FAC-004-0 | FAC | FAC-004 | Methodologies for Determining Electrical Facility Ratings | 2005-02-08 | Not Approved |  | 1900-04-01 | Not Initiated |  | 2006-08-01 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/FAC-004-0.pdf
FAC-005-0 | FAC | FAC-005 | Electrical Facility Ratings for System Modeling | 2005-02-08 | Not Approved |  | 1900-04-01 | Not Initiated |  | 2006-10-07 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/FAC-005-0.pdf
FAC-008-1 | FAC | FAC-008 | Facility Ratings Methodology | 2006-02-07 | Approved |  | 1900-04-01 | Not Initiated | 2006-02-07 | 2012-12-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/FAC-008-1.pdf
FAC-008-2 | FAC | FAC-008 | Facility Ratings | 2010-05-12 | Not Approved | 1899-12-31 | 1900-01-01 | Not Initiated |  | 2011-05-24 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/FAC-008-2.pdf
FAC-008-3 | FAC | FAC-008 | Facility Ratings | 2011-05-24 | Approved | 2011-07-13 | 2011-11-10 | Not Initiated | 2013-01-01 | 2021-09-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/FAC-008-3.pdf
FAC-008-4 | FAC | FAC-008 | Facility Ratings | 2019-05-09 | Not Approved |  | 1900-04-01 | Not Initiated |  | 2019-05-09 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/FAC-008-4.pdf
FAC-008-5 | FAC | FAC-008 | Facility Ratings | 2021-02-04 | Approved | 2021-03-09 | 2021-07-07 | Not Initiated | 2022-01-01 |  | Effective | https://www.nerc.com/pa/Stand/Reliability%20Standards/FAC-008-5.pdf
FAC-009-1 | FAC | FAC-009 | Establish and Communicate Facility Ratings | 2006-02-07 | Approved |  | 1900-04-01 | Not Initiated | 2006-02-07 | 2012-12-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/FAC-009-1.pdf
FAC-010-1 | FAC | FAC-010 | System Operating Limits Methodology for the Planning Horizon | 2006-11-01 | Approved |  | 1900-04-01 | Not Initiated | 2008-07-01 | 2009-04-28 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/FAC-010-1.pdf
FAC-010-2 | FAC | FAC-010 | System Operating Limits Methodology for the Planning Horizon | 2008-06-24 | Approved |  | 1900-04-01 | Not Initiated | 2009-04-29 | 2010-04-18 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/FAC-010_2.pdf
FAC-010-2.1 | FAC | FAC-010 | System Operating Limits Methodology for the Planning Horizon | 2009-11-05 | Approved | 2009-12-11 | 2010-04-10 | Not Initiated | 2010-04-11 | 2017-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/FAC-010-2.1.pdf
FAC-010-3 | FAC | FAC-010 | System Operating Limits Methodology for the Planning Horizon | 2014-11-13 | Approved | 2015-02-10 | 2015-06-10 | Not Initiated | 2017-04-01 | 2024-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/FAC-010-3.pdf
FAC-011-1 | FAC | FAC-011 | System Operating Limits Methodology for the Operations Horizon | 2006-11-01 | Approved |  | 1900-04-01 | Not Initiated | 2008-10-01 | 2009-04-28 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/FAC-011-1.pdf
FAC-011-2 | FAC | FAC-011 | System Operating Limits Methodology for the Operations Horizon | 2008-06-24 | Approved | 2008-07-18 | 2008-11-15 | Not Initiated | 2008-11-15 | 2017-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/FAC-011-2.pdf
FAC-011-3 | FAC | FAC-011 | System Operating Limits Methodology for the Operations Horizon | 2014-11-13 | Approved | 2015-02-10 | 2015-06-10 | Not Initiated | 2017-04-01 | 2024-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/FAC-011-3.pdf
FAC-011-4 | FAC | FAC-011 | System Operating Limits Methodology for the Operations Horizon | 2021-05-13 | Approved | 2021-07-07 | 2021-11-04 | Not Initiated | 2024-04-01 |  | Effective | https://www.nerc.com/pa/Stand/Reliability Standards/FAC-011-4.pdf
FAC-012-1 | FAC | FAC-012 | Transfer Capability Methodology | 2006-02-07 | Not Approved |  | 1900-04-01 | Not Initiated | 2006-02-07 | 2011-07-07 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/FAC-012-1.pdf
FAC-013-1 | FAC | FAC-013 | Establish and Communicate Transfer Capabilities | 2006-02-07 | Approved |  | 1900-04-01 | Not Initiated | 2006-02-07 | 2013-03-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/FAC-013-1.pdf
FAC-013-2 | FAC | FAC-013 | Assessment of Transfer Capability for the Near-Term Transmission Planning Horizon | 2011-01-24 | Approved | 2011-03-10 | 2011-07-08 | Not Initiated | 2013-04-01 | 2020-12-24 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/FAC-013-2.pdf
FAC-014-1 | FAC | FAC-014 | Establish and Communicate System Operating Limits | 2006-11-01 | Approved |  | 1900-04-01 | Not Initiated | 2009-01-01 | 2009-04-28 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/FAC-014-1.pdf
FAC-014-2 | FAC | FAC-014 | Establish and Communicate System Operating Limits | 2008-06-24 | Approved | 2008-07-18 | 2008-11-15 | Not Initiated | 2008-11-16 | 2024-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/FAC-014-2.pdf
FAC-014-3 | FAC | FAC-014 | Establish and Communicate System Operating Limits | 2021-05-13 | Approved | 2021-07-07 | 2021-11-04 | Not Initiated | 2024-04-01 |  | Effective | http://www.nerc.com/pa/Stand/Reliability Standards/FAC-014-3.pdf
INT-001-0 | INT | INT-001 | Interchange Transaction Tagging | 2005-02-08 | Not Approved |  | 1900-04-01 | Not Initiated |  | 2007-01-01 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/INT-001-0.pdf
INT-001-1 | INT | INT-001 | Interchange Information | 2006-05-02 | Not Approved |  | 1900-04-01 | Not Initiated |  | 2006-11-01 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/INT-001-1.pdf
INT-001-2 | INT | INT-001 | Interchange Transaction Tagging | 2006-11-01 | Approved |  | 1900-04-01 | Not Initiated | 2007-06-18 | 2008-08-26 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/INT-001-2.pdf
INT-001-3 | INT | INT-001 | Interchange Information | 2007-10-09 | Approved |  | 1900-04-01 | Not Initiated | 2007-10-09 | 2014-12-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/INT-001-3.pdf
INT-002-0 | INT | INT-002 | Interchange Transaction Tag Communication and Reliability Assessment | 2005-02-08 | Not Approved |  | 1900-04-01 | Not Initiated |  | 2007-01-01 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/INT-002-0.pdf
INT-003-0 | INT | INT-003 | Interchange Transaction Implementation | 2005-02-08 | Not Approved |  | 1900-04-01 | Not Initiated |  | 2007-01-01 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/INT-003-0.pdf
INT-003-1 | INT | INT-003 | Interchange Transaction Implementation | 2006-05-02 | Not Approved |  | 1900-04-01 | Not Initiated |  | 2007-01-01 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/INT-003-1.pdf
INT-003-2 | INT | INT-003 | Interchange Transaction Implementation | 2006-11-01 | Approved |  | 1900-04-01 | Not Initiated | 2006-11-01 | 2010-06-30 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/INT-003-2.pdf
INT-003-3 | INT | INT-003 | Interchange Transaction Implementation | 2009-11-05 | Approved | 2009-12-11 | 2010-04-10 | Not Initiated | 2010-07-01 | 2014-12-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/INT-003-3.pdf
INT-004-0 | INT | INT-004 | Interchange Transaction Modifications | 2005-02-08 | Not Approved |  | 1900-04-01 | Not Initiated | 2007-01-01 |  | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/INT-004-0.pdf
INT-004-1 | INT | INT-004 | Dynamic Interchange Transaction Modifications | 2006-05-02 | Approved |  | 1900-04-01 | Not Initiated | 2007-06-18 | 2008-08-26 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/INT-004-1.pdf
INT-004-2 | INT | INT-004 | Dynamic Interchange Transaction Modifications | 2007-10-09 | Approved |  |  | Not Initiated | 2007-10-09 | 2014-12-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/INT-004-2.pdf
INT-004-3 | INT | INT-004 | Dynamic Transfers | 2014-02-06 | Approved | 2014-03-03 | 2014-07-01 | Not Initiated | 2015-01-01 | 2014-11-26 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/INT-004-3.pdf
INT-004-3.1 | INT | INT-004 | Dynamic Interchange Transaction Modifications | 2014-08-20 | Approved | 1899-12-31 | 1900-01-01 | Not Initiated | 2015-01-01 | 2020-12-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/INT-004-3.1.pdf
INT-005-1 | INT | INT-005 | Interchange Authority Distributes Arranged Interchange | 2006-05-02 | Approved |  |  | Not Initiated | 2007-06-18 | 2008-08-26 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/INT-005-1.pdf
INT-005-2 | INT | INT-005 | Interchange Authority Distributes Arranged Interchange | 2007-05-02 | Approved |  |  | Not Initiated | 2007-05-02 | 2008-10-28 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/INT-005-2.pdf
INT-005-3 | INT | INT-005 | Interchange Authority Distributes Arranged Interchange | 2008-10-29 | Approved |  |  | Not Initiated | 2008-10-29 | 2014-12-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/INT-005-3.pdf
INT-006-1 | INT | INT-006 | Response to Interchange Authority | 2006-05-02 | Approved |  |  | Not Initiated | 2007-06-18 | 2008-08-26 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/INT-006-1.pdf
INT-006-2 | INT | INT-006 | Response to Interchange Authority | 2007-05-02 | Approved |  |  | Not Initiated | 2007-05-02 | 2008-10-28 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/INT-006-2.pdf
INT-006-3 | INT | INT-006 | Response to Interchange Authority | 2008-10-29 | Approved |  |  | Not Initiated | 2008-10-29 | 2014-12-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/INT-006-3.pdf
INT-006-4 | INT | INT-006 | Evaluation of Interchange Transactions | 2014-02-06 | Approved | 2014-03-03 | 2014-07-01 | Not Initiated | 2015-01-01 | 2021-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/INT-006-4.pdf
INT-006-5 | INT | INT-006 | Evaluation of Interchange Transactions | 2019-05-09 | Approved | 2019-05-09 | 2019-09-06 | Not Initiated | 2021-04-01 |  | Effective | https://www.nerc.com/pa/Stand/Reliability%20Standards/INT-006-5.pdf
INT-007-1 | INT | INT-007 | Interchange Confirmation | 2006-05-02 | Approved |  |  | Not Initiated | 2006-05-02 | 2014-12-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/INT-007-1.pdf
INT-008-1 | INT | INT-008 | Interchange Authority Distributes Status | 2006-05-02 | Approved |  |  | Not Initiated | 2007-06-18 | 2008-08-26 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/INT-008-1.pdf
INT-008-2 | INT | INT-008 | Interchange Authority Distributes Status | 2007-05-02 | Approved |  |  | Not Initiated | 2007-05-02 | 2008-10-28 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/INT-008-2.pdf
INT-008-3 | INT | INT-008 | Interchange Authority Distributes Status | 2008-10-29 | Approved |  |  | Not Initiated | 2008-10-29 | 2014-12-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/INT-008-3.pdf
INT-009-1 | INT | INT-009 | Implementation of Interchange | 2006-05-02 | Approved |  |  | Not Initiated | 2006-05-02 | 2014-12-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/INT-009-1.pdf
INT-009-2 | INT | INT-009 | Implementation of Interchange | 2014-02-06 | Approved | 2014-03-03 | 2014-07-01 | Not Initiated | 2015-01-01 | 2014-11-26 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/INT-009-2.pdf
INT-009-2.1 | INT | INT-009 | Implementation of Interchange | 2014-08-20 | Approved | 1899-12-31 | 1900-01-01 | Not Initiated | 2015-01-01 | 2021-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/INT-009-2.1.pdf
INT-009-3 | INT | INT-009 | Implementation of Interchange | 2019-05-09 | Approved | 2019-05-09 | 2019-09-06 | Not Initiated | 2021-04-01 |  | Effective | https://www.nerc.com/pa/Stand/Reliability%20Standards/INT-009-3.pdf
INT-010-1 | INT | INT-010 | Interchange Coordination Exemptions | 2006-05-02 | Approved |  |  | Not Initiated | 2006-05-02 | 2014-12-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/INT-010-1.pdf
INT-010-2 | INT | INT-010 | Interchange Initiation and Modification for Reliability | 2014-02-06 | Approved | 2014-03-03 | 2014-07-01 | Not Initiated | 2015-01-01 | 2014-11-26 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/INT-010-2.pdf
INT-010-2.1 | INT | INT-010 | Interchange Initiation and Modification for Reliability | 2014-08-20 | Approved | 1899-12-31 | 1900-01-01 | Not Initiated | 2015-01-01 | 2020-12-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/INT-010-2.1.pdf
INT-011-1 | INT | INT-011 | Intra-Balancing Authority Transaction Identification | 2014-02-06 | Approved | 2014-03-03 | 2014-07-01 | Not Initiated | 2015-01-01 | 2014-11-26 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/INT-011-1.pdf
INT-011-1.1 | INT | INT-011 | Intra-Balancing Authority Transaction Identification | 2014-08-20 | Approved | 1899-12-31 | 1900-01-01 | Not Initiated | 2015-01-01 | 2015-10-15 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/INT-011-1.1.pdf
IRO-001-0 | IRO | IRO-001 | Reliability Coordination – Responsibilities and Authorities | 2005-02-08 | Not Approved |  |  | Not Initiated |  | 2007-01-01 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/IRO-001-0.pdf
IRO-001-1 | IRO | IRO-001 | Reliability Coordination — Responsibilities and Authorities | 2006-11-01 | Approved |  |  | Not Initiated | 2006-11-01 | 2008-10-28 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/IRO-001-1.pdf
IRO-001-1.1 | IRO | IRO-001 | Reliability Coordination - Responsibilities and Authorities | 2008-10-29 | Approved | 2009-05-15 | 2009-09-12 | Not Initiated | 2008-10-29 | 2017-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/IRO-001-1_1.pdf
IRO-001-2 | IRO | IRO-001 | Reliability Coordination - Responsibilities and Authorities | 2011-08-04 | Not Approved | 1899-12-31 | 1900-01-01 | Not Initiated |  | 2012-08-16 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/IRO-001-2.pdf
IRO-001-3 | IRO | IRO-001 | Reliability Coordination - Responsibilities and Authorities | 2012-08-16 | Not Approved | 2013-04-17 | 2013-08-15 | Not Initiated |  | 2017-03-31 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/IRO-001-3.pdf
IRO-001-4 | IRO | IRO-001 | Reliability Coordination – Responsibilities | 2014-11-13 | Approved | 2015-03-25 | 2015-07-23 | Not Initiated | 2017-04-01 |  | Effective | http://www.nerc.com/pa/Stand/Reliability Standards/IRO-001-4.pdf
IRO-002-0 | IRO | IRO-002 | Reliability Coordination – Facilities | 2005-02-08 | Not Approved |  |  | Not Initiated |  | 2007-01-01 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/IRO-002-0.pdf
IRO-002-1 | IRO | IRO-002 | Reliability Coordination — Facilities | 2006-11-01 | Approved |  |  | Not Initiated | 2011-07-08 | 2011-09-30 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/IRO-002-1.pdf
IRO-002-2 | IRO | IRO-002 | Reliability Coordination - Facilities | 2008-10-17 | Approved | 1899-12-31 | 1900-01-01 | Not Initiated | 2011-10-01 | 2017-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/IRO-002-2.pdf
IRO-002-3 | IRO | IRO-002 | Reliability Coordination – Analysis Tools | 2011-08-04 | Not Approved | 2013-04-17 | 2013-08-15 | Not Initiated |  | 2016-01-26 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/IRO-002-3.pdf
IRO-002-4 | IRO | IRO-002 | Reliability Coordination — Monitoring and Analysis | 2014-11-13 | Approved | 2015-03-25 | 2015-07-23 | Not Initiated | 2017-04-01 | 2017-12-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/IRO-002-4.pdf
IRO-002-5 | IRO | IRO-002 | Reliability Coordination — Monitoring and Analysis | 2017-02-09 | Approved | 2017-03-20 | 2017-07-18 | Not Initiated | 2018-01-01 | 2019-12-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/IRO-002-5.pdf
IRO-002-6 | IRO | IRO-002 | Reliability Coordination – Monitoring and Analysis | 2019-05-09 | Approved | 2019-04-09 | 2019-08-15 | Not Initiated | 2020-01-01 | 2021-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability%20Standards/IRO-002-6.pdf
IRO-002-7 | IRO | IRO-002 | Reliability Coordination - Monitoring and Analysis | 2019-05-09 | Approved | 2019-06-07 | 2019-10-05 | Not Initiated | 2021-04-01 |  | Effective | https://www.nerc.com/pa/Stand/Project%20201803%20Standards%20Efficiency%20Review%20Require/IRO-002-7_clean_04232019.pdf
IRO-003-0 | IRO | IRO-003 | Reliability Coordination – Wide-Area View | 2005-02-08 | Not Approved |  |  | Not Initiated |  | 2006-08-01 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/IRO-003-0.pdf
IRO-003-1 | IRO | IRO-003 | Reliability Coordination – Wide-Area View | 2006-02-07 | Not Approved |  |  | Not Initiated |  | 2007-01-01 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/IRO-003-1.pdf
IRO-003-2 | IRO | IRO-003 | Reliability Coordination - Wide-Area View | 2006-11-01 | Approved | 1899-12-31 | 1900-01-01 | Not Initiated | 2006-11-01 | 2017-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/IRO-003-2.pdf
IRO-004-0 | IRO | IRO-004 | Reliability Coordination — Operations Planning | 2005-02-08 | Not Approved |  |  | Not Initiated |  | 2006-11-01 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/IRO-004-0.pdf
IRO-004-1 | IRO | IRO-004 | Reliability Coordination — Operations Planning | 2006-02-07 | Approved |  |  | Not Initiated | 2011-07-08 | 2011-09-30 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/IRO-004-1.pdf
IRO-004-2 | IRO | IRO-004 | Reliability Coordination - Operations Planning | 2008-10-17 | Approved | 1899-12-31 | 1900-01-01 | Not Initiated | 2011-10-01 | 2017-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/IRO-004-2.pdf
IRO-005-0 | IRO | IRO-005 | Reliability Coordination — Current Day Operations | 2005-02-08 | Not Approved |  |  | Not Initiated |  | 2005-02-08 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/IRO-005-0.pdf
IRO-005-1 | IRO | IRO-005 | Reliability Coordination — Current Day Operations | 2006-02-07 | Approved |  |  | Not Initiated | 2007-06-18 | 2009-01-21 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/IRO-005-1.pdf
IRO-005-2 | IRO | IRO-005 | Reliability Coordination — Current Day Operations | 2006-11-01 | Approved | 2008-08-11 | 2008-12-09 | Not Initiated | 2008-12-10 | 2009-03-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/IRO-005-2.pdf
IRO-005-2a | IRO | IRO-005 | Reliability Coordination — Current Day Operations | 2009-11-05 | Approved | 2009-12-11 | 2010-04-10 | Not Initiated | 2010-04-11 | 2011-09-30 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/IRO-005-2a.pdf
IRO-005-3 | IRO | IRO-005 | Reliability Coordination — Current Day Operations | 2008-10-17 | Approved |  |  | Not Initiated | 2009-04-01 | 2010-04-10 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/IRO-005-3.pdf
IRO-005-3.1(i)a | IRO | IRO-005 | Reliability Coordination — Current Day Operations | 2014-11-13 | Not Approved | 2015-02-10 | 2015-06-10 | Not Initiated |  | 2014-11-13 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/IRO-005-3.1(i)a.pdf
IRO-005-3.1a | IRO | IRO-005 | Reliability Coordination — Current Day Operations | 2012-03-08 | Approved | 2012-06-11 | 2012-10-09 | Not Initiated | 2012-10-10 | 2017-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/IRO-005-3_1a.pdf
IRO-005-3a | IRO | IRO-005 | Reliability Coordination — Current Day Operations | 2008-10-17 | Approved |  |  | Not Initiated | 2011-10-01 | 2012-10-09 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/IRO-005-3a.pdf
IRO-005-4 | IRO | IRO-005 | Reliability Coordination — Current Day Operations | 2011-08-04 | Not Approved | 2013-04-17 | 2013-08-15 | Not Initiated |  | 2016-01-26 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/IRO-005-4.pdf
IRO-006-0 | IRO | IRO-006 | Reliability Coordination — Transmission Loading Relief | 2005-02-08 | Not Approved |  |  | Not Initiated |  | 2005-08-08 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/IRO-006-0.pdf
IRO-006-1 | IRO | IRO-006 | Reliability Coordination — Transmission Loading Relief | 2005-02-08 | Not Approved |  |  | Not Initiated |  | 2006-09-29 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/IRO-006-1.pdf
IRO-006-2 | IRO | IRO-006 | Reliability Coordination — Transmission Loading Relief | 2006-08-02 | Not Approved |  |  | Not Initiated |  | 2006-09-29 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/IRO-006-2.pdf
IRO-006-3 | IRO | IRO-006 | Reliability Coordination — Transmission Loading Relief | 2006-08-02 | Approved |  |  | Not Initiated | 2007-06-18 | 2009-04-22 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/IRO-006-3.pdf
IRO-006-4 | IRO | IRO-006 | Reliability Coordination — Transmission Loading Relief (TLR) | 2007-10-09 | Approved | 2009-04-15 | 2009-08-13 | Not Initiated | 2009-10-01 | 2010-01-15 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/IRO-006-4.pdf
IRO-006-4.1 | IRO | IRO-006 | Reliability Coordination — Transmission Loading Relief (TLR) | 2009-04-15 | Approved | 2009-09-17 | 2010-01-15 | Not Initiated | 2010-01-16 | 2011-09-30 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/IRO-006-4.1.pdf
IRO-006-5 | IRO | IRO-006 | Reliability Coordination - Transmission Loading Relief (TLR) | 2010-11-04 | Approved | 2011-03-10 | 2011-07-08 | Not Initiated | 2011-10-01 |  | Effective | http://www.nerc.com/pa/Stand/Reliability Standards/IRO-006-5.pdf
IRO-006-EAST-1 | IRO | IRO-006 | Transmission Loading Relief Procedure for the Eastern Interconnection | 2010-11-04 | Approved | 2011-03-10 | 2011-07-08 | Not Initiated | 2011-01-01 | 2016-06-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/IRO-006-EAST-1.pdf
IRO-006-EAST-2 | IRO | IRO-006 | Transmission Loading Relief Procedure for the Eastern Interconnection | 2015-08-13 | Approved | 2015-09-22 | 2016-01-20 | Not Initiated | 2016-07-01 |  | Effective | http://www.nerc.com/pa/Stand/Reliability Standards/IRO-006-EAST-2.pdf
IRO-008-1 | IRO | IRO-008 | Reliability Coordinator Operational Analyses and Real-time Assessments | 2008-10-17 | Approved | 2010-01-26 | 2010-05-26 | Not Initiated | 2011-10-01 | 2017-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/IRO-008-1.pdf
IRO-008-2 | IRO | IRO-008 | Reliability Coordinator Operational Analyses and Real-time Assessments | 2014-11-13 | Approved | 2015-03-25 | 2015-07-23 | Not Initiated | 2017-04-01 | 2024-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/IRO-008-2.pdf
IRO-008-3 | IRO | IRO-008 | Reliability Coordinator Operational Analyses and Real-time Assessments | 2021-05-13 | Approved | 2021-07-07 | 2021-11-04 | Not Initiated | 2024-04-01 |  | Effective | https://www.nerc.com/pa/Stand/Reliability%20Standards/IRO-008-3.pdf
IRO-009-1 | IRO | IRO-009 | Reliability Coordinator Actions to Operate Within IROLs | 2008-10-17 | Approved | 2010-01-26 | 2010-05-26 | Not Initiated | 2011-10-01 | 2016-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/IRO-009-1.pdf
IRO-009-2 | IRO | IRO-009 | Reliability Coordinator Actions to Operate Within IROLs | 2015-08-13 | Approved | 2015-09-22 | 2016-01-20 | Not Initiated | 2016-04-01 |  | Effective | http://www.nerc.com/pa/Stand/Reliability Standards/IRO-009-2.pdf
IRO-010-1 | IRO | IRO-010 | Reliability Coordinator Data Specification and Collection | 2008-10-17 | Approved |  |  | Not Initiated | 2011-05-24 | 2009-08-05 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/IRO-010-1.pdf
IRO-010-1a | IRO | IRO-010 | Reliability Coordinator Data Specification and Collection | 2009-08-05 | Approved | 2010-01-26 | 2010-05-26 | Not Initiated | 2011-10-01 | 2016-12-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/IRO-010-1a.pdf
IRO-010-2 | IRO | IRO-010 | Reliability Coordinator Data Specification and Collection | 2014-11-13 | Approved | 2015-03-25 | 2015-07-23 | Not Initiated | 2017-01-01 | 2021-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/IRO-010-2.pdf
IRO-010-3 | IRO | IRO-010 | Reliability Coordinator Data Specification and Collection | 2020-01-23 | Approved | 2020-02-26 | 2020-06-25 | Not Initiated | 2020-04-01 | 2023-09-30 | Retired | https://www.nerc.com/pa/Stand/Project201707StandardsAlignmentwithRegistration/IRO-010-3%20Project%202017%2007%20Clean_January2020.pdf
IRO-010-4 | IRO | IRO-010 | Reliability Coordinator Data Specification and Collection | 2021-06-11 | Approved | 2021-10-07 | 2022-02-22 | Not Initiated | 2023-10-01 | 2025-09-30 | Effective | https://www.nerc.com/pa/Stand/Project%20201906%20Cold%20Weather%20DL/2019-06_IRO-010-4_Clean_05182021.pdf
IRO-010-5 | IRO | IRO-010 | Reliability Coordinator Data and information Specification and Collection | 2023-08-17 | Approved | 2023-11-02 | 2024-03-01 | Not Initiated | 2025-10-01 |  | Future Effective | https://www.nerc.com/pa/Stand/Reliability%20Standards/IRO-010-5.pdf
IRO-014-1 | IRO | IRO-014 | Procedures, Processes, or Plans to Support Coordination Between Reliability Coordinators | 2006-02-07 | Approved | 1899-12-31 | 1900-01-01 | Not Initiated | 2006-02-07 | 2017-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/IRO-014-1.pdf
IRO-014-2 | IRO | IRO-014 | Coordination Among Reliability Coordinators | 2011-08-04 | Not Approved | 2013-04-17 | 2013-08-15 | Not Initiated |  | 2016-01-26 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/IRO-014-2.pdf
IRO-014-3 | IRO | IRO-014 | Coordination Among Reliability Coordinators | 2014-11-13 | Approved | 2015-03-25 | 2015-07-23 | Not Initiated | 2017-04-01 |  | Effective | http://www.nerc.com/pa/Stand/Reliability Standards/IRO-014-3.pdf
IRO-015-1 | IRO | IRO-015 | Notifications and Information Exchange Between Reliability Coordinators | 2006-02-07 | Approved | 1899-12-31 | 1900-01-01 | Not Initiated | 2006-02-07 | 2017-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/IRO-015-1.pdf
IRO-016-1 | IRO | IRO-016 | Coordination of Real-time Activities Between Reliability Coordinators | 2006-02-07 | Approved | 1899-12-31 | 1900-01-01 | Not Initiated | 2006-02-07 | 2017-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/IRO-016-1.pdf
IRO-017-1 | IRO | IRO-017 | Outage Coordination | 2014-11-13 | Approved | 2015-03-25 | 2015-07-23 | Not Initiated | 2017-04-01 |  | Effective | http://www.nerc.com/pa/Stand/Reliability Standards/IRO-017-1.pdf
IRO-018-1 | IRO | IRO-018 | Reliability Coordinator Real-time Reliability Monitoring and Analysis Capabilities | 2016-02-11 | Approved | 2016-06-01 | 2016-09-29 | Not Initiated | 2018-04-01 | 2018-03-31 | Retired | http://www.nerc.com/pa/Stand/Project 200902 Rela Time Monitotring Analysis Capa/IRO_018_1_20160212_clean.pdf
IRO-018-1(i) | IRO | IRO-018 | Reliability Coordinator Real-time Reliability Monitoring and Analysis Capabilities | 2016-02-11 | Approved | 2016-06-01 | 2016-09-29 | Not Initiated | 2018-04-01 |  | Effective | https://www.nerc.com/pa/Stand/Reliability%20Standards/IRO-018-1(i).pdf
MOD-001-0 | MOD | MOD-001 | Available Transmission System Capability | 2005-02-08 | Not Approved | 1899-12-31 | 1900-01-01 | Not Initiated |  | 2009-11-24 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/MOD-001-0.pdf
MOD-001-1 | MOD | MOD-001 | Available Transmission System Capability | 2008-08-26 | Approved |  |  | Not Initiated | 2010-09-16 | 2010-09-16 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/MOD-001-1.pdf
MOD-001-1a | MOD | MOD-001 | Available Transmission System Capability | 2009-11-05 | Approved | 2009-12-18 | 2010-04-17 | Not Initiated | 2011-07-01 | 2024-02-01 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/MOD-001-1a.pdf
MOD-001-2 | MOD | MOD-001 | Available Transmission System Capability | 2014-02-06 | Not Approved | 2014-02-13 | 2014-06-12 | Not Initiated |  | 2019-05-09 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/MOD-001-2.pdf
MOD-002-0 | MOD | MOD-002 | Review of Transmission Service Provider Total Transfer Capability and Available Transfer Capability Calculations and Results | 2005-02-08 | Not Approved |  |  | Not Initiated |  | 2009-11-24 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/MOD-002-0.pdf
MOD-003-0 | MOD | MOD-003 | Regional Procedure for Input on Total Transfer Capability and Available Transfer Capability Methodologies and Values | 2005-02-08 | Not Approved |  |  | Not Initiated |  | 2009-11-24 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/MOD-003-0.pdf
MOD-004-0 | MOD | MOD-004 | Capacity Benefit Margin | 2005-02-08 | Not Approved | 1899-12-31 | 1900-01-01 | Not Initiated |  | 2009-11-24 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/MOD-004-0.pdf
MOD-004-1 | MOD | MOD-004 | Capacity Benefit Margin | 2008-11-13 | Approved | 2009-04-15 | 2009-08-13 | Not Initiated | 2011-04-01 | 2024-02-01 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/MOD-004-1.pdf
MOD-005-0 | MOD | MOD-005 | Procedure for Verifying Capacity Benefit Margin Values | 2005-02-08 | Not Approved |  |  | Not Initiated |  | 2009-11-24 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/MOD-005-0.pdf
MOD-006-0 | MOD | MOD-006 | Procedures for the Use of Capacity Benefit Margin Values | 2005-02-08 | Approved |  |  | Not Initiated | 2007-06-18 | 2009-05-12 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/MOD-006-0.pdf
MOD-006-0.1 | MOD | MOD-006 | Procedures for the Use of Capacity Benefit Margin Values | 2008-10-29 | Approved | 2009-05-15 | 2009-09-12 | Not Initiated | 2009-09-13 | 2011-03-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/MOD-006-0_1.pdf
MOD-007-0 | MOD | MOD-007 | Documentation of the Use of Capacity Benefit Margin | 2005-02-08 | Approved |  |  | Not Initiated | 2005-02-08 | 2011-03-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/MOD-007-0.pdf
MOD-008-0 | MOD | MOD-008 | TRM Calculation Methodology | 2005-02-08 | Not Approved | 1899-12-31 | 1900-01-01 | Not Initiated |  | 2009-11-24 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/MOD-008-0.pdf
MOD-008-1 | MOD | MOD-008 | Transmission Reliability Margin Calculation Methodology | 2008-08-26 | Approved | 2009-12-18 | 2010-04-17 | Not Initiated | 2011-07-01 | 2024-02-01 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/MOD-008-1.pdf
MOD-009-0 | MOD | MOD-009 | Procedure for Verifying Transmission Reliability Margin Values | 2005-02-08 | Not Approved |  |  | Not Initiated |  | 2009-11-24 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/MOD-009-0.pdf
MOD-010-0 | MOD | MOD-010 | Steady-State Data for Modeling and Simulation of the Interconnected Transmission System | 2005-02-08 | Approved | 1899-12-31 | 1900-01-01 | Not Initiated | 2005-02-08 | 2016-06-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/MOD-010-0.pdf
MOD-011-0 | MOD | MOD-011 | Maintenance and Distribution of Steady-State Data Requirements and Reporting Procedures | 2005-02-08 | Not Approved | 1899-12-31 | 1900-01-01 | Not Initiated | 2005-02-08 | 2016-06-30 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/MOD-011-0.pdf
MOD-012-0 | MOD | MOD-012 | Dynamics Data for Modeling and Simulation of the Interconnected Transmission System | 2005-02-08 | Approved | 1899-12-31 | 1900-01-01 | Not Initiated | 2005-02-08 | 2016-06-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/MOD-012-0.pdf
MOD-013-0 | MOD | MOD-013 | Maintenance and Distribution of Dynamics Data Requirements and Reporting Procedures | 2005-02-08 | Not Approved |  |  | Not Initiated |  | 2006-11-02 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/MOD-013-0.pdf
MOD-013-1 | MOD | MOD-013 | Maintenance and Distribution of Dynamics Data Requirements and Reporting Procedures | 2006-05-02 | Not Approved | 1899-12-31 | 1900-01-01 | Not Initiated | 2006-11-02 | 2016-06-30 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/MOD-013-1.pdf
MOD-014-0 | MOD | MOD-014 | Development of Steady-State System Models | 2005-02-08 | Not Approved | 1899-12-31 | 1900-01-01 | Not Initiated |  | 2016-06-30 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/MOD-014-0.pdf
MOD-015-0 | MOD | MOD-015 | Development of Dynamics System Models | 2005-02-08 | Not Approved |  |  | Not Initiated |  | 2016-06-30 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/MOD-015-0.pdf
MOD-015-0.1 | MOD | MOD-015 | Development of Dynamics System Models | 2008-10-29 | Not Approved |  |  | Not Initiated |  | 2016-06-30 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/MOD-015-0_1.pdf
MOD-016-0 | MOD | MOD-016 | Documentation of Data Reporting Requirements for Actual and Forecast Demands, Net Energy for Load, and Controllable Demand-Side Management | 2005-02-08 | Not Approved |  |  | Not Initiated |  | 2006-11-02 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/MOD-016-0.pdf
MOD-016-1 | MOD | MOD-016 | Documentation of Data Reporting Requirements for Actual and Forecast Demands, Net Energy for Load, and Controllable Demand-Side Management | 2006-05-02 | Approved |  |  | Not Initiated | 2007-06-18 | 2009-05-12 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/MOD-016-1.pdf
MOD-016-1.1 | MOD | MOD-016 | Documentation of Data Reporting Requirements for Actual and Forecast Demands, Net Energy for Load, and Controllable Demand-Side Management | 2008-10-29 | Approved | 2009-05-15 | 2009-09-12 | Not Initiated | 2009-09-13 | 2016-06-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/MOD-016-1_1.pdf
MOD-017-0 | MOD | MOD-017 | Aggregated Actual and Forecast Demands and Net Energy for Load | 2005-02-08 | Approved |  |  | Not Initiated | 2007-06-18 | 2009-05-12 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/MOD-017-0.pdf
MOD-017-0.1 | MOD | MOD-017 | Aggregated Actual and Forecast Demands and Net Energy for Load | 2008-10-29 | Approved | 2009-05-15 | 2009-09-12 | Not Initiated | 2009-09-13 | 2016-06-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/MOD-017-0_1.pdf
MOD-018-0 | MOD | MOD-018 | Treatment of Nonmember Demand Data and How Uncertainties are Addressed in the Forecasts of Demand and Net Energy for Load | 2005-02-08 | Approved | 1899-12-31 | 1900-01-01 | Not Initiated | 2005-02-08 | 2016-06-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/MOD-018-0.pdf
MOD-019-0 | MOD | MOD-019 | Reporting of Interruptible Demands and Direct Control Load Management | 2005-02-08 | Approved |  |  | Not Initiated | 2007-06-18 | 2009-05-12 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/MOD-019-0.pdf
MOD-019-0.1 | MOD | MOD-019 | Reporting of Interruptible Demands and Direct Control Load Management | 2008-10-29 | Approved | 2009-05-15 | 2009-09-12 | Not Initiated | 2009-09-13 | 2016-06-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/MOD-019-0_1.pdf
MOD-020-0 | MOD | MOD-020 | Providing Interruptible Demands and Direct Control Load Management Data to System Operators and Reliability Coordinators | 2005-02-08 | Approved | 1899-12-31 | 1900-01-01 | Not Initiated | 2005-02-08 | 2020-12-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/MOD-020-0.pdf
MOD-021-0 | MOD | MOD-021 | Documentation of the Accounting Methodology for the Effects of Controllable Demand-Side Management in Demand and Energy Forecasts | 2005-02-08 | Approved |  |  | Not Initiated | 2005-02-08 | 2010-01-15 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/MOD-021-0.pdf
MOD-021-0.1 | MOD | MOD-021 | Documentation of the Accounting Methodology for the Effects of Controllable Demand-Side Management in Demand and Energy Forecasts | 2009-04-15 | Approved | 2009-09-17 | 2010-01-15 | Not Initiated | 2010-01-16 | 2010-09-30 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/MOD-021-0.1.pdf
MOD-021-1 | MOD | MOD-021 | Documentation of the Accounting Methodology for the Effects of Demand-Side Management in Demand and Energy Forecasts | 2010-08-05 | Approved | 1899-12-31 | 1900-01-01 | Not Initiated | 2010-10-01 | 2016-06-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/MOD-021-1.pdf
MOD-024-1 | MOD | MOD-024 | Verification of Generator Gross and Net Real Power Capability | 2006-02-07 | Not Approved | 1899-12-31 | 1900-01-01 | Not Initiated | 2006-02-07 | 2016-06-30 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/MOD-024-1.pdf
MOD-025-1 | MOD | MOD-025 | Verification of Generator Gross and Net Reactive Power Capability | 2006-02-07 | Not Approved | 1899-12-31 | 1900-01-01 | Not Initiated | 2006-02-07 | 2016-06-30 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/MOD-025-1.pdf
MOD-025-2 | MOD | MOD-025 | Verification and Data Reporting of Generator Real and Reactive Power Capability and Synchronous Condenser Reactive Power Capability | 2013-02-07 | Approved | 2013-06-03 | 2013-10-01 | Not Initiated | 2016-07-01 |  | Effective | http://www.nerc.com/pa/Stand/Reliability Standards/MOD-025-2.pdf
MOD-026-1 | MOD | MOD-026 | Verification of Models and Data for Generator Excitation Control System or Plant Volt/Var Control Functions | 2013-02-07 | Approved | 2013-06-03 | 2013-10-01 | Not Initiated | 2014-07-01 |  | Effective | http://www.nerc.com/pa/Stand/Reliability Standards/MOD-026-1.pdf
MOD-027-1 | MOD | MOD-027 | Verification of Models and Data for Turbine/Governor and Load Control or Active Power/Frequency Control Functions | 2013-02-07 | Approved | 2013-06-03 | 2013-10-01 | Not Initiated | 2014-07-01 |  | Effective | http://www.nerc.com/pa/Stand/Reliability Standards/MOD-027-1.pdf
MOD-028-1 | MOD | MOD-028 | Area Interchange Methodology | 2008-08-26 | Approved | 2009-12-18 | 2010-04-17 | Not Initiated | 2011-07-01 | 2013-09-30 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/MOD-028-1.pdf
MOD-028-2 | MOD | MOD-028 | Area Interchange Methodology | 2012-02-09 | Approved | 2012-09-06 | 2013-01-04 | Not Initiated | 2013-10-01 | 2024-02-01 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/MOD-028-2.pdf
MOD-029-1 | MOD | MOD-029 | Rated System Path Methodology | 2008-08-26 | Approved |  |  | Not Initiated | 2010-09-17 | 2010-09-16 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/MOD-029-1.pdf
MOD-029-1a | MOD | MOD-029 | Rated System Path Methodology | 2009-11-05 | Approved | 2009-12-18 | 2010-04-17 | Not Initiated | 2010-04-18 | 2017-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/MOD-029-1a.pdf
MOD-029-2a | MOD | MOD-029 | Rated System Path Methodology | 2014-11-13 | Approved | 2015-02-10 | 2015-06-10 | Not Initiated | 2017-04-01 | 2024-02-01 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/MOD-029-2a.pdf
MOD-030-1 | MOD | MOD-030 | Flowgate Methodology | 2008-08-26 | Not Approved |  |  | Not Initiated |  | 2009-11-24 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/MOD-030-1.pdf
MOD-030-2 | MOD | MOD-030 | Flowgate Methodology | 2009-02-10 | Approved | 2009-12-18 | 2010-04-17 | Not Initiated | 2011-07-01 | 2017-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/MOD-030-2.pdf
MOD-030-3 | MOD | MOD-030 | Flowgate Methodology | 2014-11-13 | Approved | 2015-02-10 | 2015-06-10 | Not Initiated | 2017-04-01 | 2024-02-01 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/MOD-030-3.pdf
MOD-031-1 | MOD | MOD-031 | Demand and Energy Data | 2014-05-07 | Approved | 2014-05-16 | 2014-09-13 | Not Initiated | 2016-07-01 | 2016-09-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/MOD-031-1.pdf
MOD-031-2 | MOD | MOD-031 | Demand and Energy Data | 2015-11-05 | Approved | 2015-11-19 | 2016-03-18 | Not Initiated | 2016-10-01 | 2021-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/MOD-031-2.pdf
MOD-031-3 | MOD | MOD-031 | Demand and Energy Data | 2020-01-23 | Approved | 2020-02-26 | 2020-06-25 | Not Initiated | 2021-04-01 |  | Effective | https://www.nerc.com/pa/Stand/Project201707StandardsAlignmentwithRegistration/MOD-031-3%20Project%202017%2007%20Clean_January2020.pdf
MOD-032-1 | MOD | MOD-032 | Data for Power System Modeling and Analysis | 2014-02-06 | Approved | 2014-02-28 | 2014-06-28 | Not Initiated | 2015-07-01 |  | Effective | http://www.nerc.com/pa/Stand/Reliability Standards/MOD-032-1.pdf
MOD-033-1 | MOD | MOD-033 | Steady‐State and Dynamic System Model Validation | 2014-02-06 | Approved | 2014-02-28 | 2014-06-28 | Not Initiated | 2017-07-01 | 2020-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/MOD-033-1.pdf
MOD-033-2 | MOD | MOD-033 | Steady-State and Dynamic System Model Validation | 2020-01-23 | Approved | 2020-02-26 | 2020-06-25 | Not Initiated | 2020-04-01 |  | Effective | https://www.nerc.com/pa/Stand/Project201707StandardsAlignmentwithRegistration/MOD-033-2%20Project%202017%2007%20Clean_January2020.pdf
NUC-001-1 | NUC | NUC-001 | Nuclear Plant Interface Coordination | 2007-05-02 | Approved |  |  | Not Initiated | 2010-01-22 | 2010-03-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/NUC-001-1.pdf
NUC-001-2 | NUC | NUC-001 | Nuclear Plant Interface Coordination | 2009-08-05 | Approved | 2009-09-17 | 2010-01-15 | Not Initiated | 2010-04-01 | 2013-03-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/NUC-001-2.pdf
NUC-001-2.1 | NUC | NUC-001 | Nuclear Plant Interface Coordination | 2012-04-11 | Approved | 1899-12-31 | 1900-01-01 | Not Initiated | 2013-04-01 | 2016-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/NUC-001-2.1.pdf
NUC-001-2.1(i) | NUC | NUC-001 | Nuclear Plant Interface Coordination | 2014-11-13 | Not Approved | 2015-02-10 | 2015-06-10 | Not Initiated |  | 2014-11-13 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/NUC-001-2.1(i).pdf
NUC-001-3 | NUC | NUC-001 | Nuclear Plant Interface Coordination | 2014-08-14 | Approved | 2014-09-25 | 2015-01-13 | Not Initiated | 2016-04-01 | 2021-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/NUC-001-3.pdf
NUC-001-4 | NUC | NUC-001 | Nuclear Plant Interface Coordination | 2020-01-23 | Approved | 2020-02-21 | 2020-06-25 | Not Initiated | 2021-04-01 |  | Effective | https://www.nerc.com/pa/Stand/Project201707StandardsAlignmentwithRegistration/NUC-001-4%20Project%202017%2007%20Clean_January2020.pdf
PER-001-0 | PER | PER-001 | Operating Personnel Responsibility and Authority | 2005-02-08 | Approved |  |  | Not Initiated | 2005-02-08 | 2010-01-15 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/PER-001-0.pdf
PER-001-0.1 | PER | PER-001 | Operating Personnel Responsibility and Authority | 2009-04-15 | Approved | 2009-09-17 | 2010-01-15 | Not Initiated | 2010-01-16 | 2012-10-09 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/PER-001-0.1.pdf
PER-001-0.2 | PER | PER-001 | Operating Personnel Responsibility and Authority | 2012-03-08 | Approved | 2012-06-11 | 2012-10-09 | Not Initiated | 2012-10-10 | 2017-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/PER-001-0_2.pdf
PER-002-0 | PER | PER-002 | Operating Personnel Training | 2005-02-08 | Approved |  |  | Not Initiated | 2005-02-08 | 2013-03-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/PER-002-0.pdf
PER-003-0 | PER | PER-003 | Operating Personnel Credentials | 2005-02-08 | Approved |  |  | Not Initiated | 2005-02-08 | 2012-09-30 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/PER-003-0.pdf
PER-003-1 | PER | PER-003 | Operating Personnel Credentials | 2011-02-17 | Approved | 2011-06-14 | 2011-10-12 | Not Initiated | 2012-10-01 | 2019-06-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/PER-003-1.pdf
PER-003-2 | PER | PER-003 | Operating Personnel Credentials | 2018-05-10 | Approved | 2018-07-26 | 2018-11-24 | Not Initiated | 2019-07-01 |  | Effective | https://www.nerc.com/pa/Stand/Reliability%20Standards/PER-003-2.pdf
PER-004-0 | PER | PER-004 | Reliability Coordination — Staffing | 2005-02-08 | Not Approved |  |  | Not Initiated |  | 2007-01-01 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/PER-004-0.pdf
PER-004-1 | PER | PER-004 | Reliability Coordination — Staffing | 2006-11-01 | Approved |  |  | Not Initiated | 2006-11-01 | 2013-03-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/PER-004-1.pdf
PER-004-2 | PER | PER-004 | Reliability Coordination - Staffing | 2009-02-10 | Approved | 2009-11-04 | 2010-03-04 | Not Initiated | 2011-04-01 | 2019-06-23 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/PER-004-2.pdf
PER-005-1 | PER | PER-005 | System Personnel Training | 2009-02-10 | Approved | 2009-11-04 | 2010-03-04 | Not Initiated | 2011-04-01 | 2016-09-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/PER-005-1.pdf
PER-005-2 | PER | PER-005 | Operations Personnel Training | 2014-02-06 | Approved | 2014-03-12 | 2014-07-10 | Not Initiated | 2016-10-01 |  | Effective | http://www.nerc.com/pa/Stand/Reliability Standards/PER-005-2.pdf
PER-006-1 | PER | PER-006 | Specific Training for Personnel | 2016-08-11 | Approved | 2016-09-15 | 2017-01-12 | Not Initiated | 2021-04-01 |  | Effective | http://www.nerc.com/pa/Stand/Reliability Standards/PER-006-1.pdf
PRC-001-0 | PRC | PRC-001 | System Protection Coordination | 2005-02-08 | Not Approved |  |  | Not Initiated |  | 2007-01-01 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/PRC-001-0.pdf
PRC-001-1 | PRC | PRC-001 | System Protection Coordination | 2006-11-01 | Approved |  |  | Not Initiated | 2006-11-01 | 2013-03-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/PRC-001-1.pdf
PRC-001-1.1 | PRC | PRC-001 | System Protection Coordination | 2012-04-11 | Approved |  |  | Not Initiated | 2013-04-01 | 2015-07-15 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-001-1.1.pdf
PRC-001-1.1(i) | PRC | PRC-001 | System Protection Coordination | 2014-11-13 | Approved | 2015-02-10 | 2015-06-10 | Not Initiated | 2017-04-01 | 2015-05-28 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-001-1.1(i).pdf
PRC-001-1.1(ii) | PRC | PRC-001 | System Protection Coordination | 2015-02-12 | Approved | 2015-03-18 | 2015-07-16 | Not Initiated | 2015-07-16 | 2020-09-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-001-1.1(ii).pdf
PRC-001-2 | PRC | PRC-001 | System Protection Coordination | 2012-05-09 | Not Approved | 2013-04-17 | 2013-08-15 | Not Initiated |  | 2016-01-26 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-001-2.pdf
PRC-002-0 | PRC | PRC-002 | Define and Document Disturbance Monitoring Equipment Requirements | 2005-02-08 | Not Approved |  |  | Not Initiated |  | 2007-01-01 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/PRC-002-0.pdf
PRC-002-1 | PRC | PRC-002 | Define Regional Disturbance Monitoring and Reporting Requirements | 2006-08-02 | Not Approved |  |  | Not Initiated | 2007-05-02 | 2011-07-07 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/PRC-002-1.pdf
PRC-002-2 | PRC | PRC-002 | Disturbance Monitoring and Reporting Requirements | 2014-11-13 | Approved | 2014-12-19 | 2015-04-19 | Not Initiated | 2016-07-01 | 2024-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-002-2.pdf
PRC-002-3 | PRC | PRC-002 | Disturbance Monitoring and Reporting Requirements | 2021-05-13 | Approved | 2021-07-07 | 2021-11-04 | Not Initiated | 2022-03-14 | 2024-06-30 | Effective | https://www.nerc.com/pa/Stand/Reliability%20Standards/PRC-002-3.pdf
PRC-002-4 | PRC | PRC-002 | Disturbance Monitoring and Reporting Requirements | 2023-02-16 | Approved | 2023-12-13 | 2024-04-11 | Not Initiated | 2024-07-01 |  | Future Effective | https://www.nerc.com/pa/Stand/Reliability%20Standards/PRC-002-4.pdfhttps://www.nerc.com/pa/Stand/Reliability Standards/PRC-002-4.pdf
PRC-002-NPCC-01 | PRC | PRC-002 | Disturbance Monitoring | 2010-11-04 | Approved | 2011-06-14 | 2011-10-12 | Not Initiated | 2013-10-20 | 2016-08-16 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-002-NPCC-01.pdf
PRC-003-0 | PRC | PRC-003 | Regional Procedure for Transmission Protection System Misoperations | 2005-02-08 | Not Approved |  |  | Not Initiated |  | 2006-05-01 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/PRC-003-0.pdf
PRC-003-1 | PRC | PRC-003 | Regional Procedure for Analysis of Misoperations of Transmission and Generation Protection Systems | 2006-02-07 | Not Approved |  |  | Not Initiated | 2006-02-07 | 2011-07-07 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/PRC-003-1.pdf
PRC-004-0 | PRC | PRC-004 | Analysis and Reporting of Transmission Protection System Misoperations | 2005-02-08 | Not Approved |  |  | Not Initiated |  | 2006-08-01 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/PRC-004-0.pdf
PRC-004-1 | PRC | PRC-004 | Analysis and Mitigation of Transmission and Generation Protection System Misoperations | 2006-02-07 | Approved |  |  | Not Initiated | 2006-02-07 | 2011-10-12 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/PRC-004-1.pdf
PRC-004-1a | PRC | PRC-004 | Analysis and Mitigation of Transmission and Generation Protection System Misoperations | 2011-02-17 | Approved | 2011-06-14 | 2011-10-12 | Not Initiated | 2011-10-13 | 2012-12-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/PRC-004-1a.pdf
PRC-004-2 | PRC | PRC-004 | Analysis and Mitigation of Transmission and Generation Protection System Misoperations | 2010-08-05 | Approved | 2011-03-10 | 2011-07-08 | Not Initiated | 2011-09-27 | 2011-09-25 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-004-2.pdf
PRC-004-2.1(i)a | PRC | PRC-004 | Analysis and Mitigation of Transmission and Generation Protection System Misoperations | 2014-11-13 | Approved | 2015-02-12 | 2015-06-14 | Not Initiated | 2015-06-14 | 2016-06-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-004-2_1(i)a.pdf
PRC-004-2.1a | PRC | PRC-004 | Analysis and Mitigation of Transmission and Generation Protection System Misoperations | 2012-02-09 | Approved | 2012-09-06 | 2013-01-04 | Not Initiated | 2013-11-25 | 2015-06-13 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-004-2.1a.pdf
PRC-004-2a | PRC | PRC-004 | Analysis and Mitigation of Transmission and Generation Protection System Misoperations | 2011-02-17 | Approved | 2011-03-10 | 2011-07-08 | Not Initiated | 2013-01-01 | 2013-11-24 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/PRC-004-2a.pdf
PRC-004-3 | PRC | PRC-004 | Protection System Misoperation Identification and Correction | 2014-08-14 | Approved | 2014-09-25 | 2015-01-13 | Not Initiated | 2016-07-01 | 2016-06-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-004-3.pdf
PRC-004-3(i) | PRC | PRC-004 | Protection System Misoperation Identification and Correction | 2016-06-22 | Approved |  |  | Not Initiated | 2016-07-01 | 2016-06-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-004-3(i).pdf
PRC-004-4 | PRC | PRC-004 | Protection System Misoperation Identification and Correction | 2014-11-13 | Approved | 2015-02-12 | 2015-06-14 | Not Initiated | 2016-07-01 | 2016-06-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-004-4.pdf
PRC-004-4(i) | PRC | PRC-004 | Protection System Misoperation Identification and Correction | 2015-06-22 | Approved | 1899-12-31 | 1900-01-01 | Not Initiated | 2016-07-01 | 2017-04-01 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-004-4(i).pdf
PRC-004-5 | PRC | PRC-004 | Protection System Misoperation Identification and Correction | 2015-05-07 | Approved | 2015-06-16 | 2015-10-13 | Not Initiated | 2017-04-02 | 2017-04-01 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-004-5.pdf
PRC-004-5(i) | PRC | PRC-004 | Protection System Misoperation Identification and Correction | 2015-06-22 | Approved | 1899-12-31 | 1900-01-01 | Not Initiated | 2017-04-02 | 2021-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-004-5(i).pdf
PRC-004-6 | PRC | PRC-004 | Protection System Misoperation Identification and Correction | 2019-05-09 | Approved | 2019-05-09 | 2020-06-25 | Not Initiated | 2021-04-20 |  | Effective | https://www.nerc.com/pa/Stand/Reliability%20Standards/PRC-004-6.pdf
PRC-005-0 | PRC | PRC-005 | Transmission Protection System Maintenance and Testing | 2005-02-08 | Not Approved |  |  | Not Initiated |  | 2006-05-01 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/PRC-005-0.pdf
PRC-005-1 | PRC | PRC-005 | Transmission and Generation Protection System Maintenance and Testing | 2006-02-07 | Approved |  |  | Not Initiated | 2006-02-07 | 2011-10-12 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/PRC-005-1.pdf
PRC-005-1.1b | PRC | PRC-005 | Transmission and Generation Protection System Maintenance and Testing | 2012-05-09 | Approved | 2012-09-06 | 2013-01-04 | Not Initiated | 2013-11-25 | 2027-03-31 | Effective | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-005-1.1b.pdf
PRC-005-1a | PRC | PRC-005 | Transmission and Generation Protection System Maintenance and Testing | 2011-02-17 | Approved | 2011-06-14 | 2011-10-12 | Not Initiated | 2011-10-13 | 2012-08-15 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/PRC-005-1a.pdf
PRC-005-1b | PRC | PRC-005 | Transmission and Generation Protection System Maintenance and Testing | 2009-11-05 | Approved | 2012-04-17 | 2012-08-15 | Not Initiated | 2012-08-16 | 2013-11-24 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/PRC-005-1b.pdf
PRC-005-2 | PRC | PRC-005 | Protection System Maintenance | 2012-11-07 | Approved | 2013-03-01 | 2013-05-29 | Not Initiated | 2015-04-01 | 2015-06-13 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-005-2.pdf
PRC-005-2(i) | PRC | PRC-005 | Protection System Maintenance | 2014-11-13 | Approved | 2015-02-12 | 2015-06-14 | Not Initiated | 2015-06-14 | 2016-03-17 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-005-2(i).pdf
PRC-005-2(ii) | PRC | PRC-005 | Protection System Maintenance | 2014-11-13 | Approved | 2015-02-10 | 2015-06-10 | Not Initiated | 2017-04-01 | 2015-12-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-005-2(ii).pdf
PRC-005-3 | PRC | PRC-005 | Protection System and Automatic Reclosing Maintenance | 2012-11-07 | Not Approved | 2014-02-18 | 2014-06-19 | Not Initiated |  | 2015-12-31 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-005-3.pdf
PRC-005-3(i) | PRC | PRC-005 | Protection System and Automatic Reclosing Maintenance | 2014-11-13 | Not Approved | 2015-02-12 | 2015-06-14 | Not Initiated |  | 2015-12-31 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-005-3(i).pdf
PRC-005-3(ii) | PRC | PRC-005 | Protection System and Automatic Reclosing Maintenance | 2014-11-13 | Approved | 2015-02-10 | 2015-06-10 | Not Initiated | 2017-04-01 | 2015-12-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-005-3(ii).pdf
PRC-005-4 | PRC | PRC-005 | Protection System , Automatic Reclosing and Sudden Pressure Relaying Maintenance | 2014-11-13 | Not Approved | 2015-01-06 | 2015-05-06 | Not Initiated |  | 2015-12-31 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-005-4.pdf
PRC-005-5 | PRC | PRC-005 | Protection System , Automatic Reclosing and Sudden Pressure Relaying Maintenance | 2015-05-07 | Approved |  |  | Not Initiated | 2016-01-01 | 2015-12-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-005-5.pdf
PRC-005-6 | PRC | PRC-005 | Protection System , Automatic Reclosing and Sudden Pressure Relaying Maintenance | 2015-11-05 | Approved | 2015-11-20 | 2016-03-18 | Not Initiated | 2016-03-18 |  | Effective | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-005-6.pdf
PRC-006-0 | PRC | PRC-006 | Development and Documentation of Regional Reliability Organizations’ Underfrequency Load Shedding Programs | 2005-02-08 | Approved |  |  | Not Initiated | 2005-02-08 | 2011-07-07 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/PRC-006-0.pdf
PRC-006-1 | PRC | PRC-006 | Automatic Underfrequency Load Shedding | 2010-11-04 | Approved | 2011-04-20 | 2011-08-18 | Not Initiated | 2013-10-01 | 2015-12-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-006-1.pdf
PRC-006-1(i) | PRC | PRC-006 | Automatic Underfrequency Load Shedding | 2014-11-13 | Approved | 2015-02-10 | 2015-06-10 | Not Initiated | 2015-06-10 | 2015-10-31 | Retired
PRC-006-2 | PRC | PRC-006 | Automatic Underfrequency Load Shedding | 2014-11-13 | Approved | 2014-12-19 | 2015-04-19 | Not Initiated | 2016-01-01 | 2017-09-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-006-2.pdf
PRC-006-3 | PRC | PRC-006 | Automatic Underfrequency Load Shedding | 2017-08-10 | Approved | 1899-12-31 | 1900-01-01 | Not Initiated | 2017-10-01 | 2021-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-006-3.pdf
PRC-006-4 | PRC | PRC-006 | Automatic Underfrequency Load Shedding | 2020-02-06 | Approved | 2020-02-26 | 2020-06-25 | Not Initiated | 2021-04-01 | 2021-03-31 | Retired | https://www.nerc.com/pa/Stand/Project201707StandardsAlignmentwithRegistration/PRC-006-4%20Project%202017%2007%20Clean_January2020.pdf
PRC-006-5 | PRC | PRC-006 | Automatic Underfrequency Load Shedding | 2020-08-20 | Approved |  |  | Not Initiated | 2021-04-01 |  | Effective | https://www.nerc.com/pa/Stand/Reliability%20Standards/PRC-006-5.pdf
PRC-006-NPCC-1 | PRC | PRC-006 | Automatic Underfrequency Load Shedding | 2012-02-09 | Approved | 2012-02-13 | 2012-06-12 | Not Initiated | 2017-04-01 | 2020-06-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-006-NPCC-1.pdf
PRC-006-NPCC-2 | PRC | PRC-006 | Automatic Underfrequency Load Shedding | 2019-11-05 | Approved | 2020-01-24 | 2020-05-03 | Not Initiated | 2020-07-01 |  | Effective | https://www.nerc.com/pa/Stand/Reliability%20Standards/PRC-006-NPCC-2.pdf
PRC-007-0 | PRC | PRC-007 | Assuring Consistency of Entity Underfrequency Load Shedding Programs with Regional Reliability Organization’s Underfrequency Load Shedding Program Requirements | 2005-02-08 | Approved |  |  | Not Initiated | 2005-02-08 | 2013-09-30 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/PRC-007-0.pdf
PRC-008-0 | PRC | PRC-008 | Implementation and Documentation of Underfrequency Load Shedding Equipment Maintenance Program | 2005-02-08 | Approved | 1899-12-31 | 1900-01-01 | Not Initiated | 2005-02-08 | 2027-03-31 | Effective | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-008-0.pdf
PRC-009-0 | PRC | PRC-009 | Analysis and Documentation of Underfrequency Load Shedding Performance Following an Underfrequency Event | 2005-02-08 | Approved |  |  | Not Initiated | 2005-02-08 | 2013-09-30 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/PRC-009-0.pdf
PRC-010-0 | PRC | PRC-010 | Technical Assessment of the Design and Effectiveness of Undervoltage Load Shedding Program | 2005-02-08 | Approved | 1899-12-31 | 1900-01-01 | Not Initiated | 2005-02-08 | 2017-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-010-0.pdf
PRC-010-1 | PRC | PRC-010 | Undervoltage Load Shedding | 2014-11-13 | Approved | 2015-02-12 | 2015-06-14 | Not Initiated | 2017-04-01 | 2017-04-01 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-010-1.pdf
PRC-010-2 | PRC | PRC-010 | Undervoltage Load Shedding | 2015-05-07 | Approved | 2015-06-16 | 2015-10-13 | Not Initiated | 2017-04-02 |  | Effective | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-010-2.pdf
PRC-011-0 | PRC | PRC-011 | Undervoltage Load Shedding System Maintenance and Testing | 2005-02-08 | Approved | 1899-12-31 | 1900-01-01 | Not Initiated | 2005-02-08 | 2027-03-31 | Effective | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-011-0.pdf
PRC-012-0 | PRC | PRC-012 | Special Protection System Review Procedure | 2005-02-08 | Not Approved | 1899-12-31 | 1900-01-01 | Not Initiated | 2005-02-08 | 2011-07-07 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-012-0.pdf
PRC-012-1 | PRC | PRC-012 | Remedial Action Scheme Review Procedure | 2014-11-13 | Not Approved | 2015-02-10 | 2015-06-10 | Not Initiated |  | 2020-12-31 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-012-1.pdf
PRC-012-2 | PRC | PRC-012 | Remedial Action Schemes | 2016-05-05 | Approved | 2016-08-15 | 2016-12-13 | Not Initiated | 2021-01-01 |  | Effective | http://www.nerc.com/pa/Stand/Prjct201005_3RmdialActnSchmsPhase3ofPrtctnSystmsDL/PRC-012-2_AHM_reviewed_04292015.pdf
PRC-013-0 | PRC | PRC-013 | Special Protection System Database. | 2005-02-08 | Not Approved |  |  | Not Initiated | 2005-02-08 | 2017-03-31 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/PRC-013-0.pdf
PRC-013-1 | PRC | PRC-013 | Remedial Action Scheme Database | 2014-11-13 | Not Approved | 2015-02-10 | 2015-06-10 | Not Initiated |  | 2020-12-31 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-013-1.pdf
PRC-014-0 | PRC | PRC-014 | Special Protection System Assessment | 2005-02-08 | Not Approved |  |  | Not Initiated | 2005-02-08 | 2017-03-31 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/PRC-014-0.pdf
PRC-014-1 | PRC | PRC-014 | Remedial Action Scheme Assessment | 2014-11-13 | Not Approved | 2015-02-10 | 2015-06-10 | Not Initiated |  | 2020-12-31 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-014-1.pdf
PRC-015-0 | PRC | PRC-015 | Special Protection System Data and Documentation | 2005-02-08 | Approved | 1899-12-31 | 1900-01-01 | Not Initiated | 2005-02-08 | 2017-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-015-0.pdf
PRC-015-1 | PRC | PRC-015 | Remedial Action Scheme Data and Documentation | 2014-11-13 | Approved | 2015-02-10 | 2015-06-10 | Not Initiated | 2017-04-01 | 2020-12-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-015-1.pdf
PRC-016-0 | PRC | PRC-016 | Special Protection System Misoperations | 2005-02-08 | Approved |  |  | Not Initiated | 2007-06-18 | 2009-05-12 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/PRC-016-0.pdf
PRC-016-0.1 | PRC | PRC-016 | Special Protection System Misoperations | 2008-10-29 | Approved | 2009-05-15 | 2009-09-12 | Not Initiated | 2009-09-13 | 2017-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-016-0_1.pdf
PRC-016-1 | PRC | PRC-016 | Remedial Action Scheme Misoperations | 2014-11-13 | Approved | 2015-02-10 | 2015-06-10 | Not Initiated | 2017-04-01 | 2020-12-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-016-1.pdf
PRC-017-0 | PRC | PRC-017 | Special Protection System Maintenance and Testing | 2005-02-08 | Approved | 1899-12-31 | 1900-01-01 | Not Initiated | 2005-02-08 | 2017-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-017-0.pdf
PRC-017-1 | PRC | PRC-017 | Remedial Action Scheme Maintenance and Testing | 2014-11-13 | Approved | 2015-02-10 | 2015-06-10 | Not Initiated | 2017-04-01 | 2027-03-31 | Effective | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-017-1.pdf
PRC-018-1 | PRC | PRC-018 | Disturbance Monitoring Equipment Installation and Data Reporting | 2006-08-02 | Approved | 1899-12-31 | 1900-01-01 | Not Initiated | 2007-02-02 | 2022-06-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-018-1.pdf
PRC-019-1 | PRC | PRC-019 | Coordination of Generating Unit or Plant Capabilities, Voltage Regulating Controls, and Protection | 2013-02-07 | Approved | 2013-06-03 | 2013-10-01 | Not Initiated | 2016-07-01 | 2016-06-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-019-1.pdf
PRC-019-2 | PRC | PRC-019 | Coordination of Generating Unit or Plant Capabilities, Voltage Regulating Controls, and Protection | 2015-02-12 | Approved | 2015-03-18 | 2015-07-16 | Not Initiated | 2016-07-01 |  | Effective | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-019-2.pdf
PRC-020-1 | PRC | PRC-020 | Under-Voltage Load Shedding Program Database | 2006-02-07 | Not Approved |  |  | Not Initiated | 2006-02-07 | 2017-03-31 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/PRC-020-1.pdf
PRC-020-2 | PRC | PRC-020 | Under-Voltage Load Shedding Program Database | 2014-11-13 | Not Approved | 2015-02-10 | 2015-06-10 | Not Initiated |  | 2014-11-13 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-020-2.pdf
PRC-021-1 | PRC | PRC-021 | Under-Voltage Load Shedding Program Data | 2006-02-07 | Approved | 1899-12-31 | 1900-01-01 | Not Initiated | 2006-02-07 | 2017-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-021-1.pdf
PRC-021-2 | PRC | PRC-021 | Under-Voltage Load Shedding Program Data | 2014-11-13 | Not Approved | 2015-02-10 | 2015-06-10 | Not Initiated |  | 2014-11-13 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-021-2.pdf
PRC-022-1 | PRC | PRC-022 | Under-Voltage Load Shedding Program Performance | 2006-02-07 | Approved | 1899-12-31 | 1900-01-01 | Not Initiated | 2006-02-07 | 2017-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-022-1.pdf
PRC-023-1 | PRC | PRC-023 | Transmission Relay Loadability | 2008-02-12 | Approved | 2008-08-11 | 2008-12-09 | Not Initiated | 2009-01-01 | 2013-12-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/PRC-023-1.pdf
PRC-023-2 | PRC | PRC-023 | Transmission Relay Loadability | 2011-03-10 | Approved | 2011-04-20 | 2011-08-18 | Not Initiated | 2012-07-01 | 2014-09-30 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/PRC-023-2.pdf
PRC-023-2(i) | PRC | PRC-023 | Transmission Relay Loadability | 2014-11-13 | Not Approved | 2015-02-10 | 2015-06-10 | Not Initiated |  |  | Never Came Into Effect in Ontario
PRC-023-3 | PRC | PRC-023 | Transmission Relay Loadability | 2013-11-07 | Approved | 2013-12-17 | 2014-04-18 | Not Initiated | 2014-10-01 | 2017-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-023-3.pdf
PRC-023-4 | PRC | PRC-023 | Transmission Relay Loadability | 2014-11-13 | Approved | 2015-02-10 | 2015-06-10 | Not Initiated | 2017-04-01 | 2024-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-023-4.pdf
PRC-023-5 | PRC | PRC-023 | Transmission Relay Loadability | 2021-05-13 | Approved | 2021-07-07 | 2021-11-04 | Not Initiated | 2024-04-01 | 2024-03-31 | Retired | https://www.nerc.com/pa/Stand/Reliability Standards/PRC-023-5.pdf
PRC-023-6 | PRC | PRC-023 | Transmission Relay Loadability | 2023-02-16 | Approved | 2023-11-08 | 2024-03-07 | Not Initiated | 2024-04-01 |  | Effective | https://www.nerc.com/pa/Stand/Reliability%20Standards/PRC-023-6.pdf
PRC-024-1 | PRC | PRC-024 | Generator Frequency and Voltage Protective Relay Settings | 2013-05-09 | Approved | 2013-05-09 | 2013-10-01 | Not Initiated | 2016-07-01 | 2016-06-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-024-1.pdf
PRC-024-2 | PRC | PRC-024 | Generator Frequency and Voltage Protective Relay Settings | 2015-02-12 | Approved | 2015-03-18 | 2015-07-16 | Not Initiated | 2016-07-01 | 2022-09-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-024-2.pdf
PRC-024-3 | PRC | PRC-024 | Frequency and Voltage Protection Settings for Generating Resources | 2020-02-06 | Approved | 2020-04-13 | 2021-07-28 | Not Initiated | 2022-10-01 |  | Effective | https://www.nerc.com/pa/Stand/Reliability%20Standards/PRC-024-3.pdf
PRC-025-1 | PRC | PRC-025 | Generator Relay Loadability | 2013-08-15 | Approved | 2013-10-01 | 2014-01-29 | Not Initiated | 2014-10-01 | 2018-09-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-025-1.pdf
PRC-025-2 | PRC | PRC-025 | Generator Relay Loadability | 2018-02-08 | Approved | 2018-03-29 | 2018-07-27 | Not Initiated | 2018-10-01 |  | Effective | https://www.nerc.com/pa/Stand/Reliability Standards/PRC-025-2.pdf
PRC-026-1 | PRC | PRC-026 | Relay Performance During Stable Power Swings | 2014-12-17 | Approved | 2015-01-09 | 2015-05-10 | Not Initiated | 2018-01-01 | 2024-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-026-1.pdf
PRC-026-2 | PRC | PRC-026 | Relay Performance During Stable Power Swings | 2021-05-13 | Approved | 2021-07-07 | 2021-11-04 | Not Initiated | 2024-04-01 |  | Effective | https://www.nerc.com/pa/Stand/Reliability Standards/PRC-026-2.pdf
PRC-027-1 | PRC | PRC-027 | Coordination of Protection Systems for Performance During Faults | 2015-11-05 | Approved | 2016-09-14 | 2017-01-12 | Not Initiated | 2021-04-01 |  | Effective | http://www.nerc.com/pa/Stand/Reliability Standards/PRC-027-1.pdf
TOP-001-0 | TOP | TOP-001 | Reliability Responsibilities and Authorities | 2005-02-08 | Not Approved |  |  | Not Initiated |  | 2007-01-01 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/TOP-001-0.pdf
TOP-001-1 | TOP | TOP-001 | Reliability Responsibilities and Authorities | 2006-11-01 | Approved |  |  | Not Initiated | 2011-07-08 | 2011-11-20 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/TOP-001-1.pdf
TOP-001-1a | TOP | TOP-001 | Reliability Responsibilities and Authorities | 2010-05-12 | Approved | 2010-07-30 | 2010-11-27 | Not Initiated | 2011-11-21 | 2017-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/TOP-001-1a.pdf
TOP-001-2 | TOP | TOP-001 | Transmission Operations | 2012-05-09 | Not Approved | 2013-04-17 | 2013-08-15 | Not Initiated |  | 2016-01-26 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/TOP-001-2.pdf
TOP-001-3 | TOP | TOP-001 | Transmission Operations | 2014-11-13 | Approved | 2015-03-25 | 2015-07-23 | Not Initiated | 2017-04-01 | 2018-09-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/TOP-001-3.pdf
TOP-001-4 | TOP | TOP-001 | Transmission Operations | 2017-02-09 | Approved | 2017-03-20 | 2017-07-18 | Not Initiated | 2018-10-01 | 2021-03-31 | Retired | http://www.nerc.com/pa/Stand/Project 201601 Modifications to TOP and IRO Standa/TOP-001-4_rbs_clean_nov_27_2016.pdf
TOP-001-5 | TOP | TOP-001 | Transmission Operations | 2019-05-19 | Approved | 2019-05-26 | 2019-09-03 | Not Initiated | 2021-04-01 | 2024-03-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/TOP-001-5.pdf
TOP-001-6 | TOP | TOP-001 | Transmission Operations | 2021-05-13 | Approved | 2021-07-07 | 2021-11-04 | Not Initiated | 2024-04-01 |  | Effective | http://www.nerc.com/pa/Stand/Reliability Standards/TOP-001-6.pdf
TOP-002-0 | TOP | TOP-002 | Normal Operations Planning | 2005-02-08 | Not Approved |  |  | Not Initiated |  | 2007-08-07 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/TOP-002-0.pdf
TOP-002-1 | TOP | TOP-002 | Normal Operations Planning | 2006-08-02 | Not Approved |  |  | Not Initiated |  | 2007-01-01 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/TOP-002-1.pdf
TOP-002-2 | TOP | TOP-002 | Normal Operations Planning | 2006-11-01 | Approved |  |  | Not Initiated | 2007-08-02 | 2009-09-12 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/TOP-002-2.pdf
TOP-002-2.1b | TOP | TOP-002 | Normal Operations Planning | 2012-04-11 | Approved | 2012-06-11 | 2012-10-09 | Not Initiated | 2012-10-10 | 2017-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/TOP-002-2_1b.pdf
TOP-002-2a | TOP | TOP-002 | Normal Operations Planning | 2009-02-10 | Approved | 2009-05-15 | 2009-09-12 | Not Initiated | 2009-09-13 | 2011-10-19 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/TOP-002-2a.pdf
TOP-002-2b | TOP | TOP-002 | Normal Operations Planning | 2010-11-04 | Approved | 2011-06-14 | 2011-10-12 | Not Initiated | 2011-10-20 | 2012-10-09 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/TOP-002-2b.pdf
TOP-002-3 | TOP | TOP-002 | Operations Planning | 2012-05-09 | Not Approved | 2013-04-17 | 2013-08-15 | Not Initiated |  | 2016-01-26 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/TOP-002-3.pdf
TOP-002-4 | TOP | TOP-002 | Operations Planning | 2014-11-13 | Approved | 2015-03-25 | 2015-07-23 | Not Initiated | 2017-04-01 | 2025-09-30 | Effective | http://www.nerc.com/pa/Stand/Reliability Standards/TOP-002-4.pdf
TOP-002-5 | TOP | TOP-002 | Operations Planning | 2023-10-23 | Approved | 2023-11-15 | 2024-03-14 | Not Initiated | 2025-10-01 |  | Future Effective | https://www.nerc.com/pa/Stand/Reliability%20Standards/TOP-002-5.pdf
TOP-003-0 | TOP | TOP-003 | Planned Outage Coordination | 2005-02-08 | Approved |  |  | Not Initiated | 2011-07-08 | 2011-09-30 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/TOP-003-0.pdf
TOP-003-1 | TOP | TOP-003 | Planned Outage Coordination | 2008-10-17 | Approved | 1899-12-31 | 1900-01-01 | Not Initiated | 2011-10-01 | 2016-12-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/TOP-003-1.pdf
TOP-003-2 | TOP | TOP-003 | Operational Reliability Data | 2012-05-09 | Not Approved | 2013-04-17 | 2013-08-15 | Not Initiated |  | 2016-01-26 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/TOP-003-2.pdf
TOP-003-3 | TOP | TOP-003 | Operational Reliability Data | 2014-11-13 | Approved | 2015-03-25 | 2015-07-23 | Not Initiated | 2017-01-01 | 2021-09-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/TOP-003-3.pdf
TOP-003-4 | TOP | TOP-003 | Operational Reliability Data | 2020-01-23 | Approved | 2020-01-23 | 2020-05-22 | Not Initiated | 2021-04-01 | 2023-09-30 | Retired | https://www.nerc.com/pa/Stand/Project201707StandardsAlignmentwithRegistration/TOP-003-4%20Project%202017%2007%20Clean_January2020.pdf
TOP-003-5 | TOP | TOP-003 | Operational Reliability Data | 2021-10-06 | Approved | 2021-10-07 | 2022-02-02 | Not Initiated | 2023-10-01 | 2025-09-30 | Effective | https://www.nerc.com/pa/Stand/Project%20201906%20Cold%20Weather%20DL/2019-06_TOP-003-4_Clean_05182021.pdf
TOP-003-6.1 | TOP | TOP-003 | Transmission Operator and Balancing Authority Data and Information Specification and Collection | 2023-08-23 | Approved | 2023-11-02 | 2024-03-01 | Not Initiated | 2025-10-01 |  | Future Effective | https://www.nerc.com/pa/Stand/Reliability%20Standards/TOP-003-6.1.pdf
TOP-004-0 | TOP | TOP-004 | Transmission Operations | 2005-02-08 | Not Approved |  |  | Not Initiated |  | 2005-04-01 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/TOP-004-0.pdf
TOP-004-1 | TOP | TOP-004 | Transmission Operations | 2006-11-01 | Approved |  |  | Not Initiated | 2007-06-18 | 2009-01-21 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/TOP-004-1.pdf
TOP-004-2 | TOP | TOP-004 | Transmission Operations | 2006-11-01 | Approved | 2008-08-11 | 2008-12-09 | Not Initiated | 2009-06-25 | 2017-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/TOP-004-2.pdf
TOP-005-0 | TOP | TOP-005 | Operational Reliability Information | 2005-02-08 | Not Approved |  |  | Not Initiated |  | 2006-11-01 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/TOP-005-0.pdf
TOP-005-1 | TOP | TOP-005 | Operational Reliability Information | 2006-02-07 | Approved |  |  | Not Initiated | 2007-06-18 | 2009-05-12 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/TOP-005-1.pdf
TOP-005-1.1 | TOP | TOP-005 | Operational Reliability Information | 2008-10-29 | Approved | 2009-05-15 | 2009-09-12 | Not Initiated | 2009-09-13 | 2010-04-10 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/TOP-005-1_1.pdf
TOP-005-1.1a | TOP | TOP-005 | Operational Reliability Information | 2009-11-05 | Approved | 2009-12-11 | 2010-04-10 | Not Initiated | 2011-07-08 | 2011-09-30 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/TOP-005-1.1a.pdf
TOP-005-2 | TOP | TOP-005 | Operational Reliability Information | 2008-10-17 | Approved |  |  | Not Initiated | 2009-04-01 | 2010-03-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/TOP-005-2.pdf
TOP-005-2a | TOP | TOP-005 | Operational Reliability Information | 2009-11-05 | Approved | 1899-12-31 | 1900-01-01 | Not Initiated | 2011-10-01 | 2017-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/TOP-005-2a.pdf
TOP-005-3a | TOP | TOP-005 | Operational Reliability Information | 2014-11-13 | Not Approved | 2015-02-10 | 2015-06-10 | Not Initiated |  | 2014-11-13 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/TOP-005-3a.pdf
TOP-006-0 | TOP | TOP-006 | Monitoring System Conditions | 2005-02-08 | Not Approved |  |  | Not Initiated |  | 2007-01-01 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/TOP-006-0.pdf
TOP-006-1 | TOP | TOP-006 | Monitoring System Conditions | 2006-11-01 | Approved |  |  | Not Initiated | 2011-07-08 | 2011-09-30 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/TOP-006-1.pdf
TOP-006-2 | TOP | TOP-006 | Monitoring System Conditions | 2008-10-17 | Approved | 1899-12-31 | 1900-01-01 | Not Initiated | 2011-10-01 | 2017-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/TOP-006-2.pdf
TOP-006-3 | TOP | TOP-006 | Monitoring System Conditions | 2012-11-07 | Not Approved | 1899-12-31 | 1900-01-01 | Not Initiated |  | 2015-03-18 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/TOP-006-3.pdf
TOP-007-0 | TOP | TOP-007 | Reporting System Operating Limit (SOL) and Interconnection Reliability Operating Limit (IROL) Violations | 2005-02-08 | Approved | 1899-12-31 | 1900-01-01 | Not Initiated | 2005-02-08 | 2017-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/TOP-007-0.pdf
TOP-008-0 | TOP | TOP-008 | Response to Transmission Limit Violations | 2005-02-08 | Not Approved |  |  | Not Initiated |  | 2007-01-01 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/TOP-008-0.pdf
TOP-008-1 | TOP | TOP-008 | Response to Transmission Limit Violations | 2006-11-01 | Approved | 1899-12-31 | 1900-01-01 | Not Initiated | 2006-11-01 | 2017-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/TOP-008-1.pdf
TOP-010-1 | TOP | TOP-010 | Real-time Reliability Monitoring and Analysis Capabilities | 2016-02-11 | Approved | 2016-06-01 | 2016-09-29 | Not Initiated | 2018-04-01 | 2018-03-31 | Retired | http://www.nerc.com/pa/Stand/Project 200902 Rela Time Monitotring Analysis Capa/TOP_010_1_20160212_clean.pdf
TOP-010-1(i) | TOP | TOP-010 | Real-time Reliability Monitoring and Analysis Capabilities | 2016-02-11 | Approved | 2016-06-01 | 2016-09-29 | Not Initiated | 2018-04-01 |  | Effective | https://www.nerc.com/pa/Stand/Reliability%20Standards/TOP-010-1(i).pdf
TPL-001-0 | TPL | TPL-001 | System Performance Under Normal (No Contingency) Conditions (Category A) | 2005-02-08 | Approved |  |  | Not Initiated | 2007-06-18 | 2009-05-12 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/TPL-001-0.pdf
TPL-001-0.1 | TPL | TPL-001 | System Performance Under Normal (No Contingency) Conditions (Category A) | 2008-10-29 | Approved | 2009-05-15 | 2009-09-12 | Not Initiated | 2009-09-13 | 2014-12-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/TPL-001-0_1.pdf
TPL-001-0.1(i) | TPL | TPL-001 | System Performance Under Normal (No Contingency) Conditions (Category A) | 2014-11-13 | Approved | 2015-02-10 | 2015-06-10 | Not Initiated | 2012-07-07 | 2015-12-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/TPL-001-0.1(i).pdf
TPL-001-1 | TPL | TPL-001 | System Performance Under Normal (No Contingency) Conditions (Category A) | 2011-02-17 | Approved | 2011-04-20 | 2011-08-18 | Not Initiated | 2012-07-06 | 2012-07-06 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/TPL-001-1.pdf
TPL-001-2 | TPL | TPL-001 | Transmission System Planning Performance Requirements | 2011-08-04 | Not Approved | 2012-02-01 | 2012-05-31 | Not Initiated |  | 2013-12-23 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/TPL-001-2.pdf
TPL-001-3 | TPL | TPL-001 | System Performance Under Normal (No Contingency) Conditions (Category A) | 2013-02-07 | Not Approved | 2013-03-05 | 2013-07-03 | Not Initiated |  | 2013-12-31 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/TPL-001-3.pdf
TPL-001-4 | TPL | TPL-001 | Transmission System Planning Performance Requirements | 2013-02-07 | Approved | 2013-03-05 | 2013-07-03 | Not Initiated | 2015-01-01 | 2022-06-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/TPL-001-4.pdf
TPL-001-5 | TPL | TPL-001 | Transmission System Planning Performance Requirements | 2018-11-07 | Approved | 2018-12-12 | 2019-04-11 | Not Initiated | 2022-07-01 | 2023-06-30 | Retired | https://www.nerc.com/pa/Stand/Project_201510%20Single%20Points%20of%20Failure_TPL001_DL/TPL-001-5_clean_10112018.pdf
TPL-001-5.1 | TPL | TPL-001 | Transmission System Planning Performance Requirements | 2018-11-07 | Approved |  |  | Not Initiated | 2023-07-01 |  | Effective | https://www.nerc.com/pa/Stand/Reliability%20Standards/TPL-001-5.1.pdf
TPL-002-0 | TPL | TPL-002 | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | 2005-02-08 | Approved |  |  | Not Initiated | 2007-06-18 | 2010-04-22 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/TPL-002-0.pdf
TPL-002-0(i)b | TPL | TPL-002 | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | 2014-11-13 | Approved | 2015-02-10 | 2015-06-10 | Not Initiated | 2012-07-07 | 2015-12-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/TPL-002-0(i)b.pdf
TPL-002-0a | TPL | TPL-002 | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | 2008-07-30 | Approved | 2009-05-15 | 2009-09-12 | Not Initiated | 2011-07-08 | 2011-10-23 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/TPL-002-0a.pdf
TPL-002-0b | TPL | TPL-002 | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | 2009-11-05 | Approved | 2009-12-11 | 2010-04-10 | Not Initiated | 2011-10-24 | 2014-12-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/TPL-002-0b.pdf
TPL-002-1b | TPL | TPL-002 | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | 2011-02-17 | Approved | 2011-04-20 | 2011-08-18 | Not Initiated | 2012-07-06 | 2012-07-06 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/TPL-002-1b.pdf
TPL-002-2b | TPL | TPL-002 | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | 2013-02-07 | Not Approved | 2013-03-05 | 2013-07-03 | Not Initiated |  | 2014-12-31 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/TPL-002-2b.pdf
TPL-003-0 | TPL | TPL-003 | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | 2005-02-08 | Approved |  |  | Not Initiated | 2007-06-18 | 2010-04-22 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/TPL-003-0.pdf
TPL-003-0(i)b | TPL | TPL-003 | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | 2014-11-13 | Approved | 2015-02-10 | 2015-06-10 | Not Initiated | 2012-07-07 | 2015-12-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/TPL-003-0(i)b.pdf
TPL-003-0a | TPL | TPL-003 | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | 2008-07-30 | Approved | 2009-05-15 | 2009-09-12 | Not Initiated | 2009-09-13 | 2013-08-14 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/TPL-003-0a.pdf
TPL-003-0b | TPL | TPL-003 | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | 2013-02-07 | Approved | 2013-04-17 | 2013-08-15 | Not Initiated | 2013-08-15 | 2014-12-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/TPL-003-0b.pdf
TPL-003-1a | TPL | TPL-003 | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | 2011-02-17 | Approved | 2011-04-20 | 2011-08-18 | Not Initiated | 2012-07-06 | 2012-07-06 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/TPL-003-1a.pdf
TPL-003-2a | TPL | TPL-003 | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | 2013-02-07 | Not Approved | 2013-03-05 | 2013-07-03 | Not Initiated |  | 2014-12-31 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/TPL-003-2a.pdf
TPL-003-2b | TPL | TPL-003 | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | 2013-02-07 | Not Approved | 2013-04-17 | 2013-08-15 | Not Initiated |  | 2013-12-23 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/TPL-003-2b.pdf
TPL-004-0 | TPL | TPL-004 | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | 2005-02-08 | Approved |  |  | Not Initiated | 2005-02-08 | 2013-08-14 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/TPL-004-0.pdf
TPL-004-0(i)a | TPL | TPL-004 | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | 2014-11-13 | Approved | 2015-02-10 | 2015-06-10 | Not Initiated | 2012-07-07 | 2015-12-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/TPL-004-0(i)a.pdf
TPL-004-0a | TPL | TPL-004 | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | 2013-02-07 | Approved | 2013-04-17 | 2013-08-15 | Not Initiated | 2013-08-15 | 2014-12-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/TPL-004-0a.pdf
TPL-004-1 | TPL | TPL-004 | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | 2011-02-17 | Approved | 2011-04-20 | 2011-08-18 | Not Initiated | 2012-07-06 | 2012-07-06 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/TPL-004-1.pdf
TPL-004-2 | TPL | TPL-004 | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | 2013-02-07 | Not Approved | 2013-03-05 | 2013-07-03 | Not Initiated |  | 2014-12-31 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/TPL-004-2.pdf
TPL-004-2a | TPL | TPL-004 | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | 2013-02-08 | Not Approved | 2013-04-17 | 2013-08-15 | Not Initiated |  | 2013-12-23 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/TPL-004-2a.pdf
TPL-005-0 | TPL | TPL-005 | Regional and Interregional Self-Assessment Reliability Reports | 2005-02-08 | Not Approved |  |  | Not Initiated | 2005-02-08 | 2011-07-07 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/TPL-005-0.pdf
TPL-006-0 | TPL | TPL-006 | Data From the Regional Reliability Organization Needed to Assess Reliability | 2005-02-08 | Not Approved |  |  | Not Initiated | 2005-02-08 | 2009-04-14 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/TPL-006-0.pdf
TPL-006-0.1 | TPL | TPL-006 | Data From the Regional Reliability Organization Needed to Assess Reliability | 2009-04-15 | Not Approved |  |  | Not Initiated | 2009-04-15 | 2011-07-07 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/TPL-006-0.1.pdf
TPL-007-1 | TPL | TPL-007 | Transmission System Planned Performance for Geomagnetic Disturbance Events | 2014-12-17 | Approved | 2015-01-28 | 2015-05-28 | Not Initiated | 2017-07-01 | 2019-06-30 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/TPL-007-1.pdf
TPL-007-2 | TPL | TPL-007 | Transmission System Planned Performance for Geomagnetic Disturbance Events | 2017-11-09 | Approved | 2018-03-05 | 2018-03-26 | Review Remanded |  | 2019-06-30 | Never Came Into Effect in Ontario | http://www.nerc.com/pa/Stand/Reliability Standards/TPL-007-2.pdf
TPL-007-3 | TPL | TPL-007 | Transmission System Planned Performance for Geomagnetic Disturbance Events | 2019-02-07 | Approved | 2019-03-14 | 2019-06-21 | Not Initiated | 2019-07-01 | 2020-12-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/TPL-007-3.pdf
TPL-007-4 | TPL | TPL-007 | Transmission System Planned Performance for Geomagnetic Disturbance Events | 2020-02-06 | Approved | 2020-02-13 | 2020-06-12 | Not Initiated | 2021-01-01 |  | Effective | https://www.nerc.com/pa/Stand/Reliability%20Standards/TPL-007-4.pdf
VAR-001-0 | VAR | VAR-001 | Voltage and Reactive Control | 2005-02-08 | Not Approved |  |  | Not Initiated |  | 2007-01-01 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/VAR-001-0.pdf
VAR-001-1 | VAR | VAR-001 | Voltage and Reactive Control | 2006-08-02 | Approved |  |  | Not Initiated | 2009-05-22 | 2012-03-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/VAR-001-1.pdf
VAR-001-1a | VAR | VAR-001 | Voltage and Reactive Control | 2008-03-26 | Not Approved |  |  | Not Initiated |  | 2009-05-21 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/VAR-001-1a.pdf
VAR-001-2 | VAR | VAR-001 | Voltage and Reactive Control | 2010-08-05 | Approved | 2011-03-10 | 2011-07-08 | Not Initiated | 2012-04-01 | 2014-09-30 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/VAR-001-2.pdf
VAR-001-3 | VAR | VAR-001 | Voltage and Reactive Control | 2012-05-09 | Approved | 2013-09-25 | 2014-01-23 | Not Initiated | 2014-10-01 | 2014-12-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/VAR-001-3.pdf
VAR-001-4 | VAR | VAR-001 | Voltage and Reactive Control | 2014-02-06 | Approved | 2014-06-16 | 2014-10-14 | Not Initiated | 2015-01-01 | 2015-11-12 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/VAR-001-4.pdf
VAR-001-4.1 | VAR | VAR-001 | Voltage and Reactive Control | 2014-02-06 | Approved | 1899-12-31 | 1900-01-01 | Not Initiated | 2015-11-13 | 2017-09-25 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/VAR-001-4.1.pdf
VAR-001-4.2 | VAR | VAR-001 | Voltage and Reactive Control | 2017-08-10 | Approved | 1899-12-31 | 1900-01-01 | Not Initiated | 2017-09-26 | 2019-03-31 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/VAR-001-4.2.pdf
VAR-001-5 | VAR | VAR-001 | Voltage and Reactive Control | 2018-08-16 | Approved | 2018-09-11 | 2019-01-08 | Not Initiated | 2019-04-01 |  | Effective | https://www.nerc.com/pa/Stand/Reliability%20Standards/VAR-001-5.pdf
VAR-001-6 | VAR | VAR-001 | Voltage and Reactive Control | 2019-05-09 | Not Approved |  |  | Not Initiated |  | 2020-05-14 | Never Came Into Effect in Ontario | https://www.nerc.com/pa/Stand/Reliability%20Standards/VAR-001-6.pdf
VAR-002-1 | VAR | VAR-002 | Generator Operation for Maintaining Network Voltage Schedules | 2006-08-02 | Approved |  |  | Not Initiated | 2007-08-02 | 2008-08-26 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/VAR-002-1.pdf
VAR-002-1.1a | VAR | VAR-002 | Generator Operation for Maintaining Network Voltage Schedules | 2008-10-29 | Approved |  |  | Not Initiated | 2009-05-13 | 2010-09-15 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/VAR-002-1_1a.pdf
VAR-002-1.1b | VAR | VAR-002 | Generator Operation for Maintaining Network Voltage Schedules | 2009-02-10 | Approved |  |  | Not Initiated | 2009-02-10 | 2013-06-30 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/VAR-002-1_1b.pdf
VAR-002-1a | VAR | VAR-002 | Generator Operation for Maintaining Network Voltage Schedules | 2007-08-01 | Approved |  |  | Not Initiated | 2008-08-27 | 2009-05-12 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/VAR-002-1a.pdf
VAR-002-2b | VAR | VAR-002 | Generator Operation for Maintaining Network Voltage Schedules | 2012-08-16 | Approved | 2012-11-22 | 2013-03-22 | Not Initiated | 2013-07-01 | 2014-12-31 | Retired | https://www.nerc.com/pa/Stand/Reliability%20Standards/VAR-002-2b.pdf
VAR-002-3 | VAR | VAR-002 | Generator Operation for Maintaining Network Voltage Schedules | 2014-05-06 | Approved | 2014-06-16 | 2014-10-14 | Not Initiated | 2015-01-01 | 2015-06-13 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/VAR-002-3.pdf
VAR-002-4 | VAR | VAR-002 | Generator Operation for Maintaining Network Voltage Schedules | 2014-11-13 | Approved | 2015-02-12 | 2015-06-14 | Not Initiated | 2015-06-14 | 2017-09-25 | Retired | http://www.nerc.com/pa/Stand/Reliability Standards/VAR-002-4.pdf
VAR-002-4.1 | VAR | VAR-002 | Generator Operation for Maintaining Network Voltage Schedules | 2017-08-10 | Approved | 1899-12-31 | 1900-01-01 | Not Initiated | 2017-09-26 |  | Effective | http://www.nerc.com/pa/Stand/Reliability Standards/VAR-002-4.1.pdfhttp:/www.nerc.com/pa/Stand/Reliability Standards/VAR-002-4.1.pdf
Total Number of Standards: 577
¹ OEB Remand Process Start Date is the date when IESO posts the standard on the OEB Remand Process web page.
² OEB Remand Process End Date is 120 days after the OEB Remand Process Start Date.
³ The determination of Mandatory Enforcement Date in Ontario has taken the standard implementation period into consideration. Some standards have two mandatory enforcement periods, resulting from the Market Rule Amendment MR-00379 which became effective on July 8, 2011.
Market Rule Amendment MR-00379: http://www.ieso.ca/Documents/icms/tp/2011/05/IESOTP_250_3b_MR_00379_R00_Amendment_Proposal_v5_0.doc

## NERC Requirements
Standard Number | Document Title | Req't . | Text of Requirement | Violation Risk Factors | Status In Ontario | Requirement Enforcement Date | Requirement Inactive Date | Functional Entities | Functional Entities
BAL-001-1 | Real Power Balancing Control Performance | R1. | Each Balancing Authority shall operate such that, on a rolling 12-month basis, the average of the clock-minute averages of the Balancing Authority’s Area Control Error (ACE) divided by 10B (B is the clock-minute average of the Balancing Authority Area’s Frequency Bias) times the corresponding clock-minute averages of the Interconnection’s Frequency Error is less than a specific limit. This limit is a constant derived from a targeted frequency bound (separately calculated for each Interconnection) that is reviewed and set as necessary by the NERC Operating Committee. See Standard for Formula. | MEDIUM | Retired | 2014-07-01 | 2016-06-30 | BA
BAL-001-1 | Real Power Balancing Control Performance | R2. | Each Balancing Authority shall operate such that its average ACE for at least 90% of clockten- minute periods (6 non-overlapping periods per hour) during a calendar month is within a specific limit, referred to as L10. See Standard for Formula. | MEDIUM | Retired | 2014-07-01 | 2016-06-30 | BA
BAL-001-1 | Real Power Balancing Control Performance | R3. | Each Balancing Authority providing Overlap Regulation Service shall evaluate Requirement R1 (i.e., Control Performance Standard 1 or CPS1) and Requirement R2 (i.e., Control Performance Standard 2 or CPS2) using the characteristics of the combined ACE and combined Frequency Bias Settings. | MEDIUM | Retired | 2014-07-01 | 2016-06-30 | BA
BAL-001-1 | Real Power Balancing Control Performance | R4. | Any Balancing Authority receiving Overlap Regulation Service shall not have its control performance evaluated (i.e. from a control performance perspective, the Balancing Authority has shifted all control requirements to the Balancing Authority providing Overlap Regulation Service). | MEDIUM | Retired | 2014-07-01 | 2016-06-30 | BA
BAL-001-2 | Real Power Balancing Control Performance | R1. | The Responsible Entity shall operate such that the Control Performance Standard 1 (CPS1), calculated in accordance with Attachment 1, is greater than or equal to 100 percent for the applicable Interconnection in which it operates for each preceding 12 consecutive calendar month period, evaluated monthly. [Violation Risk Factor: Medium] [Time Horizon: Real‐time Operations] | MEDIUM | Effective | 2016-07-01 |  | BA
BAL-001-2 | Real Power Balancing Control Performance | R2. | Each Balancing Authority shall operate such that its clock‐minute average of Reporting ACE does not exceed its clock‐minute Balancing Authority ACE Limit (BAAL) for more than 30 consecutive clock‐minutes, calculated in accordance with Attachment 2, for the applicable Interconnection in which the Balancing Authority operates.[Violation Risk Factor: Medium] [Time Horizon: Real‐time Operations] | MEDIUM | Effective | 2016-07-01 |  | BA
BAL-002-1 | Disturbance Control Performance | R1. | Each Balancing Authority shall have access to and/or operate Contingency Reserve to respond to Disturbances. Contingency Reserve may be supplied from generation, controllable load resources, or coordinated adjustments to Interchange Schedules. | HIGH | Retired | 2012-10-01 | 2017-12-31 | BA
BAL-002-1 | Disturbance Control Performance | R1.1. | A Balancing Authority may elect to fulfill its Contingency Reserve obligations by participating as a member of a Reserve Sharing Group. In such cases, the Reserve Sharing Group shall have the same responsibilities and obligations as each Balancing Authority with respect to monitoring and meeting the requirements of Standard BAL-002. | HIGH | Retired | 2012-10-01 | 2017-12-31 | RSG, BA
BAL-002-1 | Disturbance Control Performance | R2. | Each Regional Reliability Organization, sub-Regional Reliability Organization or Reserve Sharing Group shall specify its Contingency Reserve policies, including: | MEDIUM | Retired | 2012-10-01 | 2017-12-31 | RSG
BAL-002-1 | Disturbance Control Performance | R2.1. | The minimum reserve requirement for the group. | HIGH | Retired | 2012-10-01 | 2017-12-31 | RSG
BAL-002-1 | Disturbance Control Performance | R2.2. | Its allocation among members. | LOWER | Retired | 2012-10-01 | 2017-12-31 | RSG
BAL-002-1 | Disturbance Control Performance | R2.3. | The permissible mix of Operating Reserve – Spinning and Operating Reserve – Supplemental that may be included in Contingency Reserve. | LOWER | Retired | 2012-10-01 | 2017-12-31 | RSG
BAL-002-1 | Disturbance Control Performance | R2.4. | The procedure for applying Contingency Reserve in practice. | LOWER | Retired | 2012-10-01 | 2017-12-31 | RSG
BAL-002-1 | Disturbance Control Performance | R2.5. | The limitations, if any, upon the amount of interruptible load that may be included. | LOWER | Retired | 2012-10-01 | 2017-12-31 | RSG
BAL-002-1 | Disturbance Control Performance | R2.6. | The same portion of resource capacity (e.g. reserves from jointly owned generation) shall not be counted more than once as Contingency Reserve by multiple Balancing Authorities. | MEDIUM | Retired | 2012-10-01 | 2017-12-31 | RSG
BAL-002-1 | Disturbance Control Performance | R3. | Each Balancing Authority or Reserve Sharing Group shall activate sufficient Contingency Reserve to comply with the DCS. | HIGH | Retired | 2012-10-01 | 2017-12-31 | RSG, BA
BAL-002-1 | Disturbance Control Performance | R3.1. | As a minimum, the Balancing Authority or Reserve Sharing Group shall carry at least enough Contingency Reserve to cover the most severe single contingency. All Balancing Authorities and Reserve Sharing Groups shall review, no less frequently than annually, their probable contingencies to determine their prospective most severe single contingencies. | HIGH | Retired | 2012-10-01 | 2017-12-31 | RSG, BA
BAL-002-1 | Disturbance Control Performance | R4. | A Balancing Authority or Reserve Sharing Group shall meet the Disturbance Recovery Criterion within the Disturbance Recovery Period for 100% of Reportable Disturbances. The Disturbance Recovery Criterion is: | MEDIUM | Retired | 2012-10-01 | 2017-12-31 | RSG, BA
BAL-002-1 | Disturbance Control Performance | R4.1. | A Balancing Authority shall return its ACE to zero if its ACE just prior to the Reportable Disturbance was positive or equal to zero. For negative initial ACE values just prior to the Disturbance, the Balancing Authority shall return ACE to its pre-Disturbance value. | MEDIUM | Retired | 2012-10-01 | 2017-12-31 | RSG, BA
BAL-002-1 | Disturbance Control Performance | R4.2. | The default Disturbance Recovery Period is 15 minutes after the start of a Reportable Disturbance. | No Individual VRF Assigned | Retired | 2012-10-01 | 2017-12-31 | RSG, BA
BAL-002-1 | Disturbance Control Performance | R5. | Each Reserve Sharing Group shall comply with the DCS. A Reserve Sharing Group shall be considered in a Reportable Disturbance condition whenever a group member has experienced a Reportable Disturbance and calls for the activation of Contingency Reserves from one or more other group members. (If a group member has experienced a Reportable Disturbance but does not call for reserve activation from other members of the Reserve Sharing Group, then that member shall report as a single Balancing Authority.) Compliance may be demonstrated by either of the following two methods: | LOWER | Retired | 2012-10-01 | 2017-12-31 | RSG
BAL-002-1 | Disturbance Control Performance | R5.1. | The Reserve Sharing Group reviews group ACE (or equivalent) and demonstrates compliance to the DCS. To be in compliance, the group ACE (or its equivalent) must meet the Disturbance Recovery Criterion after the schedule change(s) related to reserve sharing have been fully implemented, and within the Disturbance Recovery Period. or | No Individual VRF Assigned | Retired | 2012-10-01 | 2017-12-31 | RSG
BAL-002-1 | Disturbance Control Performance | R5.2. | The Reserve Sharing Group reviews each member’s ACE in response to the activation of reserves. To be in compliance, a member’s ACE (or its equivalent) must meet the Disturbance Recovery Criterion after the schedule change(s) related to reserve sharing have been fully implemented, and within the Disturbance Recovery Period. | No Individual VRF Assigned | Retired | 2012-10-01 | 2017-12-31 | RSG
BAL-002-1 | Disturbance Control Performance | R6. | A Balancing Authority or Reserve Sharing Group shall fully restore its Contingency Reserves within the Contingency Reserve Restoration Period for its Interconnection. | MEDIUM | Retired | 2012-10-01 | 2017-12-31 | RSG, BA
BAL-002-1 | Disturbance Control Performance | R6.1. | The Contingency Reserve Restoration Period begins at the end of the Disturbance Recovery Period. | No Individual VRF Assigned | Retired | 2012-10-01 | 2017-12-31 | RSG, BA
BAL-002-1 | Disturbance Control Performance | R6.2. | The default Contingency Reserve Restoration Period is 90 minutes. | No Individual VRF Assigned | Retired | 2012-10-01 | 2017-12-31 | RSG, BA
BAL-002-1a | Disturbance Control Performance | R1. | Each Balancing Authority shall have access to and/or operate Contingency Reserve to respond to Disturbances. Contingency Reserve may be supplied from generation, controllable load resources, or coordinated adjustments to Interchange Schedules. | HIGH | Retired |  |  | RSG, BA
BAL-002-1a | Disturbance Control Performance | R1.1. | A Balancing Authority may elect to fulfill its Contingency Reserve obligations by participating as a member of a Reserve Sharing Group. In such cases, the Reserve Sharing Group shall have the same responsibilities and obligations as each Balancing Authority with respect to monitoring and meeting the requirements of Standard BAL- 002. | HIGH | Retired |  |  | RSG, BA
BAL-002-1a | Disturbance Control Performance | R2. | Each Regional Reliability Organization, sub-Regional Reliability Organization or Reserve Sharing Group shall specify its Contingency Reserve policies, including: | MEDIUM | Retired |  |  | RSG
BAL-002-1a | Disturbance Control Performance | R2.1. | The minimum reserve requirement for the group. | HIGH | Retired |  |  | RSG
BAL-002-1a | Disturbance Control Performance | R2.2. | Its allocation among members. | LOWER | Retired |  |  | RSG
BAL-002-1a | Disturbance Control Performance | R2.3. | The permissible mix of Operating Reserve – Spinning and Operating Reserve – Supplemental that may be included in Contingency Reserve. | LOWER | Retired |  |  | RSG
BAL-002-1a | Disturbance Control Performance | R2.4. | The procedure for applying Contingency Reserve in practice. | LOWER | Retired |  |  | RSG
BAL-002-1a | Disturbance Control Performance | R2.5. | The limitations, if any, upon the amount of interruptible load that may be included. | LOWER | Retired |  |  | RSG
BAL-002-1a | Disturbance Control Performance | R2.6. | The same portion of resource capacity (e.g. reserves from jointly owned generation) shall not be counted more than once as Contingency Reserve by multiple Balancing Authorities. | MEDIUM | Retired |  |  | RSG
BAL-002-1a | Disturbance Control Performance | R3. | Each Balancing Authority or Reserve Sharing Group shall activate sufficient Contingency Reserve to comply with the DCS. | HIGH | Retired |  |  | RSG, BA
BAL-002-1a | Disturbance Control Performance | R3.1. | As a minimum, the Balancing Authority or Reserve Sharing Group shall carry at least enough Contingency Reserve to cover the most severe single contingency. All Balancing Authorities and Reserve Sharing Groups shall review, no less frequently than annually, their probable contingencies to determine their prospective most severe single contingencies. | HIGH | Retired |  |  | RSG, BA
BAL-002-1a | Disturbance Control Performance | R4. | A Balancing Authority or Reserve Sharing Group shall meet the Disturbance Recovery Criterion within the Disturbance Recovery Period for 100% of Reportable Disturbances. The Disturbance Recovery Criterion is: | MEDIUM | Retired |  |  | RSG, BA
BAL-002-1a | Disturbance Control Performance | R4.1. | A Balancing Authority shall return its ACE to zero if its ACE just prior to the Reportable Disturbance was positive or equal to zero. For negative initial ACE values just prior to the Disturbance, the Balancing Authority shall return ACE to its pre- Disturbance value. | MEDIUM | Retired |  |  | RSG, BA
BAL-002-1a | Disturbance Control Performance | R4.2. | The default Disturbance Recovery Period is 15 minutes after the start of a Reportable Disturbance. | No Individual VRF Assigned | Retired |  |  | RSG, BA
BAL-002-1a | Disturbance Control Performance | R5. | Each Reserve Sharing Group shall comply with the DCS. A Reserve Sharing Group shall be considered in a Reportable Disturbance condition whenever a group member has experienced a Reportable Disturbance and calls for the activation of Contingency Reserves from one or more other group members. (If a group member has experienced a Reportable Disturbance but does not call for reserve activation from other members of the Reserve Sharing Group, then that member shall report as a single Balancing Authority.) Compliance may be demonstrated by either of the following two methods: | LOWER | Retired |  |  | RSG
BAL-002-1a | Disturbance Control Performance | R5.1. | The Reserve Sharing Group reviews group ACE (or equivalent) and demonstrates compliance to the DCS. To be in compliance, the group ACE (or its equivalent) must meet the Disturbance Recovery Criterion after the schedule change(s) related to reserve sharing have been fully implemented, and within the Disturbance Recovery Period. | No Individual VRF Assigned | Retired |  |  | RSG
BAL-002-1a | Disturbance Control Performance | R5.2. | The Reserve Sharing Group reviews each member’s ACE in response to the activation of reserves. To be in compliance, a member’s ACE (or its equivalent) must meet the Disturbance Recovery Criterion after the schedule change(s) related to reserve sharing have been fully implemented, and within the Disturbance Recovery Period. | No Individual VRF Assigned | Retired |  |  | RSG
BAL-002-1a | Disturbance Control Performance | R6. | A Balancing Authority or Reserve Sharing Group shall fully restore its Contingency Reserves within the Contingency Reserve Restoration Period for its Interconnection. | MEDIUM | Retired |  |  | RSG, BA
BAL-002-1a | Disturbance Control Performance | R6.1. | The Contingency Reserve Restoration Period begins at the end of the Disturbance Recovery Period. | No Individual VRF Assigned | Retired |  |  | RSG, BA
BAL-002-1a | Disturbance Control Performance | R6.2. | The default Contingency Reserve Restoration Period is 90 minutes. | No Individual VRF Assigned | Retired |  |  | RSG, BA
BAL-002-2 | Disturbance Control Standard – Contingency Reserve for Recovery from a Balancing Contingency Event | R1. | The Responsible Entity experiencing a Reportable Balancing Contingency Event shall: [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | HIGH | Retired | 2018-01-01 | 2017-12-31 | RSG, BA
BAL-002-2 | Disturbance Control Standard – Contingency Reserve for Recovery from a Balancing Contingency Event | R1.1. | within the Contingency Event Recovery Period, demonstrate recovery by returning its Reporting ACE to at least the recovery value of: ● zero (if its Pre-Reporting Contingency Event ACE Value was positive or equal to zero); however, any Balancing Contingency Event that occurs during the Contingency Event Recovery Period shall reduce the required recovery: (i) beginning at the time of, and (ii) by the magnitude of, such individual Balancing Contingency Event, or, ● its Pre-Reporting Contingency Event ACE Value (if its Pre-Reporting Contingency Event ACE Value was negative); however, any Balancing Contingency Event that occurs during the Contingency Event Recovery Period shall reduce the required recovery: (i) beginning at the time of, and (ii) by the magnitude of, such individual Balancing Contingency Event. | MEDIUM | Retired | 2018-01-01 | 2017-12-31 | RSG, BA
BAL-002-2 | Disturbance Control Standard – Contingency Reserve for Recovery from a Balancing Contingency Event | R1.2. | document all Reportable Balancing Contingency Events using CR Form 1. | MEDIUM | Retired | 2018-01-01 | 2017-12-31 | RSG, BA
BAL-002-2 | Disturbance Control Standard – Contingency Reserve for Recovery from a Balancing Contingency Event | R1.3. | deploy Contingency Reserve, within system constraints, to respond to all Reportable Balancing Contingency Events, however, it is not subject to compliance with Requirement R1 part 1.1 if: | MEDIUM | Retired | 2018-01-01 | 2017-12-31 | RSG, BA
BAL-002-2 | Disturbance Control Standard – Contingency Reserve for Recovery from a Balancing Contingency Event | R1.3.1. | the Responsible Entity: ● is a Balancing Authority experiencing a Reliability Coordinator declared Energy Emergency Alert Level or is a Reserve Sharing Group whose member, or members, are experiencing a Reliability Coordinator declared Energy Emergency Alert level, and ● is utilizing its Contingency Reserve to mitigate an operating emergency in accordance with its emergency Operating Plan, and ● has depleted its Contingency Reserve to a level below its Most Severe Single Contingency, or, | MEDIUM | Retired | 2018-01-01 | 2017-12-31 | RSG, BA
BAL-002-2 | Disturbance Control Standard – Contingency Reserve for Recovery from a Balancing Contingency Event | R1.3.2. | the Responsible Entity experiences: ● multiple Contingencies where the combined MW loss exceeds its Most Severe Single Contingency and that are defined as a single Balancing Contingency Event, or ● multiple Balancing Contingency Events within the sum of the time periods defined by the Contingency Event Recovery Period and Contingency Reserve Restoration Period whose combined magnitude exceeds the Responsible Entity's Most Severe Single Contingency. | MEDIUM | Retired | 2018-01-01 | 2017-12-31 | RSG, BA
BAL-002-2 | Disturbance Control Standard – Contingency Reserve for Recovery from a Balancing Contingency Event | R2. | Each Responsible Entity shall develop, review and maintain annually, and implement an Operating Process as part of its Operating Plan to determine its Most Severe Single Contingency and make preparations to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency available for maintaining system reliability. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Retired | 2018-01-01 | 2017-12-31 | RSG, BA
BAL-002-2 | Disturbance Control Standard – Contingency Reserve for Recovery from a Balancing Contingency Event | R3. | Each Responsible Entity, following a Reportable Balancing Contingency Event, shall restore its Contingency Reserve to at least its Most Severe Single Contingency, before the end of the Contingency Reserve Restoration Period, but any Balancing Contingency Event that occurs before the end of a Contingency Reserve Restoration Period resets the beginning of the Contingency Event Recovery Period. [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | MEDIUM | Retired | 2018-01-01 | 2017-12-31 | RSG, BA
BAL-002-2(i) | Disturbance Control Standard – Contingency Reserve for Recovery from a Balancing Contingency Event | R1. | The Responsible Entity experiencing a Reportable Balancing Contingency Event shall: [Violation Risk Factor: High] [Time Horizon: Real-time Operations] | HIGH | Retired | 2018-01-01 | 2019-06-30 | RSG, BA
BAL-002-2(i) | Disturbance Control Standard – Contingency Reserve for Recovery from a Balancing Contingency Event | R1.1. | within the Contingency Event Recovery Period, demonstrate recovery by returning its Reporting ACE to at least the recovery value of: • zero (if its Pre-Reporting Contingency Event ACE Value was positive or equal to zero); however, any Balancing Contingency Event that occurs during the Contingency Event Recovery Period shall reduce the required recovery: (i) beginning at the time of, and (ii) by the magnitude of, such individual Balancing Contingency Event, or, • its Pre-Reporting Contingency Event ACE Value (if its Pre-Reporting Contingency Event ACE Value was negative); however, any Balancing Contingency Event that occurs during the Contingency Event Recovery Period shall reduce the required recovery: (i) beginning at the time of, and (ii) by the magnitude of, such individual Balancing Contingency Event. | HIGH | Retired | 2018-01-01 | 2019-06-30 | RSG, BA
BAL-002-2(i) | Disturbance Control Standard – Contingency Reserve for Recovery from a Balancing Contingency Event | R1.2. | document all Reportable Balancing Contingency Events using CR Form 1. | HIGH | Retired | 2018-01-01 | 2019-06-30 | RSG, BA
BAL-002-2(i) | Disturbance Control Standard – Contingency Reserve for Recovery from a Balancing Contingency Event | R1.3. | deploy Contingency Reserve, within system constraints, to respond to all Reportable Balancing Contingency Events, however, it is not subject to compliance with Requirement R1 part 1.1 if: | HIGH | Retired | 2018-01-01 | 2019-06-30 | RSG, BA
BAL-002-2(i) | Disturbance Control Standard – Contingency Reserve for Recovery from a Balancing Contingency Event | R1.3.1. | the Responsible Entity:• is a Balancing Authority experiencing a Reliability Coordinator declared Energy Emergency Alert Level or is a Reserve Sharing Group whose member, or members, are experiencing a Reliability Coordinator declared Energy Emergency Alert level, and• is utilizing its Contingency Reserve to mitigate an operating emergency in accordance with its emergency Operating Plan, and• has depleted its Contingency Reserve to a level below its Most Severe Single Contingency or, | HIGH | Retired | 2018-01-01 | 2019-06-30 | RSG, BA
BAL-002-2(i) | Disturbance Control Standard – Contingency Reserve for Recovery from a Balancing Contingency Event | R1.3.2. | the Responsible Entity experiences:• multiple Contingencies where the combined MW loss exceeds its Most Severe Single Contingency and that are defined as a single Balancing Contingency Event, or • multiple Balancing Contingency Events within the sum of the time periods defined by the Contingency Event Recovery Period and Contingency Reserve Restoration Period whose combined magnitude exceeds the Responsible Entity's Most Severe Single Contingency. | HIGH | Retired | 2018-01-01 | 2019-06-30 | RSG, BA
BAL-002-2(i) | Disturbance Control Standard – Contingency Reserve for Recovery from a Balancing Contingency Event | R2. | Each Responsible Entity shall develop, review and maintain annually, and implement an Operating Process as part of its Operating Plan to determine its Most Severe Single Contingency and make preparations to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency available for maintaining system reliability. [Violation Risk Factor: High] [Time Horizon: Operations Planning] | HIGH | Retired | 2018-01-01 | 2019-06-30 | RSG, BA
BAL-002-2(i) | Disturbance Control Standard – Contingency Reserve for Recovery from a Balancing Contingency Event | R3. | Each Responsible Entity, following a Reportable Balancing Contingency Event, shall restore its Contingency Reserve to at least its Most Severe Single Contingency, before the end of the Contingency Reserve Restoration Period, but any Balancing Contingency Event that occurs before the end of a Contingency Reserve Restoration Period resets the beginning of the Contingency Event Recovery Period. [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | MEDIUM | Retired | 2018-01-01 | 2019-06-30 | RSG, BA
BAL-002-3 | Disturbance Control Standard – Contingency Reserve for Recovery from a Balancing Contingency Event | R1. | The Responsible Entity experiencing a Reportable Balancing Contingency Event shall: [Violation Risk Factor: High] [Time Horizon: Real-time Operations] | HIGH | Effective | 2019-07-01 |  | RSG, BA
BAL-002-3 | Disturbance Control Standard – Contingency Reserve for Recovery from a Balancing Contingency Event | R1.1. | within the Contingency Event Recovery Period, demonstrate recovery by returning its Reporting ACE to at least the recovery value of:  zero (if its Pre-Reporting Contingency Event ACE Value was positive or equal to zero); however, any Balancing Contingency Event that occurs during the Contingency Event Recovery Period shall reduce the required recovery: (i) beginning at the time of, and (ii) by the magnitude of, such individual Balancing Contingency Event, or,  its Pre-Reporting Contingency Event ACE Value (if its Pre-Reporting Contingency Event ACE Value was negative); however, any Balancing Contingency Event that occurs during the Contingency Event Recovery Period shall reduce the required recovery: (i) beginning at the time of, and (ii) by the magnitude of, such individual Balancing Contingency Event. | HIGH | Effective | 2019-07-01 |  | RSG, BA
BAL-002-3 | Disturbance Control Standard – Contingency Reserve for Recovery from a Balancing Contingency Event | R1.2. | document all Reportable Balancing Contingency Events using CR Form 1. | HIGH | Effective | 2019-07-01 |  | BA, RSG
BAL-002-3 | Disturbance Control Standard – Contingency Reserve for Recovery from a Balancing Contingency Event | R1.3. | deploy Contingency Reserve, within system constraints, to respond to all Reportable Balancing Contingency Events, however, it is not subject to compliance with Requirement R1 part 1.1 if the Responsible Entity: | HIGH | Effective | 2019-07-01 |  | BA, RSG
BAL-002-3 | Disturbance Control Standard – Contingency Reserve for Recovery from a Balancing Contingency Event | R1.3.1. | is (i) a Balancing Authority or (ii) a Reserve Sharing Group with at least one member that:  is experiencing a Reliability Coordinator declared Energy Emergency Alert Level, and  is utilizing its Contingency Reserve to mitigate an operating emergency in accordance with its emergency Operating Plan, and  has depleted its Contingency Reserve to a level below its Most Severe Single Contingency, and  has, during communications with its Reliability Coordinator in accordance with the Energy Emergency Alert procedures, (i) notified the Reliability Coordinator of the conditions described in the preceding two bullet points preventing the Responsible Entity from complying with Requirement R1 part 1.1, and (ii) provided the Reliability Coordinator with an ACE recovery plan, including target recovery time or, | HIGH | Effective | 2019-07-01 |  | RSG, BA
BAL-002-3 | Disturbance Control Standard – Contingency Reserve for Recovery from a Balancing Contingency Event | R1.3.2. | the Responsible Entity experiences:  multiple Contingencies where the combined MW loss exceeds its Most Severe Single Contingency and that are defined as a single Balancing Contingency Event, or  multiple Balancing Contingency Events within the sum of the time periods defined by the Contingency Event Recovery Period and Contingency Reserve Restoration Period whose combined magnitude exceeds the Responsible Entity's Most Severe Single Contingency. | HIGH | Effective | 2019-07-01 |  | RSG, BA
BAL-002-3 | Disturbance Control Standard – Contingency Reserve for Recovery from a Balancing Contingency Event | R2. | Each Responsible Entity shall develop, review and maintain annually, and implement an Operating Process as part of its Operating Plan to determine its Most Severe Single Contingency and make preparations to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency available for maintaining system reliability. [Violation Risk Factor: High] [Time Horizon: Operations Planning] | HIGH | Effective | 2019-07-01 |  | RSG, BA
BAL-002-3 | Disturbance Control Standard – Contingency Reserve for Recovery from a Balancing Contingency Event | R3. | Each Responsible Entity, following a Reportable Balancing Contingency Event, shall restore its Contingency Reserve to at least its Most Severe Single Contingency, before the end of the Contingency Reserve Restoration Period, but any Balancing Contingency Event that occurs before the end of a Contingency Reserve Restoration Period resets the beginning of the Contingency Event Recovery Period. [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | HIGH | Effective | 2019-07-01 |  | BA, RSG
BAL-003-0.1b | Frequency Response and Bias | R1. | Each Balancing Authority shall review its Frequency Bias Settings by January 1 of each year and recalculate its setting to reflect any change in the Frequency Response of the Balancing Authority Area. | LOWER | Retired | 2009-09-13 | 2016-03-31 | BA
BAL-003-0.1b | Frequency Response and Bias | R1.1. | The Balancing Authority may change its Frequency Bias Setting, and the method used to determine the setting, whenever any of the factors used to determine the current bias value change. | LOWER | Retired | 2009-09-13 | 2016-03-31 | BA
BAL-003-0.1b | Frequency Response and Bias | R1.2. | Each Balancing Authority shall report its Frequency Bias Setting, and method for determining that setting, to the NERC Operating Committee. | LOWER | Retired | 2009-09-13 | 2016-03-31 | BA
BAL-003-0.1b | Frequency Response and Bias | R2. | Each Balancing Authority shall establish and maintain a Frequency Bias Setting that is as close as practical to, or greater than, the Balancing Authority’s Frequency Response. Frequency Bias may be calculated several ways: | MEDIUM | Retired | 2009-09-13 | 2015-03-31 | BA
BAL-003-0.1b | Frequency Response and Bias | R2.1. | The Balancing Authority may use a fixed Frequency Bias value which is based on a fixed, straight-line function of Tie Line deviation versus Frequency Deviation. The Balancing Authority shall determine the fixed value by observing and averaging the Frequency Response for several Disturbances during on-peak hours. | LOWER | Retired | 2009-09-13 | 2015-03-31 | BA
BAL-003-0.1b | Frequency Response and Bias | R2.2. | The Balancing Authority may use a variable (linear or non-linear) bias value, which is based on a variable function of Tie Line deviation to Frequency Deviation. The Balancing Authority shall determine the variable frequency bias value by analyzing Frequency Response as it varies with factors such as load, generation, governor characteristics, and frequency. | LOWER | Retired | 2009-09-13 | 2015-03-31 | BA
BAL-003-0.1b | Frequency Response and Bias | R3. | Each Balancing Authority shall operate its Automatic Generation Control (AGC) on Tie Line Frequency Bias, unless such operation is adverse to system or Interconnection reliability. | MEDIUM | Retired | 2009-09-13 | 2015-03-31 | BA
BAL-003-0.1b | Frequency Response and Bias | R4. | Balancing Authorities that use Dynamic Scheduling or Pseudo-ties for jointly owned units shall reflect their respective share of the unit governor droop response in their respective Frequency Bias Setting. | LOWER | Retired | 2009-09-13 | 2015-03-31 | BA
BAL-003-0.1b | Frequency Response and Bias | R4.1. | Fixed schedules for Jointly Owned Units mandate that Balancing Authority (A) that contains the Jointly Owned Unit must incorporate the respective share of the unit governor droop response for any Balancing Authorities that have fixed schedules (B and C). See the diagram below. See Standard for Graphic. | LOWER | Retired | 2009-09-13 | 2015-03-31 | BA
BAL-003-0.1b | Frequency Response and Bias | R4.2. | The Balancing Authorities that have a fixed schedule (B and C) but do not contain the Jointly Owned Unit shall not include their share of the governor droop response in their Frequency Bias Setting. See Standard for Graphic. | LOWER | Retired | 2009-09-13 | 2015-03-31 | BA
BAL-003-0.1b | Frequency Response and Bias | R5. | Balancing Authorities that serve native load shall have a monthly average Frequency Bias Setting that is at least 1% of the Balancing Authority’s estimated yearly peak demand per 0.1 Hz change. | MEDIUM | Retired | 2009-09-13 | 2015-03-31 | BA
BAL-003-0.1b | Frequency Response and Bias | R5.1. | Balancing Authorities that do not serve native load shall have a monthly average Frequency Bias Setting that is at least 1% of its estimated maximum generation level in the coming year per 0.1 Hz change. | MEDIUM | Retired | 2009-09-13 | 2015-03-31 | BA
BAL-003-0.1b | Frequency Response and Bias | R6. | A Balancing Authority that is performing Overlap Regulation Service shall increase its Frequency Bias Setting to match the frequency response of the entire area being controlled. A Balancing Authority shall not change its Frequency Bias Setting when performing Supplemental Regulation Service. | MEDIUM | Retired | 2009-09-13 | 2015-03-31 | BA
BAL-003-1 | Frequency Response and Frequency Bias Setting | R1. | Each Frequency Response Sharing Group (FRSG) or Balancing Authority that is not a member of a FRSG shall achieve an annual Frequency Response Measure (FRM) (as calculated and reported in accordance with Attachment A) that is equal to or more negative than its Frequency Response Obligation (FRO) to ensure that sufficient Frequency Response is provided by each FRSG or BA that is not a member of a FRSG to maintain Interconnection Frequency Response equal to or more negative than the Interconnection Frequency Response Obligation. [Risk Factor: Medium ][Time Horizon: Real-time Operations] | HIGH | Retired | 2016-04-01 | 2015-11-12 | BA
BAL-003-1 | Frequency Response and Frequency Bias Setting | R2. | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting shall implement the Frequency Bias Setting determined in accordance with Attachment A, as validated by the ERO, into its Area Control Error (ACE) calculation during the implementation period specified by the ERO and shall use this Frequency Bias Setting until directed to change by the ERO. [Risk Factor:Medium ][Time Horizon: Operations Planning] | MEDIUM | Retired | 2015-04-01 | 2015-11-12 | BA
BAL-003-1 | Frequency Response and Frequency Bias Setting | R3. | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and is utilizing a variable Frequency Bias Setting shall maintain a Frequency Bias Setting that is: [Risk Factor: Medium ][Time Horizon: Operations Planning] 1.1 Less than zero at all times, and 1.2 Equal to or more negative than its Frequency Response Obligation when Frequency varies from 60 Hz by more than +/- 0.036 Hz. | MEDIUM | Retired | 2015-04-01 | 2015-11-12 | BA
BAL-003-1 | Frequency Response and Frequency Bias Setting | R4. | Each Balancing Authority that is performing Overlap Regulation Service shall modify its Frequency Bias Setting in its ACE calculation, in order to represent the Frequency Bias Setting for the combined Balancing Authority Area, to be equivalent to either: [Risk Factor: Medium ][Time Horizon: Operations Planning]  The sum of the Frequency Bias Settings as shown on FRS Form 1 and FRS Form 2 for the participating Balancing Authorities as validated by the ERO, or  The Frequency Bias Setting shown on FRS Form 1 and FRS Form 2 for the entirety of the participating Balancing Authorities’ Areas. | MEDIUM | Retired | 2015-04-01 | 2015-11-12 | BA
BAL-003-1.1 | Frequency Response and Frequency Bias Setting | R1. | Each Frequency Response Sharing Group (FRSG) or Balancing Authority that is not a member of a FRSG shall achieve an annual Frequency Response Measure (FRM) (as calculated and reported in accordance with Attachment A) that is equal to or more negative than its Frequency Response Obligation (FRO) to ensure that sufficient Frequency Response is provided by each FRSG or BA that is not a member of a FRSG to maintain Interconnection Frequency Response equal to or more negative than the Interconnection Frequency Response Obligation. [Risk Factor: High][Time Horizon: Real-time Operations] | HIGH | Retired | 2016-04-01 | 2020-12-31 | BA
BAL-003-1.1 | Frequency Response and Frequency Bias Setting | R2. | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting shall implement the Frequency Bias Setting determined in accordance with Attachment A, as validated by the ERO, into its Area Control Error (ACE) calculation during the implementation period specified by the ERO and shall use this Frequency Bias Setting until directed to change by the ERO. [Risk Factor: Medium ][Time Horizon: Operations Planning] | MEDIUM | Retired | 2015-11-13 | 2020-12-31 | BA
BAL-003-1.1 | Frequency Response and Frequency Bias Setting | R3. | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and is utilizing a variable Frequency Bias Setting shall maintain a Frequency Bias Setting that is: [Risk Factor: Medium ][Time Horizon: Operations Planning] | MEDIUM | Retired | 2015-11-13 | 2020-12-31 | BA
BAL-003-1.1 | Frequency Response and Frequency Bias Setting | R3.1. | Less than zero at all times, and | MEDIUM | Retired | 2015-11-13 | 2020-12-31 | BA
BAL-003-1.1 | Frequency Response and Frequency Bias Setting | R3.2. | Equal to or more negative than its Frequency Response Obligation when Frequency varies from 60 Hz by more than +/- 0.036 Hz. | MEDIUM | Retired | 2015-11-13 | 2020-12-31 | BA
BAL-003-1.1 | Frequency Response and Frequency Bias Setting | R4. | Each Balancing Authority that is performing Overlap Regulation Service shall modify its Frequency Bias Setting in its ACE calculation, in order to represent the Frequency Bias Setting for the combined Balancing Authority Area, to be equivalent to either: [Risk Factor: Medium ][Time Horizon: Operations Planning] ● The sum of the Frequency Bias Settings as shown on FRS Form 1 and FRS Form 2 for the participating Balancing Authorities as validated by the ERO, or ● The Frequency Bias Setting shown on FRS Form 1 and FRS Form 2 for the entirety of the participating Balancing Authorities’ Areas. | MEDIUM | Retired | 2015-11-13 | 2020-12-31 | BA
BAL-003-2 | Frequency Response and Frequency Bias Setting | R1. | Each Frequency Response Sharing Group (FRSG) or Balancing Authority that is not a member of a FRSG shall achieve an annual Frequency Response Measure (FRM) (as calculated and reported in accordance with Attachment A) that is equal to or more negative than its Frequency Response Obligation (FRO) to ensure that sufficient Frequency Response is provided by each FRSG or BA that is not a member of a FRSG to maintain Interconnection Frequency Response equal to or more negative than the Interconnection Frequency Response Obligation. [Risk Factor: High][Time Horizon: Real-time Operations] | HIGH | Effective | 2021-01-01 |  | BA
BAL-003-2 | Frequency Response and Frequency Bias Setting | R2. | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting shall implement the Frequency Bias Setting determined in BAL-003-2 – Frequency Response and Frequency Bias Setting Page 2 of 13 accordance with Attachment A, as validated by the ERO, into its Area Control Error (ACE) calculation during the implementation period specified by the ERO and shall use this Frequency Bias Setting until directed to change by the ERO. [Risk Factor: Medium][Time Horizon: Operations Planning] | MEDIUM | Effective | 2021-01-01
BAL-003-2 | Frequency Response and Frequency Bias Setting | R3. | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and is utilizing a variable Frequency Bias Setting shall maintain a Frequency Bias Setting that is: [Risk Factor: Medium][Time Horizon: Operations Planning] | MEDIUM | Effective | 2021-01-01
BAL-003-2 | Frequency Response and Frequency Bias Setting | R3.1. | Less than zero at all times, and | MEDIUM | Effective | 2021-01-01
BAL-003-2 | Frequency Response and Frequency Bias Setting | R3.2. | Equal to or more negative than its Frequency Response Obligation when Frequency varies from 60 Hz by more than +/- 0.036 Hz. | MEDIUM | Effective | 2021-01-01
BAL-003-2 | Frequency Response and Frequency Bias Setting | R4. | Each Balancing Authority that is performing Overlap Regulation Service shall modify its Frequency Bias Setting in its ACE calculation, in order to represent the Frequency Bias Setting for the combined Balancing Authority Area, to be equivalent to either: [Risk Factor: Medium][Time Horizon: Operations Planning]  The sum of the Frequency Bias Settings as shown on FRS Form 1 and FRS Form 2 for the participating Balancing Authorities as validated by the ERO, or  The Frequency Bias Setting shown on FRS Form 1 and FRS Form 2 for the entirety of the participating Balancing Authorities’ Areas. | MEDIUM | Effective | 2021-01-01
BAL-004-0 | Time Error Correction | R1. | Only a Reliability Coordinator shall be eligible to act as Interconnection Time Monitor. A single Reliability Coordinator in each Interconnection shall be designated by the NERC Operating Committee to serve as Interconnection Time Monitor. | LOWER | Retired | 2011-07-08 | 2017-04-01 | RC
BAL-004-0 | Time Error Correction | R2. | The Interconnection Time Monitor shall monitor Time Error and shall initiate or terminate corrective action orders in accordance with the NAESB Time Error Correction Procedure. | LOWER | Retired | 2011-07-08 | 2017-04-01 | RC
BAL-004-0 | Time Error Correction | R3. | Each Balancing Authority, when requested, shall participate in a Time Error Correction by one of the following methods: | MEDIUM | Retired | 2011-07-08 | 2017-04-01 | BA
BAL-004-0 | Time Error Correction | R3.1. | The Balancing Authority shall offset its frequency schedule by 0.02 Hertz, leaving the Frequency Bias Setting normal; or | LOWER | Retired | 2011-07-08 | 2017-04-01 | BA
BAL-004-0 | Time Error Correction | R3.2. | The Balancing Authority shall offset its Net Interchange Schedule (MW) by an amount equal to the computed bias contribution during a 0.02 Hertz Frequency Deviation (i.e. 20% of the Frequency Bias Setting). | LOWER | Retired | 2011-07-08 | 2017-04-01 | BA
BAL-004-0 | Time Error Correction | R4. | Any Reliability Coordinator in an Interconnection shall have the authority to request the Interconnection Time Monitor to terminate a Time Error Correction in progress, or a scheduled Time Error Correction that has not begun, for reliability considerations. | LOWER | Retired | 2011-07-08 | 2017-04-01 | RC
BAL-004-0 | Time Error Correction | R4.1. | Balancing Authorities that have reliability concerns with the execution of a Time Error Correction shall notify their Reliability Coordinator and request the termination of a Time Error Correction in progress. | LOWER | Retired | 2011-07-08 | 2017-04-01 | BA
BAL-005-0.2b | Automatic Generation Control | R1. | All generation, transmission, and load operating within an Interconnection must be included within the metered boundaries of a Balancing Authority Area. | No Individual VRF Assigned | Retired | 2012-10-10 | 2018-12-31 | TOP, GOP
BAL-005-0.2b | Automatic Generation Control | R1.1. | Each Generator Operator with generation facilities operating in an Interconnection shall ensure that those generation facilities are included within the metered boundaries of a Balancing Authority Area. | MEDIUM | Retired | 2012-10-10 | 2018-12-31 | GOP
BAL-005-0.2b | Automatic Generation Control | R1.2. | Each Transmission Operator with transmission facilities operating in an Interconnection shall ensure that those transmission facilities are included within the metered boundaries of a Balancing Authority Area. | MEDIUM | Retired | 2012-10-10 | 2018-12-31 | TOP
BAL-005-0.2b | Automatic Generation Control | R1.3. | Each Load-Serving Entity with load operating in an Interconnection shall ensure that those loads are included within the metered boundaries of a Balancing Authority Area. | MEDIUM | Retired | 2012-10-10 | 2018-12-31
BAL-005-0.2b | Automatic Generation Control | R10. | The Balancing Authority shall include all Dynamic Schedules in the calculation of Net Scheduled Interchange for the ACE equation. | HIGH | Retired | 2012-10-10 | 2018-12-31 | BA
BAL-005-0.2b | Automatic Generation Control | R11. | Balancing Authorities shall include the effect of ramp rates, which shall be identical and agreed to between affected Balancing Authorities, in the Scheduled Interchange values to calculate ACE. | MEDIUM | Retired | 2012-10-10 | 2018-12-31 | BA
BAL-005-0.2b | Automatic Generation Control | R12. | Each Balancing Authority shall include all Tie Line flows with Adjacent Balancing Authority Areas in the ACE calculation. | MEDIUM | Retired | 2012-10-10 | 2018-12-31 | BA
BAL-005-0.2b | Automatic Generation Control | R12.1. | Balancing Authorities that share a tie shall ensure Tie Line MW metering is telemetered to both control centers, and emanates from a common, agreed-upon source using common primary metering equipment. Balancing Authorities shall ensure that megawatt-hour data is telemetered or reported at the end of each hour. | LOWER | Retired | 2012-10-10 | 2018-12-31 | BA
BAL-005-0.2b | Automatic Generation Control | R12.2. | Balancing Authorities shall ensure the power flow and ACE signals that are utilized for calculating Balancing Authority performance or that are transmitted for Regulation Service are not filtered prior to transmission, except for the Anti-aliasing Filters of Tie Lines. | MEDIUM | Retired | 2012-10-10 | 2018-12-31 | BA
BAL-005-0.2b | Automatic Generation Control | R12.3. | Balancing Authorities shall install common metering equipment where Dynamic Schedules or Pseudo-Ties are implemented between two or more Balancing Authorities to deliver the output of Jointly Owned Units or to serve remote load. | MEDIUM | Retired | 2012-10-10 | 2018-12-31 | BA
BAL-005-0.2b | Automatic Generation Control | R13. | Each Balancing Authority shall perform hourly error checks using Tie Line megawatt-hour meters with common time synchronization to determine the accuracy of its control equipment. The Balancing Authority shall adjust the component (e.g., Tie Line meter) of ACE that is in error (if known) or use the interchange meter error (IME) term of the ACE equation to compensate for any equipment error until repairs can be made. | LOWER | Retired | 2012-10-10 | 2018-12-31 | BA
BAL-005-0.2b | Automatic Generation Control | R14. | The Balancing Authority shall provide its operating personnel with sufficient instrumentation and data recording equipment to facilitate monitoring of control performance, generation response, and after-the-fact analysis of area performance. As a minimum, the Balancing Authority shall provide its operating personnel with real-time values for ACE, Interconnection frequency and Net Actual Interchange with each Adjacent Balancing Authority Area. | LOWER | Retired | 2012-10-10 | 2018-12-31 | BA
BAL-005-0.2b | Automatic Generation Control | R15. | The Balancing Authority shall provide adequate and reliable backup power supplies and shall periodically test these supplies at the Balancing Authority’s control center and other critical locations to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power supply. | LOWER | Retired | 2012-10-10 | 2018-12-31 | BA
BAL-005-0.2b | Automatic Generation Control | R16. | The Balancing Authority shall sample data at least at the same periodicity with which ACE is calculated. The Balancing Authority shall flag missing or bad data for operator display and archival purposes. The Balancing Authority shall collect coincident data to the greatest practical extent, i.e., ACE, Interconnection frequency, Net Actual Interchange, and other data shall all be sampled at the same time. | MEDIUM | Retired | 2012-10-10 | 2018-12-31 | BA
BAL-005-0.2b | Automatic Generation Control | R17. | Each Balancing Authority shall at least annually check and calibrate its time error and frequency devices against a common reference. The Balancing Authority shall adhere to the minimum values for measuring devices as listed below: Device Accuracy Digital frequency transducer ≤ 0.001 Hz MW, MVAR, and voltage transducer ≤ 0.25 % of full scale Remote terminal unit ≤ 0.25 % of full scale Potential transformer ≤ 0.30 % of full scale Current transformer ≤ 0.50 % of full scale | MEDIUM | Retired | 2012-10-10 | 2018-12-31 | BA
BAL-005-0.2b | Automatic Generation Control | R3. | A Balancing Authority providing Regulation Service shall ensure that adequate metering, communications, and control equipment are employed to prevent such service from becoming a Burden on the Interconnection or other Balancing Authority Areas. | MEDIUM | Retired | 2012-10-10 | 2018-12-31 | BA
BAL-005-0.2b | Automatic Generation Control | R4. | A Balancing Authority providing Regulation Service shall notify the Host Balancing Authority for whom it is controlling if it is unable to provide the service, as well as any Intermediate Balancing Authorities. | MEDIUM | Retired | 2012-10-10 | 2018-12-31 | BA
BAL-005-0.2b | Automatic Generation Control | R5. | A Balancing Authority receiving Regulation Service shall ensure that backup plans are in place to provide replacement Regulation Service should the supplying Balancing Authority no longer be able to provide this service. | MEDIUM | Retired | 2012-10-10 | 2018-12-31 | BA
BAL-005-0.2b | Automatic Generation Control | R6. | The Balancing Authority’s AGC shall compare total Net Actual Interchange to total Net Scheduled Interchange plus Frequency Bias obligation to determine the Balancing Authority’s ACE. Single Balancing Authorities operating asynchronously may employ alternative ACE calculations such as (but not limited to) flat frequency control. If a Balancing Authority is unable to calculate ACE for more than 30 minutes it shall notify its Reliability Coordinator. | MEDIUM | Retired | 2012-10-10 | 2018-12-31 | BA
BAL-005-0.2b | Automatic Generation Control | R7. | The Balancing Authority shall operate AGC continuously unless such operation adversely impacts the reliability of the Interconnection. If AGC has become inoperative, the Balancing Authority shall use manual control to adjust generation to maintain the Net Scheduled Interchange. | MEDIUM | Retired | 2012-10-10 | 2018-12-31 | BA
BAL-005-0.2b | Automatic Generation Control | R8. | The Balancing Authority shall ensure that data acquisition for and calculation of ACE occur at least every six seconds. | MEDIUM | Retired | 2012-10-10 | 2018-12-31 | BA
BAL-005-0.2b | Automatic Generation Control | R8.1. | Each Balancing Authority shall provide redundant and independent frequency metering equipment that shall automatically activate upon detection of failure of the primary source. This overall installation shall provide a minimum availability of 99.95%. | MEDIUM | Retired | 2012-10-10 | 2018-12-31 | BA
BAL-005-0.2b | Automatic Generation Control | R9. | The Balancing Authority shall include all Interchange Schedules with Adjacent Balancing Authorities in the calculation of Net Scheduled Interchange for the ACE equation. | LOWER | Retired | 2012-10-10 | 2018-12-31 | BA
BAL-005-0.2b | Automatic Generation Control | R9.1. | Balancing Authorities with a high voltage direct current (HVDC) link to another Balancing Authority connected asynchronously to their Interconnection may choose to omit the Interchange Schedule related to the HVDC link from the ACE equation if it is modeled as internal generation or load. | LOWER | Retired | 2012-10-10 | 2018-12-31 | BA
BAL-005-1 | Balancing Authority Control | R1. | The Balancing Authority shall use a design scan rate of no more than six seconds in acquiring data necessary to calculate Reporting ACE. | MEDIUM | Effective | 2019-01-01 |  | BA
BAL-005-1 | Balancing Authority Control | R2. | A Balancing Authority that is unable to calculate Reporting ACE for more than 30-consecutive minutes shall notify its Reliability Coordinator within 45 minutes of the beginning of the inability to calculate Reporting ACE. | MEDIUM | Effective | 2019-01-01 |  | BA
BAL-005-1 | Balancing Authority Control | R3. | Each Balancing Authority shall use frequency metering equipment for the calculation of Reporting ACE: | MEDIUM | Effective | 2019-01-01 |  | BA
BAL-005-1 | Balancing Authority Control | R3.1. | that is available a minimum of 99.95% for each calendar year; and, | MEDIUM | Effective | 2019-01-01 |  | BA
BAL-005-1 | Balancing Authority Control | R3.2. | with a minimum accuracy of 0.001 Hz. | MEDIUM | Effective | 2019-01-01 |  | BA
BAL-005-1 | Balancing Authority Control | R4. | The Balancing Authority shall make available to the operator information associated with Reporting ACE including, but not limited to, quality flags indicating missing or invalid data. | MEDIUM | Effective | 2019-01-01 |  | BA
BAL-005-1 | Balancing Authority Control | R5. | Each Balancing Authority’s system used to calculate Reporting ACE shall be available a minimum of 99.5% of each calendar year. | MEDIUM | Effective | 2019-01-01 |  | BA
BAL-005-1 | Balancing Authority Control | R6. | Each Balancing Authority that is within a multiple Balancing Authority Interconnection shall implement an Operating Process to identify and mitigate errors affecting the accuracy of scan rate data used in the calculation of Reporting ACE for each Balancing Authority Area. | MEDIUM | Effective | 2019-01-01 |  | BA
BAL-005-1 | Balancing Authority Control | R7. | Each Balancing Authority shall ensure that each Tie-Line, Pseudo-Tie, and Dynamic Schedule with an Adjacent Balancing Authority is equipped with: | MEDIUM | Effective | 2019-01-01 |  | BA
BAL-005-1 | Balancing Authority Control | R7.1. | a common source to provide information to both Balancing Authorities for the scan rate values used in the calculation of Reporting ACE; and, | MEDIUM | Effective | 2019-01-01 |  | BA
BAL-005-1 | Balancing Authority Control | R7.2. | a time synchronized common source to determine hourly megawatt-hour values agreed-upon to aid in the identification and mitigation of errors. | MEDIUM | Effective | 2019-01-01 |  | BA
BAL-006-2 | Inadvertent Interchange | R1. | Each Balancing Authority shall calculate and record hourly Inadvertent Interchange. | LOWER | Retired | 2010-07-01 | 2018-12-31 | BA
BAL-006-2 | Inadvertent Interchange | R2. | Each Balancing Authority shall include all AC tie lines that connect to its Adjacent Balancing Authority Areas in its Inadvertent Interchange account. The Balancing Authority shall take into account interchange served by jointly owned generators. | LOWER | Retired | 2010-07-01 | 2018-12-31 | BA
BAL-006-2 | Inadvertent Interchange | R3. | Each Balancing Authority shall ensure all of its Balancing Authority Area interconnection points are equipped with common megawatt-hour meters, with readings provided hourly to the control centers of Adjacent Balancing Authorities. | LOWER | Retired | 2010-07-01 | 2018-12-31 | BA
BAL-006-2 | Inadvertent Interchange | R4. | Adjacent Balancing Authority Areas shall operate to a common Net Interchange Schedule and Actual Net Interchange value and shall record these hourly quantities, with like values but opposite sign. Each Balancing Authority shall compute its Inadvertent Interchange based on the following: | LOWER | Retired | 2010-07-01 | 2018-12-31 | BA
BAL-006-2 | Inadvertent Interchange | R4.1. | Each Balancing Authority, by the end of the next business day, shall agree with its Adjacent Balancing Authorities to: | LOWER | Retired | 2010-07-01 | 2018-12-31 | BA
BAL-006-2 | Inadvertent Interchange | R4.1.1. | The hourly values of Net Interchange Schedule. | LOWER | Retired | 2010-07-01 | 2018-12-31 | BA
BAL-006-2 | Inadvertent Interchange | R4.1.2. | The hourly integrated megawatt-hour values of Net Actual Interchange. | LOWER | Retired | 2010-07-01 | 2018-12-31 | BA
BAL-006-2 | Inadvertent Interchange | R4.2. | Each Balancing Authority shall use the agreed-to daily and monthly accounting data to compile its monthly accumulated Inadvertent Interchange for the On-Peak and Off-Peak hours of the month. | LOWER | Retired | 2010-07-01 | 2018-12-31 | BA
BAL-006-2 | Inadvertent Interchange | R4.3. | A Balancing Authority shall make after-the-fact corrections to the agreed-to daily and monthly accounting data only as needed to reflect actual operating conditions (e.g. a meter being used for control was sending bad data). Changes or corrections based on non-reliability considerations shall not be reflected in the Balancing Authority’s Inadvertent Interchange. After-the-fact corrections to scheduled or actual values will not be accepted without agreement of the Adjacent Balancing Authority(ies). | LOWER | Retired | 2010-07-01 | 2018-12-31 | BA
BAL-006-2 | Inadvertent Interchange | R5. | Adjacent Balancing Authorities that cannot mutually agree upon their respective Net Actual Interchange or Net Scheduled Interchange quantities by the 15th calendar day of the following month shall, for the purposes of dispute resolution, submit a report to their respective Regional Reliability Organization Survey Contact. The report shall describe the nature and the cause of the dispute as well as a process for correcting the discrepancy. | LOWER | Retired | 2010-07-01 | 2018-12-31 | BA
CIP-002-3 | Cyber Security - Critical Cyber Asset Identification | R1. | Critical Asset Identification Method — The Responsible Entity shall identify and document a risk-based assessment methodology to use to identify its Critical Assets. | MEDIUM | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3 | Cyber Security - Critical Cyber Asset Identification | R1.1. | The Responsible Entity shall maintain documentation describing its risk-based assessment methodology that includes procedures and evaluation criteria. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3 | Cyber Security - Critical Cyber Asset Identification | R1.2. | The risk-based assessment shall consider the following assets: | MEDIUM | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3 | Cyber Security - Critical Cyber Asset Identification | R1.2.1. | Control centers and backup control centers performing the functions of the entities listed in the Applicability section of this standard. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3 | Cyber Security - Critical Cyber Asset Identification | R1.2.2. | Transmission substations that support the reliable operation of the Bulk Electric System. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3 | Cyber Security - Critical Cyber Asset Identification | R1.2.3. | Generation resources that support the reliable operation of the Bulk Electric System. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3 | Cyber Security - Critical Cyber Asset Identification | R1.2.4. | Systems and facilities critical to system restoration, including blackstart generators and substations in the electrical path of transmission lines used for initial system restoration. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3 | Cyber Security - Critical Cyber Asset Identification | R1.2.5. | Systems and facilities critical to automatic load shedding under a common control system capable of shedding 300 MW or more. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3 | Cyber Security - Critical Cyber Asset Identification | R1.2.6. | Special Protection Systems that support the reliable operation of the Bulk Electric System. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3 | Cyber Security - Critical Cyber Asset Identification | R1.2.7. | Any additional assets that support the reliable operation of the Bulk Electric System that the Responsible Entity deems appropriate to include in its assessment. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3 | Cyber Security - Critical Cyber Asset Identification | R2. | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the risk-based assessment methodology required in R1. The Responsible Entity shall review this list at least annually, and update it as necessary. | HIGH | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3 | Cyber Security - Critical Cyber Asset Identification | R3. | Critical Cyber Asset Identification — Using the list of Critical Assets developed pursuant to Requirement R2, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. Examples at control centers and backup control centers include systems and facilities at master and remote sites that provide monitoring and control, automatic generation control, real-time power system modeling, and real-time inter-utility data exchange. The Responsible Entity shall review this list at least annually, and update it as necessary. For the purpose of Standard CIP-002-3, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: | HIGH | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3 | Cyber Security - Critical Cyber Asset Identification | R3.1. | The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3 | Cyber Security - Critical Cyber Asset Identification | R3.2. | The Cyber Asset uses a routable protocol within a control center; or, | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3 | Cyber Security - Critical Cyber Asset Identification | R3.3. | The Cyber Asset is dial-up accessible. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3 | Cyber Security - Critical Cyber Asset Identification | R4. | Annual Approval — The senior manager or delegate(s) shall approve annually the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1, R2, and R3 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3(i) | Cyber Security - Critical Cyber Asset Identification | R1. | Critical Asset Identification Method — The Responsible Entity shall identify and document a risk-based assessment methodology to use to identify its Critical Assets. | MEDIUM | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3(i) | Cyber Security - Critical Cyber Asset Identification | R1.1. | The Responsible Entity shall maintain documentation describing its risk-based assessment methodology that includes procedures and evaluation criteria. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3(i) | Cyber Security - Critical Cyber Asset Identification | R1.2. | The risk-based assessment shall consider the following assets: | MEDIUM | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3(i) | Cyber Security - Critical Cyber Asset Identification | R1.2.1. | Control centers and backup control centers performing the functions of the entities listed in the Applicability section of this standard. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3(i) | Cyber Security - Critical Cyber Asset Identification | R1.2.2. | Transmission substations that support the reliable operation of the Bulk Electric System. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3(i) | Cyber Security - Critical Cyber Asset Identification | R1.2.3. | Generation resources that support the reliable operation of the Bulk Electric System. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3(i) | Cyber Security - Critical Cyber Asset Identification | R1.2.4. | Systems and facilities critical to system restoration, including blackstart generators and substations in the electrical path of transmission lines used for initial system restoration. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3(i) | Cyber Security - Critical Cyber Asset Identification | R1.2.5. | Systems and facilities critical to automatic load shedding under a common control system capable of shedding 300 MW or more. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3(i) | Cyber Security - Critical Cyber Asset Identification | R1.2.6. | Remedial Action Schemes that support the reliable operation of the Bulk Electric System. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3(i) | Cyber Security - Critical Cyber Asset Identification | R1.2.7. | Any additional assets that support the reliable operation of the Bulk Electric System that the Responsible Entity deems appropriate to include in its assessment. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3(i) | Cyber Security - Critical Cyber Asset Identification | R2. | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the risk-based assessment methodology required in R1. The Responsible Entity shall review this list at least annually, and update it as necessary. | HIGH | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3(i) | Cyber Security - Critical Cyber Asset Identification | R3. | Critical Cyber Asset Identification— Using the list of Critical Assets developed pursuant to Requirement R2, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. Examples at control centers and backup control centers include systems and facilities at master and remote sites that provide monitoring and control, automatic generation control, real-time power system modeling, and real-time inter-utility data exchange. The Responsible Entity shall review this list at least annually, and update it as necessary. For the purpose of Standard CIP-002-3(i), Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: | HIGH | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3(i) | Cyber Security - Critical Cyber Asset Identification | R3.1. | The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3(i) | Cyber Security - Critical Cyber Asset Identification | R3.2. | The Cyber Asset uses a routable protocol within a control center; or, | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3(i) | Cyber Security - Critical Cyber Asset Identification | R3.3. | The Cyber Asset is dial-up accessible. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3(i) | Cyber Security - Critical Cyber Asset Identification | R4. | Annual Approval — The senior manager or delegate(s) shall approve annually the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1, R2, and R3 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3(i)b | Cyber Security - Critical Cyber Asset Identification | R1. | Critical Asset Identification Method — The Responsible Entity shall identify and document a risk-based assessment methodology to use to identify its Critical Assets. | MEDIUM | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3(i)b | Cyber Security - Critical Cyber Asset Identification | R1.1. | The Responsible Entity shall maintain documentation describing its risk-based assessment methodology that includes procedures and evaluation criteria. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3(i)b | Cyber Security - Critical Cyber Asset Identification | R1.2. | The risk-based assessment shall consider the following assets: | MEDIUM | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3(i)b | Cyber Security - Critical Cyber Asset Identification | R1.2.1. | Control centers and backup control centers performing the functions of the entities listed in the Applicability section of this standard. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3(i)b | Cyber Security - Critical Cyber Asset Identification | R1.2.2. | Transmission substations that support the reliable operation of the Bulk Electric System. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3(i)b | Cyber Security - Critical Cyber Asset Identification | R1.2.3. | Generation resources that support the reliable operation of the Bulk Electric System. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3(i)b | Cyber Security - Critical Cyber Asset Identification | R1.2.4. | Systems and facilities critical to system restoration, including blackstart generators and substations in the electrical path of transmission lines used for initial system restoration. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3(i)b | Cyber Security - Critical Cyber Asset Identification | R1.2.5. | Systems and facilities critical to automatic load shedding under a common control system capable of shedding 300 MW or more. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3(i)b | Cyber Security - Critical Cyber Asset Identification | R1.2.6. | Remedial Action Schemes that support the reliable operation of the Bulk Electric System. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3(i)b | Cyber Security - Critical Cyber Asset Identification | R1.2.7. | Any additional assets that support the reliable operation of the Bulk Electric System that the Responsible Entity deems appropriate to include in its assessment. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3(i)b | Cyber Security - Critical Cyber Asset Identification | R2. | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the risk-based assessment methodology required in R1. The Responsible Entity shall review this list at least annually, and update it as necessary. | HIGH | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3(i)b | Cyber Security - Critical Cyber Asset Identification | R3. | Critical Cyber Asset Identification — Using the list of Critical Assets developed pursuant to Requirement R2, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. Examples at control centers and backup control centers include systems and facilities at master and remote sites that provide monitoring and control, automatic generation control, real-time power system modeling, and real-time inter-utility data exchange. The Responsible Entity shall review this list at least annually, and update it as necessary. For the purpose of Standard CIP-002-3(i)b, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: | HIGH | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3(i)b | Cyber Security - Critical Cyber Asset Identification | R3.1. | The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3(i)b | Cyber Security - Critical Cyber Asset Identification | R3.2. | The Cyber Asset uses a routable protocol within a control center; or, | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3(i)b | Cyber Security - Critical Cyber Asset Identification | R3.3. | The Cyber Asset is dial-up accessible. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3(i)b | Cyber Security - Critical Cyber Asset Identification | R4. | Annual Approval — The senior manager or delegate(s) shall approve annually the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1, R2, and R3 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3a | Cyber Security - Critical Cyber Asset Identification | R1. | Critical Asset Identification Method —The Responsible Entity shall identify and document a risk-based assessment methodology to use to identify its Critical Assets. | MEDIUM | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3a | Cyber Security - Critical Cyber Asset Identification | R1.1. | The Responsible Entity shall maintain documentation describing its risk-based assessment methodology that includes procedures and evaluation criteria. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3a | Cyber Security - Critical Cyber Asset Identification | R1.2. | The risk-based assessment shall consider the following assets: | MEDIUM | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3a | Cyber Security - Critical Cyber Asset Identification | R1.2.1. | Control centers and backup control centers performing the functions of the entities listed in the Applicability section of this standard. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3a | Cyber Security - Critical Cyber Asset Identification | R1.2.2. | Transmission substations that support the reliable operation of the Bulk Electric System | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3a | Cyber Security - Critical Cyber Asset Identification | R1.2.3. | Generation resources that support the reliable operation of the Bulk Electric System | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3a | Cyber Security - Critical Cyber Asset Identification | R1.2.4. | Systems and facilities critical to system restoration, including blackstart generators and substations in the electrical path of transmission lines used for initial system restoration. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3a | Cyber Security - Critical Cyber Asset Identification | R1.2.5. | Systems and facilities critical to automatic load shedding under a common control system capable of shedding 300 MW or more. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3a | Cyber Security - Critical Cyber Asset Identification | R1.2.6. | Special Protection Systems that support the reliable operation of the Bulk Electric System. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3a | Cyber Security - Critical Cyber Asset Identification | R1.2.7. | Any additional assets that support the reliable operation of the Bulk Electric System that the Responsible Entity deems appropriate to include in its assessment. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3a | Cyber Security - Critical Cyber Asset Identification | R2. | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the risk-based assessment methodology required in R1. The Responsible Entity shall review this list at least annually, and update it as necessary. | HIGH | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3a | Cyber Security - Critical Cyber Asset Identification | R3. | Critical Cyber Asset Identification — Using the list of Critical Assets developed pursuant to Requirement R2, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. Examples at control centers and backup control centers include systems and facilities at master and remote sites that provide monitoring and control, automatic generation control, real-time power system modeling, and real-time interutility data exchange. The Responsible Entity shall review this list at least annually, and update it as necessary. For the purpose of Standard CIP-002-3, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: | HIGH | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3a | Cyber Security - Critical Cyber Asset Identification | R3.1. | The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3a | Cyber Security - Critical Cyber Asset Identification | R3.2. | The Cyber Asset uses a routable protocol within a control center; or, | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3a | Cyber Security - Critical Cyber Asset Identification | R3.3. | The Cyber Asset is dial-up accessible. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3a | Cyber Security - Critical Cyber Asset Identification | R4. | Annual Approval —The senior manager or delegate(s) shall approve annually the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1, R2, and R3 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-3b | Cyber Security - Critical Cyber Asset Identification | R1. | Critical Asset Identification Method — The Responsible Entity shall identify and document a risk-based assessment methodology to use to identify its Critical Assets. |  | Never Came Into Effect in Ontario |  |  | TOP, TO, RC, GOP, GO, BA
CIP-002-3b | Cyber Security - Critical Cyber Asset Identification | R1.1. | The Responsible Entity shall maintain documentation describing its risk-based assessment methodology that includes procedures and evaluation criteria. |  | Never Came Into Effect in Ontario |  |  | TOP, TO, RC, GOP, GO, BA
CIP-002-3b | Cyber Security - Critical Cyber Asset Identification | R1.2. | The risk-based assessment shall consider the following assets: |  | Never Came Into Effect in Ontario |  |  | TOP, TO, RC, GOP, GO, BA
CIP-002-3b | Cyber Security - Critical Cyber Asset Identification | R1.2.1. | Control centers and backup control centers performing the functions of the entities listed in the Applicability section of this standard. |  | Never Came Into Effect in Ontario |  |  | TOP, TO, RC, GOP, GO, BA
CIP-002-3b | Cyber Security - Critical Cyber Asset Identification | R1.2.2. | Transmission substations that support the reliable operation of the Bulk Electric System. |  | Never Came Into Effect in Ontario |  |  | TOP, TO, RC, GOP, GO, BA
CIP-002-3b | Cyber Security - Critical Cyber Asset Identification | R1.2.3. | Generation resources that support the reliable operation of the Bulk Electric System. |  | Never Came Into Effect in Ontario |  |  | TOP, TO, RC, GOP, GO, BA
CIP-002-3b | Cyber Security - Critical Cyber Asset Identification | R1.2.4. | Systems and facilities critical to system restoration, including blackstart generators and substations in the electrical path of transmission lines used for initial system restoration. |  | Never Came Into Effect in Ontario |  |  | TOP, TO, RC, GOP, GO, BA
CIP-002-3b | Cyber Security - Critical Cyber Asset Identification | R1.2.5. | Systems and facilities critical to automatic load shedding under a common control system capable of shedding 300 MW or more. |  | Never Came Into Effect in Ontario |  |  | TOP, TO, RC, GOP, GO, BA
CIP-002-3b | Cyber Security - Critical Cyber Asset Identification | R1.2.6. | Special Protection Systems that support the reliable operation of the Bulk Electric System. |  | Never Came Into Effect in Ontario |  |  | TOP, TO, RC, GOP, GO, BA
CIP-002-3b | Cyber Security - Critical Cyber Asset Identification | R1.2.7. | Any additional assets that support the reliable operation of the Bulk Electric System that the Responsible Entity deems appropriate to include in its assessment. |  | Never Came Into Effect in Ontario |  |  | TOP, TO, RC, GOP, GO, BA
CIP-002-3b | Cyber Security - Critical Cyber Asset Identification | R2. | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the risk-based assessment methodology required in R1. The Responsible Entity shall review this list at least annually, and update it as necessary. |  | Never Came Into Effect in Ontario |  |  | TOP, TO, RC, GOP, GO, BA
CIP-002-3b | Cyber Security - Critical Cyber Asset Identification | R3. | Critical Cyber Asset Identification — Using the list of Critical Assets developed pursuant to Requirement R2, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. Examples at control centers and backup control centers include systems and facilities at master and remote sites that provide monitoring and control, automatic generation control, real-time power system modeling, and real-time inter-utility data exchange. The Responsible Entity shall review this list at least annually, and update it as necessary. For the purpose of Standard CIP-002-3, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: |  | Never Came Into Effect in Ontario |  |  | TOP, TO, RC, GOP, GO, BA
CIP-002-3b | Cyber Security - Critical Cyber Asset Identification | R3.1. | The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, |  | Never Came Into Effect in Ontario |  |  | TOP, TO, RC, GOP, GO, BA
CIP-002-3b | Cyber Security - Critical Cyber Asset Identification | R3.2. | The Cyber Asset uses a routable protocol within a control center; or, |  | Never Came Into Effect in Ontario |  |  | TOP, TO, RC, GOP, GO, BA
CIP-002-3b | Cyber Security - Critical Cyber Asset Identification | R3.3. | The Cyber Asset is dial-up accessible. |  | Never Came Into Effect in Ontario |  |  | TOP, TO, RC, GOP, GO, BA
CIP-002-3b | Cyber Security - Critical Cyber Asset Identification | R4. | Annual Approval — The senior manager or delegate(s) shall approve annually the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1, R2, and R3 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) |  | Never Came Into Effect in Ontario |  |  | TOP, TO, RC, GOP, GO, BA
CIP-002-4 | Cyber Security — Critical Cyber Asset Identification | R1. | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the criteria contained in CIP-002-4 Attachment 1 – Critical Asset Criteria. The Responsible Entity shall update this list as necessary, and review it at least annually. | HIGH | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-4 | Cyber Security — Critical Cyber Asset Identification | R2. | Critical Cyber Asset Identification— Using the list of Critical Assets developed pursuant to Requirement R1, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. The Responsible Entity shall update this list as necessary, and review it at least annually. For each group of generating units (including nuclear generation) at a single plant location identified in Attachment 1, criterion 1.1, the only Cyber Assets that must be considered are those shared Cyber Assets that could, within 15 minutes, adversely impact the reliable operation of any combination of units that in aggregate equal or exceed Attachment 1, criterion 1.1. For the purpose of Standard CIP-002-4, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: • The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, • The Cyber Asset uses a routable protocol within a control center; or, • The Cyber Asset is dial-up accessible. | HIGH | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-4 | Cyber Security — Critical Cyber Asset Identification | R3. | Annual Approval —The senior manager or delegate(s) shall approve annually the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1 and R2 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-4a | Cyber Security — Critical Cyber Asset Identification | R1. | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the criteria contained in CIP-002-4 Attachment 1 – Critical Asset Criteria. The Responsible Entity shall update this list as necessary, and review it at least annually. |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-4a | Cyber Security — Critical Cyber Asset Identification | R2. | Critical Cyber Asset Identification— Using the list of Critical Assets developed pursuant to Requirement R1, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. The Responsible Entity shall update this list as necessary, and review it at least annually. For each group of generating units (including nuclear generation) at a single plant location identified in Attachment 1, criterion 1.1, the only Cyber Assets that must be considered are those shared Cyber Assets that could, within 15 minutes, adversely impact the reliable operation of any combination of units that in aggregate equal or exceed Attachment 1, criterion 1.1. For the purpose of Standard CIP-002-4, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: • The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, • The Cyber Asset uses a routable protocol within a control center; or, • The Cyber Asset is dial-up accessible. |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-4a | Cyber Security — Critical Cyber Asset Identification | R3. | Annual Approval —The senior manager or delegate(s) shall approve annually the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1 and R2 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-002-5 | Cyber Security — BES Cyber System Categorization | R1. | Each Responsible Entity shall implement a process that considers each of the following assets for purposes of parts 1.1 through 1.3: [Violation Risk Factor: High][Time Horizon: Operations Planning] i.Control Centers and backup Control Centers; ii.Transmission stations and substations; iii.Generation resources; iv.Systems and facilities critical to system restoration, including Blackstart Resources and Cranking Paths and initial switching requirements; v.Special Protection Systems that support the reliable operation of the Bulk Electric System; and vi.For Distribution Providers, Protection Systems specified in Applicability section 4.2.1 above. | HIGH | Never Came Into Effect in Ontario |  |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-002-5 | Cyber Security — BES Cyber System Categorization | R1.1. | 1.1. Identify each of the high impact BES Cyber Systems according to Attachment 1, Section 1, if any, at each asset; | HIGH | Never Came Into Effect in Ontario |  |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-002-5 | Cyber Security — BES Cyber System Categorization | R1.2. | 1.2. Identify each of the medium impact BES Cyber Systems according to Attachment 1, Section 2, if any, at each asset; and | HIGH | Never Came Into Effect in Ontario |  |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-002-5 | Cyber Security — BES Cyber System Categorization | R1.3. | 1.3. Identify each asset that contains a low impact BES Cyber System according to Attachment 1, Section 3, if any (a discrete list of low impact BES Cyber Systems is not required). | HIGH | Never Came Into Effect in Ontario |  |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-002-5 | Cyber Security — BES Cyber System Categorization | R2. | The Responsible Entity shall: [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Never Came Into Effect in Ontario |  |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-002-5 | Cyber Security — BES Cyber System Categorization | R2.1. | 2.1 Review the identifications in Requirement R1 and its parts (and update them if there are changes identified) at least once every 15 calendar months, even if it has no identified items in Requirement R1, and | LOWER | Never Came Into Effect in Ontario |  |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-002-5 | Cyber Security — BES Cyber System Categorization | R2.2. | 2.2 Have its CIP Senior Manager or delegate approve the identifications required by Requirement R1 at least once every 15 calendar months, even if it has no identified items in Requirement R1. | LOWER | Never Came Into Effect in Ontario |  |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-002-5.1 | Cyber Security — BES Cyber System Categorization | R1. | Each Responsible Entity shall implement a process that considers each of the following assets for purposes of parts 1.1 through 1.3: [Violation Risk Factor: High][Time Horizon: Operations Planning] i.Control Centers and backup Control Centers; ii.Transmission stations and substations; iii.Generation resources; iv.Systems and facilities critical to system restoration, including Blackstart Resources and Cranking Paths and initial switching requirements; v.Special Protection Systems that support the reliable operation of the Bulk Electric System; and vi.For Distribution Providers, Protection Systems specified in Applicability section 4.2.1 above. | HIGH | Retired |  |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-002-5.1 | Cyber Security — BES Cyber System Categorization | R1.1. | Identify each of the high impact BES Cyber Systems according to Attachment 1, Section 1, if any, at each asset; | HIGH | Retired |  |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-002-5.1 | Cyber Security — BES Cyber System Categorization | R1.2. | Identify each of the medium impact BES Cyber Systems according to Attachment 1, Section 2, if any, at each asset; and | HIGH | Retired |  |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-002-5.1 | Cyber Security — BES Cyber System Categorization | R1.3. | Identify each asset that contains a low impact BES Cyber System according to Attachment 1, Section 3, if any (a discrete list of low impact BES Cyber Systems is not required). | HIGH | Retired |  |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-002-5.1 | Cyber Security — BES Cyber System Categorization | R2. | The Responsible Entity shall: [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Retired |  |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-002-5.1 | Cyber Security — BES Cyber System Categorization | R2.1. | Review the identifications in Requirement R1 and its parts (and update them if there are changes identified) at least once every 15 calendar months, even if it has no identified items in Requirement R1, and | LOWER | Retired |  |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-002-5.1 | Cyber Security — BES Cyber System Categorization | R2.2. | Have its CIP Senior Manager or delegate approve the identifications required by Requirement R1 at least once every 15 calendar months, even if it has no identified items in Requirement R1. | LOWER | Retired |  |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-002-5.1a | Cyber Security — BES Cyber System Categorization | R1. | Each Responsible Entity shall implement a process that considers each of the following assets for purposes of parts 1.1 through 1.3: [Violation Risk Factor: High][Time Horizon: Operations Planning] i.Control Centers and backup Control Centers; ii.Transmission stations and substations; iii.Generation resources; iv.Systems and facilities critical to system restoration, including Blackstart Resources and Cranking Paths and initial switching requirements; v.Special Protection Systems that support the reliable operation of the Bulk Electric System; and vi.For Distribution Providers, Protection Systems specified in Applicability section 4.2.1 above. | HIGH | Effective |  |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-002-5.1a | Cyber Security — BES Cyber System Categorization | R1.1. | Identify each of the high impact BES Cyber Systems according to Attachment 1, Section 1, if any, at each asset; | HIGH | Effective |  |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-002-5.1a | Cyber Security — BES Cyber System Categorization | R1.2. | Identify each of the medium impact BES Cyber Systems according to Attachment 1, Section 2, if any, at each asset; and | HIGH | Effective |  |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-002-5.1a | Cyber Security — BES Cyber System Categorization | R1.3. | Identify each asset that contains a low impact BES Cyber System according to Attachment 1, Section 3, if any (a discrete list of low impact BES Cyber Systems is not required). | HIGH | Effective |  |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-002-5.1a | Cyber Security — BES Cyber System Categorization | R2. | The Responsible Entity shall: [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Effective |  |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-002-5.1a | Cyber Security — BES Cyber System Categorization | R2.1. | Review the identifications in Requirement R1 and its parts (and update them if there are changes identified) at least once every 15 calendar months, even if it has no identified items in Requirement R1, and | LOWER | Effective |  |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-002-5.1a | Cyber Security — BES Cyber System Categorization | R2.2. | Have its CIP Senior Manager or delegate approve the identifications required by Requirement R1 at least once every 15 calendar months, even if it has no identified items in Requirement R1. | LOWER | Effective |  |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-003-3 | Cyber Security - Security Management Controls | R1. | Cyber Security Policy — The Responsible Entity shall document and implement a cyber security policy that represents management’s commitment and ability to secure its Critical Cyber Assets. The Responsible Entity shall, at minimum, ensure the following: | MEDIUM | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-3 | Cyber Security - Security Management Controls | R1.1. | The cyber security policy addresses the requirements in Standards CIP-002-3 through CIP-009-3, including provision for emergency situations. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-3 | Cyber Security - Security Management Controls | R1.3. | Annual review and approval of the cyber security policy by the senior manager assigned pursuant to R2. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-3 | Cyber Security - Security Management Controls | R2. | Leadership — The Responsible Entity shall assign a single senior manager with overall responsibility and authority for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002-3 through CIP-009-3. | MEDIUM | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-3 | Cyber Security - Security Management Controls | R2.1. | The senior manager shall be identified by name, title, and date of designation. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-3 | Cyber Security - Security Management Controls | R2.2. | Changes to the senior manager must be documented within thirty calendar days of the effective date. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-3 | Cyber Security - Security Management Controls | R2.3. | Where allowed by Standards CIP-002-3 through CIP-009-3, the senior manager may delegate authority for specific actions to a named delegate or delegates. These delegations shall be documented in the same manner as R2.1 and R2.2, and approved by the senior manager. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-3 | Cyber Security - Security Management Controls | R2.4. | The senior manager or delegate(s), shall authorize and document any exception from the requirements of the cyber security policy. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-3 | Cyber Security - Security Management Controls | R4. | Information Protection — The Responsible Entity shall implement and document a program to identify, classify, and protect information associated with Critical Cyber Assets. | MEDIUM | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-3 | Cyber Security - Security Management Controls | R4.1. | The Critical Cyber Asset information to be protected shall include, at a minimum and regardless of media type, operational procedures, lists as required in Standard CIP-002-3, network topology or similar diagrams, floor plans of computing centers that contain Critical Cyber Assets, equipment layouts of Critical Cyber Assets, disaster recovery plans, incident response plans, and security configuration information. | MEDIUM | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-3 | Cyber Security - Security Management Controls | R4.3. | The Responsible Entity shall, at least annually, assess adherence to its Critical Cyber Asset information protection program, document the assessment results, and implement an action plan to remediate deficiencies identified during the assessment. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-3 | Cyber Security - Security Management Controls | R5. | Access Control — The Responsible Entity shall document and implement a program for managing access to protected Critical Cyber Asset information. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-3 | Cyber Security - Security Management Controls | R5.1. | The Responsible Entity shall maintain a list of designated personnel who are responsible for authorizing logical or physical access to protected information. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-3 | Cyber Security - Security Management Controls | R5.1.1. | Personnel shall be identified by name, title, and the information for which they are responsible for authorizing access. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-3 | Cyber Security - Security Management Controls | R5.1.2. | The list of personnel responsible for authorizing access to protected information shall be verified at least annually. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-3 | Cyber Security - Security Management Controls | R5.2. | The Responsible Entity shall review at least annually the access privileges to protected information to confirm that access privileges are correct and that they correspond with the Responsible Entity’s needs and appropriate personnel roles and responsibilities. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-3 | Cyber Security - Security Management Controls | R5.3. | The Responsible Entity shall assess and document at least annually the processes for controlling access privileges to protected information. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-3 | Cyber Security - Security Management Controls | R6. | Change Control and Configuration Management — The Responsible Entity shall establish and document a process of change control and configuration management for adding, modifying, replacing, or removing Critical Cyber Asset hardware or software, and implement supporting configuration management activities to identify, control and document all entity or vendor-related changes to hardware and software components of Critical Cyber Assets pursuant to the change control process. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-3a | Cyber Security - Security Management Controls | R1. | Cyber Security Policy — The Responsible Entity shall document and implement a cyber security policy that represents management’s commitment and ability to secure its Critical Cyber Assets. The Responsible Entity shall, at minimum, ensure the following: | MEDIUM | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-3a | Cyber Security - Security Management Controls | R1.1. | The cyber security policy addresses the requirements in Standards CIP-002-3 through CIP-009-3, including provision for emergency situations. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-3a | Cyber Security - Security Management Controls | R1.2. | The cyber security policy is readily available to all personnel who have access to, or are responsible for, Critical Cyber Assets. (Retirement approved by FERC effective January 21, 2014.) | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-3a | Cyber Security - Security Management Controls | R1.3. | Annual review and approval of the cyber security policy by the senior manager assigned pursuant to R2. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-3a | Cyber Security - Security Management Controls | R2. | Leadership — The Responsible Entity shall assign a single senior manager with overall responsibility and authority for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002-3 through CIP-009-3. | MEDIUM | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-3a | Cyber Security - Security Management Controls | R2.1. | The senior manager shall be identified by name, title, and date of designation. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-3a | Cyber Security - Security Management Controls | R2.2. | Changes to the senior manager must be documented within thirty calendar days of the effective date. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-3a | Cyber Security - Security Management Controls | R2.3. | Where allowed by Standards CIP-002-3 through CIP-009-3, the senior manager may delegate authority for specific actions to a named delegate or delegates. These delegations shall be documented in the same manner as R2.1 and R2.2, and approved by the senior manager. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-3a | Cyber Security - Security Management Controls | R2.4. | The senior manager or delegate(s), shall authorize and document any exception from the requirements of the cyber security policy. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-3a | Cyber Security - Security Management Controls | R3. | Exceptions — Instances where the Responsible Entity cannot conform to its cyber security policy must be documented as exceptions and authorized by the senior manager or delegate(s). (Retirement approved by FERC effective January 21, 2014.) | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-3a | Cyber Security - Security Management Controls | R3.1. | Exceptions to the Responsible Entity’s cyber security policy must be documented within thirty days of being approved by the senior manager or delegate(s). (Retirement approved by FERC effective January 21, 2014.) | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-3a | Cyber Security - Security Management Controls | R3.2. | Documented exceptions to the cyber security policy must include an explanation as to why the exception is necessary and any compensating measures. (Retirement approved by FERC effective January 21, 2014.) | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-3a | Cyber Security - Security Management Controls | R3.3. | Authorized exceptions to the cyber security policy must be reviewed and approved annually by the senior manager or delegate(s) to ensure the exceptions are still required and valid. Such review and approval shall be documented. (Retirement approved by FERC effective January 21, 2014.) | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-3a | Cyber Security - Security Management Controls | R4. | Information Protection — The Responsible Entity shall implement and document a program to identify, classify, and protect information associated with Critical Cyber Assets. | MEDIUM | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-3a | Cyber Security - Security Management Controls | R4.1. | The Critical Cyber Asset information to be protected shall include, at a minimum and regardless of media type, operational procedures, lists as required in Standard CIP- 002-3, network topology or similar diagrams, floor plans of computing centers that contain Critical Cyber Assets, equipment layouts of Critical Cyber Assets, disaster recovery plans, incident response plans, and security configuration information. | MEDIUM | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-3a | Cyber Security - Security Management Controls | R4.2. | The Responsible Entity shall classify information to be protected under this program based on the sensitivity of the Critical Cyber Asset information. (Retirement approved by FERC effective January 21, 2014.) | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-3a | Cyber Security - Security Management Controls | R4.3. | The Responsible Entity shall, at least annually, assess adherence to its Critical Cyber Asset information protection program, document the assessment results, and implement an action plan to remediate deficiencies identified during the assessment. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-3a | Cyber Security - Security Management Controls | R5. | Access Control — The Responsible Entity shall document and implement a program for managing access to protected Critical Cyber Asset information. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-3a | Cyber Security - Security Management Controls | R5.1. | The Responsible Entity shall maintain a list of designated personnel who are responsible for authorizing logical or physical access to protected information. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-3a | Cyber Security - Security Management Controls | R5.1.1. | Personnel shall be identified by name, title, and the information for which they are responsible for authorizing access. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-3a | Cyber Security - Security Management Controls | R5.1.2. | The list of personnel responsible for authorizing access to protected information shall be verified at least annually. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-3a | Cyber Security - Security Management Controls | R5.2. | The Responsible Entity shall review at least annually the access privileges to protected information to confirm that access privileges are correct and that they correspond with the Responsible Entity’s needs and appropriate personnel roles and responsibilities. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-3a | Cyber Security - Security Management Controls | R5.3. | The Responsible Entity shall assess and document at least annually the processes for controlling access privileges to protected information. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-3a | Cyber Security - Security Management Controls | R6. | Change Control and Configuration Management — The Responsible Entity shall establish and document a process of change control and configuration management for adding, modifying, replacing, or removing Critical Cyber Asset hardware or software, and implement supporting configuration management activities to identify, control and document all entity or vendorrelated changes to hardware and software components of Critical Cyber Assets pursuant to the change control process. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-4 | Cyber Security — Security Management Controls | R1. | Cyber Security Policy —The Responsible Entity shall document and implement a cyber security policy that represents management’s commitment and ability to secure its Critical Cyber Assets. The Responsible Entity shall, at minimum, ensure the following: | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-4 | Cyber Security — Security Management Controls | R1.1. | The cyber security policy addresses the requirements in Standards CIP-002-4 through CIP-009-4, including provision for emergency situations. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-4 | Cyber Security — Security Management Controls | R1.2. | The cyber security policy is readily available to all personnel who have access to, or are responsible for, Critical Cyber Assets. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-4 | Cyber Security — Security Management Controls | R1.3. | Annual review and approval of the cyber security policy by the senior manager assigned pursuant to R2. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-4 | Cyber Security — Security Management Controls | R2. | Leadership —The Responsible Entity shall assign a single senior manager with overall responsibility and authority for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002-4 through CIP-009-4. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-4 | Cyber Security — Security Management Controls | R2.1. | The senior manager shall be identified by name, title, and date of designation. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-4 | Cyber Security — Security Management Controls | R2.2. | Changes to the senior manager must be documented within thirty calendar days of the effective date. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-4 | Cyber Security — Security Management Controls | R2.3. | Where allowed by Standards CIP-002-4 through CIP-009-4, the senior manager may delegate authority for specific actions to a named delegate or delegates. These delegations shall be documented in the same manner as R2.1 and R2.2, and approved by the senior manager. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-4 | Cyber Security — Security Management Controls | R2.4. | The senior manager or delegate(s), shall authorize and document any exception from the requirements of the cyber security policy. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-4 | Cyber Security — Security Management Controls | R3. | Exceptions — Instances where the Responsible Entity cannot conform to its cyber security policy must be documented as exceptions and authorized by the senior manager or delegate(s). | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-4 | Cyber Security — Security Management Controls | R3.1. | Exceptions to the Responsible Entity’s cyber security policy must be documented within thirty days of being approved by the senior manager or delegate(s). | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-4 | Cyber Security — Security Management Controls | R3.2. | Documented exceptions to the cyber security policy must include an explanation as to why the exception is necessary and any compensating measures. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-4 | Cyber Security — Security Management Controls | R3.3. | Authorized exceptions to the cyber security policy must be reviewed and approved annually by the senior manager or delegate(s) to ensure the exceptions are still required and valid. Such review and approval shall be documented. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-4 | Cyber Security — Security Management Controls | R4. | Information Protection —The Responsible Entity shall implement and document a program to identify, classify, and protect information associated with Critical Cyber Assets. | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-4 | Cyber Security — Security Management Controls | R4.1. | The Critical Cyber Asset information to be protected shall include, at a minimum and regardless of media type, operational procedures, lists as required in standard CIP-002-4, network topology or similar diagrams, floor plans of computing centers that contain Critical Cyber Assets, equipment layouts of Critical Cyber Assets, disaster recovery plans, incident response plans, and security configuration information. | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-4 | Cyber Security — Security Management Controls | R4.2. | The Responsible Entity shall classify information to be protected under this program based on the sensitivity of the Critical Cyber Asset information. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-4 | Cyber Security — Security Management Controls | R4.3. | The Responsible Entity shall, at least annually, assess adherence to its Critical Cyber Asset information protection program, document the assessment results, and implement an action plan to remediate deficiencies identified during the assessment. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-4 | Cyber Security — Security Management Controls | R5. | Access Control —The Responsible Entity shall document and implement a program for managing access to protected Critical Cyber Asset information. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-4 | Cyber Security — Security Management Controls | R5.1. | The Responsible Entity shall maintain a list of designated personnel who are responsible for authorizing logical or physical access to protected information. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-4 | Cyber Security — Security Management Controls | R5.1.1. | Personnel shall be identified by name, title, and the information for which they are responsible for authorizing access. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-4 | Cyber Security — Security Management Controls | R5.1.2. | The list of personnel responsible for authorizing access to protected information shall be verified at least annually. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-4 | Cyber Security — Security Management Controls | R5.2. | The Responsible Entity shall review at least annually the access privileges to protected information to confirm that access privileges are correct and that they correspond with the Responsible Entity’s needs and appropriate personnel roles and responsibilities. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-4 | Cyber Security — Security Management Controls | R5.3. | The Responsible Entity shall assess and document at least annually the processes for controlling access privileges to protected information. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-4 | Cyber Security — Security Management Controls | R6. | Change Control and Configuration Management — The Responsible Entity shall establish and document a process of change control and configuration management for adding, modifying, replacing, or removing Critical Cyber Asset hardware or software, and implement supporting configuration management activities to identify, control and document all entity or vendor-related changes to hardware and software components of Critical Cyber Assets pursuant to the change control process. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-003-5 | Cyber Security — Security Management Controls | R1. | Each Responsible Entity, for its high impact and medium impact BES Cyber Systems, shall review and obtain CIP Senior Manager approval at least once every 15 calendar months for one or more documented cyber security policies that collectively address the following topics: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] 1.1 Personnel & training (CIP-004); 1.2 Electronic Security Perimeters (CIP-005) including Interactive Remote Access; 1.3 Physical security of BES Cyber Systems (CIP-006); 1.4 System security management (CIP-007); 1.5 Incident reporting and response planning (CIP-008); 1.6 Recovery plans for BES Cyber Systems (CIP-009); 1.7 Configuration change management and vulnerability assessments (CIP-010); 1.8 Information protection (CIP-011); and 1.9 Declaring and responding to CIP Exceptional Circumstances. | MEDIUM | Retired |  |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-003-5 | Cyber Security — Security Management Controls | R2. | Each Responsible Entity for its assets identified in CIP-002-5, Requirement R1, Part R1.3, shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented cyber security policies that collectively address the following topics, and review and obtain CIP Senior Manager approval for those policies at least once every 15 calendar months: [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] 2.1 Cyber security awareness; 2.2 Physical security controls; 2.3 Electronic access controls for external routable protocol connections and Dial-up Connectivity; and 2.4 Incident response to a Cyber Security Incident. An inventory, list, or discrete identification of low impact BES Cyber Systems or their BES Cyber Assets is not required. | LOWER | Retired |  |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-003-5 | Cyber Security — Security Management Controls | R3. | Each Responsible Entity shall identify a CIP Senior Manager by name and document any change within 30 calendar days of the change. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Retired |  |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-003-5 | Cyber Security — Security Management Controls | R4. | The Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, a documented process to delegate authority, unless no delegations are used. Where allowed by the CIP Standards, the CIP Senior Manager may delegate authority for specific actions to a delegate or delegates. These delegations shall be documented, including the name or title of the delegate, the specific actions delegated, and the date of the delegation; approved by the CIP Senior Manager; and updated within 30 days of any change to the delegation. Delegation changes do not need to be reinstated with a change to the delegator. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Retired |  |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-003-6 | Cyber Security — Security Management Controls | R1.1. | 1.1 For its high impact and medium impact BES Cyber Systems, if any: 1.1.1. Personnel and training (CIP-004); 1.1.2. Electronic Security Perimeters (CIP-005) including Interactive Remote Access; 1.1.3. Physical security of BES Cyber Systems (CIP-006); 1.1.4. System security management (CIP-007); 1.1.5. Incident reporting and response planning (CIP-008); 1.1.6. Recovery plans for BES Cyber Systems (CIP-009); 1.1.7. Configuration change management and vulnerability assessments (CIP-010); 1.1.8. Information protection (CIP-011); and 1.1.9. Declaring and responding to CIP Exceptional Circumstances. | MEDIUM | Retired | 2016-07-01 | 2019-12-31 | TOP, TO, RC, GOP, GO, DP, BA
CIP-003-6 | Cyber Security — Security Management Controls | R1.2. | 1.2 For its assets identified in CIP-002 containing low impact BES Cyber Systems, if any: 1.2.1. Cyber security awareness; 1.2.2. Physical security controls; 1.2.3. Electronic access controls for Low Impact External Routable Connectivity (LERC) and Dial-up Connectivity; and 1.2.4. Cyber Security Incident response | MEDIUM | Retired | 2016-07-01 | 2019-12-31 | TOP, TO, RC, GOP, GO, DP, BA
CIP-003-6 | Cyber Security — Security Management Controls | R2. | Each Responsible Entity with at least one asset identified in CIP-002 containing low impact BES Cyber Systems shall implement one or more documented cyber security plan(s) for its low impact BES Cyber Systems that include the sections in Attachment 1. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] Note: An inventory, list, or discrete identification of low impact BES Cyber Systems or their BES Cyber Assets is not required. Lists of authorized users are not required. | MEDIUM | Retired | 2016-07-01 | 2019-12-31 | TOP, TO, RC, GOP, GO, DP, BA
CIP-003-6 | Cyber Security — Security Management Controls | R3. | Each Responsible Entity shall identify a CIP Senior Manager by name and document any change within 30 calendar days of the change. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Retired | 2016-07-01 | 2019-12-31 | TOP, TO, RC, GOP, GO, DP, BA
CIP-003-6 | Cyber Security — Security Management Controls | R4. | The Responsible Entity shall implement a documented process to delegate authority, unless no delegations are used. Where allowed by the CIP Standards, the CIP Senior Manager may delegate authority for specific actions to a delegate or delegates. These delegations shall be documented, including the name or title of the delegate, the specific actions delegated, and the date of the delegation; approved by the CIP Senior Manager; and updated within 30 days of any change to the delegation. Delegation changes do not need to be reinstated with a change to the delegator. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | MEDIUM | Retired | 2016-07-01 | 2019-12-31 | TOP, TO, RC, GOP, GO, DP, BA
CIP-003-7 | Cyber Security — Security Management Controls | R1. | Each Responsible Entity shall review and obtain CIP Senior Manager approval at least once every 15 calendar months for one or more documented cyber security policies that collectively address the following topics: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Retired | 2020-01-01 | 2020-03-31 | TOP, TO, RC, GOP, GO, DP, BA
CIP-003-7 | Cyber Security — Security Management Controls | R1.1. | For its high impact and medium impact BES Cyber Systems, if any: 1.1.1. Personnel and training (CIP-004); 1.1.2. Electronic Security Perimeters (CIP-005) including Interactive Remote Access; 1.1.3. Physical security of BES Cyber Systems (CIP-006); 1.1.4. System security management (CIP-007); 1.1.5. Incident reporting and response planning (CIP-008); 1.1.6. Recovery plans for BES Cyber Systems (CIP-009); 1.1.7. Configuration change management and vulnerability assessments (CIP-010); 1.1.8. Information protection (CIP-011); and 1.1.9. Declaring and responding to CIP Exceptional Circumstances. | MEDIUM | Retired | 2020-01-01 | 2020-03-31 | TOP, TO, RC, GOP, GO, DP, BA
CIP-003-7 | Cyber Security — Security Management Controls | R1.2. | For its assets identified in CIP-002 containing low impact BES Cyber Systems, if any: 1.2.1. Cyber security awareness; 1.2.2. Physical security controls; 1.2.3. Electronic access controls; 1.2.4. Cyber Security Incident response; 1.2.5. Transient Cyber Assets and Removable Media malicious code risk mitigation; and 1.2.6. Declaring and responding to CIP Exceptional Circumstances. | MEDIUM | Retired | 2020-01-01 | 2020-03-31 | TOP, TO, RC, GOP, GO, DP, BA
CIP-003-7 | Cyber Security — Security Management Controls | R2. | Each Responsible Entity with at least one asset identified in CIP-002 containing low impact BES Cyber Systems shall implement one or more documented cyber security plan(s) for its low impact BES Cyber Systems that include the sections in Attachment 1. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | MEDIUM | Retired | 2020-01-01 | 2020-03-31 | TOP, TO, RC, GOP, GO, DP, BA
CIP-003-7 | Cyber Security — Security Management Controls | R3. | Each Responsible Entity shall identify a CIP Senior Manager by name and document any change within 30 calendar days of the change. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Retired | 2020-01-01 | 2020-03-31 | TOP, TO, RC, GOP, GO, DP, BA
CIP-003-7 | Cyber Security — Security Management Controls | R4. | The Responsible Entity shall implement a documented process to delegate authority, unless no delegations are used. Where allowed by the CIP Standards, the CIP Senior Manager may delegate authority for specific actions to a delegate or delegates. These delegations shall be documented, including the name or title of the delegate, the specific actions delegated, and the date of the delegation; approved by the CIP Senior Manager; and updated within 30 days of any change to the delegation. Delegation changes do not need to be reinstated with a change to the delegator. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | MEDIUM | Retired | 2020-01-01 | 2020-03-31 | TOP, TO, RC, GOP, GO, DP, BA
CIP-003-8 | Cyber Security — Security Management Controls | R1. | Each Responsible Entity shall review and obtain CIP Senior Manager approval at least once every 15 calendar months for one or more documented cyber security policies that collectively address the following topics: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Effective | 2020-04-01 |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-003-8 | Cyber Security — Security Management Controls | R1.1. | For its high impact and medium impact BES Cyber Systems, if any: 1.1.1. Personnel and training (CIP-004); 1.1.2. Electronic Security Perimeters (CIP-005) including Interactive Remote Access; 1.1.3. Physical security of BES Cyber Systems (CIP-006); 1.1.4. System security management (CIP-007); 1.1.5. Incident reporting and response planning (CIP-008); 1.1.6. Recovery plans for BES Cyber Systems (CIP-009); 1.1.7. Configuration change management and vulnerability assessments (CIP-010); 1.1.8. Information protection (CIP-011); and 1.1.9. Declaring and responding to CIP Exceptional Circumstances. | MEDIUM | Effective | 2020-04-01 |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-003-8 | Cyber Security — Security Management Controls | R1.2. | For its assets identified in CIP-002 containing low impact BES Cyber Systems, if any: 1.2.1. Cyber security awareness; 1.2.2. Physical security controls; 1.2.3. Electronic access controls; 1.2.4. Cyber Security Incident response; 1.2.5. Transient Cyber Assets and Removable Media malicious code risk mitigation; and 1.2.6. Declaring and responding to CIP Exceptional Circumstances. | MEDIUM | Effective | 2020-04-01 |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-003-8 | Cyber Security — Security Management Controls | R2. | Each Responsible Entity with at least one asset identified in CIP-002 containing low impact BES Cyber Systems shall implement one or more documented cyber security plan(s) for its low impact BES Cyber Systems that include the sections in Attachment 1. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | MEDIUM | Effective | 2020-04-01 |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-003-8 | Cyber Security — Security Management Controls | R3. | Each Responsible Entity shall identify a CIP Senior Manager by name and document any change within 30 calendar days of the change. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Effective | 2020-04-01 |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-003-8 | Cyber Security — Security Management Controls | R4. | The Responsible Entity shall implement a documented process to delegate authority, unless no delegations are used. Where allowed by the CIP Standards, the CIP Senior Manager may delegate authority for specific actions to a delegate or delegates. These delegations shall be documented, including the name or title of the delegate, the specific actions delegated, and the date of the delegation; approved by the CIP Senior Manager; and updated within 30 days of any change to the delegation. Delegation changes do not need to be reinstated with a change to the delegator. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | MEDIUM | Effective | 2020-04-01 |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-003-9 | Cyber Security — Security Management Controls | R1. | Each Responsible Entity shall review and obtain CIP Senior Manager approval at least once every 15 calendar months for one or more documented cyber security policies that collectively address the following topics: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Future Effective | 2026-07-01 |  | TO, TOP, RC, GO, GOP, DP, BA
CIP-003-9 | Cyber Security — Security Management Controls | R1.1. | For its high impact and medium impact BES Cyber Systems, if any: 1.1.1. Personnel and training (CIP‐004); 1.1.2. Electronic Security Perimeters (CIP‐005) including Interactive Remote Access; 1.1.3. Physical security of BES Cyber Systems (CIP‐006); 1.1.4. System security management (CIP‐007); 1.1.5. Incident reporting and response planning (CIP‐008); 1.1.6. Recovery plans for BES Cyber Systems(CIP‐009); 1.1.7. Configuration change management and vulnerability assessments (CIP‐ 010); 1.1.8. Information protection (CIP‐011); and 1.1.9. Declaring and responding to CIP Exceptional Circumstances. | MEDIUM | Future Effective | 2026-07-01 |  | TO, TOP, RC, GO, GOP, DP, BA
CIP-003-9 | Cyber Security — Security Management Controls | R1.2. | For its assets identified in CIP‐002 containing low impact BES Cyber Systems,if any: 1.2.1. Cyber security awareness; 1.2.2. Physical security controls; 1.2.3. Electronic access controls; 1.2.4. Cyber Security Incident response; 1.2.5. Transient Cyber Assets and Removable Media malicious code risk mitigation; 1.2.6. Vendor electronic remote access security controls; and 1.2.7. Declaring and responding to CIP Exceptional Circumstances. | MEDIUM | Future Effective | 2026-07-01 |  | TO, TOP, RC, GO, GOP, DP, BA
CIP-003-9 | Cyber Security — Security Management Controls | R2. | Each Responsible Entity with at least one asset identified in CIP‐002 containing low impact BES Cyber Systems shall implement one or more documented cyber security plan(s) for its low impact BES Cyber Systems that include the sections in Attachment 1. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning | LOWER | Future Effective | 2026-07-01 |  | TO, TOP, RC, GO, GOP, DP, BA
CIP-003-9 | Cyber Security — Security Management Controls | R3. | Each Responsible Entity shall identify a CIP Senior Manager by name and document any change within 30 calendar days of the change. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Future Effective | 2026-07-01 |  | TO, TOP, RC, GO, GOP, DP, BA
CIP-003-9 | Cyber Security — Security Management Controls | R4. | The Responsible Entity shall implement a documented process to delegate authority, unless no delegations are used. Where allowed by the CIP Standards, the CIP Senior Manager may delegate authority for specific actions to a delegate or delegates.These delegations shall be documented, including the name or title of the delegate, the specific actions delegated, and the date of the delegation; approved by the CIP Senior Manager; and updated within 30 days of any change to the delegation. Delegation changes do not need to be reinstated with a change to the delegator. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Future Effective | 2026-07-01 |  | TO, TOP, RC, GO, GOP, DP, BA
CIP-004-3a | Cyber Security - Personnel & Training | R1. | Awareness —The Responsible Entity shall establish, document, implement, and maintain a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets receive on-going reinforcement in sound security practices. The program shall include security awareness reinforcement on at least a quarterly basis using mechanisms such as: • Direct communications (e.g., emails, memos, computer based training, etc.); • Indirect communications (e.g., posters, intranet, brochures, etc.); • Management support and reinforcement (e.g., presentations, meetings, etc.). | LOWER | Retired | 2013-09-18 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-004-3a | Cyber Security - Personnel & Training | R2. | Training —The Responsible Entity shall establish, document, implement, and maintain an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. The cyber security training program shall be reviewed annually, at a minimum, and shall be updated whenever necessary. | LOWER | Retired | 2013-09-18 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-004-3a | Cyber Security - Personnel & Training | R2.1. | This program will ensure that all personnel having such access to Critical Cyber Assets, including contractors and service vendors, are trained prior to their being granted such access except in specified circumstances such as an emergency. | MEDIUM | Retired | 2013-09-18 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-004-3a | Cyber Security - Personnel & Training | R2.2. | Training shall cover the policies, access controls, and procedures as developed for the Critical Cyber Assets covered by CIP-004-3, and include, at a minimum, the following required items appropriate to personnel roles and responsibilities: | MEDIUM | Retired | 2013-09-18 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-004-3a | Cyber Security - Personnel & Training | R2.2.1. | The proper use of Critical Cyber Assets; | LOWER | Retired | 2013-09-18 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-004-3a | Cyber Security - Personnel & Training | R2.2.2. | Physical and electronic access controls to Critical Cyber Assets; | LOWER | Retired | 2013-09-18 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-004-3a | Cyber Security - Personnel & Training | R2.2.3. | The proper handling of Critical Cyber Asset information; and, | LOWER | Retired | 2013-09-18 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-004-3a | Cyber Security - Personnel & Training | R2.2.4. | Action plans and procedures to recover or re-establish Critical Cyber Assets and access thereto following a Cyber Security Incident. | MEDIUM | Retired | 2013-09-18 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-004-3a | Cyber Security - Personnel & Training | R2.3. | The Responsible Entity shall maintain documentation that training is conducted at least annually, including the date the training was completed and attendance records. | LOWER | Retired | 2013-09-18 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-004-3a | Cyber Security - Personnel & Training | R3. | Personnel Risk Assessment —The Responsible Entity shall have a documented personnel risk assessment program, in accordance with federal, state, provincial, and local laws, and subject to existing collective bargaining unit agreements, for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. A personnel risk assessment shall be conducted pursuant to that program prior to such personnel being granted such access except in specified circumstances such as an emergency. The personnel risk assessment program shall at a minimum include: | MEDIUM | Retired | 2013-09-18 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-004-3a | Cyber Security - Personnel & Training | R3.1. | The Responsible Entity shall ensure that each assessment conducted include, at least, identity verification (e.g., Social Security Number verification in the U.S.) and sevenyear criminal check. The Responsible Entity may conduct more detailed reviews, as permitted by law and subject to existing collective bargaining unit agreements, depending upon the criticality of the position. | LOWER | Retired | 2013-09-18 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-004-3a | Cyber Security - Personnel & Training | R3.2. | The Responsible Entity shall update each personnel risk assessment at least every seven years after the initial personnel risk assessment or for cause. | LOWER | Retired | 2013-09-18 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-004-3a | Cyber Security - Personnel & Training | R3.3. | The Responsible Entity shall document the results of personnel risk assessments of its personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, and that personnel risk assessments of contractor and service vendor personnel with such access are conducted pursuant to Standard CIP-004-3. | LOWER | Retired | 2013-09-18 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-004-3a | Cyber Security - Personnel & Training | R4. | Access —The Responsible Entity shall maintain list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets. | LOWER | Retired | 2013-09-18 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-004-3a | Cyber Security - Personnel & Training | R4.1. | The Responsible Entity shall review the list(s) of its personnel who have such access to Critical Cyber Assets quarterly, and update the list(s) within seven calendar days of any change of personnel with such access to Critical Cyber Assets, or any change in the access rights of such personnel. The Responsible Entity shall ensure access list(s) for contractors and service vendors are properly maintained. | LOWER | Retired | 2013-09-18 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-004-3a | Cyber Security - Personnel & Training | R4.2. | The Responsible Entity shall revoke such access to Critical Cyber Assets within 24 hours for personnel terminated for cause and within seven calendar days for personnel who no longer require such access to Critical Cyber Assets. | LOWER | Retired | 2013-09-18 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-004-4 | Cyber Security — Personnel & Training | R1. | Awareness —The Responsible Entity shall establish, document, implement, and maintain a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets receive on-going reinforcement in sound security practices. The program shall include security awareness reinforcement on at least a quarterly basis using mechanisms such as: • Direct communications (e.g., emails, memos, computer based training, etc.); • Indirect communications (e.g., posters, intranet, brochures, etc.); • Management support and reinforcement (e.g., presentations, meetings, etc.). |  | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-004-4 | Cyber Security — Personnel & Training | R2. | Training —The Responsible Entity shall establish, document, implement, and maintain an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. The cyber security training program shall be reviewed annually, at a minimum, and shall be updated whenever necessary. |  | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-004-4 | Cyber Security — Personnel & Training | R2.1. | This program will ensure that all personnel having such access to Critical Cyber Assets, including contractors and service vendors, are trained prior to their being granted such access except in specified circumstances such as an emergency. |  | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-004-4 | Cyber Security — Personnel & Training | R2.2. | Training shall cover the policies, access controls, and procedures as developed for the Critical Cyber Assets covered by CIP-004-4, and include, at a minimum, the following required items appropriate to personnel roles and responsibilities: |  | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-004-4 | Cyber Security — Personnel & Training | R2.2.1. | The proper use of Critical Cyber Assets; |  | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-004-4 | Cyber Security — Personnel & Training | R2.2.2. | Physical and electronic access controls to Critical Cyber Assets; |  | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-004-4 | Cyber Security — Personnel & Training | R2.2.3. | The proper handling of Critical Cyber Asset information; and, |  | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-004-4 | Cyber Security — Personnel & Training | R2.2.4. | Action plans and procedures to recover or re-establish Critical Cyber Assets and access thereto following a Cyber Security Incident. |  | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-004-4 | Cyber Security — Personnel & Training | R2.3. | The Responsible Entity shall maintain documentation that training is conducted at least annually, including the date the training was completed and attendance records. |  | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-004-4 | Cyber Security — Personnel & Training | R3. | Personnel Risk Assessment —The Responsible Entity shall have a documented personnel risk assessment program, in accordance with federal, state, provincial, and local laws, and subject to existing collective bargaining unit agreements, for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. A personnel risk assessment shall be conducted pursuant to that program prior to such personnel being granted such access except in specified circumstances such as an emergency. The personnel risk assessment program shall at a minimum include: |  | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-004-4 | Cyber Security — Personnel & Training | R3.1. | The Responsible Entity shall ensure that each assessment conducted include, at least, identity verification (e.g., Social Security Number verification in the U.S.) and seven-year criminal check. The Responsible Entity may conduct more detailed reviews, as permitted by law and subject to existing collective bargaining unit agreements, depending upon the criticality of the position. |  | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-004-4 | Cyber Security — Personnel & Training | R3.2. | The Responsible Entity shall update each personnel risk assessment at least every seven years after the initial personnel risk assessment or for cause. |  | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-004-4 | Cyber Security — Personnel & Training | R3.3. | The Responsible Entity shall document the results of personnel risk assessments of its personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, and that personnel risk assessments of contractor and service vendor personnel with such access are conducted pursuant to Standard CIP-004-4. |  | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-004-4 | Cyber Security — Personnel & Training | R4. | Access —The Responsible Entity shall maintain list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets. |  | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-004-4 | Cyber Security — Personnel & Training | R4.1. | The Responsible Entity shall review the list(s) of its personnel who have such access to Critical Cyber Assets quarterly, and update the list(s) within seven calendar days of any change of personnel with such access to Critical Cyber Assets, or any change in the access rights of such personnel. The Responsible Entity shall ensure access list(s) for contractors and service vendors are properly maintained. |  | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-004-4 | Cyber Security — Personnel & Training | R4.2. | The Responsible Entity shall revoke such access to Critical Cyber Assets within 24 hours for personnel terminated for cause and within seven calendar days for personnel who no longer require such access to Critical Cyber Assets. |  | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-004-4a | Cyber Security — Personnel & Training | R1. | Awareness —The Responsible Entity shall establish, document, implement, and maintain a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets receive on-going reinforcement in sound security practices. The program shall include security awareness reinforcement on at least a quarterly basis using mechanisms such as: • Direct communications (e.g., emails, memos, computer based training, etc.); • Indirect communications (e.g., posters, intranet, brochures, etc.); • Management support and reinforcement (e.g., presentations, meetings, etc.). | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-004-4a | Cyber Security — Personnel & Training | R2. | Training —The Responsible Entity shall establish, document, implement, and maintain an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. The cyber security training program shall be reviewed annually, at a minimum, and shall be updated whenever necessary. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-004-4a | Cyber Security — Personnel & Training | R2.1. | This program will ensure that all personnel having such access to Critical Cyber Assets, including contractors and service vendors, are trained prior to their being granted such access except in specified circumstances such as an emergency. | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-004-4a | Cyber Security — Personnel & Training | R2.2. | Training shall cover the policies, access controls, and procedures as developed for the Critical Cyber Assets covered by CIP-004-4, and include, at a minimum, the following required items appropriate to personnel roles and responsibilities: | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-004-4a | Cyber Security — Personnel & Training | R2.2.1. | The proper use of Critical Cyber Assets; | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-004-4a | Cyber Security — Personnel & Training | R2.2.2. | Physical and electronic access controls to Critical Cyber Assets; | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-004-4a | Cyber Security — Personnel & Training | R2.2.3. | The proper handling of Critical Cyber Asset information; and, | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-004-4a | Cyber Security — Personnel & Training | R2.2.4. | Action plans and procedures to recover or re-establish Critical Cyber Assets and access thereto following a Cyber Security Incident. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-004-4a | Cyber Security — Personnel & Training | R2.3. | The Responsible Entity shall maintain documentation that training is conducted at least annually, including the date the training was completed and attendance records. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-004-4a | Cyber Security — Personnel & Training | R3. | Personnel Risk Assessment —The Responsible Entity shall have a documented personnel risk assessment program, in accordance with federal, state, provincial, and local laws, and subject to existing collective bargaining unit agreements, for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. A personnel risk assessment shall be conducted pursuant to that program prior to such personnel being granted such access except in specified circumstances such as an emergency. The personnel risk assessment program shall at a minimum include: | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-004-4a | Cyber Security — Personnel & Training | R3.1. | The Responsible Entity shall ensure that each assessment conducted include, at least, identity verification (e.g., Social Security Number verification in the U.S.) and seven-year criminal check. The Responsible Entity may conduct more detailed reviews, as permitted by law and subject to existing collective bargaining unit agreements, depending upon the criticality of the position. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-004-4a | Cyber Security — Personnel & Training | R3.2. | The Responsible Entity shall update each personnel risk assessment at least every seven years after the initial personnel risk assessment or for cause. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-004-4a | Cyber Security — Personnel & Training | R3.3. | The Responsible Entity shall document the results of personnel risk assessments of its personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, and that personnel risk assessments of contractor and service vendor personnel with such access are conducted pursuant to Standard CIP-004-4. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-004-4a | Cyber Security — Personnel & Training | R4. | Access —The Responsible Entity shall maintain list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-004-4a | Cyber Security — Personnel & Training | R4.1. | The Responsible Entity shall review the list(s) of its personnel who have such access to Critical Cyber Assets quarterly, and update the list(s) within seven calendar days of any change of personnel with such access to Critical Cyber Assets, or any change in the access rights of such personnel. The Responsible Entity shall ensure access list(s) for contractors and service vendors are properly maintained. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-004-4a | Cyber Security — Personnel & Training | R4.2. | The Responsible Entity shall revoke such access to Critical Cyber Assets within 24 hours for personnel terminated for cause and within seven calendar days for personnel who no longer require such access to Critical Cyber Assets. | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-004-5 | Cyber Security — Personnel & Training | R1. | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP‐004‐5 Table R1 – Security Awareness Program. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Never Came Into Effect in Ontario |  |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-004-5 | Cyber Security — Personnel & Training | R2. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, a cyber security training program(s) appropriate to individual roles, functions, or responsibilities that collectively includes each of the applicable requirement parts in CIP‐004‐5 Table R2 – Cyber Security Training Program. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Never Came Into Effect in Ontario |  |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-004-5 | Cyber Security — Personnel & Training | R3. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented personnel risk assessment programs to attain and retain authorized electronic or authorized unescorted physical access to BES Cyber Systems that collectively include each of the applicable requirement parts in CIP‐004‐5 Table R3 – Personnel Risk Assessment Program. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning]. | MEDIUM | Never Came Into Effect in Ontario |  |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-004-5 | Cyber Security — Personnel & Training | R4. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented access management programs that collectively include each of the applicable requirement parts in CIP‐004‐5 Table R4 – Access Management Program. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning and Same Day Operations]. | LOWER | Never Came Into Effect in Ontario |  |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-004-5 | Cyber Security — Personnel & Training | R5. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented access revocation programs that collectively include each of the applicable requirement parts in CIP‐004‐5 Table R5 – Access Revocation. [Violation Risk Factor: Medium] [Time Horizon: Same Day Operations and Operations Planning]. | MEDIUM | Never Came Into Effect in Ontario |  |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-004-5.1 | Cyber Security — Personnel & Training | R1. | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R1 – Security Awareness Program. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Retired |  |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-004-5.1 | Cyber Security — Personnel & Training | R2. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, a cyber security training program(s) appropriate to individual roles, functions, or responsibilities that collectively includes each of the applicable requirement parts in CIP-004-5.1 Table R2 – Cyber Security Training Program. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Retired |  |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-004-5.1 | Cyber Security — Personnel & Training | R3. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented personnel risk assessment programs to attain and retain authorized electronic or authorized unescorted physical access to BES Cyber Systems that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R3 – Personnel Risk Assessment Program. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning]. | MEDIUM | Retired |  |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-004-5.1 | Cyber Security — Personnel & Training | R4. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented access management programs that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R4 – Access Management Program. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning and Same Day Operations]. | MEDIUM | Retired |  |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-004-5.1 | Cyber Security — Personnel & Training | R5. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented access revocation programs that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R5 – Access Revocation. [Violation Risk Factor: Medium] [Time Horizon: Same Day Operations and Operations Planning]. | MEDIUM | Retired |  |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-004-6 | Cyber Security — Personnel & Training | R1. | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-004-6 Table R1 – Security Awareness Program. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Effective | 2016-07-01 |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-004-6 | Cyber Security — Personnel & Training | R2. | Each Responsible Entity shall implement one or more cyber security training program(s) appropriate to individual roles, functions, or responsibilities that collectively includes each of the applicable requirement parts in CIP-004-6 Table R2 – Cyber Security Training Program. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Effective | 2016-07-01 |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-004-6 | Cyber Security — Personnel & Training | R3. | Each Responsible Entity shall implement one or more documented personnel risk assessment program(s) to attain and retain authorized electronic or authorized unescorted physical access to BES Cyber Systems that collectively include each of the applicable requirement parts in CIP-004-6 Table R3 – Personnel Risk Assessment Program. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning]. | MEDIUM | Effective | 2016-07-01 |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-004-6 | Cyber Security — Personnel & Training | R4. | Each Responsible Entity shall implement one or more documented access management program(s) that collectively include each of the applicable requirement parts in CIP-004-6 Table R4 – Access Management Program. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning and Same Day Operations]. | MEDIUM | Effective | 2016-07-01 |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-004-6 | Cyber Security — Personnel & Training | R5. | Each Responsible Entity shall implement one or more documented access revocation program(s) that collectively include each of the applicable requirement parts in CIP-004-6 Table R5 – Access Revocation. [Violation Risk Factor: Medium] [Time Horizon: Same Day Operations and Operations Planning]. | MEDIUM | Effective | 2016-07-01 |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-004-7 | Cyber Security — Personnel & Training | R1. | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-004-7 Table R1 – Security Awareness Program. | LOWER | Effective |  |  | PC
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R1. | Electronic Security Perimeter —The Responsible Entity shall ensure that every Critical Cyber Asset resides within an Electronic Security Perimeter. The Responsible Entity shall identify and document the Electronic Security Perimeter(s) and all access points to the perimeter(s). | MEDIUM | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R1.1. | Access points to the Electronic Security Perimeter(s) shall include any externally connected communication end point (for example, dial-up modems) terminating at any device within the Electronic Security Perimeter(s). | MEDIUM | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R1.2. | For a dial-up accessible Critical Cyber Asset that uses a non-routable protocol, the Responsible Entity shall define an Electronic Security Perimeter for that single access point at the dial-up device. | MEDIUM | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R1.3. | Communication links connecting discrete Electronic Security Perimeters shall not be considered part of the Electronic Security Perimeter. However, end points of these communication links within the Electronic Security Perimeter(s) shall be considered access points to the Electronic Security Perimeter(s). | MEDIUM | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R1.4. | Any non-critical Cyber Asset within a defined Electronic Security Perimeter shall be identified and protected pursuant to the requirements of Standard CIP-005-3. | MEDIUM | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R1.5. | Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall be afforded the protective measures as a specified in Standard CIP-003-3; Standard CIP-004-3 Requirement R3; Standard CIP-005-3 Requirements R2 and R3; Standard CIP-006-3 Requirement R3; Standard CIP-007-3 Requirements R1 and R3 through R9; Standard CIP-008-3; and Standard CIP-009-3. | MEDIUM | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R1.6. | The Responsible Entity shall maintain documentation of Electronic Security Perimeter(s), all interconnected Critical and non-critical Cyber Assets within the Electronic Security Perimeter(s), all electronic access points to the Electronic Security Perimeter(s) and the Cyber Assets deployed for the access control and monitoring of these access points. | LOWER | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R2. | Electronic Access Controls — The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). | MEDIUM | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R2.1. | These processes and mechanisms shall use an access control model that denies access by default, such that explicit access permissions must be specified. | MEDIUM | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R2.2. | At all access points to the Electronic Security Perimeter(s), the Responsible Entity shall enable only ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter, and shall document, individually or by specified grouping, the configuration of those ports and services. | MEDIUM | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R2.3. | The Responsible Entity shall implement and maintain a procedure for securing dial-up access to the Electronic Security Perimeter(s). | MEDIUM | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R2.4. | Where external interactive access into the Electronic Security Perimeter has been enabled, the Responsible Entity shall implement strong procedural or technical controls at the access points to ensure authenticity of the accessing party, where technically feasible. | MEDIUM | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R2.5. | The required documentation shall, at least, identify and describe: | LOWER | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R2.5.1. | The processes for access request and authorization. | LOWER | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R2.5.2. | The authentication methods. | LOWER | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R2.5.3. | The review process for authorization rights, in accordance with Standard CIP-004-3 Requirement R4. | LOWER | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R2.5.4. | The controls used to secure dial-up accessible connections. | LOWER | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R3. | Monitoring Electronic Access —The Responsible Entity shall implement and document an electronic or manual process(es) for monitoring and logging access at access points to the Electronic Security Perimeter(s) twenty-four hours a day, seven days a week. | MEDIUM | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R3.1. | For dial-up accessible Critical Cyber Assets that use non-routable protocols, the Responsible Entity shall implement and document monitoring process(es) at each access point to the dial-up device, where technically feasible. | MEDIUM | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R3.2. | Where technically feasible, the security monitoring process(es) shall detect and alert for attempts at or actual unauthorized accesses. These alerts shall provide for appropriate notification to designated response personnel. Where alerting is not technically feasible, the Responsible Entity shall review or otherwise assess access logs for attempts at or actual unauthorized accesses at least every ninety calendar days. | MEDIUM | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R4. | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of the electronic access points to the Electronic Security Perimeter(s) at least annually. The vulnerability assessment shall include, at a minimum, the following: | MEDIUM | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R4.1. | A document identifying the vulnerability assessment process; | LOWER | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R4.2. | A review to verify that only ports and services required for operations at these access points are enabled; | MEDIUM | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R4.3. | The discovery of all access points to the Electronic Security Perimeter; | MEDIUM | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R4.4. | A review of controls for default accounts, passwords, and network management community strings; | MEDIUM | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R4.5. | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. | MEDIUM | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R5. | Documentation Review and Maintenance —The Responsible Entity shall review, update, and maintain all documentation to support compliance with the requirements of Standard CIP-005-3. | LOWER | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R5.1. | The Responsible Entity shall ensure that all documentation required by Standard CIP-005-3 reflect current configurations and processes and shall review the documents and procedures referenced in Standard CIP-005-3 at least annually. | LOWER | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R5.2. | The Responsible Entity shall update the documentation to reflect the modification of the network or controls within ninety calendar days of the change. | LOWER | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R5.3. | The Responsible Entity shall retain electronic access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-3. | LOWER | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R1. | Electronic Security Perimeter —The Responsible Entity shall ensure that every Critical Cyber Asset resides within an Electronic Security Perimeter. The Responsible Entity shall identify and document the Electronic Security Perimeter(s) and all access points to the perimeter(s). | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R1.1. | Access points to the Electronic Security Perimeter(s) shall include any externally connected communication end point (for example, dial-up modems) terminating at any device within the Electronic Security Perimeter(s). | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R1.2. | For a dial-up accessible Critical Cyber Asset that uses a non-routable protocol, the Responsible Entity shall define an Electronic Security Perimeter for that single access point at the dial-up device. | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R1.3. | Communication links connecting discrete Electronic Security Perimeters shall not be considered part of the Electronic Security Perimeter. However, end points of these communication links within the Electronic Security Perimeter(s) shall be considered access points to the Electronic Security Perimeter(s). | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R1.4. | Any non-critical Cyber Asset within a defined Electronic Security Perimeter shall be identified and protected pursuant to the requirements of Standard CIP-005-4a. | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R1.5. | Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall be afforded the protective measures as a specified in Standard CIP-003-4; Standard CIP-004-4 Requirement R3; Standard CIP-005-4a Requirements R2 and R3; Standard CIP-006-4c Requirement R3; Standard CIP-007-4 Requirements R1 and R3 through R9; Standard CIP-008-4; and Standard CIP-009-4. | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R1.6. | The Responsible Entity shall maintain documentation of Electronic Security Perimeter(s), all interconnected Critical and non-critical Cyber Assets within the Electronic Security Perimeter(s), all electronic access points to the Electronic Security Perimeter(s) and the Cyber Assets deployed for the access control and monitoring of these access points. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R2. | Electronic Access Controls — The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R2.1. | These processes and mechanisms shall use an access control model that denies access by default, such that explicit access permissions must be specified. | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R2.2. | At all access points to the Electronic Security Perimeter(s), the Responsible Entity shall enable only ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter, and shall document, individually or by specified grouping, the configuration of those ports and services. | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R2.3. | The Responsible Entity shall implement and maintain a procedure for securing dial-up access to the Electronic Security Perimeter(s). | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R2.4. | Where external interactive access into the Electronic Security Perimeter has been enabled, the Responsible Entity shall implement strong procedural or technical controls at the access points to ensure authenticity of the accessing party, where technically feasible. | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R2.5. | The required documentation shall, at least, identify and describe: | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R2.5.1. | The processes for access request and authorization. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R2.5.2. | The authentication methods. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R2.5.3. | The review process for authorization rights, in accordance with Standard CIP-004-4 Requirement R4. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R2.5.4. | The controls used to secure dial-up accessible connections. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R2.6. | Appropriate Use Banner —Where technically feasible, electronic access control devices shall display an appropriate use banner on the user screen upon all interactive access attempts. The Responsible Entity shall maintain a document identifying the content of the banner. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R3. | Monitoring Electronic Access —The Responsible Entity shall implement and document an electronic or manual process(es) for monitoring and logging access at access points to the Electronic Security Perimeter(s) twenty-four hours a day, seven days a week. | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R3.1. | For dial-up accessible Critical Cyber Assets that use non-routable protocols, the Responsible Entity shall implement and document monitoring process(es) at each access point to the dial-up device, where technically feasible. | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R3.2. | Where technically feasible, the security monitoring process(es) shall detect and alert for attempts at or actual unauthorized accesses. These alerts shall provide for appropriate notification to designated response personnel. Where alerting is not technically feasible, the Responsible Entity shall review or otherwise assess access logs for attempts at or actual unauthorized accesses at least every ninety calendar days. | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R4. | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of the electronic access points to the Electronic Security Perimeter(s) at least annually. The vulnerability assessment shall include, at a minimum, the following: | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R4.1. | A document identifying the vulnerability assessment process; | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R4.2. | A review to verify that only ports and services required for operations at these access points are enabled; | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R4.3. | The discovery of all access points to the Electronic Security Perimeter; | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R4.4. | A review of controls for default accounts, passwords, and network management community strings; | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R4.5. | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R5. | Documentation Review and Maintenance —The Responsible Entity shall review, update, and maintain all documentation to support compliance with the requirements of Standard CIP-005-4a. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R5.1. | The Responsible Entity shall ensure that all documentation required by Standard CIP-005-4a reflect current configurations and processes and shall review the documents and procedures referenced in Standard CIP-005-4a at least annually. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R5.2. | The Responsible Entity shall update the documentation to reflect the modification of the network or controls within ninety calendar days of the change. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R5.3. | The Responsible Entity shall retain electronic access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-4. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-005-5 | Cyber Security — Electronic Security Perimeter(s) | R1. | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP‐005‐5 Table R1 – Electronic Security Perimeter. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning and Same Day Operations]. | MEDIUM | Retired | 2016-07-01 | 2020-06-30 | TOP, TO, RC, GOP, GO, DP, BA
CIP-005-5 | Cyber Security — Electronic Security Perimeter(s) | R2. | Each Responsible Entity allowing Interactive Remote Access to BES Cyber Systems shall implement one or more documented processes that collectively include the applicable requirement parts, where technically feasible, in CIP‐005‐5 Table R2 – Interactive Remote Access Management. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning and Same Day Operations]. | MEDIUM | Retired | 2016-07-01 | 2020-06-30 | TOP, TO, RC, GOP, GO, DP, BA
CIP-005-6 | Cyber Security — Electronic Security Perimeter(s) | R1. | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-005-6 Table R1 – Electronic Security Perimeter. | MEDIUM | Retired | 2020-10-01 | 2022-10-31 | TOP, TO, RC, GOP, GO, DP, BA
CIP-005-6 | Cyber Security — Electronic Security Perimeter(s) | R2. | Each Responsible Entity shall implement one or more documented processes that collectively include the applicable requirement parts, where technically feasible, in CIP-005-6 Table R2 –Remote Access Management. | MEDIUM | Retired | 2020-10-01 | 2022-10-31 | TOP, TO, RC, GOP, GO, DP, BA
CIP-005-7 | Cyber Security – Electronic Security Perimeter(s) | R1. | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-005-7 Table R1 – Electronic Security Perimeter. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning and Same Day Operations] | MEDIUM | Effective | 2022-10-01 |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-005-7 | Cyber Security – Electronic Security Perimeter(s) | R2. | Each Responsible Entity shall implement one or more documented processes that collectively include the applicable requirement parts, where technically feasible, in CIP-005-7 Table R2 –Remote Access Management. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning and Same Day Operations]. | MEDIUM | Effective | 2022-10-01
CIP-005-7 | Cyber Security – Electronic Security Perimeter(s) | R3. | Each Responsible Entity shall implement one or more documented processes that collectively include the applicable requirement parts in CIP-005-7 Table R3 –Vendor Remote Access Management for EACMS and PACS. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning and Same Day Operations]. | MEDIUM | Effective | 2022-10-01
CIP-006-3c | Cyber Security — Physical Security of Critical Cyber Assets | R1. | Physical Security Plan — The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: | MEDIUM | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-3c | Cyber Security — Physical Security of Critical Cyber Assets | R1.1. | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. | MEDIUM | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-3c | Cyber Security — Physical Security of Critical Cyber Assets | R1.2. | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. | MEDIUM | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-3c | Cyber Security — Physical Security of Critical Cyber Assets | R1.3. | Processes, tools, and procedures to monitor physical access to the perimeter(s). | MEDIUM | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-3c | Cyber Security — Physical Security of Critical Cyber Assets | R1.4. | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. | MEDIUM | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-3c | Cyber Security — Physical Security of Critical Cyber Assets | R1.5. | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-3 Requirement R4. | MEDIUM | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-3c | Cyber Security — Physical Security of Critical Cyber Assets | R1.6. | A visitor control program for visitors (personnel without authorized unescorted access to a Physical Security Perimeter), containing at a minimum the following: | MEDIUM | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-3c | Cyber Security — Physical Security of Critical Cyber Assets | R1.6.1. | Logs (manual or automated) to document the entry and exit of visitors, including the date and time, to and from Physical Security Perimeters. | MEDIUM | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-3c | Cyber Security — Physical Security of Critical Cyber Assets | R1.6.2. | Continuous escorted access of visitors within the Physical Security Perimeter. | MEDIUM | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-3c | Cyber Security — Physical Security of Critical Cyber Assets | R1.7. | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls. | LOWER | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-3c | Cyber Security — Physical Security of Critical Cyber Assets | R1.8. | Annual review of the physical security plan. | LOWER | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-3c | Cyber Security — Physical Security of Critical Cyber Assets | R2. | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: | MEDIUM | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-3c | Cyber Security — Physical Security of Critical Cyber Assets | R2.1. | Be protected from unauthorized physical access. | MEDIUM | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-3c | Cyber Security — Physical Security of Critical Cyber Assets | R2.2. | Be afforded the protective measures specified in Standard CIP-003-3; Standard CIP-004-3 Requirement R3; Standard CIP-005-3 Requirements R2 and R3; Standard CIP-006-3 Requirements R4 and R5; Standard CIP-007-3; Standard CIP-008-3; and Standard CIP-009-3. | MEDIUM | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-3c | Cyber Security — Physical Security of Critical Cyber Assets | R3. | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. | MEDIUM | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-3c | Cyber Security — Physical Security of Critical Cyber Assets | R4. | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: • Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. • Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. • Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. • Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. | MEDIUM | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-3c | Cyber Security — Physical Security of Critical Cyber Assets | R5. | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-3. One or more of the following monitoring methods shall be used: • Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. • Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. | MEDIUM | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-3c | Cyber Security — Physical Security of Critical Cyber Assets | R6. | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: • Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. • Video Recording: Electronic capture of video images of sufficient quality to determine identity. • Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. | LOWER | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-3c | Cyber Security — Physical Security of Critical Cyber Assets | R7. | Access Log Retention — The Responsible Entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-3. | LOWER | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-3c | Cyber Security — Physical Security of Critical Cyber Assets | R8. | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: | MEDIUM | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-3c | Cyber Security — Physical Security of Critical Cyber Assets | R8.1. | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. | MEDIUM | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-3c | Cyber Security — Physical Security of Critical Cyber Assets | R8.2. | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. | LOWER | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-3c | Cyber Security — Physical Security of Critical Cyber Assets | R8.3. | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. | LOWER | Retired | 2011-04-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-3d | Cyber Security — Physical Security of Critical Cyber Assets | R1. | Physical Security Plan —The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-3d | Cyber Security — Physical Security of Critical Cyber Assets | R1.1. | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-3d | Cyber Security — Physical Security of Critical Cyber Assets | R1.2. | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-3d | Cyber Security — Physical Security of Critical Cyber Assets | R1.3. | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-3d | Cyber Security — Physical Security of Critical Cyber Assets | R1.4. | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-3d | Cyber Security — Physical Security of Critical Cyber Assets | R1.5. | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-3 Requirement R4. |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-3d | Cyber Security — Physical Security of Critical Cyber Assets | R1.6. | A visitor control program for visitors (personnel without authorized unescorted access to a Physical Security Perimeter), containing at a minimum the following: |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-3d | Cyber Security — Physical Security of Critical Cyber Assets | R1.6.1. | Logs (manual or automated) to document the entry and exit of visitors, including the date and time, to and from Physical Security Perimeters. |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-3d | Cyber Security — Physical Security of Critical Cyber Assets | R1.6.2. | Continuous escorted access of visitors within the Physical Security Perimeter. |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-3d | Cyber Security — Physical Security of Critical Cyber Assets | R1.7. | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls. |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-3d | Cyber Security — Physical Security of Critical Cyber Assets | R1.8. | Annual review of the physical security plan. |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-3d | Cyber Security — Physical Security of Critical Cyber Assets | R2. | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-3d | Cyber Security — Physical Security of Critical Cyber Assets | R2.1. | Be protected from unauthorized physical access. |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-3d | Cyber Security — Physical Security of Critical Cyber Assets | R2.2. | Be afforded the protective measures specified in Standard CIP-003-3; Standard CIP-004-3 Requirement R3; Standard CIP-005-3 Requirements R2 and R3; Standard CIP-006-3 Requirements R4 and R5; Standard CIP-007-3; Standard CIP-008-3; and Standard CIP-009-3. |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-3d | Cyber Security — Physical Security of Critical Cyber Assets | R3. | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-3d | Cyber Security — Physical Security of Critical Cyber Assets | R4. | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: • Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. • Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. • Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. • Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-3d | Cyber Security — Physical Security of Critical Cyber Assets | R5. | Monitoring Physical Access —The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-3. One or more of the following monitoring methods shall be used: • Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. • Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-3d | Cyber Security — Physical Security of Critical Cyber Assets | R6. | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: • Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. • Video Recording: Electronic capture of video images of sufficient quality to determine identity. • Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-3d | Cyber Security — Physical Security of Critical Cyber Assets | R7. | Access Log Retention —The Responsible Entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-3. |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-3d | Cyber Security — Physical Security of Critical Cyber Assets | R8. | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-3d | Cyber Security — Physical Security of Critical Cyber Assets | R8.1. | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-3d | Cyber Security — Physical Security of Critical Cyber Assets | R8.2. | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-3d | Cyber Security — Physical Security of Critical Cyber Assets | R8.3. | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-4c | Cyber Security — Physical Security of Critical Cyber Assets | R1. | Physical Security Plan —The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-4c | Cyber Security — Physical Security of Critical Cyber Assets | R1.1. | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-4c | Cyber Security — Physical Security of Critical Cyber Assets | R1.2. | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-4c | Cyber Security — Physical Security of Critical Cyber Assets | R1.3. | Processes, tools, and procedures to monitor physical access to the perimeter(s). | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-4c | Cyber Security — Physical Security of Critical Cyber Assets | R1.4. | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-4c | Cyber Security — Physical Security of Critical Cyber Assets | R1.5. | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-4 Requirement R4. | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-4c | Cyber Security — Physical Security of Critical Cyber Assets | R1.6. | A visitor control program for visitors (personnel without authorized unescorted access to a Physical Security Perimeter), containing at a minimum the following: | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-4c | Cyber Security — Physical Security of Critical Cyber Assets | R1.6.1. | Logs (manual or automated) to document the entry and exit of visitors, including the date and time, to and from Physical Security Perimeters. | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-4c | Cyber Security — Physical Security of Critical Cyber Assets | R1.6.2. | Continuous escorted access of visitors within the Physical Security Perimeter. | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-4c | Cyber Security — Physical Security of Critical Cyber Assets | R1.7. | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-4c | Cyber Security — Physical Security of Critical Cyber Assets | R1.8. | Annual review of the physical security plan. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-4c | Cyber Security — Physical Security of Critical Cyber Assets | R2. | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-4c | Cyber Security — Physical Security of Critical Cyber Assets | R2.1. | Be protected from unauthorized physical access. | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-4c | Cyber Security — Physical Security of Critical Cyber Assets | R2.2. | Be afforded the protective measures specified in Standard CIP-003-4; Standard CIP-004-4 Requirement R3; Standard CIP-005-4a Requirements R2 and R3; Standard CIP-006-4c Requirements R4 and R5; Standard CIP-007-4; Standard CIP-008-4; and Standard CIP-009-4. | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-4c | Cyber Security — Physical Security of Critical Cyber Assets | R3. | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-4c | Cyber Security — Physical Security of Critical Cyber Assets | R4. | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: • Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. • Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. • Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. • Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-4c | Cyber Security — Physical Security of Critical Cyber Assets | R5. | Monitoring Physical Access —The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-4. One or more of the following monitoring methods shall be used: • Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. • Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-4c | Cyber Security — Physical Security of Critical Cyber Assets | R6. | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: • Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. • Video Recording: Electronic capture of video images of sufficient quality to determine identity. • Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-4c | Cyber Security — Physical Security of Critical Cyber Assets | R7. | Access Log Retention —The Responsible Entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-4. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-4c | Cyber Security — Physical Security of Critical Cyber Assets | R8. | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-4c | Cyber Security — Physical Security of Critical Cyber Assets | R8.1. | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-4c | Cyber Security — Physical Security of Critical Cyber Assets | R8.2. | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-4c | Cyber Security — Physical Security of Critical Cyber Assets | R8.3. | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-4d | Cyber Security — Physical Security of Critical Cyber Assets | R1. | Physical Security Plan —The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-4d | Cyber Security — Physical Security of Critical Cyber Assets | R1.1. | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-4d | Cyber Security — Physical Security of Critical Cyber Assets | R1.2. | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-4d | Cyber Security — Physical Security of Critical Cyber Assets | R1.3. | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-4d | Cyber Security — Physical Security of Critical Cyber Assets | R1.4. | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-4d | Cyber Security — Physical Security of Critical Cyber Assets | R1.5. | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-4 Requirement R4. |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-4d | Cyber Security — Physical Security of Critical Cyber Assets | R1.6. | A visitor control program for visitors (personnel without authorized unescorted access to a Physical Security Perimeter), containing at a minimum the following: |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-4d | Cyber Security — Physical Security of Critical Cyber Assets | R1.6.1. | Logs (manual or automated) to document the entry and exit of visitors, including the date and time, to and from Physical Security Perimeters. |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-4d | Cyber Security — Physical Security of Critical Cyber Assets | R1.6.2. | Continuous escorted access of visitors within the Physical Security Perimeter. |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-4d | Cyber Security — Physical Security of Critical Cyber Assets | R1.7. | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls. |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-4d | Cyber Security — Physical Security of Critical Cyber Assets | R1.8. | Annual review of the physical security plan. |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-4d | Cyber Security — Physical Security of Critical Cyber Assets | R2. | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-4d | Cyber Security — Physical Security of Critical Cyber Assets | R2.1. | Be protected from unauthorized physical access. |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-4d | Cyber Security — Physical Security of Critical Cyber Assets | R2.2. | Be afforded the protective measures specified in Standard CIP-003-4; Standard CIP-004-4 Requirement R3; Standard CIP-005-4 Requirements R2 and R3; Standard CIP-006-4 Requirements R4 and R5; Standard CIP-007-4; Standard CIP-008-4; and Standard CIP-009-4. |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-4d | Cyber Security — Physical Security of Critical Cyber Assets | R3. | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-4d | Cyber Security — Physical Security of Critical Cyber Assets | R4. | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: • Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. • Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. • Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. • Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-4d | Cyber Security — Physical Security of Critical Cyber Assets | R5. | Monitoring Physical Access —The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-4. One or more of the following monitoring methods shall be used: • Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. • Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-4d | Cyber Security — Physical Security of Critical Cyber Assets | R6. | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: • Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. • Video Recording: Electronic capture of video images of sufficient quality to determine identity. • Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-4d | Cyber Security — Physical Security of Critical Cyber Assets | R7. | Access Log Retention —The Responsible Entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-4. |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-4d | Cyber Security — Physical Security of Critical Cyber Assets | R8. | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-4d | Cyber Security — Physical Security of Critical Cyber Assets | R8.1. | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-4d | Cyber Security — Physical Security of Critical Cyber Assets | R8.2. | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-4d | Cyber Security — Physical Security of Critical Cyber Assets | R8.3. | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-006-5 | Cyber Security — Physical Security of BES Cyber Systems | R1. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented physical security plans that collectively include all of the applicable requirement parts in CIP‐006‐5 Table R1 – Physical Security Plan. [Violation Risk Factor: Medium] [Time Horizon: Long Term Planning and Same Day Operations]. | MEDIUM | Retired |  | 2022-09-30 | TOP, TO, RC, GOP, GO, DP, BA
CIP-006-5 | Cyber Security — Physical Security of BES Cyber Systems | R2. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented visitor control programs that include each of the applicable requirement parts in CIP‐006‐5 Table R2 – Visitor Control Program. [Violation Risk Factor: Medium] [Time Horizon: Same Day Operations.] | MEDIUM | Retired |  | 2022-09-30 | TOP, TO, RC, GOP, GO, DP, BA
CIP-006-5 | Cyber Security — Physical Security of BES Cyber Systems | R3. | Each Responsible Entity shall implement one or more documented Physical Access Control System maintenance and testing programs that collectively include each of the applicable requirement parts in CIP‐006‐5 Table R3 – Maintenance and Testing Program. [Violation Risk Factor: Lower] [Time Horizon: Long Term Planning]. | MEDIUM | Retired |  | 2022-09-30 | TOP, TO, RC, GOP, GO, DP, BA
CIP-006-6 | Cyber Security — Physical Security of BES Cyber Systems | R1. | Each Responsible Entity shall implement one or more documented physical security plan(s) that collectively include all of the applicable requirement parts in CIP-006-6 Table R1 – Physical Security Plan. [Violation Risk Factor: Medium] [Time Horizon: Long Term Planning and Same Day Operations]. | MEDIUM | Effective | 2016-07-01 |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-006-6 | Cyber Security — Physical Security of BES Cyber Systems | R2. | Each Responsible Entity shall implement one or more documented visitor control program(s) that include each of the applicable requirement parts in CIP-006-6 Table R2 – Visitor Control Program. [Violation Risk Factor: Medium] [Time Horizon: Same Day Operations.] | MEDIUM | Effective | 2016-07-01 |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-006-6 | Cyber Security — Physical Security of BES Cyber Systems | R3. | Each Responsible Entity shall implement one or more documented Physical Access Control System maintenance and testing program(s) that collectively include each of the applicable requirement parts in CIP-006-6 Table R3 – Maintenance and Testing Program. [Violation Risk Factor: Medium] [Time Horizon: Long Term Planning]. | MEDIUM | Effective | 2016-07-01 |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-007-3 | Cyber Security — Systems Security Management | R1. | Test Procedures — The Responsible Entity shall ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls. For purposes of Standard CIP-007-3, a significant change shall, at a minimum, include implementation of security patches, cumulative service packs, vendor releases, and version upgrades of operating systems, applications, database platforms, or other third-party software or firmware. |  | Pending Approval |  |  | GOP, GO, TOP, TO, TSP, BA, RC
CIP-007-3 | Cyber Security — Systems Security Management | R1.1. | The Responsible Entity shall create, implement, and maintain cyber security test procedures in a manner that minimizes adverse effects on the production system or its operation. |  | Pending Approval |  |  | GOP, GO, TOP, TO, TSP, BA, RC
CIP-007-3 | Cyber Security — Systems Security Management | R1.2. | The Responsible Entity shall document that testing is performed in a manner that reflects the production environment. |  | Pending Approval |  |  | GOP, GO, TOP, TO, TSP, RC, BA
CIP-007-3 | Cyber Security — Systems Security Management | R1.3. | The Responsible Entity shall document test results. |  | Pending Approval |  |  | GOP, GO, TOP, TO, TSP, RC, BA
CIP-007-3 | Cyber Security — Systems Security Management | R2. | Ports and Services — The Responsible Entity shall establish, document and implement a process to ensure that only those ports and services required for normal and emergency operations are enabled. |  | Pending Approval |  |  | GOP, GO, TOP, TO, TSP, RC, BA
CIP-007-3 | Cyber Security — Systems Security Management | R2.1. | The Responsible Entity shall enable only those ports and services required for normal and emergency operations. |  | Pending Approval |  |  | GOP, GO, TOP, TO, TSP, RC, BA
CIP-007-3 | Cyber Security — Systems Security Management | R2.2. | The Responsible Entity shall disable other ports and services, including those used for testing purposes, prior to production use of all Cyber Assets inside the Electronic Security Perimeter(s). |  | Pending Approval |  |  | GOP, GO, TOP, TO, TSP, RC, BA
CIP-007-3 | Cyber Security — Systems Security Management | R2.3. | In the case where unused ports and services cannot be disabled due to technical limitations, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | Pending Approval |  |  | GOP, GO, TOP, TO, TSP, RC, BA
CIP-007-3 | Cyber Security — Systems Security Management | R3. | Security Patch Management — The Responsible Entity, either separately or as a component of the documented configuration management process specified in CIP-003-3 Requirement R6, shall establish, document and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). |  | Pending Approval |  |  | RC, BA, GOP, GO, TOP, TO, TSP
CIP-007-3 | Cyber Security — Systems Security Management | R3.1. | The Responsible Entity shall document the assessment of security patches and security upgrades for applicability within thirty calendar days of availability of the patches or upgrades. |  | Pending Approval |  |  | GOP, GO, TOP, TO, TSP, RC, BA
CIP-007-3 | Cyber Security — Systems Security Management | R3.2. | The Responsible Entity shall document the implementation of security patches. In any case where the patch is not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | Pending Approval |  |  | GOP, GO, TOP, TO, TSP, RC, BA
CIP-007-3 | Cyber Security — Systems Security Management | R4. | Malicious Software Prevention — The Responsible Entity shall use anti-virus software and other malicious software (“malware”) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter(s). |  | Pending Approval |  |  | GOP, GO, TOP, TO, TSP, RC, BA
CIP-007-3 | Cyber Security — Systems Security Management | R4.1. | The Responsible Entity shall document and implement anti-virus and malware prevention tools. In the case where anti-virus software and malware prevention tools are not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | Pending Approval |  |  | GOP, GO, TOP, TO, TSP, RC, BA
CIP-007-3 | Cyber Security — Systems Security Management | R4.2. | The Responsible Entity shall document and implement a process for the update of anti-virus and malware prevention “signatures.” The process must address testing and installing the signatures. |  | Pending Approval |  |  | GOP, GO, TOP, TO, TSP, RC, BA
CIP-007-3 | Cyber Security — Systems Security Management | R5. | Account Management — The Responsible Entity shall establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. |  | Pending Approval |  |  | GOP, GO, TOP, TO, TSP, RC, BA
CIP-007-3 | Cyber Security — Systems Security Management | R5.1. | The Responsible Entity shall ensure that individual and shared system accounts and authorized access permissions are consistent with the concept of “need to know” with respect to work functions performed. |  | Pending Approval |  |  | GOP, GO, TOP, TO, TSP, RC, BA
CIP-007-3 | Cyber Security — Systems Security Management | R5.1.1.1. | The Responsible Entity shall ensure that user accounts are implemented as approved by designated personnel. Refer to Standard CIP-003-3 Requirement R5. |  | Pending Approval |  |  | GOP, GO, TOP, TO, TSP, RC, BA
CIP-007-3 | Cyber Security — Systems Security Management | R5.1.2. | The Responsible Entity shall establish methods, processes, and procedures that generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of ninety days. |  | Pending Approval |  |  | GOP, GO, TOP, TO, TSP, RC, BA
CIP-007-3 | Cyber Security — Systems Security Management | R5.1.3. | The Responsible Entity shall review, at least annually, user accounts to verify access privileges are in accordance with Standard CIP-003-3 Requirement R5 and Standard CIP-004-3 Requirement R4. |  | Pending Approval |  |  | GOP, GO, TOP, TO, TSP, RC, BA
CIP-007-3 | Cyber Security — Systems Security Management | R5.2. | The Responsible Entity shall implement a policy to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts. |  | Pending Approval |  |  | GOP, GO, TOP, TO, TSP, RC, BA
CIP-007-3 | Cyber Security — Systems Security Management | R5.2.1. | The policy shall include the removal, disabling, or renaming of such accounts where possible. For such accounts that must remain enabled, passwords shall be changed prior to putting any system into service. |  | Pending Approval |  |  | GOP, GO, TOP, TO, TSP, RC, BA
CIP-007-3 | Cyber Security — Systems Security Management | R5.2.2. | The Responsible Entity shall identify those individuals with access to shared accounts. |  | Pending Approval |  |  | GOP, GO, TOP, TO, TSP, RC, BA
CIP-007-3 | Cyber Security — Systems Security Management | R5.2.3. | Where such accounts must be shared, the Responsible Entity shall have a policy for managing the use of such accounts that limits access to only those with authorization, an audit trail of the account use (automated or manual), and steps for securing the account in the event of personnel changes (for example, change in assignment or termination). |  | Pending Approval |  |  | GOP, GO, TOP, TO, TSP, RC, BA
CIP-007-3 | Cyber Security — Systems Security Management | R5.3. | At a minimum, the Responsible Entity shall require and use passwords, subject to the following, as technically feasible: R5.3.1. Each password shall be a minimum of six characters. R5.3.2. Each password shall consist of a combination of alpha, numeric, and “special” characters. R5.3.3. Each password shall be changed at least annually, or more frequently based on risk. |  | Pending Approval |  |  | GOP, GO, TOP, TO, TSP, RC, BA
CIP-007-3 | Cyber Security — Systems Security Management | R6. | Security Status Monitoring — The Responsible Entity shall ensure that all Cyber Assets within the Electronic Security Perimeter, as technically feasible, implement automated tools or organizational process controls to monitor system events that are related to cyber security. |  | Pending Approval |  |  | GOP, GO, TOP, TO, TSP, RC, BA
CIP-007-3 | Cyber Security — Systems Security Management | R6.1. | The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for monitoring for security events on all Cyber Assets within the Electronic Security Perimeter. |  | Pending Approval |  |  | GOP, GO, TOP, TO, TSP, RC, BA
CIP-007-3 | Cyber Security — Systems Security Management | R6.2. | The security monitoring controls shall issue automated or manual alerts for detected Cyber Security Incidents. |  | Pending Approval |  |  | GOP, GO, TOP, TO, TSP, RC, BA
CIP-007-3 | Cyber Security — Systems Security Management | R6.3. | The Responsible Entity shall maintain logs of system events related to cyber security, where technically feasible, to support incident response as required in Standard CIP008-3. |  | Pending Approval |  |  | TSP, GOP, GO, TO, TOP, RC, BA
CIP-007-3 | Cyber Security — Systems Security Management | R6.4. | The Responsible Entity shall retain all logs specified in Requirement R6 for ninety calendar days. |  | Pending Approval |  |  | GOP, GO, TOP, TO, TSP, RC, BA
CIP-007-3 | Cyber Security — Systems Security Management | R6.5. | The Responsible Entity shall review logs of system events related to cyber security and maintain records documenting review of logs. |  | Pending Approval |  |  | GOP, GO, TOP, TO, TSP, RC, BA
CIP-007-3 | Cyber Security — Systems Security Management | R7. | Disposal or Redeployment — The Responsible Entity shall establish and implement formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-3. |  | Pending Approval |  |  | GOP, GO, TOP, TO, TSP, RC, BA
CIP-007-3 | Cyber Security — Systems Security Management | R7.1. | Prior to the disposal of such assets, the Responsible Entity shall destroy or erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  | Pending Approval |  |  | GOP, GO, TOP, TO, TSP, RC, BA
CIP-007-3 | Cyber Security — Systems Security Management | R7.2. | Prior to redeployment of such assets, the Responsible Entity shall, at a minimum, erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  | Pending Approval |  |  | GOP, GO, TOP, TO, TSP, RC, BA
CIP-007-3 | Cyber Security — Systems Security Management | R7.3. | The Responsible Entity shall maintain records that such assets were disposed of or redeployed in accordance with documented procedures. |  | Pending Approval |  |  | GOP, GO, TOP, TO, TSP, RC, BA
CIP-007-3 | Cyber Security — Systems Security Management | R8.1. | R8. Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter at least annually. The vulnerability assessment shall include, at a minimum, the following: R8.1. A document identifying the vulnerability assessment process |  | Pending Approval |  |  | TO, TOP, GO, GOP, TSP, BA, RC
CIP-007-3 | Cyber Security — Systems Security Management | R8.2. | R8. Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter at least annually. The vulnerability assessment shall include, at a minimum, the following: R8.2. A review to verify that only ports and services required for operation of the Cyber Assets within the Electronic Security Perimeter are enabled |  | Pending Approval |  |  | GOP, GO, TOP, TO, TSP, BA, RC
CIP-007-3 | Cyber Security — Systems Security Management | R8.3. | R8. Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter at least annually. The vulnerability assessment shall include, at a minimum, the following: R8.3. A review of controls for default accounts |  | Pending Approval |  |  | TSP, GO, GOP, TOP, TO, RC, BA
CIP-007-3 | Cyber Security — Systems Security Management | R8.4. | R8. Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter at least annually. The vulnerability assessment shall include, at a minimum, the following: R8.4. Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  | Pending Approval |  |  | GOP, GO, TOP, TO, TSP, RC, BA
CIP-007-3 | Cyber Security — Systems Security Management | R9. | Documentation Review and Maintenance — The Responsible Entity shall review and update the documentation specified in Standard CIP-007-3 at least annually. Changes resulting from modifications to the systems or controls shall be documented within thirty calendar days of the change being completed. |  | Pending Approval |  |  | GOP, GO, TOP, TO, TSP, BA, RC
CIP-007-3a | Cyber Security - Systems Security Management | R1. | Test Procedures — The Responsible Entity shall ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls. For purposes of Standard CIP-007-3, a significant change shall, at a minimum, include implementation of security patches, cumulative service packs, vendor releases, and version upgrades of operating systems, applications, database platforms, or other third-party software or firmware. | MEDIUM | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3a | Cyber Security - Systems Security Management | R1.1. | The Responsible Entity shall create, implement, and maintain cyber security test procedures in a manner that minimizes adverse effects on the production system or its operation. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3a | Cyber Security - Systems Security Management | R1.2. | The Responsible Entity shall document that testing is performed in a manner that reflects the production environment. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3a | Cyber Security - Systems Security Management | R1.3. | The Responsible Entity shall document test results. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3a | Cyber Security - Systems Security Management | R2. | Ports and Services — The Responsible Entity shall establish, document and implement a process to ensure that only those ports and services required for normal and emergency operations are enabled. | MEDIUM | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3a | Cyber Security - Systems Security Management | R2.1. | The Responsible Entity shall enable only those ports and services required for normal and emergency operations. | MEDIUM | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3a | Cyber Security - Systems Security Management | R2.2. | The Responsible Entity shall disable other ports and services, including those used for testing purposes, prior to production use of all Cyber Assets inside the Electronic Security Perimeter(s). | MEDIUM | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3a | Cyber Security - Systems Security Management | R2.3. | In the case where unused ports and services cannot be disabled due to technical limitations, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. | MEDIUM | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3a | Cyber Security - Systems Security Management | R3. | Security Patch Management — The Responsible Entity, either separately or as a component of the documented configuration management process specified in CIP-003-3 Requirement R6, shall establish, document and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3a | Cyber Security - Systems Security Management | R3.1. | The Responsible Entity shall document the assessment of security patches and security upgrades for applicability within thirty calendar days of availability of the patches or upgrades. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3a | Cyber Security - Systems Security Management | R3.2. | The Responsible Entity shall document the implementation of security patches. In any case where the patch is not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3a | Cyber Security - Systems Security Management | R4. | Malicious Software Prevention — The Responsible Entity shall use anti-virus software and other malicious software (“malware”) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter(s). | MEDIUM | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3a | Cyber Security - Systems Security Management | R4.1. | The Responsible Entity shall document and implement anti-virus and malware prevention tools. In the case where anti-virus software and malware prevention tools are not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. | MEDIUM | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3a | Cyber Security - Systems Security Management | R4.2. | The Responsible Entity shall document and implement a process for the update of anti-virus and malware prevention “signatures.” The process must address testing and installing the signatures. | MEDIUM | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3a | Cyber Security - Systems Security Management | R5. | Account Management — The Responsible Entity shall establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3a | Cyber Security - Systems Security Management | R5.1. | The Responsible Entity shall ensure that individual and shared system accounts and authorized access permissions are consistent with the concept of “need to know” with respect to work functions performed. | MEDIUM | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3a | Cyber Security - Systems Security Management | R5.1.1. | The Responsible Entity shall ensure that user accounts are implemented as approved by designated personnel. Refer to Standard CIP-003-3 Requirement R5. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3a | Cyber Security - Systems Security Management | R5.1.2. | The Responsible Entity shall establish methods, processes, and procedures that generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of ninety days. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3a | Cyber Security - Systems Security Management | R5.1.3. | The Responsible Entity shall review, at least annually, user accounts to verify access privileges are in accordance with Standard CIP-003-3 Requirement R5 and Standard CIP-004-3 Requirement R4. | MEDIUM | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3a | Cyber Security - Systems Security Management | R5.2. | The Responsible Entity shall implement a policy to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3a | Cyber Security - Systems Security Management | R5.2.1. | The policy shall include the removal, disabling, or renaming of such accounts where possible. For such accounts that must remain enabled, passwords shall be changed prior to putting any system into service. | MEDIUM | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3a | Cyber Security - Systems Security Management | R5.2.2. | The Responsible Entity shall identify those individuals with access to shared accounts. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3a | Cyber Security - Systems Security Management | R5.2.3. | Where such accounts must be shared, the Responsible Entity shall have a policy for managing the use of such accounts that limits access to only those with authorization, an audit trail of the account use (automated or manual), and steps for securing the account in the event of personnel changes (for example, change in assignment or termination). | MEDIUM | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3a | Cyber Security - Systems Security Management | R5.3. | At a minimum, the Responsible Entity shall require and use passwords, subject to the following, as technically feasible: | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3a | Cyber Security - Systems Security Management | R5.3.1. | Each password shall be a minimum of six characters. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3a | Cyber Security - Systems Security Management | R5.3.2. | Each password shall consist of a combination of alpha, numeric, and “special” characters. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3a | Cyber Security - Systems Security Management | R5.3.3. | Each password shall be changed at least annually, or more frequently based on risk. | MEDIUM | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3a | Cyber Security - Systems Security Management | R6. | Security Status Monitoring — The Responsible Entity shall ensure that all Cyber Assets within the Electronic Security Perimeter, as technically feasible, implement automated tools or organizational process controls to monitor system events that are related to cyber security. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3a | Cyber Security - Systems Security Management | R6.1. | The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for monitoring for security events on all Cyber Assets within the Electronic Security Perimeter. | MEDIUM | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3a | Cyber Security - Systems Security Management | R6.2. | The security monitoring controls shall issue automated or manual alerts for detected Cyber Security Incidents. | MEDIUM | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3a | Cyber Security - Systems Security Management | R6.3. | The Responsible Entity shall maintain logs of system events related to cyber security, where technically feasible, to support incident response as required in Standard CIP-008-3. | MEDIUM | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3a | Cyber Security - Systems Security Management | R6.4. | The Responsible Entity shall retain all logs specified in Requirement R6 for ninety calendar days. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3a | Cyber Security - Systems Security Management | R6.5. | The Responsible Entity shall review logs of system events related to cyber security and maintain records documenting review of logs. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3a | Cyber Security - Systems Security Management | R7. | Disposal or Redeployment — The Responsible Entity shall establish and implement formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-3. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3a | Cyber Security - Systems Security Management | R7.1. | Prior to the disposal of such assets, the Responsible Entity shall destroy or erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3a | Cyber Security - Systems Security Management | R7.2. | Prior to redeployment of such assets, the Responsible Entity shall, at a minimum, erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3a | Cyber Security - Systems Security Management | R8. | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter at least annually. The vulnerability assessment shall include, at a minimum, the following: | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3a | Cyber Security - Systems Security Management | R8.1. | A document identifying the vulnerability assessment process; | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3a | Cyber Security - Systems Security Management | R8.2. | A review to verify that only ports and services required for operation of the Cyber Assets within the Electronic Security Perimeter are enabled; | MEDIUM | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3a | Cyber Security - Systems Security Management | R8.3. | A review of controls for default accounts; and, | MEDIUM | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3a | Cyber Security - Systems Security Management | R8.4. | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. | MEDIUM | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3a | Cyber Security - Systems Security Management | R9. | Documentation Review and Maintenance — The Responsible Entity shall review and update the documentation specified in Standard CIP-007-3 at least annually. Changes resulting from modifications to the systems or controls shall be documented within thirty calendar days of the change being completed. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3b | Cyber Security - Systems Security Management | R1. | Test Procedures—The Responsible Entity shall ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls. For purposes of Standard CIP-007-3, a significant change shall, at a minimum, include implementation of security patches, cumulative service packs, vendor releases, and version upgrades of operating systems, applications, database platforms, or other third-party software or firmware. | MEDIUM | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3b | Cyber Security - Systems Security Management | R1.1. | The Responsible Entity shall create, implement, and maintain cyber security test procedures in a manner that minimizes adverse effects on the production system or its operation. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3b | Cyber Security - Systems Security Management | R1.2. | The Responsible Entity shall document that testing is performed in a manner that reflects the production environment. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3b | Cyber Security - Systems Security Management | R1.3. | The Responsible Entity shall document test results. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3b | Cyber Security - Systems Security Management | R2. | Ports and Services — The Responsible Entity shall establish, document and implement a process to ensure that only those ports and services required for normal and emergency operations are enabled. | MEDIUM | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3b | Cyber Security - Systems Security Management | R2.1. | The Responsible Entity shall enable only those ports and services required for normal and emergency operations. | MEDIUM | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3b | Cyber Security - Systems Security Management | R2.2. | The Responsible Entity shall disable other ports and services, including those used for testing purposes, prior to production use of all Cyber Assets inside the Electronic Security Perimeter(s). | MEDIUM | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3b | Cyber Security - Systems Security Management | R2.3. | In the case where unused ports and services cannot be disabled due to technical limitations, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. | MEDIUM | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3b | Cyber Security - Systems Security Management | R3. | Security Patch Management — The Responsible Entity, either separately or as a component of the documented configuration management process specified in CIP-003-3 Requirement R6, shall establish, document and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3b | Cyber Security - Systems Security Management | R3.1. | The Responsible Entity shall document the assessment of security patches and security upgrades for applicability within thirty calendar days of availability of the patches or upgrades. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3b | Cyber Security - Systems Security Management | R3.2. | The Responsible Entity shall document the implementation of security patches. In any case where the patch is not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3b | Cyber Security - Systems Security Management | R4. | Malicious Software Prevention — The Responsible Entity shall use anti-virus software and other malicious software (“malware”) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter(s). | MEDIUM | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3b | Cyber Security - Systems Security Management | R4.1. | The Responsible Entity shall document and implement anti-virus and malware prevention tools. In the case where anti-virus software and malware prevention tools are not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. | MEDIUM | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3b | Cyber Security - Systems Security Management | R4.2. | The Responsible Entity shall document and implement a process for the update of anti-virus and malware prevention “signatures.” The process must address testing and installing the signatures. | MEDIUM | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3b | Cyber Security - Systems Security Management | R5. | Account Management — The Responsible Entity shall establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3b | Cyber Security - Systems Security Management | R5.1. | The Responsible Entity shall ensure that individual and shared system accounts and authorized access permissions are consistent with the concept of “need to know” with respect to work functions performed. | MEDIUM | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3b | Cyber Security - Systems Security Management | R5.1.1. | The Responsible Entity shall ensure that user accounts are implemented as approved by designated personnel. Refer to Standard CIP-003-3 Requirement R5. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3b | Cyber Security - Systems Security Management | R5.1.2. | The Responsible Entity shall establish methods, processes, and procedures that generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of ninety days. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3b | Cyber Security - Systems Security Management | R5.1.3. | The Responsible Entity shall review, at least annually, user accounts to verify access privileges are in accordance with Standard CIP-003-3 Requirement R5 and Standard CIP-004-3 Requirement R4. | MEDIUM | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3b | Cyber Security - Systems Security Management | R5.2. | The Responsible Entity shall implement a policy to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3b | Cyber Security - Systems Security Management | R5.2.1. | The policy shall include the removal, disabling, or renaming of such accounts where possible. For such accounts that must remain enabled, passwords shall be changed prior to putting any system into service. | MEDIUM | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3b | Cyber Security - Systems Security Management | R5.2.2. | The Responsible Entity shall identify those individuals with access to shared accounts. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3b | Cyber Security - Systems Security Management | R5.2.3. | Where such accounts must be shared, the Responsible Entity shall have a policy for managing the use of such accounts that limits access to only those with authorization, an audit trail of the account use (automated or manual), and steps for securing the account in the event of personnel changes (for example, change in assignment or termination). | MEDIUM | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3b | Cyber Security - Systems Security Management | R5.3. | At a minimum, the Responsible Entity shall require and use passwords, subject to the following, as technically feasible: | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3b | Cyber Security - Systems Security Management | R5.3.1. | Each password shall be a minimum of six characters. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3b | Cyber Security - Systems Security Management | R5.3.2. | Each password shall consist of a combination of alpha, numeric, and “special” characters. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3b | Cyber Security - Systems Security Management | R5.3.3. | Each password shall be changed at least annually, or more frequently based on risk. | MEDIUM | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3b | Cyber Security - Systems Security Management | R6. | Security Status Monitoring — The Responsible Entity shall ensure that all Cyber Assets within the Electronic Security Perimeter, as technically feasible, implement automated tools or organizational process controls to monitor system events that are related to cyber security. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3b | Cyber Security - Systems Security Management | R6.1. | The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for monitoring for security events on all Cyber Assets within the Electronic Security Perimeter. | MEDIUM | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3b | Cyber Security - Systems Security Management | R6.2. | The security monitoring controls shall issue automated or manual alerts for detected Cyber Security Incidents. | MEDIUM | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3b | Cyber Security - Systems Security Management | R6.3. | The Responsible Entity shall maintain logs of system events related to cyber security, where technically feasible, to support incident response as required in Standard CIP-008-3. | MEDIUM | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3b | Cyber Security - Systems Security Management | R6.4. | The Responsible Entity shall retain all logs specified in Requirement R6 for ninety calendar days. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3b | Cyber Security - Systems Security Management | R6.5. | The Responsible Entity shall review logs of system events related to cyber security and maintain records documenting review of logs. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3b | Cyber Security - Systems Security Management | R7. | Disposal or Redeployment — The Responsible Entity shall establish and implement formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-3. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3b | Cyber Security - Systems Security Management | R7.1. | Prior to the disposal of such assets, the Responsible Entity shall destroy or erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3b | Cyber Security - Systems Security Management | R7.2. | Prior to redeployment of such assets, the Responsible Entity shall, at a minimum, erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3b | Cyber Security - Systems Security Management | R7.3. | The Responsible Entity shall maintain records that such assets were disposed of or redeployed in accordance with documented procedures. (Retirement approved by FERC effective January 21, 2014.) | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3b | Cyber Security - Systems Security Management | R8. | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter at least annually. The vulnerability assessment shall include, at a minimum, the following: | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3b | Cyber Security - Systems Security Management | R8.1. | A document identifying the vulnerability assessment process; | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3b | Cyber Security - Systems Security Management | R8.2. | A review to verify that only ports and services required for operation of the Cyber Assets within the Electronic Security Perimeter are enabled; | MEDIUM | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3b | Cyber Security - Systems Security Management | R8.3. | A review of controls for default accounts; and, | MEDIUM | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3b | Cyber Security - Systems Security Management | R8.4. | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. | MEDIUM | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-3b | Cyber Security - Systems Security Management | R9. | Documentation Review and Maintenance — The Responsible Entity shall review and update the documentation specified in Standard CIP-007-3 at least annually. Changes resulting from modifications to the systems or controls shall be documented within thirty calendar days of the change being completed. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-4a | Cyber Security — Systems Security Management | R1. | Test Procedures —The Responsible Entity shall ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls. For purposes of Standard CIP-007-4, a significant change shall, at a minimum, include implementation of security patches, cumulative service packs, vendor releases, and version upgrades of operating systems, applications, database platforms, or other third-party software or firmware. | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-4a | Cyber Security — Systems Security Management | R1.1. | The Responsible Entity shall create, implement, and maintain cyber security test procedures in a manner that minimizes adverse effects on the production system or its operation. | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-4a | Cyber Security — Systems Security Management | R1.2. | The Responsible Entity shall document that testing is performed in a manner that reflects the production environment. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-4a | Cyber Security — Systems Security Management | R1.3. | The Responsible Entity shall document test results. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-4a | Cyber Security — Systems Security Management | R2. | Ports and Services —The Responsible Entity shall establish, document and implement a process to ensure that only those ports and services required for normal and emergency operations are enabled. | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-4a | Cyber Security — Systems Security Management | R2.1. | The Responsible Entity shall enable only those ports and services required for normal and emergency operations. | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-4a | Cyber Security — Systems Security Management | R2.2. | The Responsible Entity shall disable other ports and services, including those used for testing purposes, prior to production use of all Cyber Assets inside the Electronic Security Perimeter(s). | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-4a | Cyber Security — Systems Security Management | R2.3. | In the case where unused ports and services cannot be disabled due to technical limitations, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-4a | Cyber Security — Systems Security Management | R3. | Security Patch Management —The Responsible Entity, either separately or as a component of the documented configuration management process specified in CIP-003-4 Requirement R6, shall establish, document and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-4a | Cyber Security — Systems Security Management | R3.1. | The Responsible Entity shall document the assessment of security patches and security upgrades for applicability within thirty calendar days of availability of the patches or upgrades. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-4a | Cyber Security — Systems Security Management | R3.2. | The Responsible Entity shall document the implementation of security patches. In any case where the patch is not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-4a | Cyber Security — Systems Security Management | R4. | Malicious Software Prevention —The Responsible Entity shall use anti-virus software and other malicious software (“malware”) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter(s). | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-4a | Cyber Security — Systems Security Management | R4.1. | The Responsible Entity shall document and implement anti-virus and malware prevention tools. In the case where anti-virus software and malware prevention tools are not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-4a | Cyber Security — Systems Security Management | R4.2. | The Responsible Entity shall document and implement a process for the update of anti-virus and malware prevention “signatures.” The process must address testing and installing the signatures. | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-4a | Cyber Security — Systems Security Management | R5. | Account Management — The Responsible Entity shall establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-4a | Cyber Security — Systems Security Management | R5.1. | The Responsible Entity shall ensure that individual and shared system accounts and authorized access permissions are consistent with the concept of “need to know” with respect to work functions performed. | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-4a | Cyber Security — Systems Security Management | R5.1.1. | The Responsible Entity shall ensure that user accounts are implemented as approved by designated personnel. Refer to Standard CIP-003-4 Requirement R5. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-4a | Cyber Security — Systems Security Management | R5.1.2. | The Responsible Entity shall establish methods, processes, and procedures that generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of ninety days. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-4a | Cyber Security — Systems Security Management | R5.1.3. | The Responsible Entity shall review, at least annually, user accounts to verify access privileges are in accordance with Standard CIP-003-4 Requirement R5 and Standard CIP-004-4 Requirement R4. | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-4a | Cyber Security — Systems Security Management | R5.2. | The Responsible Entity shall implement a policy to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-4a | Cyber Security — Systems Security Management | R5.2.1. | The policy shall include the removal, disabling, or renaming of such accounts where possible. For such accounts that must remain enabled, passwords shall be changed prior to putting any system into service. | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-4a | Cyber Security — Systems Security Management | R5.2.2. | The Responsible Entity shall identify those individuals with access to shared accounts. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-4a | Cyber Security — Systems Security Management | R5.2.3. | Where such accounts must be shared, the Responsible Entity shall have a policy for managing the use of such accounts that limits access to only those with authorization, an audit trail of the account use (automated or manual), and steps for securing the account in the event of personnel changes (for example, change in assignment or termination). | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-4a | Cyber Security — Systems Security Management | R5.3. | At a minimum, the Responsible Entity shall require and use passwords, subject to the following, as technically feasible: | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-4a | Cyber Security — Systems Security Management | R5.3.1. | Each password shall be a minimum of six characters. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-4a | Cyber Security — Systems Security Management | R5.3.2. | Each password shall consist of a combination of alpha, numeric, and “special” characters. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-4a | Cyber Security — Systems Security Management | R5.3.3. | Each password shall be changed at least annually, or more frequently based on risk. | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-4a | Cyber Security — Systems Security Management | R6. | Security Status Monitoring — The Responsible Entity shall ensure that all Cyber Assets within the Electronic Security Perimeter, as technically feasible, implement automated tools or organizational process controls to monitor system events that are related to cyber security. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-4a | Cyber Security — Systems Security Management | R6.1. | The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for monitoring for security events on all Cyber Assets within the Electronic Security Perimeter. | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-4a | Cyber Security — Systems Security Management | R6.2. | The security monitoring controls shall issue automated or manual alerts for detected Cyber Security Incidents. | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-4a | Cyber Security — Systems Security Management | R6.3. | The Responsible Entity shall maintain logs of system events related to cyber security, where technically feasible, to support incident response as required in Standard CIP-008-4. | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-4a | Cyber Security — Systems Security Management | R6.4. | The Responsible Entity shall retain all logs specified in Requirement R6 for ninety calendar days. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-4a | Cyber Security — Systems Security Management | R6.5. | The Responsible Entity shall review logs of system events related to cyber security and maintain records documenting review of logs. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-4a | Cyber Security — Systems Security Management | R7. | Disposal or Redeployment — The Responsible Entity shall establish and implement formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-4. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-4a | Cyber Security — Systems Security Management | R7.1. | Prior to the disposal of such assets, the Responsible Entity shall destroy or erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-4a | Cyber Security — Systems Security Management | R7.2. | Prior to redeployment of such assets, the Responsible Entity shall, at a minimum, erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-4a | Cyber Security — Systems Security Management | R7.3. | The Responsible Entity shall maintain records that such assets were disposed of or redeployed in accordance with documented procedures. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-4a | Cyber Security — Systems Security Management | R8. | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter at least annually. The vulnerability assessment shall include, at a minimum, the following: | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-4a | Cyber Security — Systems Security Management | R8.1. | A document identifying the vulnerability assessment process; | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-4a | Cyber Security — Systems Security Management | R8.2. | A review to verify that only ports and services required for operation of the Cyber Assets within the Electronic Security Perimeter are enabled; | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-4a | Cyber Security — Systems Security Management | R8.3. | A review of controls for default accounts; and, | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-4a | Cyber Security — Systems Security Management | R8.4. | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-4a | Cyber Security — Systems Security Management | R9. | Documentation Review and Maintenance —The Responsible Entity shall review and update the documentation specified in Standard CIP-007-4 at least annually. Changes resulting from modifications to the systems or controls shall be documented within thirty calendar days of the change being completed. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-007-5 | Cyber Security — Systems Security Management | R1. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP‐007‐5 Table R1 – Ports and Services. [Violation Risk Factor: Medium] [Time Horizon: Same Day Operations.] | MEDIUM | Retired |  |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-007-5 | Cyber Security — Systems Security Management | R2. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP‐007‐5 Table R2 – Security Patch Management. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Retired |  |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-007-5 | Cyber Security — Systems Security Management | R3. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP‐007‐5 Table R3 – Malicious Code Prevention. [Violation Risk Factor: Medium] [Time Horizon: Same Day Operations]. | MEDIUM | Retired |  |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-007-5 | Cyber Security — Systems Security Management | R4. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP‐007‐5 Table R4 – Security Event Monitoring. [Violation Risk Factor: Medium] [Time Horizon: Same Day Operations and Operations Assessment.] | MEDIUM | Retired |  |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-007-5 | Cyber Security — Systems Security Management | R5. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP‐007‐5 Table R5 – System Access Controls. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning]. | MEDIUM | Retired |  |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-007-6 | Cyber Security — Systems Security Management | R1. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R1 – Ports and Services. [Violation Risk Factor: Medium] [Time Horizon: Same Day Operations.] | MEDIUM | Effective | 2016-07-01 |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-007-6 | Cyber Security — Systems Security Management | R2. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R2 – Security Patch Management. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning]. | MEDIUM | Effective | 2016-07-01 |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-007-6 | Cyber Security — Systems Security Management | R3. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R3 – Malicious Code Prevention. [Violation Risk Factor: Medium] [Time Horizon: Same Day Operations]. | MEDIUM | Effective | 2016-07-01 |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-007-6 | Cyber Security — Systems Security Management | R4. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R4 – Security Event Monitoring. [Violation Risk Factor: Medium] [Time Horizon: Same Day Operations and Operations Assessment.] | MEDIUM | Effective | 2016-07-01 |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-007-6 | Cyber Security — Systems Security Management | R5. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R5 – System Access Controls. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning]. | MEDIUM | Effective | 2016-07-01 |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-008-3 | Cyber Security - Incident Reporting and Response Planning | R1. | Cyber Security Incident Response Plan — The Responsible Entity shall develop and maintain a Cyber Security Incident response plan and implement the plan in response to Cyber Security Incidents. The Cyber Security Incident response plan shall address, at a minimum, the following: | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-008-3 | Cyber Security - Incident Reporting and Response Planning | R1.1. | Procedures to characterize and classify events as reportable Cyber Security Incidents. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-008-3 | Cyber Security - Incident Reporting and Response Planning | R1.2. | Response actions, including roles and responsibilities of Cyber Security Incident response teams, Cyber Security Incident handling procedures, and communication plans. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-008-3 | Cyber Security - Incident Reporting and Response Planning | R1.3. | Process for reporting Cyber Security Incidents to the Electricity Sector Information Sharing and Analysis Center (ES-ISAC). The Responsible Entity must ensure that all reportable Cyber Security Incidents are reported to the ES-ISAC either directly or through an intermediary. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-008-3 | Cyber Security - Incident Reporting and Response Planning | R1.4. | Process for updating the Cyber Security Incident response plan within thirty calendar days of any changes. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-008-3 | Cyber Security - Incident Reporting and Response Planning | R1.5. | Process for ensuring that the Cyber Security Incident response plan is reviewed at least annually. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-008-3 | Cyber Security - Incident Reporting and Response Planning | R1.6. | Process for ensuring the Cyber Security Incident response plan is tested at least annually. A test of the Cyber Security Incident response plan can range from a paper drill, to a full operational exercise, to the response to an actual incident. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-008-3 | Cyber Security - Incident Reporting and Response Planning | R2. | Cyber Security Incident Documentation — The Responsible Entity shall keep relevant documentation related to Cyber Security Incidents reportable per Requirement R1.1 for three calendar years. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-008-4 | Cyber Security — Incident Reporting and Response Planning | R1. | Cyber Security Incident Response Plan —The Responsible Entity shall develop and maintain a Cyber Security Incident response plan and implement the plan in response to Cyber Security Incidents. The Cyber Security Incident response plan shall address, at a minimum, the following: | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-008-4 | Cyber Security — Incident Reporting and Response Planning | R1.1. | Procedures to characterize and classify events as reportable Cyber Security Incidents. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-008-4 | Cyber Security — Incident Reporting and Response Planning | R1.2. | Response actions, including roles and responsibilities of Cyber Security Incident response teams, Cyber Security Incident handling procedures, and communication plans. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-008-4 | Cyber Security — Incident Reporting and Response Planning | R1.3. | Process for reporting Cyber Security Incidents to the Electricity Sector Information Sharing and Analysis Center (ES-ISAC). The Responsible Entity must ensure that all reportable Cyber Security Incidents are reported to the ES-ISAC either directly or through an intermediary. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-008-4 | Cyber Security — Incident Reporting and Response Planning | R1.4. | Process for updating the Cyber Security Incident response plan within thirty calendar days of any changes. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-008-4 | Cyber Security — Incident Reporting and Response Planning | R1.5. | Process for ensuring that the Cyber Security Incident response plan is reviewed at least annually. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-008-4 | Cyber Security — Incident Reporting and Response Planning | R1.6. | Process for ensuring the Cyber Security Incident response plan is tested at least annually. A test of the Cyber Security Incident response plan can range from a paper drill, to a full operational exercise, to the response to an actual incident. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-008-4 | Cyber Security — Incident Reporting and Response Planning | R2. | Cyber Security Incident Documentation —The Responsible Entity shall keep relevant documentation related to Cyber Security Incidents reportable per Requirement R1.1 for three calendar years. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-008-5 | Cyber Security — Incident Reporting and Response Planning | R1. | Each Responsible Entity shall document one or more Cyber Security Incident response plan(s) that collectively include each of the applicable requirement parts in CIP‐008‐5 Table R1 – Cyber Security Incident Response Plan Specifications. [Violation Risk Factor: Lower] [Time Horizon: Long Term Planning]. | LOWER | Retired | 2016-07-01 | 2021-03-31 | TOP, TO, RC, GOP, GO, DP, BA
CIP-008-5 | Cyber Security — Incident Reporting and Response Planning | R2. | Each Responsible Entity shall implement each of its documented Cyber Security Incident response plans to collectively include each of the applicable requirement parts in CIP‐008‐5 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning and Real‐Time Operations]. | LOWER | Retired | 2016-07-01 | 2021-03-31 | TOP, TO, RC, GOP, GO, DP, BA
CIP-008-5 | Cyber Security — Incident Reporting and Response Planning | R3. | Each Responsible Entity shall maintain each of its Cyber Security Incident response plans according to each of the applicable requirement parts in CIP‐008‐5 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. [Violation Risk Factor: Lower] [Time Horizon: Operations Assessment]. | LOWER | Retired | 2016-07-01 | 2021-03-31 | TOP, TO, RC, GOP, GO, DP, BA
CIP-008-6 | Cyber Security — Incident Reporting and Response Planning | R1. | Each Responsible Entity shall document one or more Cyber Security Incident response plan(s) that collectively include each of the applicable requirement parts in CIP-008-6 Table R1 – Cyber Security Incident Response Plan Specifications. [Violation Risk Factor: Lower] [Time Horizon: Long Term Planning]. | LOWER | Effective | 2021-04-01 |  | TO, TOP, RC, GOP, GO, DP, BA
CIP-008-6 | Cyber Security — Incident Reporting and Response Planning | R2. | Each Responsible Entity shall implement each of its documented Cyber Security Incident response plans to collectively include each of the applicable requirement parts in CIP-008-6 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning and Real-Time Operations]. | LOWER | Effective | 2021-04-01 |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-008-6 | Cyber Security — Incident Reporting and Response Planning | R3. | Each Responsible Entity shall maintain each of its Cyber Security Incident response plans according to each of the applicable requirement parts in CIP-008-6 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. [Violation Risk Factor: Lower] [Time Horizon: Operations Assessment]. | LOWER | Effective | 2021-04-01 |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-008-6 | Cyber Security — Incident Reporting and Response Planning | R4. | Each Responsible Entity shall notify the Electricity Information Sharing and Analysis Center (E-ISAC) and, if subject to the jurisdiction of the United States, the United States National Cybersecurity and Communications Integration Center (NCCIC),1 or their successors, of a Reportable Cyber Security Incident and a Cyber Security Incident that was an attempt to compromise, as determined by applying the criteria from Requirement R1, Part 1.2.1, a system identified in the “Applicable Systems” column, unless prohibited by law, in accordance with each of the applicable requirement parts in CIP-008-6 Table R4 – Notifications and Reporting for Cyber Security Incidents. [Violation Risk Factor: Lower] [Time Horizon: Operations Assessment]. | LOWER | Effective | 2021-04-01 |  | TOP, TO, RC, DP, BA, GOP, GO
CIP-009-3 | Cyber Security - Recovery Plans for Critical Cyber Assets | R1. | Recovery Plans — The Responsible Entity shall create and annually review recovery plan(s) for Critical Cyber Assets. The recovery plan(s) shall address at a minimum the following: | MEDIUM | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-009-3 | Cyber Security - Recovery Plans for Critical Cyber Assets | R1.1. | Specify the required actions in response to events or conditions of varying duration and severity that would activate the recovery plan(s). | MEDIUM | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-009-3 | Cyber Security - Recovery Plans for Critical Cyber Assets | R1.2. | Define the roles and responsibilities of responders. | MEDIUM | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-009-3 | Cyber Security - Recovery Plans for Critical Cyber Assets | R2. | Exercises — The recovery plan(s) shall be exercised at least annually. An exercise of the recovery plan(s) can range from a paper drill, to a full operational exercise, to recovery from an actual incident. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-009-3 | Cyber Security - Recovery Plans for Critical Cyber Assets | R3. | Change Control — Recovery plan(s) shall be updated to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident. Updates shall be communicated to personnel responsible for the activation and implementation of the recovery plan(s) within thirty calendar days of the change being completed. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-009-3 | Cyber Security - Recovery Plans for Critical Cyber Assets | R4. | Backup and Restore — The recovery plan(s) shall include processes and procedures for the backup and storage of information required to successfully restore Critical Cyber Assets. For example, backups may include spare electronic components or equipment, written documentation of configuration settings, tape backup, etc. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-009-3 | Cyber Security - Recovery Plans for Critical Cyber Assets | R5. | Testing Backup Media — Information essential to recovery that is stored on backup media shall be tested at least annually to ensure that the information is available. Testing can be completed off site. | LOWER | Retired | 2011-01-01 | 2016-06-30 | TSP, TOP, TO, RC, GOP, GO, BA
CIP-009-4 | Cyber Security — Recovery Plans for Critical Cyber Assets | R1. | Recovery Plans —The Responsible Entity shall create and annually review recovery plan(s) for Critical Cyber Assets. The recovery plan(s) shall address at a minimum the following: | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-009-4 | Cyber Security — Recovery Plans for Critical Cyber Assets | R1.1. | Specify the required actions in response to events or conditions of varying duration and severity that would activate the recovery plan(s). | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-009-4 | Cyber Security — Recovery Plans for Critical Cyber Assets | R1.2. | Define the roles and responsibilities of responders. | MEDIUM | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-009-4 | Cyber Security — Recovery Plans for Critical Cyber Assets | R2. | Exercises —The recovery plan(s) shall be exercised at least annually. An exercise of the recovery plan(s) can range from a paper drill, to a full operational exercise, to recovery from an actual incident. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-009-4 | Cyber Security — Recovery Plans for Critical Cyber Assets | R3. | Change Control — Recovery plan(s) shall be updated to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident. Updates shall be communicated to personnel responsible for the activation and implementation of the recovery plan(s) within thirty calendar days of the change being completed. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-009-4 | Cyber Security — Recovery Plans for Critical Cyber Assets | R4. | Backup and Restore —The recovery plan(s) shall include processes and procedures for the backup and storage of information required to successfully restore Critical Cyber Assets. For example, backups may include spare electronic components or equipment, written documentation of configuration settings, tape backup, etc. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-009-4 | Cyber Security — Recovery Plans for Critical Cyber Assets | R5. | Testing Backup Media — Information essential to recovery that is stored on backup media shall be tested at least annually to ensure that the information is available. Testing can be completed off site. | LOWER | Retired |  |  | TSP, TOP, TO, RC, GOP, GO, BA
CIP-009-5 | Cyber Security — Recovery Plans for BES Cyber Systems | R1. | Each Responsible Entity shall have one or more documented recovery plans that collectively include each of the applicable requirement parts in CIP‐009‐5 Table R1 – Recovery Plan Specifications. [Violation Risk Factor: Medium] [Time Horizon: Long Term Planning]. | MEDIUM | Retired |  |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-009-5 | Cyber Security — Recovery Plans for BES Cyber Systems | R2. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, its documentedrecovery plan(s) to collectively include each of the applicable requirement parts in CIP‐009‐5 Table R2 – Recovery Plan Implementation and Testing. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning and Real‐time Operations.] | LOWER | Retired |  |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-009-5 | Cyber Security — Recovery Plans for BES Cyber Systems | R3. | Each Responsible Entity shall maintain each of its recovery plans in accordance with each of the applicable requirement parts in CIP‐009‐5 Table R3 – Recovery Plan Review, Update and Communication. [Violation Risk Factor: Lower] [Time Horizon: Operations Assessment]. | LOWER | Retired |  |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-009-6 | Cyber Security — Recovery Plans for BES Cyber Systems | R1. | Each Responsible Entity shall have one or more documented recovery plan(s) that collectively include each of the applicable requirement parts in CIP-009-6 Table R1 – Recovery Plan Specifications. [Violation Risk Factor: Medium] [Time Horizon: Long Term Planning]. | MEDIUM | Effective | 2016-07-01 |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-009-6 | Cyber Security — Recovery Plans for BES Cyber Systems | R2. | Each Responsible Entity shall implement its documented recovery plan(s) to collectively include each of the applicable requirement parts in CIP-009-6 Table R2 – Recovery Plan Implementation and Testing. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning and Real-time Operations.] | LOWER | Effective | 2016-07-01 |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-009-6 | Cyber Security — Recovery Plans for BES Cyber Systems | R3. | Each Responsible Entity shall maintain each of its recovery plan(s) in accordance with each of the applicable requirement parts in CIP-009-6 Table R3 – Recovery Plan Review, Update and Communication. [Violation Risk Factor: Lower] [Time Horizon: Operations Assessment]. | LOWER | Effective | 2016-07-01 |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-010-1 | Cyber Security — Configuration Change Management and Vulnerability Assessments | R1. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP‐010‐1 Table R1 – Configuration Change Management. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning]. | MEDIUM | Retired |  |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-010-1 | Cyber Security — Configuration Change Management and Vulnerability Assessments | R2. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP‐010‐1 Table R2 – Configuration Monitoring. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning]. | MEDIUM | Retired |  |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-010-1 | Cyber Security — Configuration Change Management and Vulnerability Assessments | R3. | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP‐010‐1 Table R3– Vulnerability Assessments. [Violation Risk Factor: Medium] [Time Horizon: Long‐term Planning and Operations Planning] | MEDIUM | Retired |  |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-010-2 | Cyber Security — Configuration Change Management and Vulnerability Assessments | R1. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-010-2 Table R1 – Configuration Change Management. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning]. | MEDIUM | Retired | 2016-07-01 | 2020-06-30 | TOP, TO, RC, GOP, GO, DP, BA
CIP-010-2 | Cyber Security — Configuration Change Management and Vulnerability Assessments | R2. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-010-2 Table R2 – Configuration Monitoring. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning]. | MEDIUM | Retired | 2016-07-01 | 2020-06-30 | TOP, TO, RC, GOP, GO, DP, BA
CIP-010-2 | Cyber Security — Configuration Change Management and Vulnerability Assessments | R3. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-010-2 Table R3– Vulnerability Assessments. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning and Operations Planning] | MEDIUM | Retired | 2016-07-01 | 2020-06-30 | TOP, TO, RC, GOP, GO, DP, BA
CIP-010-2 | Cyber Security — Configuration Change Management and Vulnerability Assessments | R4. | Each Responsible Entity, for its high impact and medium impact BES Cyber Systems and associated Protected Cyber Assets, shall implement, except under CIP Exceptional Circumstances, one or more documented plan(s) for Transient Cyber Assets and Removable Media that include the sections in Attachment 1. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning and Operations Planning] | MEDIUM | Retired | 2017-04-01 | 2020-06-30 | TOP, TO, RC, GOP, GO, DP, BA
CIP-010-3 | Cyber Security — Configuration Change Management and Vulnerability Assessments | R1. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-010-3 Table R1 – Configuration Change Management. | MEDIUM | Retired | 2020-10-01 | 2022-09-30 | TOP, TO, RC, GOP, GO, DP, BA
CIP-010-3 | Cyber Security — Configuration Change Management and Vulnerability Assessments | R1. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-010-3 Table R1 – Configuration Change Management. | MEDIUM | Retired | 2020-10-01 | 2022-09-30 | TOP, TO, RC, GOP, GO, DP, BA
CIP-010-3 | Cyber Security — Configuration Change Management and Vulnerability Assessments | R2. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-010-3 Table R2 – Configuration Monitoring. | MEDIUM | Retired | 2020-10-01 | 2022-09-30 | TOP, TO, RC, GOP, GO, DP, BA
CIP-010-3 | Cyber Security — Configuration Change Management and Vulnerability Assessments | R3. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-010-3 Table R3– Vulnerability Assessments. | MEDIUM | Retired | 2020-10-01 | 2022-09-30 | TOP, TO, RC, GOP, GO, DP, BA
CIP-010-3 | Cyber Security — Configuration Change Management and Vulnerability Assessments | R4. | Each Responsible Entity, for its high impact and medium impact BES Cyber Systems and associated Protected Cyber Assets, shall implement, except under CIP Exceptional Circumstances, one or more documented plan(s) for Transient Cyber Assets and Removable Media that include the sections in Attachment 1. | MEDIUM | Retired | 2020-10-01 | 2022-09-30 | TOP, TO, RC, GOP, GO, DP, BA
CIP-010-4 | – Cyber Security — Configuration Change Management and Vulnerability Assessments | R1. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-010-4 Table R1 – Configuration Change Management. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning]. | MEDIUM | Effective | 2022-10-01 |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-010-4 | – Cyber Security — Configuration Change Management and Vulnerability Assessments | R2. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-010-4 Table R2 – Configuration Monitoring. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning]. | MEDIUM | Effective | 2022-10-01
CIP-010-4 | – Cyber Security — Configuration Change Management and Vulnerability Assessments | R3. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-010-3 Table R3– Vulnerability Assessments. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning and Operations Planning] | MEDIUM | Effective | 2022-10-01
CIP-010-4 | – Cyber Security — Configuration Change Management and Vulnerability Assessments | R4. | Each Responsible Entity, for its high impact and medium impact BES Cyber Systems and associated Protected Cyber Assets, shall implement, except under CIP Exceptional Circumstances, one or more documented plan(s) for Transient Cyber Assets and Removable Media that include the sections in Attachment 1. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning and Operations Planning] | MEDIUM | Effective | 2022-10-01
CIP-011-1 | Cyber Security Information Protection | R1. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented information protection program(s) that collectively includes each of the applicable requirement parts in CIP‐011‐1 Table R1 – Information Protection. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning]. | MEDIUM | Never Came Into Effect in Ontario |  |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-011-1 | Cyber Security Information Protection | R2. | Each Responsible Entity shall implement one or more documented processes that collectively include the applicable requirement parts in CIP‐011‐1 Table R2 – BES Cyber Asset Reuse and Disposal. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning]. | LOWER | Never Came Into Effect in Ontario |  |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-011-2 | Cyber Security Information Protection | R1. | Each Responsible Entity shall implement one or more documented information protection program(s) that collectively includes each of the applicable requirement parts in CIP-011-2 Table R1 – Information Protection. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning]. | MEDIUM | Effective | 2016-07-01 |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-011-2 | Cyber Security Information Protection | R2. | Each Responsible Entity shall implement one or more documented process(es) that collectively include the applicable requirement parts in CIP-011-2 Table R2 – BES Cyber Asset Reuse and Disposal. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning]. | LOWER | Effective | 2016-07-01 |  | TOP, TO, RC, GOP, GO, DP, BA
CIP-011-3 | Cyber Security — Information Protection | R1. | Each Responsible Entity shall implement one or more documented information protection program(s) for BES Cyber System Information (BCSI) pertaining to “Applicable Systems” identified in CIP-011-3 Table R1 – Information Protection Program that collectively includes each of the applicable requirement parts in CIP-011-3 Table R1 – Information Protection Program. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning]. | MEDIUM | Effective | 2024-04-01 |  | TO, TOP, RC, GO, GOP, DP, BA
CIP-011-3 | Cyber Security — Information Protection | R2. | Each Responsible Entity shall implement one or more documented process(es) that collectively include the applicable requirement parts in CIP-011-3 Table R2 – BES Cyber Asset Reuse and Disposal. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning]. | LOWER | Effective | 2024-04-01 |  | TO, TOP, RC, GO, GOP, DP, BA
CIP-012-1 | Cyber Security – Control Center Communication Networks | R1. | The Responsible Entity shall implement, except under CIP Exceptional Circumstances, one or more documented plan(s) to mitigate the risks posed by unauthorized disclosure and unauthorized modification of Real-time Assessment and Real-time monitoring data while being transmitted between any applicable Control Centers. The Responsible Entity is not required to include oral communications in its plan. The plan shall include: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Effective | 2022-07-01 |  | TO, TOP, RC, GOP, GO, BA
CIP-012-1 | Cyber Security – Control Center Communication Networks | R1.1. | Identification of security protection used to mitigate the risks posed by unauthorized disclosure and unauthorized modification of Real-time Assessment and Real-time monitoring data while being transmitted between Control Centers; | MEDIUM | Effective | 2022-07-01 |  | TOP, TO, RC, GOP, GO, BA
CIP-012-1 | Cyber Security – Control Center Communication Networks | R1.2. | Identification of where the Responsible Entity applied security protection for transmitting Real-time Assessment and Real-time monitoring data between Control Centers; and | MEDIUM | Effective | 2022-07-01 |  | TO, TOP, RC, GOP, GO, BA
CIP-012-1 | Cyber Security – Control Center Communication Networks | R1.3. | If the Control Centers are owned or operated by different Responsible Entities, identification of the responsibilities of each Responsible Entity for applying security protection to the transmission of Real-time Assessment and Real-time monitoring data between those Control Centers. | MEDIUM | Effective | 2022-07-01 |  | TOP, TO, RC, GOP, GO, BA
CIP-012-2 | Cyber Security – Communications between Control Centers | R1. | The Responsible Entity shall implement, except under CIP Exceptional Circumstances, one or more documented plan(s) to mitigate the risks posed by unauthorized disclosure, unauthorized modification, and loss of availability, of data used in Real-time Assessment and Real-time monitoring while such data is being transmitted between any applicable Control Centers. The Responsible Entity is not required to include oral communications in its plan. The plan shall include: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Pending Approval |  |  | TO, TOP, RC, GO, GOP, BA
CIP-012-2 | Cyber Security – Communications between Control Centers | R1.1. | Identification of method(s) used to mitigate the risk(s) posed by unauthorized disclosure and unauthorized modification of data used in Real-time Assessment and Real-time monitoring while such data is being transmitted between Control Centers | MEDIUM | Pending Approval |  |  | TO, TOP, RC, GO, GOP, BA
CIP-012-2 | Cyber Security – Communications between Control Centers | R1.2. | Identification of method(s) used to mitigate the risk(s) posed by the loss of the ability to communicate Real-time Assessment and Real-time monitoring data between Control Centers | MEDIUM | Pending Approval |  |  | TO, TOP, RC, GO, GOP, BA
CIP-012-2 | Cyber Security – Communications between Control Centers | R1.3. | Identification of method(s) used to initiate the recovery of communication links used to transmit Real-time Assessment and Real-time monitoring data between Control Centers | MEDIUM | Pending Approval |  |  | TO, TOP, RC, GO, GOP, BA
CIP-012-2 | Cyber Security – Communications between Control Centers | R1.4. | Identification of where the Responsible Entity implemented method(s)as required in Parts 1.1 and 1.2 | MEDIUM | Pending Approval |  |  | TO, TOP, RC, GO, GOP, BA
CIP-012-2 | Cyber Security – Communications between Control Centers | R1.5. | If the Control Centers are owned or operated by different ResponsibleEntities, identification of the responsibilities of each Responsible Entity for implementing method(s) as required in Parts 1.1, 1.2, and 1.3 | MEDIUM | Pending Approval |  |  | TO, TOP, RC, GO, GOP, BA
CIP-013-1 | Cyber Security - Supply Chain Risk Management | R1. | Each Responsible Entity shall develop one or more documented supply chain cyber security risk management plan(s) for high and medium impact BES Cyber Systems. The plan(s) shall include: | MEDIUM | Retired | 2020-10-01 | 2022-09-30 | TOP, TO, RC, GOP, GO, DP, BA
CIP-013-1 | Cyber Security - Supply Chain Risk Management | R1. | Each Responsible Entity shall develop one or more documented supply chain cyber security risk management plan(s) for high and medium impact BES Cyber Systems. The plan(s) shall include: | MEDIUM | Retired | 2020-10-01 | 2022-09-30 | TOP, TO, RC, GOP, GO, DP, BA
CIP-013-1 | Cyber Security - Supply Chain Risk Management | R1.1. | One or more process(es) used in planning for the procurement of BES Cyber Systems to identify and assess cyber security risk(s) to the Bulk Electric System from vendor products or services resulting from: (i) procuring and installing vendor equipment and software; and (ii) transitions from one vendor(s) to another vendor(s). | MEDIUM | Retired | 2020-10-01 | 2022-09-30 | TOP, TO, RC, GOP, GO, DP, BA
CIP-013-1 | Cyber Security - Supply Chain Risk Management | R1.2. | One or more process(es) used in procuring BES Cyber Systems that address the following, as applicable: | MEDIUM | Retired | 2020-10-01 | 2022-09-30 | TOP, TO, RC, GOP, GO, DP, BA
CIP-013-1 | Cyber Security - Supply Chain Risk Management | R1.2.1. | Notification by the vendor of vendor-identified incidents related to the products or services provided to the Responsible Entity that pose cyber security risk to the Responsible Entity; | MEDIUM | Retired | 2020-10-01 | 2022-09-30 | TOP, TO, RC, GOP, GO, DP, BA
CIP-013-1 | Cyber Security - Supply Chain Risk Management | R1.2.2. | Coordination of responses to vendor-identified incidents related to the products or services provided to the Responsible Entity that pose cyber security risk to the Responsible Entity; | MEDIUM | Retired | 2020-10-01 | 2022-09-30 | TOP, TO, RC, GOP, GO, DP, BA
CIP-013-1 | Cyber Security - Supply Chain Risk Management | R1.2.3. | Notification by vendors when remote or onsite access should no longer be granted to vendor representatives; | MEDIUM | Retired | 2020-10-01 | 2022-09-30 | TOP, TO, RC, GOP, GO, DP, BA
CIP-013-1 | Cyber Security - Supply Chain Risk Management | R1.2.4. | Disclosure by vendors of known vulnerabilities related to the products or services provided to the Responsible Entity; | MEDIUM | Retired | 2020-10-01 | 2022-09-30 | TOP, TO, RC, GOP, GO, DP, BA
CIP-013-1 | Cyber Security - Supply Chain Risk Management | R1.2.5. | Verification of software integrity and authenticity of all software and patches provided by the vendor for use in the BES Cyber System; and | MEDIUM | Retired | 2020-10-01 | 2022-09-30 | TOP, TO, RC, GOP, GO, DP, BA
CIP-013-1 | Cyber Security - Supply Chain Risk Management | R1.2.6. | Coordination of controls for (i) vendor-initiated Interactive Remote Access, and (ii) system-to-system remote access with a vendor(s). | MEDIUM | Retired | 2020-10-01 | 2022-09-30 | TOP, TO, RC, GOP, GO, DP, BA
CIP-013-1 | Cyber Security - Supply Chain Risk Management | R2. | Each Responsible Entity shall implement its supply chain cyber security risk management plan(s) specified in Requirement R1. Note: Implementation of the plan does not require the Responsible Entity to renegotiate or abrogate existing contracts (including amendments to master agreements and purchase orders). Additionally, the following issues are beyond the scope of Requirement R2: (1) the actual terms and conditions of a procurement contract; and (2) vendor performance and adherence to a contract. | MEDIUM | Retired | 2020-10-01 | 2022-09-30 | TOP, TO, RC, GOP, GO, DP, BA
CIP-013-1 | Cyber Security - Supply Chain Risk Management | R3. | Each Responsible Entity shall review and obtain CIP Senior Manager or delegate approval of its supply chain cyber security risk management plan(s) specified in Requirement R1 at least once every 15 calendar months. | MEDIUM | Retired | 2020-10-01 | 2022-09-30 | TOP, TO, RC, GOP, GO, DP, BA
CIP-013-2 | Cyber Security - Supply Chain Risk Management | R1. | Each Responsible Entity shall develop one or more documented supply chain cyber security risk management plan(s) for high and medium impact BES Cyber Systems and their associated Electronic Access Control or Monitoring Systems (EACMS) and Physical Access Control Systems (PACS). The plan(s) shall include: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Effective | 2022-10-01
CIP-013-2 | Cyber Security - Supply Chain Risk Management | R1.1. | One or more process(es) used in planning for the procurement of BES Cyber Systems and their associated EACMS and PACS to identify and assess cyber security risk(s) to the Bulk Electric System from vendor products or services resulting from: (i) procuring and installing vendor equipment and software; and (ii) transitions from one vendor(s) to another vendor(s). | MEDIUM | Effective | 2022-10-01
CIP-013-2 | Cyber Security - Supply Chain Risk Management | R1.2. | One or more process(es) used in procuring BES Cyber Systems, and their associated EACMS and PACS, that address the following, as applicable: | MEDIUM | Effective | 2022-10-01
CIP-013-2 | Cyber Security - Supply Chain Risk Management | R1.2.1. | Notification by the vendor of vendor-identified incidents related to the products or services provided to the Responsible Entity that pose cyber security risk to the Responsible Entity; | MEDIUM | Effective | 2022-10-01
CIP-013-2 | Cyber Security - Supply Chain Risk Management | R1.2.2. | Coordination of responses to vendor-identified incidents related to the products or services provided to the Responsible Entity that pose cyber security risk to the Responsible Entity; | MEDIUM | Effective | 2022-10-01
CIP-013-2 | Cyber Security - Supply Chain Risk Management | R1.2.3. | Notification by vendors when remote or onsite access should no longer be granted to vendor representatives; | MEDIUM | Effective | 2022-10-01
CIP-013-2 | Cyber Security - Supply Chain Risk Management | R1.2.4. | Disclosure by vendors of known vulnerabilities related to the products or services provided to the Responsible Entity; | MEDIUM | Effective | 2022-10-01
CIP-013-2 | Cyber Security - Supply Chain Risk Management | R1.2.5. | Verification of software integrity and authenticity of all software and patches provided by the vendor for use in the BES Cyber System and their associated EACMS and PACS; and | MEDIUM | Effective | 2022-10-01
CIP-013-2 | Cyber Security - Supply Chain Risk Management | R1.2.6. | Coordination of controls for vendor-initiated remote access | MEDIUM | Effective | 2022-10-01
CIP-013-2 | Cyber Security - Supply Chain Risk Management | R2. | Each Responsible Entity shall implement its supply chain cyber security risk management plan(s) specified in Requirement R1. Note: Implementation of the plan does not require the Responsible Entity to renegotiate or abrogate existing contracts (including amendments to master agreements and purchase orders). Additionally, the following issues are beyond the scope of Requirement R2: (1) the actual terms and conditions of a procurement contract; and (2) vendor performance and adherence to a contract. | MEDIUM | Effective | 2022-10-01
CIP-013-2 | Cyber Security - Supply Chain Risk Management | R3. | Each Responsible Entity shall review and obtain CIP Senior Manager or delegate approval of its supply chain cyber security risk management plan(s) specified in Requirement R1 at least once every 15 calendar months. | MEDIUM | Effective | 2022-10-01
CIP-014-1 | Physical Security | R1. | Each Transmission Owner shall perform an initial risk assessment and subsequent risk assessments of its Transmission stations and Transmission substations (existing and planned to be in service within 24 months) that meet the criteria specified in Applicability Section 4.1.1. The initial and subsequent risk assessments shall consist of a transmission analysis or transmission analyses designed to identify the Transmission station(s) and Transmission substation(s) that if rendered inoperable or damaged could result in widespread instability, uncontrolled separation, or Cascading within an Interconnection. [VRF: High; Time-Horizon: Long-term Planning] | HIGH | Retired | 2015-10-01 | 2015-10-01 | TO
CIP-014-1 | Physical Security | R1.1. | Subsequent risk assessments shall be performed:  At least once every 30 calendar months for a Transmission Owner that has identified in its previous risk assessment (as verified according to Requirement R2) one or more Transmission stations or Transmission substations that if rendered inoperable or damaged could result in widespread instability, uncontrolled separation, or Cascading within an Interconnection; or  At least once every 60 calendar months for a Transmission Owner that has not identified in its previous risk assessment (as verified according to Requirement R2) any Transmission stations or Transmission substations that if rendered inoperable or damaged could result in widespread instability, uncontrolled separation, or Cascading within an Interconnection. | HIGH | Retired | 2015-10-01 | 2015-10-01 | TO
CIP-014-1 | Physical Security | R1.2. | The Transmission Owner shall identify the primary control center that operationally controls each Transmission station or Transmission substation identified in the Requirement R1 risk assessment. | HIGH | Retired | 2015-10-01 | 2015-10-01 | TO
CIP-014-1 | Physical Security | R2. | Each Transmission Owner shall have an unaffiliated third party verify the risk assessment performed under Requirement R1. The verification may occur concurrent with or after the risk assessment performed under Requirement R1. [VRF: Medium; Time-Horizon: Long-term Planning] | MEDIUM | Retired | 2015-10-01 | 2015-10-01 | TO
CIP-014-1 | Physical Security | R2.1. | Each Transmission Owner shall select an unaffiliated verifying entity that is either:  A registered Planning Coordinator, Transmission Planner, or Reliability Coordinator; or  An entity that has transmission planning or analysis experience. | MEDIUM | Retired | 2015-10-01 | 2015-10-01 | TO
CIP-014-1 | Physical Security | R2.2. | The unaffiliated third party verification shall verify the Transmission Owner’s risk assessment performed under Requirement R1, which may include recommendations for the addition or deletion of a Transmission station(s) or Transmission substation(s). The Transmission Owner shall ensure the verification is completed within 90 calendar days following the completion of the Requirement R1 risk assessment. | MEDIUM | Retired | 2015-10-01 | 2015-10-01 | TO
CIP-014-1 | Physical Security | R2.3. | If the unaffiliated verifying entity recommends that the Transmission Owner add a Transmission station(s) or Transmission substation(s) to, or remove a Transmission station(s) or Transmission substation(s) from, its identification under Requirement R1, the Transmission Owner shall either, within 60 calendar days of completion of the verification, for each recommended addition or removal of a Transmission station or Transmission substation:  Modify its identification under Requirement R1 consistent with the recommendation; or  Document the technical basis for not modifying the identification in accordance with the recommendation. | MEDIUM | Retired | 2015-10-01 | 2015-10-01 | TO
CIP-014-1 | Physical Security | R2.4. | Each Transmission Owner shall implement procedures, such as the use of non-disclosure agreements, for protecting sensitive or confidential information made available to the unaffiliated third party verifier and to protect or exempt sensitive or confidential information developed pursuant to this Reliability Standard from public disclosure. | MEDIUM | Retired | 2015-10-01 | 2015-10-01 | TO
CIP-014-1 | Physical Security | R3. | For a primary control center(s) identified by the Transmission Owner according to Requirement R1, Part 1.2 that a) operationally controls an identified Transmission station or Transmission substation verified according to Requirement R2, and b) is not under the operational control of the Transmission Owner: the Transmission Owner shall, within seven calendar days following completion of Requirement R2, notify the Transmission Operator that has operational control of the primary control center of such identification and the date of completion of Requirement R2. [VRF: Lower; Time-Horizon: Long-term Planning] | LOWER | Retired | 2015-10-01 | 2015-10-01 | TO
CIP-014-1 | Physical Security | R3.1. | If a Transmission station or Transmission substation previously identified under Requirement R1 and verified according to Requirement R2 is removed from the identification during a subsequent risk assessment performed according to Requirement R1 or a verification according to Requirement R2, then the Transmission Owner shall, within seven calendar days following the verification or the subsequent risk assessment, notify the Transmission Operator that has operational control of the primary control center of the removal. | LOWER | Retired | 2015-10-01 | 2015-10-01 | TO
CIP-014-1 | Physical Security | R4. | Each Transmission Owner that identified a Transmission station, Transmission substation, or a primary control center in Requirement R1 and verified according to Requirement R2, and each Transmission Operator notified by a Transmission Owner according to Requirement R3, shall conduct an evaluation of the potential threats and vulnerabilities of a physical attack to each of their respective Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 and verified according to Requirement R2. The evaluation shall consider the following: [VRF: Medium; Time-Horizon: Operations Planning, Long-term Planning] | MEDIUM | Retired | 2015-10-01 | 2015-10-01 | TOP, TO
CIP-014-1 | Physical Security | R4.1. | Unique characteristics of the identified and verified Transmission station(s), Transmission substation(s), and primary control center(s); | MEDIUM | Retired | 2015-10-01 | 2015-10-01 | TOP, TO
CIP-014-1 | Physical Security | R4.2. | Prior history of attack on similar facilities taking into account the frequency, geographic proximity, and severity of past physical security related events; and | MEDIUM | Retired | 2015-10-01 | 2015-10-01 | TOP, TO
CIP-014-1 | Physical Security | R4.3. | Intelligence or threat warnings received from sources such as law enforcement, the Electric Reliability Organization (ERO), the Electricity Sector Information Sharing and Analysis Center (ES-ISAC), U.S. federal and/or Canadian governmental agencies, or their successors. | MEDIUM | Retired | 2015-10-01 | 2015-10-01 | TOP, TO
CIP-014-1 | Physical Security | R5. | Each Transmission Owner that identified a Transmission station, Transmission substation, or primary control center in Requirement R1 and verified according to Requirement R2, and each Transmission Operator notified by a Transmission Owner according to Requirement R3, shall develop and implement a documented physical security plan(s) that covers their respective Transmission station(s), Transmission substation(s), and primary control center(s). The physical security plan(s) shall be developed within 120 calendar days following the completion of Requirement R2 and executed according to the timeline specified in the physical security plan(s). The physical security plan(s) shall include the following attributes: [VRF: High; Time-Horizon: Long-term Planning] | HIGH | Retired | 2015-10-01 | 2015-10-01 | TOP, TO
CIP-014-1 | Physical Security | R5.1. | Resiliency or security measures designed collectively to deter, detect, delay, assess, communicate, and respond to potential physical threats and vulnerabilities identified during the evaluation conducted in Requirement R4. | HIGH | Retired | 2015-10-01 | 2015-10-01 | TOP, TO
CIP-014-1 | Physical Security | R5.2. | Law enforcement contact and coordination information. | HIGH | Retired | 2015-10-01 | 2015-10-01 | TOP, TO
CIP-014-1 | Physical Security | R5.3. | A timeline for executing the physical security enhancements and modifications specified in the physical security plan. | HIGH | Retired | 2015-10-01 | 2015-10-01 | TOP, TO
CIP-014-1 | Physical Security | R5.4. | Provisions to evaluate evolving physical threats, and their corresponding security measures, to the Transmission station(s), Transmission substation(s), or primary control center(s). | HIGH | Retired | 2015-10-01 | 2015-10-01 | TOP, TO
CIP-014-1 | Physical Security | R6. | Each Transmission Owner that identified a Transmission station, Transmission substation, or primary control center in Requirement R1 and verified according to Requirement R2, and each Transmission Operator notified by a Transmission Owner according to Requirement R3, shall have an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5. The review may occur concurrently with or after completion of the evaluation performed under Requirement R4 and the security plan development under Requirement R5. [VRF: Medium; Time-Horizon: Long-term Planning] | MEDIUM | Retired | 2015-10-01 | 2015-10-01 | TOP, TO
CIP-014-1 | Physical Security | R6.1. | Each Transmission Owner and Transmission Operator shall select an unaffiliated third party reviewer from the following:  An entity or organization with electric industry physical security experience and whose review staff has at least one member who holds either a Certified Protection Professional (CPP) or Physical Security Professional (PSP) certification.  An entity or organization approved by the ERO.  A governmental agency with physical security expertise.  An entity or organization with demonstrated law enforcement, government, or military physical security expertise. | MEDIUM | Retired | 2015-10-01 | 2015-10-01 | TOP, TO
CIP-014-1 | Physical Security | R6.2. | The Transmission Owner or Transmission Operator, respectively, shall ensure that the unaffiliated third party review is completed within 90 calendar days of completing the security plan(s) developed in Requirement R5. The unaffiliated third party review may, but is not required to, include recommended changes to the evaluation performed under Requirement R4 or the security plan(s) developed under Requirement R5. | MEDIUM | Retired | 2015-10-01 | 2015-10-01 | TOP, TO
CIP-014-1 | Physical Security | R6.3. | If the unaffiliated third party reviewer recommends changes to the evaluation performed under Requirement R4 or security plan(s) developed under Requirement R5, the Transmission Owner or Transmission Operator shall, within 60 calendar days of the completion of the unaffiliated third party review, for each recommendation:  Modify its evaluation or security plan(s) consistent with the recommendation; or  Document the reason(s) for not modifying the evaluation or security plan(s) consistent with the recommendation. | MEDIUM | Retired | 2015-10-01 | 2015-10-01 | TOP, TO
CIP-014-1 | Physical Security | R6.4. | Each Transmission Owner and Transmission Operator shall implement procedures, such as the use of non-disclosure agreements, for protecting sensitive or confidential information made available to the unaffiliated third party reviewer and to protect or exempt sensitive or confidential information developed pursuant to this Reliability Standard from public disclosure. | MEDIUM | Retired | 2015-10-01 | 2015-10-01 | TOP, TO
CIP-014-2 | Physical Security | R1. | Each Transmission Owner shall perform an initial risk assessment and subsequent risk assessments of its Transmission stations and Transmission substations (existing and planned to be in service within 24 months) that meet the criteria specified in Applicability Section 4.1.1. The initial and subsequent risk assessments shall consist of a transmission analysis or transmission analyses designed to identify the Transmission station(s) and Transmission substation(s) that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection. [VRF: High; Time-Horizon: Long-term Planning] | HIGH | Effective | 2015-10-02 |  | TO
CIP-014-2 | Physical Security | R1.1. | Subsequent risk assessments shall be performed:  At least once every 30 calendar months for a Transmission Owner that has identified in its previous risk assessment (as verified according to Requirement R2) one or more Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection; or  At least once every 60 calendar months for a Transmission Owner that has not identified in its previous risk assessment (as verified according to Requirement R2) any Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection. | HIGH | Effective | 2015-10-02 |  | TO
CIP-014-2 | Physical Security | R1.2. | The Transmission Owner shall identify the primary control center that operationally controls each Transmission station or Transmission substation identified in the Requirement R1 risk assessment. | HIGH | Effective | 2015-10-02 |  | TO
CIP-014-2 | Physical Security | R2. | Each Transmission Owner shall have an unaffiliated third party verify the risk assessment performed under Requirement R1. The verification may occur concurrent with or after the risk assessment performed under Requirement R1. [VRF: Medium; Time-Horizon: Long-term Planning] | MEDIUM | Effective | 2015-10-02 |  | TO
CIP-014-2 | Physical Security | R2.1. | Each Transmission Owner shall select an unaffiliated verifying entity that is either:  A registered Planning Coordinator, Transmission Planner, or Reliability Coordinator; or  An entity that has transmission planning or analysis experience. | MEDIUM | Effective | 2015-10-02 |  | TO
CIP-014-2 | Physical Security | R2.2. | The unaffiliated third party verification shall verify the Transmission Owner’s risk assessment performed under Requirement R1, which may include recommendations for the addition or deletion of a Transmission station(s) or Transmission substation(s). The Transmission Owner shall ensure the verification is completed within 90 calendar days following the completion of the Requirement R1 risk assessment. | MEDIUM | Effective | 2015-10-02 |  | TO
CIP-014-2 | Physical Security | R2.3. | If the unaffiliated verifying entity recommends that the Transmission Owner add a Transmission station(s) or Transmission substation(s) to, or remove a Transmission station(s) or Transmission substation(s) from, its identification under Requirement R1, the Transmission Owner shall either, within 60 calendar days of completion of the verification, for each recommended addition or removal of a Transmission station or Transmission substation:  Modify its identification under Requirement R1 consistent with the recommendation; or  Document the technical basis for not modifying the identification in accordance with the recommendation. | MEDIUM | Effective | 2015-10-02 |  | TO
CIP-014-2 | Physical Security | R2.4. | Each Transmission Owner shall implement procedures, such as the use of non-disclosure agreements, for protecting sensitive or confidential information made available to the unaffiliated third party verifier and to protect or exempt sensitive or confidential information developed pursuant to this Reliability Standard from public disclosure. | MEDIUM | Effective | 2015-10-02 |  | TO
CIP-014-2 | Physical Security | R3. | For a primary control center(s) identified by the Transmission Owner according to Requirement R1, Part 1.2 that a) operationally controls an identified Transmission station or Transmission substation verified according to Requirement R2, and b) is not under the operational control of the Transmission Owner: the Transmission Owner shall, within seven calendar days following completion of Requirement R2, notify the Transmission Operator that has operational control of the primary control center of such identification and the date of completion of Requirement R2. [VRF: Lower; Time-Horizon: Long-term Planning] | LOWER | Effective | 2015-10-02 |  | TO
CIP-014-2 | Physical Security | R3.1. | If a Transmission station or Transmission substation previously identified under Requirement R1 and verified according to Requirement R2 is removed from the identification during a subsequent risk assessment performed according to Requirement R1 or a verification according to Requirement R2, then the Transmission Owner shall, within seven calendar days following the verification or the subsequent risk assessment, notify the Transmission Operator that has operational control of the primary control center of the removal. | LOWER | Effective | 2015-10-02 |  | TO
CIP-014-2 | Physical Security | R4. | Each Transmission Owner that identified a Transmission station, Transmission substation, or a primary control center in Requirement R1 and verified according to Requirement R2, and each Transmission Operator notified by a Transmission Owner according to Requirement R3, shall conduct an evaluation of the potential threats and vulnerabilities of a physical attack to each of their respective Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 and verified according to Requirement R2. The evaluation shall consider the following: [VRF: Medium; Time-Horizon: Operations Planning, Long-term Planning] | MEDIUM | Effective | 2015-10-02 |  | TOP, TO
CIP-014-2 | Physical Security | R4.1. | Unique characteristics of the identified and verified Transmission station(s), Transmission substation(s), and primary control center(s); | MEDIUM | Effective | 2015-10-02 |  | TOP, TO
CIP-014-2 | Physical Security | R4.2. | Prior history of attack on similar facilities taking into account the frequency, geographic proximity, and severity of past physical security related events; and | MEDIUM | Effective | 2015-10-02 |  | TOP, TO
CIP-014-2 | Physical Security | R4.3. | Intelligence or threat warnings received from sources such as law enforcement, the Electric Reliability Organization (ERO), the Electricity Sector Information Sharing and Analysis Center (ES-ISAC), U.S. federal and/or Canadian governmental agencies, or their successors. | MEDIUM | Effective | 2015-10-02 |  | TOP, TO
CIP-014-2 | Physical Security | R5. | Each Transmission Owner that identified a Transmission station, Transmission substation, or primary control center in Requirement R1 and verified according to Requirement R2, and each Transmission Operator notified by a Transmission Owner according to Requirement R3, shall develop and implement a documented physical security plan(s) that covers their respective Transmission station(s), Transmission substation(s), and primary control center(s). The physical security plan(s) shall be developed within 120 calendar days following the completion of Requirement R2 and executed according to the timeline specified in the physical security plan(s). The physical security plan(s) shall include the following attributes: [VRF: High; Time-Horizon: Long-term Planning] | HIGH | Effective | 2015-10-02 |  | TOP, TO
CIP-014-2 | Physical Security | R5.1. | Resiliency or security measures designed collectively to deter, detect, delay, assess, communicate, and respond to potential physical threats and vulnerabilities identified during the evaluation conducted in Requirement R4. | HIGH | Effective | 2015-10-02 |  | TOP, TO
CIP-014-2 | Physical Security | R5.2. | Law enforcement contact and coordination information. | HIGH | Effective | 2015-10-02 |  | TOP, TO
CIP-014-2 | Physical Security | R5.3. | A timeline for executing the physical security enhancements and modifications specified in the physical security plan. | HIGH | Effective | 2015-10-02 |  | TOP, TO
CIP-014-2 | Physical Security | R5.4. | Provisions to evaluate evolving physical threats, and their corresponding security measures, to the Transmission station(s), Transmission substation(s), or primary control center(s). | HIGH | Effective | 2015-10-02 |  | TOP, TO
CIP-014-2 | Physical Security | R6. | Each Transmission Owner that identified a Transmission station, Transmission substation, or primary control center in Requirement R1 and verified according to Requirement R2, and each Transmission Operator notified by a Transmission Owner according to Requirement R3, shall have an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5. The review may occur concurrently with or after completion of the evaluation performed under Requirement R4 and the security plan development under Requirement R5. [VRF: Medium; Time-Horizon: Long-term Planning] | MEDIUM | Effective | 2015-10-02 |  | TOP, TO
CIP-014-2 | Physical Security | R6.1. | Each Transmission Owner and Transmission Operator shall select an unaffiliated third party reviewer from the following:  An entity or organization with electric industry physical security experience and whose review staff has at least one member who holds either a Certified Protection Professional (CPP) or Physical Security Professional (PSP) certification.  An entity or organization approved by the ERO.  A governmental agency with physical security expertise.  An entity or organization with demonstrated law enforcement, government, or military physical security expertise. | MEDIUM | Effective | 2015-10-02 |  | TOP, TO
CIP-014-2 | Physical Security | R6.2. | The Transmission Owner or Transmission Operator, respectively, shall ensure that the unaffiliated third party review is completed within 90 calendar days of completing the security plan(s) developed in Requirement R5. The unaffiliated third party review may, but is not required to, include recommended changes to the evaluation performed under Requirement R4 or the security plan(s) developed under Requirement R5. | MEDIUM | Effective | 2015-10-02 |  | TOP, TO
CIP-014-2 | Physical Security | R6.3. | If the unaffiliated third party reviewer recommends changes to the evaluation performed under Requirement R4 or security plan(s) developed under Requirement R5, the Transmission Owner or Transmission Operator shall, within 60 calendar days of the completion of the unaffiliated third party review, for each recommendation:  Modify its evaluation or security plan(s) consistent with the recommendation; or  Document the reason(s) for not modifying the evaluation or security plan(s) consistent with the recommendation. | MEDIUM | Effective | 2015-10-02 |  | TOP, TO
CIP-014-2 | Physical Security | R6.4. | Each Transmission Owner and Transmission Operator shall implement procedures, such as the use of non-disclosure agreements, for protecting sensitive or confidential information made available to the unaffiliated third party reviewer and to protect or exempt sensitive or confidential information developed pursuant to this Reliability Standard from public disclosure. | MEDIUM | Effective | 2015-10-02 |  | TOP, TO
CIP-014-3 | Physical Security | R1. | Each Transmission Owner shall perform an initial risk assessment and subsequent risk assessments of its Transmission stations and Transmission substations (existing and planned to be in service within 24 months) that meet the criteria specified in Applicability Section 4.1.1. The initial and subsequent risk assessments shall consist of a transmission analysis or transmission analyses designed to identify the Transmission station(s) and Transmission substation(s) that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection. [VRF: High; Time-Horizon: Long-term Planning] | HIGH | Effective | 2022-06-16 |  | TO
CIP-014-3 | Physical Security | R1.1. | Subsequent risk assessments shall be performed: • At least once every 30 calendar months for a Transmission Owner that has identified in its previous risk assessment (as verified according to Requirement R2) one or more Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection; or • At least once every 60 calendar months for a Transmission Owner that has not identified in its previous risk assessment (as verified according to Requirement R2) any Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection. | HIGH | Effective | 2022-06-16 |  | TO
CIP-014-3 | Physical Security | R1.2. | The Transmission Owner shall identify the primary control center that operationally controls each Transmission station or Transmission substation identified in the Requirement R1 risk assessment. | HIGH | Effective | 2022-06-16 |  | TO
CIP-014-3 | Physical Security | R2. | Each Transmission Owner shall have an unaffiliated third party verify the risk assessment performed under Requirement R1. The verification may occur concurrent with or after the risk assessment performed under Requirement R1. [VRF: Medium; Time-Horizon: Long-term Planning] | MEDIUM | Effective | 2022-06-16 |  | TO
CIP-014-3 | Physical Security | R2.1. | Each Transmission Owner shall select an unaffiliated verifying entity that is either: • A registered Planning Coordinator, Transmission Planner, or Reliability Coordinator; or • An entity that has transmission planning or analysis experience | MEDIUM | Effective | 2022-06-16 |  | TO
CIP-014-3 | Physical Security | R2.2. | The unaffiliated third party verification shall verify the Transmission Owner’s risk assessment performed under Requirement R1, which may include recommendations for the addition or deletion of a Transmission station(s) or Transmission substation(s). The Transmission Owner shall ensure the verification is completed within 90 calendar days following the completion of the Requirement R1 risk assessment | MEDIUM | Effective | 2022-06-16 |  | TO
CIP-014-3 | Physical Security | R2.3. | If the unaffiliated verifying entity recommends that the Transmission Owner add a Transmission station(s) or Transmission substation(s) to, or remove a Transmission station(s) or Transmission substation(s) from, its identification under Requirement R1, the Transmission Owner shall either, within 60 calendar days of completion of the verification, for each recommended addition or removal of a Transmission station or Transmission substation: • Modify its identification under Requirement R1 consistent with the recommendation; or • Document the technical basis for not modifying the identification in accordance with the recommendation | MEDIUM | Effective | 2022-06-16 |  | TO
CIP-014-3 | Physical Security | R2.4. | Each Transmission Owner shall implement procedures, such as the use of nondisclosure agreements, for protecting sensitive or confidential information made available to the unaffiliated third party verifier and to protect or exempt sensitive or confidential information developed pursuant to this Reliability Standard from public disclosure | MEDIUM | Effective | 2022-06-16 |  | TO
CIP-014-3 | Physical Security | R3. | For a primary control center(s) identified by the Transmission Owner according to Requirement R1, Part 1.2 that a) operationally controls an identified Transmission station or Transmission substation verified according to Requirement R2, and b) is not under the operational control of the Transmission Owner: the Transmission Owner shall, within seven calendar days following completion of Requirement R2, notify the Transmission Operator that has operational control of the primary control center of such identification and the date of completion of Requirement R2. [VRF: Lower; TimeHorizon: Long-term Planning] | LOWER | Effective | 2022-06-16 |  | TO
CIP-014-3 | Physical Security | R3.1. | If a Transmission station or Transmission substation previously identified under Requirement R1 and verified according to Requirement R2 is removed from the identification during a subsequent risk assessment performed according to Requirement R1 or a verification according to Requirement R2, then the Transmission Owner shall, within seven calendar days following the verification or the subsequent risk assessment, notify the Transmission Operator that has operational control of the primary control center of the removal. | LOWER | Effective | 2022-06-16 |  | TO
CIP-014-3 | Physical Security | R4. | Each Transmission Owner that identified a Transmission station, Transmission substation, or a primary control center in Requirement R1 and verified according to Requirement R2, and each Transmission Operator notified by a Transmission Owner according to Requirement R3, shall conduct an evaluation of the potential threats and vulnerabilities of a physical attack to each of their respective Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 and verified according to Requirement R2. The evaluation shall consider the following: [VRF: Medium; Time-Horizon: Operations Planning, Long-term Planning] | MEDIUM | Effective | 2022-06-16 |  | TO, TOP
CIP-014-3 | Physical Security | R4.1. | Unique characteristics of the identified and verified Transmission station(s), Transmission substation(s), and primary control center(s) | MEDIUM | Effective | 2022-06-16 |  | TO, TOP
CIP-014-3 | Physical Security | R4.2. | Prior history of attack on similar facilities taking into account the frequency, geographic proximity, and severity of past physical security related events | MEDIUM | Effective | 2022-06-16 |  | TO, TOP
CIP-014-3 | Physical Security | R4.3. | Intelligence or threat warnings received from sources such as law enforcement, the Electric Reliability Organization (ERO), the Electricity Sector Information Sharing and Analysis Center (ES-ISAC), U.S. federal and/or Canadian governmental agencies, or their successors. | MEDIUM | Effective | 2022-06-16 |  | TO, TOP
CIP-014-3 | Physical Security | R5. | Each Transmission Owner that identified a Transmission station, Transmission substation, or primary control center in Requirement R1 and verified according to Requirement R2, and each Transmission Operator notified by a Transmission Owner according to Requirement R3, shall develop and implement a documented physical security plan(s) that covers their respective Transmission station(s), Transmission substation(s), and primary control center(s). The physical security plan(s) shall be developed within 120 calendar days following the completion of Requirement R2 and executed according to the timeline specified in the physical security plan(s). The physical security plan(s) shall include the following attributes: [VRF: High; TimeHorizon: Long-term Planning] | HIGH | Effective | 2022-06-16 |  | TO, TOP
CIP-014-3 | Physical Security | R5.1. | Resiliency or security measures designed collectively to deter, detect, delay, assess, communicate, and respond to potential physical threats and vulnerabilities identified during the evaluation conducted in Requirement R4. | HIGH | Effective | 2022-06-16 |  | TO, TOP
CIP-014-3 | Physical Security | R5.2. | Law enforcement contact and coordination information. | HIGH | Effective | 2022-06-16 |  | TO, TOP
CIP-014-3 | Physical Security | R5.3. | A timeline for executing the physical security enhancements and modifications specified in the physical security plan. | HIGH | Effective | 2022-06-16 |  | TO, TOP
CIP-014-3 | Physical Security | R5.4. | Provisions to evaluate evolving physical threats, and their corresponding security measures, to the Transmission station(s), Transmission substation(s), or primary control center(s). | HIGH | Effective | 2022-06-16 |  | TO, TOP
CIP-014-3 | Physical Security | R6. | Each Transmission Owner that identified a Transmission station, Transmission substation, or primary control center in Requirement R1 and verified according to Requirement R2, and each Transmission Operator notified by a Transmission Owner according to Requirement R3, shall have an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5. The review may occur concurrently with or after completion of the evaluation performed under Requirement R4 and the security plan development under Requirement R5. [VRF: Medium; Time-Horizon: Long-term Planning] | MEDIUM | Effective | 2022-06-16 |  | TO, TOP
CIP-014-3 | Physical Security | R6.1. | Each Transmission Owner and Transmission Operator shall select an unaffiliated third party reviewer from the following: • An entity or organization with electric industry physical security experience and whose review staff has at least one member who holds either a Certified Protection Professional (CPP) or Physical Security Professional (PSP) certification. • An entity or organization approved by the ERO. • A governmental agency with physical security expertise. An entity or organization with demonstrated law enforcement, government, or military physical security expertise. | MEDIUM | Effective | 2022-06-16 |  | TO, TOP
CIP-014-3 | Physical Security | R6.2. | The Transmission Owner or Transmission Operator, respectively, shall ensure that the unaffiliated third party review is completed within 90 calendar days of completing the security plan(s) developed in Requirement R5. The unaffiliated third party review may, but is not required to, include recommended changes to the evaluation performed under Requirement R4 or the security plan(s) developed under Requirement R5. | MEDIUM | Effective | 2022-06-16 |  | TO, TOP
CIP-014-3 | Physical Security | R6.3. | If the unaffiliated third party reviewer recommends changes to the evaluation performed under Requirement R4 or security plan(s) developed under Requirement R5, the Transmission Owner or Transmission Operator shall, within 60 calendar days of the completion of the unaffiliated third party review, for each recommendation: • Modify its evaluation or security plan(s) consistent with the recommendation; or • Document the reason(s) for not modifying the evaluation or security plan(s) consistent with the recommendation. | MEDIUM | Effective | 2022-06-16 |  | TO, TOP
CIP-014-3 | Physical Security | R6.4. | Each Transmission Owner and Transmission Operator shall implement procedures, such as the use of non-disclosure agreements, for protecting sensitive or confidential information made available to the unaffiliated third party reviewer and to protect or exempt sensitive or confidential information developed pursuant to this Reliability Standard from public disclosure. | MEDIUM | Effective | 2022-06-16 |  | TO, TOP
COM-001-1.1 | Telecommunications | R1. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall provide adequate and reliable telecommunications facilities for the exchange of Interconnection and operating information: | HIGH | Retired | 2009-09-13 | 2015-09-20 | TOP, RC, BA
COM-001-1.1 | Telecommunications | R1.1. | Internally. | HIGH | Retired | 2009-09-13 | 2015-09-20 | TOP, RC, BA
COM-001-1.1 | Telecommunications | R1.2. | Between the Reliability Coordinator and its Transmission Operators and Balancing Authorities. | HIGH | Retired | 2009-09-13 | 2015-09-20 | TOP, RC, BA
COM-001-1.1 | Telecommunications | R1.3. | With other Reliability Coordinators, Transmission Operators, and Balancing Authorities as necessary to maintain reliability. | HIGH | Retired | 2009-09-13 | 2015-09-20 | TOP, RC, BA
COM-001-1.1 | Telecommunications | R1.4. | Where applicable, these facilities shall be redundant and diversely routed. | HIGH | Retired | 2009-09-13 | 2015-09-20 | TOP, RC, BA
COM-001-1.1 | Telecommunications | R2. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall manage, alarm, test and/or actively monitor vital telecommunications facilities. Special attention shall be given to emergency telecommunications facilities and equipment not used for routine communications. | MEDIUM | Retired | 2009-09-13 | 2015-09-20 | TOP, RC, BA
COM-001-1.1 | Telecommunications | R3. | Each Reliability Coordinator, Transmission Operator and Balancing Authority shall provide a means to coordinate telecommunications among their respective areas. This coordination shall include the ability to investigate and recommend solutions to telecommunications problems within the area and with other areas. | LOWER | Retired | 2009-09-13 | 2015-09-20 | TOP, RC, BA
COM-001-1.1 | Telecommunications | R4. | Unless agreed to otherwise, each Reliability Coordinator, Transmission Operator, and Balancing Authority shall use English as the language for all communications between and among operating personnel responsible for the real-time generation control and operation of the interconnected Bulk Electric System. Transmission Operators and Balancing Authorities may use an alternate language for internal operations. | MEDIUM | Retired | 2009-09-13 | 2016-06-30 | TOP, RC, BA
COM-001-1.1 | Telecommunications | R5. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall have written operating instructions and procedures to enable continued operation of the system during the loss of telecommunications facilities. | LOWER | Retired | 2009-09-13 | 2015-09-20 | TOP, RC, BA
COM-001-1.1 | Telecommunications | R6. | Each NERCNet User Organization shall adhere to the requirements in Attachment 1-COM-001-0, “NERCNet Security Policy.” | LOWER | Retired | 2009-09-13 | 2015-09-20
COM-001-2 | Communications | R1. | Each Reliability Coordinator shall have Interpersonal Communication capability with the following entities (unless the Reliability Coordinator detects a failure of its Interpersonal Communication capability in which case Requirement R10 shall apply): [Violation Risk Factor: High] [Time Horizon: Real-time Operations] | HIGH | Retired | 2015-10-01 | 2015-11-12 | RC
COM-001-2 | Communications | R1.1. | All Transmission Operators and Balancing Authorities within its Reliability Coordinator Area. | HIGH | Retired | 2015-10-01 | 2015-11-12 | RC
COM-001-2 | Communications | R1.2. | Each adjacent Reliability Coordinator within the same Interconnection. | HIGH | Retired | 2015-10-01 | 2015-11-12 | RC
COM-001-2 | Communications | R10. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall notify entities as identified in Requirements R1, R3, and R5, respectively within 60 minutes of the detection of a failure of its Interpersonal Communication capability that lasts 30 minutes or longer. [Violation Risk Factor: Medium] [Time Horizon: Realtime Operations] | MEDIUM | Retired | 2015-10-01 | 2015-11-12 | TOP, RC, BA
COM-001-2 | Communications | R11. | Each Distribution Provider and Generator Operator that detects a failure of its Interpersonal Communication capability shall consult each entity affected by the failure, as identified in Requirement R7 for a Distribution Provider or Requirement R8 for a Generator Operator, to determine a mutually agreeable action for the restoration of its Interpersonal Communication capability. [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | MEDIUM | Retired | 2015-10-01 | 2015-11-12 | GOP, DP
COM-001-2 | Communications | R2. | Each Reliability Coordinator shall designate an Alternative Interpersonal Communication capability with the following entities: [Violation Risk Factor: High] [Time Horizon: Real-time Operations] | HIGH | Retired | 2015-10-01 | 2015-11-12 | RC
COM-001-2 | Communications | R2.1. | All Transmission Operators and Balancing Authorities within its Reliability Coordinator Area. | HIGH | Retired | 2015-10-01 | 2015-11-12 | RC
COM-001-2 | Communications | R2.2. | Each adjacent Reliability Coordinator within the same Interconnection. | HIGH | Retired | 2015-10-01 | 2015-11-12 | RC
COM-001-2 | Communications | R3. | Each Transmission Operator shall have Interpersonal Communication capability with the following entities (unless the Transmission Operator detects a failure of its Interpersonal Communication capability in which case Requirement R10 shall apply): [Violation Risk Factor: High] [Time Horizon: Real-time Operations] | HIGH | Retired | 2015-10-01 | 2015-11-12 | TOP
COM-001-2 | Communications | R3.1. | Its Reliability Coordinator. | HIGH | Retired | 2015-10-01 | 2015-11-12 | TOP
COM-001-2 | Communications | R3.2. | Each Balancing Authority within its Transmission Operator Area. | HIGH | Retired | 2015-10-01 | 2015-11-12 | TOP
COM-001-2 | Communications | R3.3. | Each Distribution Provider within its Transmission Operator Area. | HIGH | Retired | 2015-10-01 | 2015-11-12 | TOP
COM-001-2 | Communications | R3.4. | Each Generator Operator within its Transmission Operator Area. | HIGH | Retired | 2015-10-01 | 2015-11-12 | TOP
COM-001-2 | Communications | R3.5. | Each adjacent Transmission Operator synchronously connected. | HIGH | Retired | 2015-10-01 | 2015-11-12 | TOP
COM-001-2 | Communications | R3.6. | Each adjacent Transmission Operator asynchronously connected. | HIGH | Retired | 2015-10-01 | 2015-11-12 | TOP
COM-001-2 | Communications | R4. | Each Transmission Operator shall designate an Alternative Interpersonal Communication capability with the following entities: [Violation Risk Factor: High] [Time Horizon: Real-time Operations] | HIGH | Retired | 2015-10-01 | 2015-11-12 | TOP
COM-001-2 | Communications | R4.1. | Its Reliability Coordinator. | HIGH | Retired | 2015-10-01 | 2015-11-12 | TOP
COM-001-2 | Communications | R4.2. | Each Balancing Authority within its Transmission Operator Area. | HIGH | Retired | 2015-10-01 | 2015-11-12 | TOP
COM-001-2 | Communications | R4.3. | Each adjacent Transmission Operator synchronously connected. | HIGH | Retired | 2015-10-01 | 2015-11-12 | TOP
COM-001-2 | Communications | R4.4. | Each adjacent Transmission Operator asynchronously connected. | HIGH | Retired | 2015-10-01 | 2015-11-12 | TOP
COM-001-2 | Communications | R5. | Each Balancing Authority shall have Interpersonal Communication capability with the following entities (unless the Balancing Authority detects a failure of its Interpersonal Communication capability in which case Requirement R10 shall apply): [Violation Risk Factor: High] [Time Horizon: Real-time Operations] | HIGH | Retired | 2015-10-01 | 2015-11-12 | BA
COM-001-2 | Communications | R5.1. | Its Reliability Coordinator. | HIGH | Retired | 2015-10-01 | 2015-11-12 | BA
COM-001-2 | Communications | R5.2. | Each Transmission Operator that operates Facilities within its Balancing Authority Area. | HIGH | Retired | 2015-10-01 | 2015-11-12 | BA
COM-001-2 | Communications | R5.3. | Each Distribution Provider within its Balancing Authority Area. | HIGH | Retired | 2015-10-01 | 2015-11-12 | BA
COM-001-2 | Communications | R5.4. | Each Generator Operator that operates Facilities within its Balancing Authority Area. | HIGH | Retired | 2015-10-01 | 2015-11-12 | BA
COM-001-2 | Communications | R5.5. | Each Adjacent Balancing Authority. | HIGH | Retired | 2015-10-01 | 2015-11-12 | BA
COM-001-2 | Communications | R6. | Each Balancing Authority shall designate an Alternative Interpersonal Communication capability with the following entities: [Violation Risk Factor: High] [Time Horizon: Real-time Operations] | HIGH | Retired | 2015-10-01 | 2015-11-12 | BA
COM-001-2 | Communications | R6.1. | Its Reliability Coordinator. | HIGH | Retired | 2015-10-01 | 2015-11-12 | BA
COM-001-2 | Communications | R6.2. | Each Transmission Operator that operates Facilities within its Balancing Authority Area. | HIGH | Retired | 2015-10-01 | 2015-11-12 | BA
COM-001-2 | Communications | R6.3. | Each Adjacent Balancing Authority. | HIGH | Retired | 2015-10-01 | 2015-11-12 | BA
COM-001-2 | Communications | R7. | Each Distribution Provider shall have Interpersonal Communication capability with the following entities (unless the Distribution Provider detects a failure of its Interpersonal Communication capability in which case Requirement R11 shall apply): [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | MEDIUM | Retired | 2015-10-01 | 2015-11-12 | DP
COM-001-2 | Communications | R7.1. | Its Balancing Authority. | MEDIUM | Retired | 2015-10-01 | 2015-11-12
COM-001-2 | Communications | R7.2. | Its Transmission Operator. | MEDIUM | Retired | 2015-10-01 | 2015-11-12
COM-001-2 | Communications | R8. | Each Generator Operator shall have Interpersonal Communication capability with the following entities (unless the Generator Operator detects a failure of its Interpersonal Communication capability in which case Requirement R11 shall apply): [Violation Risk Factor: High] [Time Horizon: Real-time Operations] | HIGH | Retired | 2015-10-01 | 2015-11-12 | GOP
COM-001-2 | Communications | R8.1. | Its Balancing Authority. | HIGH | Retired | 2015-10-01 | 2015-11-12 | GOP
COM-001-2 | Communications | R8.2. | Its Transmission Operator. | HIGH | Retired | 2015-10-01 | 2015-11-12
COM-001-2 | Communications | R9. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall test its Alternative Interpersonal Communication capability at least once each calendar month. If the test is unsuccessful, the responsible entity shall initiate action to repair or designate a replacement Alternative Interpersonal Communication capability within 2 hours. [Violation Risk Factor: Medium][Time Horizon: Real-time Operations, Sameday Operations] | MEDIUM | Retired | 2015-10-01 | 2015-11-12 | TOP, RC, BA
COM-001-2.1 | Communications | R1. | Each Reliability Coordinator shall have Interpersonal Communication capability with the following entities (unless the Reliability Coordinator detects a failure of its Interpersonal Communication capability in which case Requirement R10 shall apply): [Violation Risk Factor: High] [Time Horizon: Real-time Operations] | HIGH | Retired | 2015-11-13 | 2017-09-30 | RC
COM-001-2.1 | Communications | R1.1. | All Transmission Operators and Balancing Authorities within its Reliability Coordinator Area. | HIGH | Retired | 2015-11-13 | 2017-09-30 | RC
COM-001-2.1 | Communications | R1.2. | Each adjacent Reliability Coordinator within the same Interconnection. | HIGH | Retired | 2015-11-13 | 2017-09-30 | RC
COM-001-2.1 | Communications | R10. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall notify entities as identified in Requirements R1, R3, and R5, respectively within 60 minutes of the detection of a failure of its Interpersonal Communication capability that lasts 30 minutes or longer. [Violation Risk Factor: Medium] [Time Horizon: Realtime Operations] | MEDIUM | Retired | 2015-11-13 | 2017-09-30 | TOP, RC, BA
COM-001-2.1 | Communications | R11. | Each Distribution Provider and Generator Operator that detects a failure of its Interpersonal Communication capability shall consult each entity affected by the failure, as identified in Requirement R7 for a Distribution Provider or Requirement R8 for a Generator Operator, to determine a mutually agreeable action for the restoration of its Interpersonal Communication capability. [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | MEDIUM | Retired | 2015-11-13 | 2017-09-30 | GOP, DP
COM-001-2.1 | Communications | R2. | Each Reliability Coordinator shall designate an Alternative Interpersonal Communication capability with the following entities: [Violation Risk Factor: High] [Time Horizon: Real-time Operations] | HIGH | Retired | 2015-11-13 | 2017-09-30 | RC
COM-001-2.1 | Communications | R2.1. | All Transmission Operators and Balancing Authorities within its Reliability Coordinator Area. | HIGH | Retired | 2015-11-13 | 2017-09-30 | RC
COM-001-2.1 | Communications | R2.2. | Each adjacent Reliability Coordinator within the same Interconnection. | HIGH | Retired | 2015-11-13 | 2017-09-30 | RC
COM-001-2.1 | Communications | R3. | Each Transmission Operator shall have Interpersonal Communication capability with the following entities (unless the Transmission Operator detects a failure of its Interpersonal Communication capability in which case Requirement R10 shall apply): [Violation Risk Factor: High] [Time Horizon: Real-time Operations] | HIGH | Retired | 2015-11-13 | 2017-09-30 | TOP
COM-001-2.1 | Communications | R3.1. | Its Reliability Coordinator. | HIGH | Retired | 2015-11-13 | 2017-09-30 | TOP
COM-001-2.1 | Communications | R3.2. | Each Balancing Authority within its Transmission Operator Area. | HIGH | Retired | 2015-11-13 | 2017-09-30 | TOP
COM-001-2.1 | Communications | R3.3. | Each Distribution Provider within its Transmission Operator Area. | HIGH | Retired | 2015-11-13 | 2017-09-30 | TOP
COM-001-2.1 | Communications | R3.4. | Each Generator Operator within its Transmission Operator Area. | HIGH | Retired | 2015-11-13 | 2017-09-30 | TOP
COM-001-2.1 | Communications | R3.5. | Each adjacent Transmission Operator synchronously connected. | HIGH | Retired | 2015-11-13 | 2017-09-30 | TOP
COM-001-2.1 | Communications | R3.6. | Each adjacent Transmission Operator asynchronously connected. | HIGH | Retired | 2015-11-13 | 2017-09-30 | TOP
COM-001-2.1 | Communications | R4. | Each Transmission Operator shall designate an Alternative Interpersonal Communication capability with the following entities: [Violation Risk Factor: High] [Time Horizon: Real-time Operations] | HIGH | Retired | 2015-11-13 | 2017-09-30 | TOP
COM-001-2.1 | Communications | R4.1. | Its Reliability Coordinator. | HIGH | Retired | 2015-11-13 | 2017-09-30 | TOP
COM-001-2.1 | Communications | R4.2. | Each Balancing Authority within its Transmission Operator Area. | HIGH | Retired | 2015-11-13 | 2017-09-30 | TOP
COM-001-2.1 | Communications | R4.3. | Each adjacent Transmission Operator synchronously connected. | HIGH | Retired | 2015-11-13 | 2017-09-30 | TOP
COM-001-2.1 | Communications | R4.4. | Each adjacent Transmission Operator asynchronously connected. | HIGH | Retired | 2015-11-13 | 2017-09-30 | TOP
COM-001-2.1 | Communications | R5. | Each Balancing Authority shall have Interpersonal Communication capability with the following entities (unless the Balancing Authority detects a failure of its Interpersonal Communication capability in which case Requirement R10 shall apply): [Violation Risk Factor: High] [Time Horizon: Real-time Operations] | HIGH | Retired | 2015-11-13 | 2017-09-30 | BA
COM-001-2.1 | Communications | R5.1. | Its Reliability Coordinator. | HIGH | Retired | 2015-11-13 | 2017-09-30 | BA
COM-001-2.1 | Communications | R5.2. | Each Transmission Operator that operates Facilities within its Balancing Authority Area. | HIGH | Retired | 2015-11-13 | 2017-09-30 | BA
COM-001-2.1 | Communications | R5.3. | Each Distribution Provider within its Balancing Authority Area. | HIGH | Retired | 2015-11-13 | 2017-09-30 | BA
COM-001-2.1 | Communications | R5.4. | Each Generator Operator that operates Facilities within its Balancing Authority Area. | HIGH | Retired | 2015-11-13 | 2017-09-30 | BA
COM-001-2.1 | Communications | R5.5. | Each Adjacent Balancing Authority. | HIGH | Retired | 2015-11-13 | 2017-09-30 | BA
COM-001-2.1 | Communications | R6. | Each Balancing Authority shall designate an Alternative Interpersonal Communication capability with the following entities: [Violation Risk Factor: High] [Time Horizon: Real-time Operations] | HIGH | Retired | 2015-11-13 | 2017-09-30 | BA
COM-001-2.1 | Communications | R6.1. | Its Reliability Coordinator. | HIGH | Retired | 2015-11-13 | 2017-09-30 | BA
COM-001-2.1 | Communications | R6.2. | Each Transmission Operator that operates Facilities within its Balancing Authority Area. | HIGH | Retired | 2015-11-13 | 2017-09-30 | BA
COM-001-2.1 | Communications | R6.3. | Each Adjacent Balancing Authority. | HIGH | Retired | 2015-11-13 | 2017-09-30 | BA
COM-001-2.1 | Communications | R7. | Each Distribution Provider shall have Interpersonal Communication capability with the following entities (unless the Distribution Provider detects a failure of its Interpersonal Communication capability in which case Requirement R11 shall apply): [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | MEDIUM | Retired | 2015-11-13 | 2017-09-30 | DP
COM-001-2.1 | Communications | R7.1. | Its Balancing Authority. | MEDIUM | Retired | 2015-11-13 | 2017-09-30
COM-001-2.1 | Communications | R7.2. | Its Transmission Operator. | MEDIUM | Retired | 2015-11-13 | 2017-09-30
COM-001-2.1 | Communications | R8. | Each Generator Operator shall have Interpersonal Communication capability with the following entities (unless the Generator Operator detects a failure of its Interpersonal Communication capability in which case Requirement R11 shall apply): [Violation Risk Factor: High] [Time Horizon: Real-time Operations] | HIGH | Retired | 2015-11-13 | 2017-09-30 | GOP
COM-001-2.1 | Communications | R8.1. | Its Balancing Authority. | HIGH | Retired | 2015-11-13 | 2017-09-30 | GOP
COM-001-2.1 | Communications | R8.2. | Its Transmission Operator. | HIGH | Retired | 2015-11-13 | 2017-09-30
COM-001-2.1 | Communications | R9. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall test its Alternative Interpersonal Communication capability at least once each calendar month. If the test is unsuccessful, the responsible entity shall initiate action to repair or designate a replacement Alternative Interpersonal Communication capability within 2 hours. [Violation Risk Factor: Medium][Time Horizon: Real-time Operations, Sameday Operations] | MEDIUM | Retired | 2015-11-13 | 2017-09-30 | TOP, RC, BA
COM-001-3 | Communications | R1. | Each Reliability Coordinator shall have Interpersonal Communication capability with the following entities (unless the Reliability Coordinator detects a failure of its Interpersonal Communication capability in which case Requirement R10 shall apply): | HIGH | Effective | 2017-10-01 |  | RC
COM-001-3 | Communications | R1.1. | All Transmission Operators and Balancing Authorities within its Reliability Coordinator Area. | HIGH | Effective | 2017-10-01 |  | RC
COM-001-3 | Communications | R1.2. | Each adjacent Reliability Coordinator within the same Interconnection. | HIGH | Effective | 2017-10-01 |  | RC
COM-001-3 | Communications | R10. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall notify entities as identified in Requirements R1, R3, and R5, respectively within 60 minutes of the detection of a failure of its Interpersonal Communication capability that lasts 30 minutes or longer. | MEDIUM | Effective | 2017-10-01 |  | TOP, RC, BA
COM-001-3 | Communications | R11. | Each Distribution Provider and Generator Operator that detects a failure of its Interpersonal Communication capability shall consult each entity affected by the failure, as identified in Requirement R7 for a Distribution Provider or Requirement R8 for a Generator Operator, to determine a mutually agreeable action for the restoration of its Interpersonal Communication capability. | MEDIUM | Effective | 2017-10-01 |  | GOP, DP
COM-001-3 | Communications | R12. | Each Reliability Coordinator, Transmission Operator, Generator Operator, and Balancing Authority shall have internal Interpersonal Communication capabilities for the exchange of information necessary for the Reliable Operation of the BES. This includes communication capabilities between Control Centers within the same functional entity, and/or between a Control Center and field personnel. | HIGH | Effective | 2017-10-01 |  | TOP, RC, GOP, BA
COM-001-3 | Communications | R13. | Each Distribution Provider shall have internal Interpersonal Communication capabilities for the exchange of information necessary for the Reliable Operation of the BES. This includes communication capabilities between control centers within the same functional entity, and/or between a control center and field personnel. | MEDIUM | Effective | 2017-10-01 |  | DP
COM-001-3 | Communications | R2. | Each Reliability Coordinator shall designate an Alternative Interpersonal Communication capability with the following entities: | HIGH | Effective | 2017-10-01 |  | RC
COM-001-3 | Communications | R2.1. | All Transmission Operators and Balancing Authorities within its Reliability Coordinator Area. | HIGH | Effective | 2017-10-01 |  | RC
COM-001-3 | Communications | R2.2. | Each adjacent Reliability Coordinator within the same Interconnection. | HIGH | Effective | 2017-10-01 |  | RC
COM-001-3 | Communications | R3. | Each Transmission Operator shall have Interpersonal Communication capability with the following entities (unless the Transmission Operator detects a failure of its Interpersonal Communication capability in which case Requirement R10 shall apply): [Violation Risk Factor: High] [Time Horizon: Real-time Operations] | HIGH | Effective | 2017-10-01 |  | TOP
COM-001-3 | Communications | R3.1. | Its Reliability Coordinator. | HIGH | Effective | 2017-10-01 |  | TOP
COM-001-3 | Communications | R3.2. | Each Balancing Authority within its Transmission Operator Area. | HIGH | Effective | 2017-10-01 |  | TOP
COM-001-3 | Communications | R3.3. | Each Distribution Provider within its Transmission Operator Area. | HIGH | Effective | 2017-10-01 |  | TOP
COM-001-3 | Communications | R3.4. | Each Generator Operator within its Transmission Operator Area. | HIGH | Effective | 2017-10-01 |  | TOP
COM-001-3 | Communications | R3.5. | Each adjacent Transmission Operator synchronously connected. | HIGH | Effective | 2017-10-01 |  | TOP
COM-001-3 | Communications | R3.6. | Each adjacent Transmission Operator asynchronously connected. | HIGH | Effective | 2017-10-01 |  | TOP
COM-001-3 | Communications | R4. | Each Transmission Operator shall designate an Alternative Interpersonal Communication capability with the following entities: | HIGH | Effective | 2017-10-01 |  | TOP
COM-001-3 | Communications | R4.1. | Its Reliability Coordinator. | HIGH | Effective | 2017-10-01 |  | TOP
COM-001-3 | Communications | R4.2. | Each Balancing Authority within its Transmission Operator Area. | HIGH | Effective | 2017-10-01 |  | TOP
COM-001-3 | Communications | R4.3. | Each adjacent Transmission Operator synchronously connected. | HIGH | Effective | 2017-10-01 |  | TOP
COM-001-3 | Communications | R4.4. | Each adjacent Transmission Operator asynchronously connected. | HIGH | Effective | 2017-10-01 |  | TOP
COM-001-3 | Communications | R5. | Each Balancing Authority shall have Interpersonal Communication capability with the following entities (unless the Balancing Authority detects a failure of its Interpersonal Communication capability in which case Requirement R10 shall apply): | HIGH | Effective | 2017-10-01 |  | BA
COM-001-3 | Communications | R5.1. | Its Reliability Coordinator. | HIGH | Effective | 2017-10-01 |  | BA
COM-001-3 | Communications | R5.2. | Each Transmission Operator that operates Facilities within its Balancing Authority Area. | HIGH | Effective | 2017-10-01 |  | BA
COM-001-3 | Communications | R5.3. | Each Distribution Provider within its Balancing Authority Area. | HIGH | Effective | 2017-10-01 |  | BA
COM-001-3 | Communications | R5.4. | Each Generator Operator that operates Facilities within its Balancing Authority Area. | HIGH | Effective | 2017-10-01 |  | BA
COM-001-3 | Communications | R5.5. | Each Adjacent Balancing Authority. | HIGH | Effective | 2017-10-01 |  | BA
COM-001-3 | Communications | R6. | Each Balancing Authority shall designate an Alternative Interpersonal Communication capability with the following entities: | HIGH | Effective | 2017-10-01 |  | BA
COM-001-3 | Communications | R6.1. | Its Reliability Coordinator. | HIGH | Effective | 2017-10-01 |  | BA
COM-001-3 | Communications | R6.2. | Each Transmission Operator that operates Facilities within its Balancing Authority Area. | HIGH | Effective | 2017-10-01 |  | BA
COM-001-3 | Communications | R6.3. | Each Adjacent Balancing Authority. | HIGH | Effective | 2017-10-01 |  | BA
COM-001-3 | Communications | R7. | Each Distribution Provider shall have Interpersonal Communication capability with the following entities (unless the Distribution Provider detects a failure of its Interpersonal Communication capability in which case Requirement R11 shall apply): | MEDIUM | Effective | 2017-10-01 |  | DP
COM-001-3 | Communications | R7.1. | Its Balancing Authority. | MEDIUM | Effective | 2017-10-01 |  | DP
COM-001-3 | Communications | R7.2. | Its Transmission Operator. | MEDIUM | Effective | 2017-10-01 |  | DP
COM-001-3 | Communications | R8. | Each Generator Operator shall have Interpersonal Communication capability with the following entities (unless the Generator Operator detects a failure of its Interpersonal Communication capability in which case Requirement R11 shall apply): | HIGH | Effective | 2017-10-01 |  | GOP
COM-001-3 | Communications | R8.1. | Its Balancing Authority. | HIGH | Effective | 2017-10-01 |  | GOP
COM-001-3 | Communications | R8.2. | Its Transmission Operator. | HIGH | Effective | 2017-10-01 |  | GOP
COM-001-3 | Communications | R9. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall test its Alternative Interpersonal Communication capability at least once each calendar month. If the test is unsuccessful, the responsible entity shall initiate action to repair or designate a replacement Alternative Interpersonal Communication capability within 2 hours. | MEDIUM | Effective | 2017-10-01 |  | TOP, RC, BA
COM-002-2 | Communications and Coordination | R1. | Each Transmission Operator, Balancing Authority, and Generator Operator shall have communications (voice and data links) with appropriate Reliability Coordinators, Balancing Authorities, and Transmission Operators. Such communications shall be staffed and available for addressing a real-time emergency condition. | HIGH | Retired | 2006-11-01 | 2016-06-30 | TOP, GOP, BA
COM-002-2 | Communications and Coordination | R1.1. | Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator, and all other potentially affected Balancing Authorities and Transmission Operators through predetermined communication paths of any condition that could threaten the reliability of its area or when firm load shedding is anticipated. | HIGH | Retired | 2006-11-01 | 2016-06-30 | TOP, BA
COM-002-2 | Communications and Coordination | R2. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall issue directives in a clear, concise, and definitive manner; shall ensure the recipient of the directive repeats the information back correctly; and shall acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. | MEDIUM | Retired | 2006-11-01 | 2016-06-30 | TOP, RC, BA
COM-002-2a | Communications and Coordination | R1. | Each Transmission Operator, Balancing Authority, and Generator Operator shall have communications (voice and data links) with appropriate Reliability Coordinators, Balancing Authorities, and Transmission Operators. Such communications shall be staffed and available for addressing a real-time emergency condition. | HIGH | Never Came Into Effect in Ontario |  |  | TOP, GOP, BA
COM-002-2a | Communications and Coordination | R1.1. | Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator, and all other potentially affected Balancing Authorities and Transmission Operators through predetermined communication paths of any condition that could threaten the reliability of its area or when firm load shedding is anticipated. | HIGH | Never Came Into Effect in Ontario |  |  | TOP, BA
COM-002-2a | Communications and Coordination | R2. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall issue directives in a clear, concise, and definitive manner; shall ensure the recipient of the directive repeats the information back correctly; and shall acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. | MEDIUM | Never Came Into Effect in Ontario |  |  | TOP, RC, BA
COM-002-3 | Communications and Coordination | R1. | When a Reliability Coordinator, Transmission Operator, or Balancing Authority requires actions to be executed as a Reliability Directive, the Reliability Coordinator, Transmission Operator, or Balancing Authority shall identify the action as a Reliability Directive to the recipient. [Violation Risk Factor: High][Time Horizon: Real-Time] | HIGH | Never Came Into Effect in Ontario |  |  | TOP, RC, BA
COM-002-3 | Communications and Coordination | R2. | Each Balancing Authority, Transmission Operator, Generator Operator, and Distribution Provider that is the recipient of a Reliability Directive shall repeat, restate, rephrase, or recapitulate the Reliability Directive. [Violation Risk Factor: High][Time Horizon: Real-Time] | HIGH | Never Came Into Effect in Ontario |  |  | TOP, GOP, DP, BA
COM-002-3 | Communications and Coordination | R3. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority that issues a Reliability Directive shall either: [Violation Risk Factor: High][Time Horizon: Real-Time]  Confirm that the response from the recipient of the Reliability Directive (in accordance with Requirement R2) was accurate, or  Reissue the Reliability Directive to resolve a misunderstanding. | HIGH | Never Came Into Effect in Ontario |  |  | TOP, RC, BA
COM-002-4 | Operating Personnel Communications Protocols | R1. | Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall develop documented communications protocols for its operating personnel that issue and receive Operating Instructions. The protocols shall, at a minimum: [Violation Risk Factor: Low][Time Horizon: Long-term Planning] | LOWER | Effective | 2016-07-01 |  | TOP, RC, BA
COM-002-4 | Operating Personnel Communications Protocols | R1.1. | Require its operating personnel that issue and receive an oral or written Operating Instruction to use the English language, unless agreed to otherwise. An alternate language may be used for internal operations. | LOWER | Effective | 2016-07-01 |  | TOP, RC, BA
COM-002-4 | Operating Personnel Communications Protocols | R1.2. | Require its operating personnel that issue an oral two-party, person-to-person Operating Instruction to take one of the following actions:  Confirm the receiver’s response if the repeated information is correct.  Reissue the Operating Instruction if the repeated information is incorrect or if requested by the receiver.  Take an alternative action if a response is not received or if the Operating Instruction was not understood by the receiver. | LOWER | Effective | 2016-07-01 |  | TOP, RC, BA
COM-002-4 | Operating Personnel Communications Protocols | R1.3. | Require its operating personnel that receive an oral two-party, person-to-person Operating Instruction to take one of the following actions:  Repeat, not necessarily verbatim, the Operating Instruction and receive confirmation from the issuer that the response was correct.  Request that the issuer reissue the Operating Instruction. | LOWER | Effective | 2016-07-01 |  | TOP, RC, BA
COM-002-4 | Operating Personnel Communications Protocols | R1.4. | Require its operating personnel that issue a written or oral single-party to multiple-party burst Operating Instruction to confirm or verify that the Operating Instruction was received by at least one receiver of the Operating Instruction. | LOWER | Effective | 2016-07-01 |  | TOP, RC, BA
COM-002-4 | Operating Personnel Communications Protocols | R1.5. | Specify the instances that require time identification when issuing an oral or written Operating Instruction and the format for that time identification. | LOWER | Effective | 2016-07-01 |  | TOP, RC, BA
COM-002-4 | Operating Personnel Communications Protocols | R1.6. | Specify the nomenclature for Transmission interface Elements and Transmission interface Facilities when issuing an oral or written Operating Instruction. | LOWER | Effective | 2016-07-01 |  | TOP, RC, BA
COM-002-4 | Operating Personnel Communications Protocols | R2. | Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall conduct initial training for each of its operating personnel responsible for the Real-time operation of the interconnected Bulk Electric System on the documented communications protocols developed in Requirement R1 prior to that individual operator issuing an Operating Instruction. [Violation Risk Factor: Low][Time Horizon: Long-term Planning] | LOWER | Effective | 2016-07-01 |  | TOP, RC, BA
COM-002-4 | Operating Personnel Communications Protocols | R3. | Each Distribution Provider and Generator Operator shall conduct initial training for each of its operating personnel who can receive an oral two-party, person-to-person Operating Instruction prior to that individual operator receiving an oral two-party, person-to-person Operating Instruction to either: [Violation Risk Factor: Low][Time Horizon: Long-term Planning]  Repeat, not necessarily verbatim, the Operating Instruction and receive confirmation from the issuer that the response was correct, or  Request that the issuer reissue the Operating Instruction. | LOWER | Effective | 2016-07-01 |  | GOP, DP
COM-002-4 | Operating Personnel Communications Protocols | R4. | Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall at least once every twelve (12) calendar months: [Violation Risk Factor: Medium][Time Horizon: Operations Planning] | MEDIUM | Effective | 2016-07-01 |  | TOP, RC, BA
COM-002-4 | Operating Personnel Communications Protocols | R4.1. | Assess adherence to the documented communications protocols in Requirement R1 by its operating personnel that issue and receive Operating Instructions, provide feedback to those operating personnel and take corrective action, as deemed appropriate by the entity, to address deviations from the documented protocols. | MEDIUM | Effective | 2016-07-01 |  | TOP, RC, BA
COM-002-4 | Operating Personnel Communications Protocols | R4.2. | Assess the effectiveness of its documented communications protocols in Requirement R1 for its operating personnel that issue and receive Operating Instructions and modify its documented communication protocols, as necessary. | MEDIUM | Effective | 2016-07-01 |  | TOP, RC, BA
COM-002-4 | Operating Personnel Communications Protocols | R5. | Each Balancing Authority, Reliability Coordinator, and Transmission Operator that issues an oral two-party, person-to-person Operating Instruction during an Emergency, excluding written or oral single-party to multiple-party burst Operating Instructions, shall either: [Violation Risk Factor: High][Time Horizon: Real-time Operations]  Confirm the receiver’s response if the repeated information is correct (in accordance with Requirement R6).  Reissue the Operating Instruction if the repeated information is incorrect or if requested by the receiver, or  Take an alternative action if a response is not received or if the Operating Instruction was not understood by the receiver. | HIGH | Effective | 2016-07-01 |  | TOP, RC, BA
COM-002-4 | Operating Personnel Communications Protocols | R6. | Each Balancing Authority, Distribution Provider, Generator Operator, and Transmission Operator that receives an oral two-party, person-to-person Operating Instruction during an Emergency, excluding written or oral single-party to multiple-party burst Operating Instructions, shall either: [Violation Risk Factor: High][Time Horizon: Real-time Operations]  Repeat, not necessarily verbatim, the Operating Instruction and receive confirmation from the issuer that the response was correct, or  Request that the issuer reissue the Operating Instruction. | HIGH | Effective | 2016-07-01 |  | TOP, GOP, DP, BA
COM-002-4 | Operating Personnel Communications Protocols | R7. | Each Balancing Authority, Reliability Coordinator, and Transmission Operator that issues a written or oral single-party to multiple-party burst Operating Instruction during an Emergency shall confirm or verify that the Operating Instruction was received by at least one receiver of the Operating Instruction. [Violation Risk Factor: High][Time Horizon: Real-time Operations] | HIGH | Effective | 2016-07-01 |  | TOP, RC, BA
EOP-001-1 | Emergency Operations Planning | R1. | Balancing Authorities shall have operating agreements with adjacent Balancing Authorities that shall, at a minimum, contain provisions for emergency assistance, including provisions to obtain emergency assistance from remote Balancing Authorities. |  | Never Came Into Effect in Ontario |  |  | BA
EOP-001-1 | Emergency Operations Planning | R2. | Each Transmission Operator and Balancing Authority shall: |  | Never Came Into Effect in Ontario |  |  | TOP, BA
EOP-001-1 | Emergency Operations Planning | R2. | Each Transmission Operator and Balancing Authority shall: |  | Never Came Into Effect in Ontario |  |  | TOP, BA
EOP-001-1 | Emergency Operations Planning | R2.1. | Develop, maintain, and implement a set of plans to mitigate operating emergencies for insufficient generating capacity. |  | Never Came Into Effect in Ontario |  |  | TOP, BA
EOP-001-1 | Emergency Operations Planning | R2.2. | Develop, maintain, and implement a set of plans to mitigate operating emergencies on the transmission system. |  | Never Came Into Effect in Ontario |  |  | TOP, BA
EOP-001-1 | Emergency Operations Planning | R2.3. | Develop, maintain, and implement a set of plans for load shedding. |  | Never Came Into Effect in Ontario |  |  | TOP, BA
EOP-001-1 | Emergency Operations Planning | R2.4. | Develop, maintain, and implement a set of plans for system restoration. |  | Never Came Into Effect in Ontario |  |  | TOP, BA
EOP-001-1 | Emergency Operations Planning | R3. | Each Transmission Operator and Balancing Authority shall have emergency plans that will enable it to mitigate operating emergencies. At a minimum, Transmission Operator and Balancing Authority emergency plans shall include: |  | Never Came Into Effect in Ontario |  |  | TOP, BA
EOP-001-1 | Emergency Operations Planning | R3.1. | Communications protocols to be used during emergencies. |  | Never Came Into Effect in Ontario |  |  | TOP, BA
EOP-001-1 | Emergency Operations Planning | R3.2. | A list of controlling actions to resolve the emergency. Load reduction, in sufficient quantity to resolve the emergency within NERC-established timelines, shall be one of the controlling actions. |  | Never Came Into Effect in Ontario |  |  | TOP, BA
EOP-001-1 | Emergency Operations Planning | R3.3. | The tasks to be coordinated with and among adjacent Transmission Operators and Balancing Authorities. |  | Never Came Into Effect in Ontario |  |  | TOP, BA
EOP-001-1 | Emergency Operations Planning | R3.4. | Staffing levels for the emergency. |  | Never Came Into Effect in Ontario |  |  | TOP, BA
EOP-001-1 | Emergency Operations Planning | R4. | Each Transmission Operator and Balancing Authority shall include the applicable elements in Attachment 1-EOP-001-0 when developing an emergency plan. |  | Never Came Into Effect in Ontario |  |  | TOP, BA
EOP-001-1 | Emergency Operations Planning | R5. | The Transmission Operator and Balancing Authority shall annually review and update each emergency plan. The Transmission Operator and Balancing Authority shall provide a copy of its updated emergency plans to its Reliability Coordinator and to neighboring Transmission Operators and Balancing Authorities. |  | Never Came Into Effect in Ontario |  |  | TOP, BA
EOP-001-1 | Emergency Operations Planning | R6. | The Transmission Operator and Balancing Authority shall coordinate its emergency plans with other Transmission Operators and Balancing Authorities as appropriate. This coordination includes the following steps, as applicable: |  | Never Came Into Effect in Ontario |  |  | TOP, BA
EOP-001-1 | Emergency Operations Planning | R6. | The Transmission Operator and Balancing Authority shall coordinate its emergency plans with other Transmission Operators and Balancing Authorities as appropriate. This coordination includes the following steps, as applicable: |  | Never Came Into Effect in Ontario |  |  | TOP, BA
EOP-001-1 | Emergency Operations Planning | R6. | The Transmission Operator and Balancing Authority shall coordinate its emergency plans with other Transmission Operators and Balancing Authorities as appropriate. This coordination includes the following steps, as applicable: |  | Never Came Into Effect in Ontario |  |  | TOP, BA
EOP-001-1 | Emergency Operations Planning | R6.1. | The Transmission Operator and Balancing Authority shall establish and maintain reliable communications between interconnected systems. |  | Never Came Into Effect in Ontario |  |  | TOP, BA
EOP-001-1 | Emergency Operations Planning | R6.2. | The Transmission Operator and Balancing Authority shall arrange new interchange agreements to provide for emergency capacity or energy transfers if existing agreements cannot be used. |  | Never Came Into Effect in Ontario |  |  | TOP, BA
EOP-001-1 | Emergency Operations Planning | R6.3. | The Transmission Operator and Balancing Authority shall coordinate transmission and generator maintenance schedules to maximize capacity or conserve the fuel in short supply. (This includes water for hydro generators.) |  | Never Came Into Effect in Ontario |  |  | TOP, BA
EOP-001-1 | Emergency Operations Planning | R6.4. | The Transmission Operator and Balancing Authority shall arrange deliveries of electrical energy or fuel from remote systems through normal operating channels. |  | Never Came Into Effect in Ontario |  |  | TOP, BA
EOP-001-2 | Emergency Operations Planning | R1. | Balancing Authorities shall have operating agreements with adjacent Balancing Authorities that shall, at a minimum, contain provisions for emergency assistance, including provisions to obtain emergency assistance from remote Balancing Authorities. | HIGH | Retired |  |  | BA
EOP-001-2 | Emergency Operations Planning | R2. | Each Transmission Operator and Balancing Authority shall: | MEDIUM | Retired |  |  | TOP, BA
EOP-001-2 | Emergency Operations Planning | R2. | Each Transmission Operator and Balancing Authority shall: | MEDIUM | Retired |  |  | TOP, BA
EOP-001-2 | Emergency Operations Planning | R2.1. | Develop, maintain, and implement a set of plans to mitigate operating emergencies for insufficient generating capacity. | MEDIUM | Retired |  |  | TOP, BA
EOP-001-2 | Emergency Operations Planning | R2.2. | Develop, maintain, and implement a set of plans to mitigate operating emergencies on the transmission system. | MEDIUM | Retired |  |  | TOP, BA
EOP-001-2 | Emergency Operations Planning | R2.3. | Develop, maintain, and implement a set of plans for load shedding. | MEDIUM | Retired |  |  | TOP, BA
EOP-001-2 | Emergency Operations Planning | R3. | Each Transmission Operator and Balancing Authority shall have emergency plans that will enable it to mitigate operating emergencies. At a minimum, Transmission Operator and Balancing Authority emergency plans shall include: | MEDIUM | Retired |  |  | TOP, BA
EOP-001-2 | Emergency Operations Planning | R3.1. | Communications protocols to be used during emergencies. | MEDIUM | Retired |  |  | TOP, BA
EOP-001-2 | Emergency Operations Planning | R3.2. | A list of controlling actions to resolve the emergency. Load reduction, in sufficient quantity to resolve the emergency within NERC-established timelines, shall be one of the controlling actions. | MEDIUM | Retired |  |  | TOP, BA
EOP-001-2 | Emergency Operations Planning | R3.3. | The tasks to be coordinated with and among adjacent Transmission Operators and Balancing Authorities. | MEDIUM | Retired |  |  | TOP, BA
EOP-001-2 | Emergency Operations Planning | R3.4. | Staffing levels for the emergency. | MEDIUM | Retired |  |  | TOP, BA
EOP-001-2 | Emergency Operations Planning | R4. | Each Transmission Operator and Balancing Authority shall include the applicable elements in Attachment 1-EOP-001-0 when developing an emergency plan. | MEDIUM | Retired |  |  | TOP, BA
EOP-001-2 | Emergency Operations Planning | R5. | The Transmission Operator and Balancing Authority shall annually review and update each emergency plan. The Transmission Operator and Balancing Authority shall provide a copy of its updated emergency plans to its Reliability Coordinator and to neighboring Transmission Operators and Balancing Authorities. | MEDIUM | Retired |  |  | TOP, BA
EOP-001-2 | Emergency Operations Planning | R6. | The Transmission Operator and Balancing Authority shall coordinate its emergency plans with other Transmission Operators and Balancing Authorities as appropriate. This coordination includes the following steps, as applicable: | MEDIUM | Retired |  |  | TOP, BA
EOP-001-2 | Emergency Operations Planning | R6. | The Transmission Operator and Balancing Authority shall coordinate its emergency plans with other Transmission Operators and Balancing Authorities as appropriate. This coordination includes the following steps, as applicable: | MEDIUM | Retired |  |  | TOP, BA
EOP-001-2 | Emergency Operations Planning | R6. | The Transmission Operator and Balancing Authority shall coordinate its emergency plans with other Transmission Operators and Balancing Authorities as appropriate. This coordination includes the following steps, as applicable: | MEDIUM | Retired |  |  | TOP, BA
EOP-001-2 | Emergency Operations Planning | R6.1. | The Transmission Operator and Balancing Authority shall establish and maintain reliable communications between interconnected systems. | MEDIUM | Retired |  |  | TOP, BA
EOP-001-2 | Emergency Operations Planning | R6.2. | The Transmission Operator and Balancing Authority shall arrange new interchange agreements to provide for emergency capacity or energy transfers if existing agreements cannot be used. | MEDIUM | Retired |  |  | TOP, BA
EOP-001-2 | Emergency Operations Planning | R6.3. | The Transmission Operator and Balancing Authority shall coordinate transmission and generator maintenance schedules to maximize capacity or conserve the fuel in short supply. (This includes water for hydro generators.) | MEDIUM | Retired |  |  | TOP, BA
EOP-001-2 | Emergency Operations Planning | R6.4. | The Transmission Operator and Balancing Authority shall arrange deliveries of electrical energy or fuel from remote systems through normal operating channels. | MEDIUM | Retired |  |  | TOP, BA
EOP-001-2.1b | Emergency Operations Planning | R1. | Balancing Authorities shall have operating agreements with adjacent Balancing Authorities that shall, at a minimum, contain provisions for emergency assistance, including provisions to obtain emergency assistance from remote Balancing Authorities. | HIGH | Retired | 2013-07-01 | 2017-03-31 | BA
EOP-001-2.1b | Emergency Operations Planning | R2. | Each Transmission Operator and Balancing Authority shall: | MEDIUM | Retired | 2013-07-01 | 2017-03-31 | TOP, BA
EOP-001-2.1b | Emergency Operations Planning | R2. | Each Transmission Operator and Balancing Authority shall: | MEDIUM | Retired | 2013-07-01 | 2017-03-31 | TOP, BA
EOP-001-2.1b | Emergency Operations Planning | R2.1. | Develop, maintain, and implement a set of plans to mitigate operating emergencies for insufficient generating capacity. | MEDIUM | Retired | 2013-07-01 | 2017-03-31 | TOP, BA
EOP-001-2.1b | Emergency Operations Planning | R2.2. | Develop, maintain, and implement a set of plans to mitigate operating emergencies on the transmission system. | MEDIUM | Retired | 2013-07-01 | 2017-03-31 | TOP, BA
EOP-001-2.1b | Emergency Operations Planning | R2.3. | Develop, maintain, and implement a set of plans for load shedding. | MEDIUM | Retired | 2013-07-01 | 2017-03-31 | TOP, BA
EOP-001-2.1b | Emergency Operations Planning | R3. | Each Transmission Operator and Balancing Authority shall have emergency plans that will enable it to mitigate operating emergencies. At a minimum, Transmission Operator and Balancing Authority emergency plans shall include: | MEDIUM | Retired | 2013-07-01 | 2017-03-31 | TOP, BA
EOP-001-2.1b | Emergency Operations Planning | R3.1. | Communications protocols to be used during emergencies. | MEDIUM | Retired | 2013-07-01 | 2017-03-31 | TOP, BA
EOP-001-2.1b | Emergency Operations Planning | R3.2. | A list of controlling actions to resolve the emergency. Load reduction, in sufficient quantity to resolve the emergency within NERC-established timelines, shall be one of the controlling actions. | MEDIUM | Retired | 2013-07-01 | 2017-03-31 | TOP, BA
EOP-001-2.1b | Emergency Operations Planning | R3.3. | The tasks to be coordinated with and among adjacent Transmission Operators and Balancing Authorities. | MEDIUM | Retired | 2013-07-01 | 2017-03-31 | TOP, BA
EOP-001-2.1b | Emergency Operations Planning | R3.4. | Staffing levels for the emergency. | MEDIUM | Retired | 2013-07-01 | 2017-03-31 | TOP, BA
EOP-001-2.1b | Emergency Operations Planning | R4. | Each Transmission Operator and Balancing Authority shall include the applicable elements in Attachment 1-EOP-001 when developing an emergency plan. | MEDIUM | Retired | 2013-07-01 | 2017-03-31 | TOP, BA
EOP-001-2.1b | Emergency Operations Planning | R5. | The Transmission Operator and Balancing Authority shall annually review and update each emergency plan. The Transmission Operator and Balancing Authority shall provide a copy of its updated emergency plans to its Reliability Coordinator and to neighboring Transmission Operators and Balancing Authorities. | MEDIUM | Retired | 2013-07-01 | 2017-03-31 | TOP, BA
EOP-001-2.1b | Emergency Operations Planning | R6. | The Transmission Operator and Balancing Authority shall coordinate its emergency plans with other Transmission Operators and Balancing Authorities as appropriate. This coordination includes the following steps, as applicable: | MEDIUM | Retired | 2013-07-01 | 2017-03-31 | TOP, BA
EOP-001-2.1b | Emergency Operations Planning | R6. | The Transmission Operator and Balancing Authority shall coordinate its emergency plans with other Transmission Operators and Balancing Authorities as appropriate. This coordination includes the following steps, as applicable: | MEDIUM | Retired | 2013-07-01 | 2017-03-31 | TOP, BA
EOP-001-2.1b | Emergency Operations Planning | R6. | The Transmission Operator and Balancing Authority shall coordinate its emergency plans with other Transmission Operators and Balancing Authorities as appropriate. This coordination includes the following steps, as applicable: | MEDIUM | Retired | 2013-07-01 | 2017-03-31 | TOP, BA
EOP-001-2.1b | Emergency Operations Planning | R6.1. | The Transmission Operator and Balancing Authority shall establish and maintain reliable communications between interconnected systems. | MEDIUM | Retired | 2013-07-01 | 2017-03-31 | TOP, BA
EOP-001-2.1b | Emergency Operations Planning | R6.2. | The Transmission Operator and Balancing Authority shall arrange new interchange agreements to provide for emergency capacity or energy transfers if existing agreements cannot be used. | MEDIUM | Retired | 2013-07-01 | 2017-03-31 | TOP, BA
EOP-001-2.1b | Emergency Operations Planning | R6.3. | The Transmission Operator and Balancing Authority shall coordinate transmission and generator maintenance schedules to maximize capacity or conserve the fuel in short supply. (This includes water for hydro generators.) | MEDIUM | Retired | 2013-07-01 | 2017-03-31 | TOP, BA
EOP-001-2.1b | Emergency Operations Planning | R6.4. | The Transmission Operator and Balancing Authority shall arrange deliveries of electrical energy or fuel from remote systems through normal operating channels. | MEDIUM | Retired | 2013-07-01 | 2017-03-31 | TOP, BA
EOP-001-2b | Emergency Operations Planning | R1. | Balancing Authorities shall have operating agreements with adjacent Balancing Authorities that shall, at a minimum, contain provisions for emergency assistance, including provisions to obtain emergency assistance from remote Balancing Authorities. | HIGH | Retired |  |  | BA
EOP-001-2b | Emergency Operations Planning | R2. | Each Transmission Operator and Balancing Authority shall: | MEDIUM | Retired |  |  | TOP, BA
EOP-001-2b | Emergency Operations Planning | R2. | Each Transmission Operator and Balancing Authority shall: | MEDIUM | Retired |  |  | TOP, BA
EOP-001-2b | Emergency Operations Planning | R2.1. | Develop, maintain, and implement a set of plans to mitigate operating emergencies for insufficient generating capacity. | MEDIUM | Retired |  |  | TOP, BA
EOP-001-2b | Emergency Operations Planning | R2.2. | Develop, maintain, and implement a set of plans to mitigate operating emergencies on the transmission system. | MEDIUM | Retired |  |  | TOP, BA
EOP-001-2b | Emergency Operations Planning | R2.3. | Develop, maintain, and implement a set of plans for load shedding. | MEDIUM | Retired |  |  | TOP, BA
EOP-001-2b | Emergency Operations Planning | R3. | Each Transmission Operator and Balancing Authority shall have emergency plans that will enable it to mitigate operating emergencies. At a minimum, Transmission Operator and Balancing Authority emergency plans shall include: | MEDIUM | Retired |  |  | TOP, BA
EOP-001-2b | Emergency Operations Planning | R3.1. | Communications protocols to be used during emergencies. | MEDIUM | Retired |  |  | TOP, BA
EOP-001-2b | Emergency Operations Planning | R3.2. | A list of controlling actions to resolve the emergency. Load reduction, in sufficient quantity to resolve the emergency within NERC-established timelines, shall be one of the controlling actions. | MEDIUM | Retired |  |  | TOP, BA
EOP-001-2b | Emergency Operations Planning | R3.3. | The tasks to be coordinated with and among adjacent Transmission Operators and Balancing Authorities. | MEDIUM | Retired |  |  | TOP, BA
EOP-001-2b | Emergency Operations Planning | R3.4. | Staffing levels for the emergency. | MEDIUM | Retired |  |  | TOP, BA
EOP-001-2b | Emergency Operations Planning | R4. | Each Transmission Operator and Balancing Authority shall include the applicable elements in Attachment 1-EOP-001-0 when developing an emergency plan. | MEDIUM | Retired |  |  | TOP, BA
EOP-001-2b | Emergency Operations Planning | R5. | The Transmission Operator and Balancing Authority shall annually review and update each emergency plan. The Transmission Operator and Balancing Authority shall provide a copy of its updated emergency plans to its Reliability Coordinator and to neighboring Transmission Operators and Balancing Authorities. | MEDIUM | Retired |  |  | TOP, BA
EOP-001-2b | Emergency Operations Planning | R6. | The Transmission Operator and Balancing Authority shall coordinate its emergency plans with other Transmission Operators and Balancing Authorities as appropriate. This coordination includes the following steps, as applicable: | MEDIUM | Retired |  |  | TOP, BA
EOP-001-2b | Emergency Operations Planning | R6. | The Transmission Operator and Balancing Authority shall coordinate its emergency plans with other Transmission Operators and Balancing Authorities as appropriate. This coordination includes the following steps, as applicable: | MEDIUM | Retired |  |  | TOP, BA
EOP-001-2b | Emergency Operations Planning | R6. | The Transmission Operator and Balancing Authority shall coordinate its emergency plans with other Transmission Operators and Balancing Authorities as appropriate. This coordination includes the following steps, as applicable: | MEDIUM | Retired |  |  | TOP, BA
EOP-001-2b | Emergency Operations Planning | R6.1. | The Transmission Operator and Balancing Authority shall establish and maintain reliable communications between interconnected systems. | MEDIUM | Retired |  |  | TOP, BA
EOP-001-2b | Emergency Operations Planning | R6.2. | The Transmission Operator and Balancing Authority shall arrange new interchange agreements to provide for emergency capacity or energy transfers if existing agreements cannot be used. | MEDIUM | Retired |  |  | TOP, BA
EOP-001-2b | Emergency Operations Planning | R6.3. | The Transmission Operator and Balancing Authority shall coordinate transmission and generator maintenance schedules to maximize capacity or conserve the fuel in short supply. (This includes water for hydro generators.) | MEDIUM | Retired |  |  | TOP, BA
EOP-001-2b | Emergency Operations Planning | R6.4. | The Transmission Operator and Balancing Authority shall arrange deliveries of electrical energy or fuel from remote systems through normal operating channels. | MEDIUM | Retired |  |  | TOP, BA
EOP-002-3.1 | Capacity and Energy Emergencies | R1. | Each Balancing Authority and Reliability Coordinator shall have the responsibility and clear decision-making authority to take whatever actions are needed to ensure the reliability of its respective area and shall exercise specific authority to alleviate capacity and energy emergencies. | HIGH | Retired | 2012-10-10 | 2017-03-31 | RC, BA
EOP-002-3.1 | Capacity and Energy Emergencies | R2. | Each Balancing Authority shall, when required and as appropriate, take one or more actions as described in its capacity and energy emergency plan to reduce risks to the interconnected system. | HIGH | Retired | 2012-10-10 | 2017-03-31 | BA
EOP-002-3.1 | Capacity and Energy Emergencies | R3. | A Balancing Authority that is experiencing an operating capacity or energy emergency shall communicate its current and future system conditions to its Reliability Coordinator and neighboring Balancing Authorities. | HIGH | Retired | 2012-10-10 | 2017-03-31 | BA
EOP-002-3.1 | Capacity and Energy Emergencies | R4. | A Balancing Authority anticipating an operating capacity or energy emergency shall perform all actions necessary including bringing on all available generation, postponing equipment maintenance, scheduling interchange purchases in advance, and being prepared to reduce firm load. | HIGH | Retired | 2012-10-10 | 2017-03-31 | BA
EOP-002-3.1 | Capacity and Energy Emergencies | R5. | A deficient Balancing Authority shall only use the assistance provided by the Interconnection’s frequency bias for the time needed to implement corrective actions. The Balancing Authority shall not unilaterally adjust generation in an attempt to return Interconnection frequency to normal beyond that supplied through frequency bias action and Interchange Schedule changes. Such unilateral adjustment may overload transmission facilities. | HIGH | Retired | 2012-10-10 | 2017-03-31 | BA
EOP-002-3.1 | Capacity and Energy Emergencies | R6. | If the Balancing Authority cannot comply with the Control Performance and Disturbance Control Standards, then it shall immediately implement remedies to do so. These remedies include, but are not limited to: | HIGH | Retired | 2012-10-10 | 2017-03-31 | BA
EOP-002-3.1 | Capacity and Energy Emergencies | R6.1. | Loading all available generating capacity. | HIGH | Retired | 2012-10-10 | 2017-03-31 | BA
EOP-002-3.1 | Capacity and Energy Emergencies | R6.2. | Deploying all available operating reserve. | HIGH | Retired | 2012-10-10 | 2017-03-31 | BA
EOP-002-3.1 | Capacity and Energy Emergencies | R6.3. | Interrupting interruptible load and exports. | HIGH | Retired | 2012-10-10 | 2017-03-31 | BA
EOP-002-3.1 | Capacity and Energy Emergencies | R6.4. | Requesting emergency assistance from other Balancing Authorities. | HIGH | Retired | 2012-10-10 | 2017-03-31 | BA
EOP-002-3.1 | Capacity and Energy Emergencies | R6.5. | Declaring an Energy Emergency through its Reliability Coordinator; and | HIGH | Retired | 2012-10-10 | 2017-03-31 | BA
EOP-002-3.1 | Capacity and Energy Emergencies | R6.6. | Reducing load, through procedures such as public appeals, voltage reductions, curtailing interruptible loads and firm loads. | HIGH | Retired | 2012-10-10 | 2017-03-31 | BA
EOP-002-3.1 | Capacity and Energy Emergencies | R7. | Once the Balancing Authority has exhausted the steps listed in Requirement 6, or if these steps cannot be completed in sufficient time to resolve the emergency condition, the Balancing Authority shall: | HIGH | Retired | 2012-10-10 | 2017-03-31 | BA
EOP-002-3.1 | Capacity and Energy Emergencies | R7.1. | Manually shed firm load without delay to return its ACE to zero; and | HIGH | Retired | 2012-10-10 | 2017-03-31 | BA
EOP-002-3.1 | Capacity and Energy Emergencies | R7.2. | Request the Reliability Coordinator to declare an Energy Emergency Alert in accordance with Attachment 1-EOP-002 “Energy Emergency Alerts.” | HIGH | Retired | 2012-10-10 | 2017-03-31 | BA
EOP-002-3.1 | Capacity and Energy Emergencies | R8. | A Reliability Coordinator that has any Balancing Authority within its Reliability Coordinator area experiencing a potential or actual Energy Emergency shall initiate an Energy Emergency Alert as detailed in Attachment 1-EOP-002 “Energy Emergency Alerts.” The Reliability Coordinator shall act to mitigate the emergency condition, including a request for emergency assistance if required. | HIGH | Retired | 2012-10-10 | 2017-03-31 | RC
EOP-002-3.1 | Capacity and Energy Emergencies | R9. | When a Transmission Service Provider expects to elevate the transmission service priority of an Interchange Transaction from Priority 6 (Network Integration Transmission Service from Non-designated Resources) to Priority 7 (Network Integration Transmission Service from designated Network Resources) as permitted in its transmission tariff: | HIGH | Retired | 2012-10-10 | 2017-03-31 | RC
EOP-002-3.1 | Capacity and Energy Emergencies | R9.1. | The deficient Load-Serving Entity shall request its Reliability Coordinator to initiate an Energy Emergency Alert in accordance with Attachment 1-EOP-002 “Energy Emergency Alerts.” | HIGH | Retired | 2012-10-10 | 2017-03-31
EOP-002-3.1 | Capacity and Energy Emergencies | R9.2. | The Reliability Coordinator shall submit the report to NERC for posting on the NERC Website, noting the expected total MW that may have its transmission service priority changed. | HIGH | Retired | 2012-10-10 | 2017-03-31 | RC
EOP-002-3.1 | Capacity and Energy Emergencies | R9.3. | The Reliability Coordinator shall use EEA 1 to forecast the change of the priority of transmission service of an Interchange Transaction on the system from Priority 6 to Priority 7. | LOWER | Retired | 2012-10-10 | 2017-03-31 | RC
EOP-002-3.1 | Capacity and Energy Emergencies | R9.4. | The Reliability Coordinator shall use EEA 2 to announce the change of the priority of transmission service of an Interchange Transaction on the system from Priority 6 to Priority 7. | LOWER | Retired | 2012-10-10 | 2017-03-31 | RC
EOP-003-2 | Load Shedding Plans | R1. | After taking all other remedial steps, a Transmission Operator or Balancing Authority operating with insufficient generation or transmission capacity shall shed customer load rather than risk an uncontrolled failure of components or cascading outages of the Interconnection. | HIGH | Retired | 2013-10-01 | 2017-03-31 | TOP, BA
EOP-003-2 | Load Shedding Plans | R2. | Each Transmission Operator shall establish plans for automatic load shedding for undervoltage conditions if the Transmission Operator or its associated Transmission Planner(s) or Planning Coordinator(s) determine that an under-voltage load shedding scheme is required. | HIGH | Retired | 2013-10-01 | 2017-03-31 | TOP
EOP-003-2 | Load Shedding Plans | R3. | Each Transmission Operator and Balancing Authority shall coordinate load shedding plans, excluding automatic under-frequency load shedding plans, among other interconnected Transmission Operators and Balancing Authorities. | HIGH | Retired | 2013-10-01 | 2017-03-31 | TOP, BA
EOP-003-2 | Load Shedding Plans | R4. | A Transmission Operator shall consider one or more of these factors in designing an automatic under voltage load shedding scheme: voltage level, rate of voltage decay, or power flow levels. | HIGH | Retired | 2013-10-01 | 2017-03-31 | TOP
EOP-003-2 | Load Shedding Plans | R4. | A Transmission Operator shall consider one or more of these factors in designing an automatic under voltage load shedding scheme: voltage level, rate of voltage decay, or power flow levels. | HIGH | Retired | 2013-10-01 | 2017-03-31 | TOP
EOP-003-2 | Load Shedding Plans | R5. | A Transmission Operator or Balancing Authority shall implement load shedding, excluding automatic under-frequency load shedding, in steps established to minimize the risk of further uncontrolled separation, loss of generation, or system shutdown. | HIGH | Retired | 2013-10-01 | 2017-03-31 | TOP, BA
EOP-003-2 | Load Shedding Plans | R6. | After a Transmission Operator or Balancing Authority Area separates from the Interconnection, if there is insufficient generating capacity to restore system frequency following automatic underfrequency load shedding, the Transmission Operator or Balancing Authority shall shed additional load. | HIGH | Retired | 2013-10-01 | 2017-03-31 | TOP, BA
EOP-003-2 | Load Shedding Plans | R7. | The Transmission Operator shall coordinate automatic undervoltage load shedding throughout their areas with tripping of shunt capacitors, and other automatic actions that will occur under abnormal voltage, or power flow conditions | HIGH | Retired | 2013-10-01 | 2017-03-31 | TOP
EOP-003-2 | Load Shedding Plans | R8. | Each Transmission Operator or Balancing Authority shall have plans for operator controlled manual load shedding to respond to real-time emergencies. The Transmission Operator or Balancing Authority shall be capable of implementing the load shedding in a timeframe adequate for responding to the emergency. | HIGH | Retired | 2013-10-01 | 2017-03-31 | TOP, BA
EOP-004-2 | Event Reporting | R1. | Each Responsible Entity shall have an event reporting Operating Plan in accordance with EOP-004-2 Attachment 1 that includes the protocol(s) for reporting to the Electric Reliability Organization and other organizations (e.g., the Regional Entity, company personnel, the Responsible Entity’s Reliability Coordinator, law enforcement, or governmental authority). | LOWER | Retired | 2014-01-01 | 2017-03-31 | TOP, TO, RC, GOP, GO, DP, BA
EOP-004-2 | Event Reporting | R1. | Each Responsible Entity shall have an event reporting Operating Plan in accordance with EOP-004-2 Attachment 1 that includes the protocol(s) for reporting to the Electric Reliability Organization and other organizations (e.g., the Regional Entity, company personnel, the Responsible Entity’s Reliability Coordinator, law enforcement, or governmental authority). | LOWER | Retired | 2014-01-01 | 2017-03-31 | TOP, TO, RC, GOP, GO, DP, BA
EOP-004-2 | Event Reporting | R2. | Each Responsible Entity shall report events per their Operating Plan within 24 hours of recognition of meeting an event type threshold for reporting or by the end of the next business day if the event occurs on a weekend (which is recognized to be 4 PM local time on Friday to 8 AM Monday local time). | MEDIUM | Retired | 2014-01-01 | 2017-03-31 | TOP, TO, RC, GOP, GO, DP, BA
EOP-004-2 | Event Reporting | R2. | Each Responsible Entity shall report events per their Operating Plan within 24 hours of recognition of meeting an event type threshold for reporting or by the end of the next business day if the event occurs on a weekend (which is recognized to be 4 PM local time on Friday to 8 AM Monday local time). | MEDIUM | Retired | 2014-01-01 | 2017-03-31 | TOP, TO, RC, GOP, GO, DP, BA
EOP-004-2 | Event Reporting | R3. | Each Responsible Entity shall validate all contact information contained in the Operating Plan pursuant to Requirement R1 each calendar year. | MEDIUM | Retired | 2014-01-01 | 2017-03-31 | TOP, TO, RC, GOP, GO, DP, BA
EOP-004-2 | Event Reporting | R3. | Each Responsible Entity shall validate all contact information contained in the Operating Plan pursuant to Requirement R1 each calendar year. | MEDIUM | Retired | 2014-01-01 | 2017-03-31 | TOP, TO, RC, GOP, GO, DP, BA
EOP-004-3 | Event Reporting | R1. | Each Responsible Entity shall have an event reporting Operating Plan in accordance with EOP-004-2-3 Attachment 1 that includes the protocol(s) for reporting to the Electric Reliability Organization and other organizations (e.g., the Regional Entity, company personnel, the Responsible Entity’s Reliability Coordinator, law enforcement, or governmental authority). [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Retired | 2017-04-01 | 2019-03-31 | TOP, TO, RC, GOP, GO, DP, BA
EOP-004-3 | Event Reporting | R2. | Each Responsible Entity shall report events per their Operating Plan within 24 hours of recognition of meeting an event type threshold for reporting or by the end of the next business day if the event occurs on a weekend (which is recognized to be 4 PM local time on Friday to 8 AM Monday local time). [Violation Risk Factor: Medium] [Time Horizon: Operations Assessment] | MEDIUM | Retired | 2017-04-01 | 2019-03-31 | TOP, TO, RC, GOP, GO, DP, BA
EOP-004-3 | Event Reporting | R3. | Each Responsible Entity shall validate all contact information contained in the Operating Plan pursuant to Requirement R1 each calendar year. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Retired | 2017-04-01 | 2019-03-31 | TOP, TO, RC, GOP, GO, DP, BA
EOP-004-4 | Event Reporting | R1. | Each Responsible Entity shall have an event reporting Operating Plan in accordance with EOP-004-4 Attachment 1 that includes the protocol(s) for reporting to the Electric Reliability Organization and other organizations (e.g., the Regional Entity, company personnel, the Responsible Entity’s Reliability Coordinator, law enforcement, or governmental authority). [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Effective | 2019-04-01 |  | TOP, TO, RC, GOP, GO, DP, BA
EOP-004-4 | Event Reporting | R2. | Each Responsible Entity shall report events specified in EOP-004-4 Attachment 1 to the entities specified per their event reporting Operating Plan by the later of 24 hours of recognition of meeting an event type threshold for reporting or by the end of the Responsible Entity’s next business day (4 p.m. local time will be considered the end of the business day). [Violation Risk Factor: Medium] [Time Horizon: Operations Assessment] | MEDIUM | Effective | 2019-04-01 |  | TOP, TO, RC, GOP, GO, DP, BA
EOP-005-2 | System Restoration from Blackstart Resources | R1. | Each Transmission Operator shall have a restoration plan approved by its Reliability Coordinator. The restoration plan shall allow for restoring the Transmission Operator’s System following a Disturbance in which one or more areas of the Bulk Electric System (BES) shuts down and the use of Blackstart Resources is required to restore the shut down area to service, to a state whereby the choice of the next Load to be restored is not driven by the need to control frequency or voltage regardless of whether the Blackstart Resource is located within the Transmission Operator’s System. The restoration plan shall include: | HIGH | Retired | 2013-07-01 | 2019-03-31 | TOP
EOP-005-2 | System Restoration from Blackstart Resources | R1.1. | Strategies for system restoration that are coordinated with the Reliability Coordinator’s high level strategy for restoring the Interconnection. | HIGH | Retired | 2013-07-01 | 2019-03-31 | TOP
EOP-005-2 | System Restoration from Blackstart Resources | R1.2. | A description of how all Agreements or mutually agreed upon procedures or protocols for off-site power requirements of nuclear power plants, including priority of restoration, will be fulfilled during System restoration. | HIGH | Retired | 2013-07-01 | 2019-03-31 | TOP
EOP-005-2 | System Restoration from Blackstart Resources | R1.3. | Procedures for restoring interconnections with other Transmission Operators under the direction of the Reliability Coordinator. | HIGH | Retired | 2013-07-01 | 2019-03-31 | TOP
EOP-005-2 | System Restoration from Blackstart Resources | R1.4. | Identification of each Blackstart Resource and its characteristics including but not limited to the following: the name of the Blackstart Resource, location, megawatt and megavar capacity, and type of unit. | HIGH | Retired | 2013-07-01 | 2019-03-31 | TOP
EOP-005-2 | System Restoration from Blackstart Resources | R1.5. | Identification of Cranking Paths and initial switching requirements between each Blackstart Resource and the unit(s) to be started. | HIGH | Retired | 2013-07-01 | 2019-03-31 | TOP
EOP-005-2 | System Restoration from Blackstart Resources | R1.6. | Identification of acceptable operating voltage and frequency limits during restoration. | HIGH | Retired | 2013-07-01 | 2019-03-31 | TOP
EOP-005-2 | System Restoration from Blackstart Resources | R1.7. | Operating Processes to reestablish connections within the Transmission Operator’s System for areas that have been restored and are prepared for reconnection. | HIGH | Retired | 2013-07-01 | 2019-03-31 | TOP
EOP-005-2 | System Restoration from Blackstart Resources | R1.8. | Operating Processes to restore Loads required to restore the System, such as station service for substations, units to be restarted or stabilized, the Load needed to stabilize generation and frequency, and provide voltage control. | HIGH | Retired | 2013-07-01 | 2019-03-31 | TOP
EOP-005-2 | System Restoration from Blackstart Resources | R1.9. | Operating Processes for transferring authority back to the Balancing Authority in accordance with the Reliability Coordinator’s criteria. | HIGH | Retired | 2013-07-01 | 2019-03-31 | TOP
EOP-005-2 | System Restoration from Blackstart Resources | R10. | Each Transmission Operator shall include within its operations training program, annual System restoration training for its System Operators to assure the proper execution of its restoration plan. This training program shall include training on the following: | MEDIUM | Retired | 2013-07-01 | 2019-03-31 | TOP
EOP-005-2 | System Restoration from Blackstart Resources | R10.1. | System restoration plan including coordination with the Reliability Coordinator and Generator Operators included in the restoration plan. | MEDIUM | Retired | 2013-07-01 | 2019-03-31 | TOP
EOP-005-2 | System Restoration from Blackstart Resources | R10.2. | Restoration priorities. | MEDIUM | Retired | 2013-07-01 | 2019-03-31 | TOP
EOP-005-2 | System Restoration from Blackstart Resources | R10.3. | Building of cranking paths. | MEDIUM | Retired | 2013-07-01 | 2019-03-31 | TOP
EOP-005-2 | System Restoration from Blackstart Resources | R10.4. | Synchronizing (re-energized sections of the System). | MEDIUM | Retired | 2013-07-01 | 2019-03-31 | TOP
EOP-005-2 | System Restoration from Blackstart Resources | R11. | Each Transmission Operator, each applicable Transmission Owner, and each applicable Distribution Provider shall provide a minimum of two hours of System restoration training every two calendar years to their field switching personnel identified as performing unique tasks associated with the Transmission Operator’s restoration plan that are outside of their normal tasks. | MEDIUM | Retired | 2013-07-01 | 2019-03-31 | TOP, TO, DP
EOP-005-2 | System Restoration from Blackstart Resources | R12. | Each Transmission Operator shall participate in its Reliability Coordinator’s restoration drills, exercises, or simulations as requested by its Reliability Coordinator. | MEDIUM | Retired | 2013-07-01 | 2019-03-31 | TOP
EOP-005-2 | System Restoration from Blackstart Resources | R13. | Each Transmission Operator and each Generator Operator with a Blackstart Resource shall have written Blackstart Resource Agreements or mutually agreed upon procedures or protocols, specifying the terms and conditions of their arrangement. Such Agreements shall include references to the Blackstart Resource testing requirements. | MEDIUM | Retired | 2013-07-01 | 2019-03-31 | TOP, GOP
EOP-005-2 | System Restoration from Blackstart Resources | R14. | Each Generator Operator with a Blackstart Resource shall have documented procedures for starting each Blackstart Resource and energizing a bus. | MEDIUM | Retired | 2013-07-01 | 2019-03-31 | GOP
EOP-005-2 | System Restoration from Blackstart Resources | R15. | Each Generator Operator with a Blackstart Resource shall notify its Transmission Operator of any known changes to the capabilities of that Blackstart Resource affecting the ability to meet the Transmission Operator’s restoration plan within 24 hours following such change. | MEDIUM | Retired | 2013-07-01 | 2019-03-31 | GOP
EOP-005-2 | System Restoration from Blackstart Resources | R16. | Each Generator Operator with a Blackstart Resource shall perform Blackstart Resource tests, and maintain records of such testing, in accordance with the testing requirements set by the Transmission Operator to verify that the Blackstart Resource can perform as specified in the restoration plan. | MEDIUM | Retired | 2013-07-01 | 2019-03-31 | GOP
EOP-005-2 | System Restoration from Blackstart Resources | R16.1. | Testing records shall include at a minimum: name of the Blackstart Resource, unit tested, date of the test, duration of the test, time required to start the unit, an indication of any testing requirements not met under Requirement R9. | MEDIUM | Retired | 2013-07-01 | 2019-03-31 | GOP
EOP-005-2 | System Restoration from Blackstart Resources | R16.2. | Each Generator Operator shall provide the blackstart test results within 30 calendar days following a request from its Reliability Coordinator or Transmission Operator. | MEDIUM | Retired | 2013-07-01 | 2019-03-31 | GOP
EOP-005-2 | System Restoration from Blackstart Resources | R17. | Each Generator Operator with a Blackstart Resource shall provide a minimum of two hours of training every two calendar years to each of its operating personnel responsible for the startup of its Blackstart Resource generation units and energizing a bus. The training program shall include training on the following: | MEDIUM | Retired | 2013-07-01 | 2019-03-31 | GOP
EOP-005-2 | System Restoration from Blackstart Resources | R17.1. | System restoration plan including coordination with the Transmission Operator. | MEDIUM | Retired | 2013-07-01 | 2019-03-31 | GOP
EOP-005-2 | System Restoration from Blackstart Resources | R17.2. | The procedures documented in Requirement R14. | MEDIUM | Retired | 2013-07-01 | 2019-03-31 | GOP
EOP-005-2 | System Restoration from Blackstart Resources | R18. | Each Generator Operator shall participate in the Reliability Coordinator’s restoration drills, exercises, or simulations as requested by the Reliability Coordinator. | MEDIUM | Retired | 2013-07-01 | 2019-03-31 | GOP
EOP-005-2 | System Restoration from Blackstart Resources | R2. | Each Transmission Operator shall provide the entities identified in its approved restoration plan with a description of any changes to their roles and specific tasks prior to the implementation date of the plan. | MEDIUM | Retired | 2013-07-01 | 2019-03-31 | TOP
EOP-005-2 | System Restoration from Blackstart Resources | R3. | Each Transmission Operator shall review its restoration plan and submit it to its Reliability Coordinator annually on a mutually agreed predetermined schedule. | MEDIUM | Retired | 2013-07-01 | 2019-03-31 | TOP
EOP-005-2 | System Restoration from Blackstart Resources | R4. | Each Transmission Operator shall update its restoration plan within 90 calendar days after identifying any unplanned permanent System modifications, or prior to implementing a planned BES modification, that would change the implementation of its restoration plan. | MEDIUM | Retired | 2013-07-01 | 2019-03-31 | TOP
EOP-005-2 | System Restoration from Blackstart Resources | R4.1. | Each Transmission Operator shall submit its revised restoration plan to itsReliability Coordinator for approval within the same 90 calendar day period. | MEDIUM | Retired | 2013-07-01 | 2019-03-31 | TOP
EOP-005-2 | System Restoration from Blackstart Resources | R5. | Each Transmission Operator shall have a copy of its latest Reliability Coordinator approved restoration plan within its primary and backup control rooms so that it is available to all of its System Operators prior to its implementation date. | LOWER | Retired | 2013-07-01 | 2019-03-31 | TOP
EOP-005-2 | System Restoration from Blackstart Resources | R6. | Each Transmission Operator shall verify through analysis of actual events, steady state and dynamic simulations, or testing that its restoration plan accomplishes its intended function. This shall be completed every five years at a minimum. Such analysis, simulations or testing shall verify: | MEDIUM | Retired | 2013-07-01 | 2019-03-31 | TOP
EOP-005-2 | System Restoration from Blackstart Resources | R6. | Each Transmission Operator shall verify through analysis of actual events, steady state and dynamic simulations, or testing that its restoration plan accomplishes its intended function. This shall be completed every five years at a minimum. Such analysis, simulations or testing shall verify: | MEDIUM | Retired | 2013-07-01 | 2019-03-31 | TOP
EOP-005-2 | System Restoration from Blackstart Resources | R6.1. | The capability of Blackstart Resources to meet the Real and Reactive Power requirements of the Cranking Paths and the dynamic capability to supply initial Loads. | MEDIUM | Retired | 2013-07-01 | 2019-03-31 | TOP
EOP-005-2 | System Restoration from Blackstart Resources | R6.2. | The location and magnitude of Loads required to control voltages and frequency within acceptable operating limits. | MEDIUM | Retired | 2013-07-01 | 2019-03-31 | TOP
EOP-005-2 | System Restoration from Blackstart Resources | R6.3. | The capability of generating resources required to control voltages and frequency within acceptable operating limits. | MEDIUM | Retired | 2013-07-01 | 2019-03-31 | TOP
EOP-005-2 | System Restoration from Blackstart Resources | R7. | Following a Disturbance in which one or more areas of the BES shuts down and the use of Blackstart Resources is required to restore the shut down area to service, each affected Transmission Operator shall implement its restoration plan. If the restoration plan cannot be executed as expected the Transmission Operator shall utilize its restoration strategies to facilitate restoration. | MEDIUM | Retired | 2013-07-01 | 2019-03-31 | TOP
EOP-005-2 | System Restoration from Blackstart Resources | R8. | Following a Disturbance in which one or more areas of the BES shuts down and the use of Blackstart Resources is required to restore the shut down area to service, the Transmission Operator shall resynchronize area(s) with neighboring Transmission Operator area(s) only with the authorization of the Reliability Coordinator or in accordance with the established procedures of the Reliability Coordinator. | MEDIUM | Retired | 2013-07-01 | 2019-03-31 | TOP
EOP-005-2 | System Restoration from Blackstart Resources | R9. | Each Transmission Operator shall have Blackstart Resource testing requirements to verify that each Blackstart Resource is capable of meeting the requirements of its restoration plan. These Blackstart Resource testing requirements shall include: | MEDIUM | Retired | 2013-07-01 | 2019-03-31 | TOP
EOP-005-2 | System Restoration from Blackstart Resources | R9.1. | The frequency of testing such that each Blackstart Resource is tested at least once every three calendar years. | MEDIUM | Retired | 2013-07-01 | 2019-03-31 | TOP
EOP-005-2 | System Restoration from Blackstart Resources | R9.2. | A list of required tests including: | MEDIUM | Retired | 2013-07-01 | 2019-03-31 | TOP
EOP-005-2 | System Restoration from Blackstart Resources | R9.2.1. | The ability to start the unit when isolated with no support from the BES or when designed to remain energized without connection to the remainder of the System. | MEDIUM | Retired | 2013-07-01 | 2019-03-31 | TOP
EOP-005-2 | System Restoration from Blackstart Resources | R9.2.2. | The ability to energize a bus. If it is not possible to energize a bus during the test, the testing entity must affirm that the unit has the capability to energize a bus such as verifying that the breaker close coil relay can be energized with the voltage and frequency monitor controls disconnected from the synchronizing circuits. | MEDIUM | Retired | 2013-07-01 | 2019-03-31 | TOP
EOP-005-2 | System Restoration from Blackstart Resources | R9.3. | The minimum duration of each of the required tests. | MEDIUM | Retired | 2013-07-01 | 2019-03-31 | TOP
EOP-005-3 | System Restoration from Blackstart Resources | R1. | Each Transmission Operator shall develop and implement a restoration plan approved by its Reliability Coordinator. The restoration plan shall be implemented to restore the Transmission Operator’s System following a Disturbance in which one or more areas of the Bulk Electric System (BES) shuts down and the use of Blackstart Resources is required to restore the shutdown area to a state whereby the choice of the next Load to be restored is not driven by the need to control frequency or voltage regardless of whether the Blackstart Resource is located within the Transmission Operator’s System. The restoration plan shall include: [Violation Risk Factor = High] [Time Horizon = Operations Planning, Real-time Operations] | HIGH | Effective | 2019-04-01 |  | TOP
EOP-005-3 | System Restoration from Blackstart Resources | R1.1. | Strategies for System restoration that are coordinated with its Reliability Coordinator’s high level strategy for restoring the Interconnection. | HIGH | Effective | 2019-04-01 |  | TOP
EOP-005-3 | System Restoration from Blackstart Resources | R1.2. | 1.2. A description of how all Agreements or mutually-agreed upon procedures or protocols for off-site power requirements of nuclear power plants, including priority of restoration, will be fulfilled during System restoration. | HIGH | Effective | 2019-04-01 |  | TOP
EOP-005-3 | System Restoration from Blackstart Resources | R1.3. | 1.3. Procedures for restoring interconnections with other Transmission Operators under the direction of its Reliability Coordinator. | HIGH | Effective | 2019-04-01 |  | TOP
EOP-005-3 | System Restoration from Blackstart Resources | R1.4. | 1.4. Identification of each Blackstart Resource and its characteristics including but not limited to the following: the name of the Blackstart Resource, location, megawatt and megavar capacity, and type of unit. | HIGH | Effective | 2019-04-01 |  | TOP
EOP-005-3 | System Restoration from Blackstart Resources | R1.5. | Identification of Cranking Paths and initial switching requirements between each Blackstart Resource and the unit(s) to be started. | HIGH | Effective | 2019-04-01 |  | TOP
EOP-005-3 | System Restoration from Blackstart Resources | R1.6. | 1.6. Identification of acceptable operating voltage and frequency limits during restoration. | HIGH | Effective | 2019-04-01 |  | TOP
EOP-005-3 | System Restoration from Blackstart Resources | R1.7. | 1.7. Operating Processes to reestablish connections within the Transmission Operator’s System for areas that have been restored and are prepared for reconnection. | HIGH | Effective | 2019-04-01 |  | TOP
EOP-005-3 | System Restoration from Blackstart Resources | R1.8. | 1.8. Operating Processes to restore Loads required to restore the System, such as station service for substations, units to be restarted or stabilized, the Load needed to stabilize generation and frequency, and provide voltage control. | HIGH | Effective | 2019-04-01 |  | TOP
EOP-005-3 | System Restoration from Blackstart Resources | R1.9. | 1.9. Operating Processes for transferring operations back to the Balancing Authority in accordance with its Reliability Coordinator’s criteria. | HIGH | Effective | 2019-04-01 |  | TOP
EOP-005-3 | System Restoration from Blackstart Resources | R10. | Each Transmission Operator shall participate in its Reliability Coordinator’s restoration drills, exercises, or simulations as requested by its Reliability Coordinator. [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | MEDIUM | Effective | 2019-04-01 |  | TOP
EOP-005-3 | System Restoration from Blackstart Resources | R11. | Each Transmission Operator and each Generator Operator with a Blackstart Resource shall have written Blackstart Resource Agreements or mutually agreed upon procedures or protocols, specifying the terms and conditions of their arrangement. Such Agreements shall include references to the Blackstart Resource testing requirements. [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | MEDIUM | Effective | 2019-04-01 |  | TOP, GOP
EOP-005-3 | System Restoration from Blackstart Resources | R12. | Each Generator Operator with a Blackstart Resource shall have documented procedures for starting each Blackstart Resource and energizing a bus. [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | MEDIUM | Effective | 2019-04-01 |  | GOP
EOP-005-3 | System Restoration from Blackstart Resources | R13. | Each Generator Operator with a Blackstart Resource shall notify its Transmission Operator of any known changes to the capabilities of that Blackstart Resource affecting the ability to meet the Transmission Operator’s restoration plan within 24 hours following such change. [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | MEDIUM | Effective | 2019-04-01 |  | GOP
EOP-005-3 | System Restoration from Blackstart Resources | R14. | Each Generator Operator with a Blackstart Resource shall perform Blackstart Resource tests, and maintain records of such testing, in accordance with the testing requirements set by the Transmission Operator to verify that the Blackstart Resource can perform as specified in the restoration plan. [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | MEDIUM | Effective | 2019-04-01 |  | GOP
EOP-005-3 | System Restoration from Blackstart Resources | R14.1. | Testing records shall include at a minimum: name of the Blackstart Resource, unit tested, date of the test, duration of the test, time required to start the unit, an indication of any testing requirements not met under Requirement R7. | MEDIUM | Effective | 2019-04-01 |  | GOP
EOP-005-3 | System Restoration from Blackstart Resources | R14.2. | Each Generator Operator shall provide the blackstart test results within 30 calendar days following a request from its Reliability Coordinator or Transmission Operator. | MEDIUM | Effective | 2019-04-01 |  | GOP
EOP-005-3 | System Restoration from Blackstart Resources | R15. | Each Generator Operator with a Blackstart Resource shall provide a minimum of two hours of training every two calendar years to each of its operating personnel responsible for the startup of its Blackstart Resource generation units and energizing a bus. The training program shall include training on the following: [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | MEDIUM | Effective | 2019-04-01 |  | GOP
EOP-005-3 | System Restoration from Blackstart Resources | R15.1. | System restoration plan including coordination with the Transmission Operator | MEDIUM | Effective | 2019-04-01 |  | GOP
EOP-005-3 | System Restoration from Blackstart Resources | R15.2. | The procedures documented in Requirement R12 | MEDIUM | Effective | 2019-04-01 |  | GOP
EOP-005-3 | System Restoration from Blackstart Resources | R16. | Each Generator Operator shall participate in its Reliability Coordinator’s restoration drills, exercises, or simulations as requested by its Reliability Coordinator. [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | MEDIUM | Effective | 2019-04-01 |  | GOP
EOP-005-3 | System Restoration from Blackstart Resources | R2. | Each Transmission Operator shall provide the entities identified in its approved restoration plan with a description of any changes to their roles and specific tasks prior to the effective date of the plan. [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | MEDIUM | Effective | 2019-04-01 |  | TOP
EOP-005-3 | System Restoration from Blackstart Resources | R3. | Each Transmission Operator shall review its restoration plan and submit it to its Reliability Coordinator annually on a mutually-agreed, predetermined schedule. [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | MEDIUM | Effective | 2019-04-01 |  | TOP
EOP-005-3 | System Restoration from Blackstart Resources | R4. | Each Transmission Operator shall submit its revised restoration plan to its Reliability Coordinator for approval, when the revision would change its ability to implement its restoration plan, as follows: [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | MEDIUM | Effective | 2019-04-01 |  | TOP
EOP-005-3 | System Restoration from Blackstart Resources | R4.1. | Within 90 calendar days after identifying any unplanned permanent BES modifications. | MEDIUM | Effective | 2019-04-01 |  | TOP
EOP-005-3 | System Restoration from Blackstart Resources | R4.2. | 4.2. Prior to implementing a planned permanent BES modification subject to its Reliability Coordinator approval requirements per EOP-006. | MEDIUM | Effective | 2019-04-01 |  | TOP
EOP-005-3 | System Restoration from Blackstart Resources | R5. | Each Transmission Operator shall have a copy of its latest Reliability Coordinator approved restoration plan within its primary and backup control rooms so that it is available to all of its System Operators prior to its effective date. [Violation Risk Factor = Lower] [Time Horizon = Operations Planning] | LOWER | Effective | 2019-04-01 |  | TOP
EOP-005-3 | System Restoration from Blackstart Resources | R6. | Each Transmission Operator shall verify through analysis of actual events, a combination of steady state and dynamic simulations, or testing that its restoration plan accomplishes its intended function. This shall be completed at least once every five years. Such analysis, simulations or testing shall verify: [Violation Risk Factor = Medium] [Time Horizon = Long-term Planning] | MEDIUM | Effective | 2019-04-01 |  | TOP
EOP-005-3 | System Restoration from Blackstart Resources | R6. | Each Transmission Operator shall verify through analysis of actual events, a combination of steady state and dynamic simulations, or testing that its restoration plan accomplishes its intended function. This shall be completed at least once every five years. Such analysis, simulations or testing shall verify: [Violation Risk Factor = Medium] [Time Horizon = Long-term Planning] | MEDIUM | Effective | 2019-04-01 |  | TOP
EOP-005-3 | System Restoration from Blackstart Resources | R6.1. | The capability of Blackstart Resources to meet the Real and Reactive Power requirements of the Cranking Paths and the dynamic capability to supply initial Loads. | MEDIUM | Effective | 2019-04-01 |  | TOP
EOP-005-3 | System Restoration from Blackstart Resources | R6.2. | The location and magnitude of Loads required to control voltages and frequency within acceptable operating limits. | MEDIUM | Effective | 2019-04-01 |  | TOP
EOP-005-3 | System Restoration from Blackstart Resources | R6.3. | The capability of generating resources required to control voltages and frequency within acceptable operating limits. | MEDIUM | Effective | 2019-04-01 |  | TOP
EOP-005-3 | System Restoration from Blackstart Resources | R7. | Each Transmission Operator shall have Blackstart Resource testing requirements to verify that each Blackstart Resource is capable of meeting the requirements of its restoration plan. These Blackstart Resource testing requirements shall include: [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | MEDIUM | Effective | 2019-04-01 |  | TOP
EOP-005-3 | System Restoration from Blackstart Resources | R7.1. | The frequency of testing such that each Blackstart Resource is tested at least once every three calendar years. | MEDIUM | Effective | 2019-04-01 |  | TOP
EOP-005-3 | System Restoration from Blackstart Resources | R7.2. | A list of required tests including: | MEDIUM | Effective | 2019-04-01 |  | TOP
EOP-005-3 | System Restoration from Blackstart Resources | R7.2.1. | The ability to start the unit when isolated with no support from the BES or when designed to remain energized without connection to the remainder of the System. | MEDIUM | Effective | 2019-04-01 |  | TOP
EOP-005-3 | System Restoration from Blackstart Resources | R7.2.2. | The ability to energize a bus. If it is not possible to energize a bus during the test, the testing entity must affirm that the unit has the capability to energize a bus such as verifying that the breaker close coil relay can be energized with the voltage and frequency monitor controls disconnected from the synchronizing circuits. | MEDIUM | Effective | 2019-04-01 |  | TOP
EOP-005-3 | System Restoration from Blackstart Resources | R7.3. | The minimum duration of each of the required tests. | MEDIUM | Effective | 2019-04-01 |  | TOP
EOP-005-3 | System Restoration from Blackstart Resources | R8. | Each Transmission Operator shall include within its operations training program, annual System restoration training for its System Operators. This training program shall include training on the following: [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | MEDIUM | Effective | 2019-04-01 |  | TOP
EOP-005-3 | System Restoration from Blackstart Resources | R8.1. | System restoration plan including coordination with its Reliability Coordinator and Generator Operators included in the restoration plan. | MEDIUM | Effective | 2019-04-01 |  | TOP
EOP-005-3 | System Restoration from Blackstart Resources | R8.2. | Restoration priorities. | MEDIUM | Effective | 2019-04-01 |  | TOP
EOP-005-3 | System Restoration from Blackstart Resources | R8.3. | Building of cranking paths. | MEDIUM | Effective | 2019-04-01 |  | TOP
EOP-005-3 | System Restoration from Blackstart Resources | R8.4. | Synchronizing (re-energized sections of the System). | MEDIUM | Effective | 2019-04-01 |  | TOP
EOP-005-3 | System Restoration from Blackstart Resources | R8.5. | Transition of Demand and resource balance within its area to the Balancing Authority | MEDIUM | Effective | 2019-04-01 |  | TOP
EOP-005-3 | System Restoration from Blackstart Resources | R9. | Each Transmission Operator, each applicable Transmission Owner, and each applicable Distribution Provider shall provide a minimum of two hours of System restoration training every two calendar years to their field switching personnel identified as performing unique tasks associated with the Transmission Operator’s restoration plan that are outside of their normal tasks. [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | MEDIUM | Effective | 2019-04-01 |  | TOP, TO, DP
EOP-006-2 | System Restoration Coordination | R1. | Each Reliability Coordinator shall have a Reliability Coordinator Area restoration plan. The scope of the Reliability Coordinator’s restoration plan starts when Blackstart Resources are utilized to re-energize a shut down area of the Bulk Electric System (BES), or separation has occurred between neighboring Reliability Coordinators, or an energized island has been formed on the BES within the Reliability Coordinator Area. The scope of the Reliability Coordinator’s restoration plan ends when all of its Transmission Operators are interconnected and it its Reliability Coordinator Area is connected to all of its neighboring Reliability Coordinator Areas. The restoration plan shall include: | HIGH | Retired | 2013-07-01 | 2019-03-31 | RC
EOP-006-2 | System Restoration Coordination | R1.1. | A description of the high level strategy to be employed during restoration events for restoring the Interconnection including minimum criteria for meeting the objectives of the Reliability Coordinator’s restoration plan. | No Individual VRF Assigned | Retired | 2013-07-01 | 2019-03-31 | RC
EOP-006-2 | System Restoration Coordination | R1.2. | Operating Processes for restoring the Interconnection. | No Individual VRF Assigned | Retired | 2013-07-01 | 2019-03-31 | RC
EOP-006-2 | System Restoration Coordination | R1.3. | Descriptions of the elements of coordination between individual Transmission Operator restoration plans. | No Individual VRF Assigned | Retired | 2013-07-01 | 2019-03-31 | RC
EOP-006-2 | System Restoration Coordination | R1.4. | Descriptions of the elements of coordination of restoration plans with neighboring Reliability Coordinators. | No Individual VRF Assigned | Retired | 2013-07-01 | 2019-03-31 | RC
EOP-006-2 | System Restoration Coordination | R1.5. | Criteria and conditions for reestablishing interconnections with other Transmission Operators within its Reliability Coordinator Area, with Transmission Operators in other Reliability Coordinator Areas, and with other Reliability Coordinators. | No Individual VRF Assigned | Retired | 2013-07-01 | 2019-03-31 | RC
EOP-006-2 | System Restoration Coordination | R1.6. | Reporting requirements for the entities within the Reliability Coordinator Area during a restoration event. | No Individual VRF Assigned | Retired | 2013-07-01 | 2019-03-31 | RC
EOP-006-2 | System Restoration Coordination | R1.7. | Criteria for sharing information regarding restoration with neighboring Reliability Coordinators and with Transmission Operators and Balancing Authorities within its Reliability Coordinator Area. | No Individual VRF Assigned | Retired | 2013-07-01 | 2019-03-31 | RC
EOP-006-2 | System Restoration Coordination | R1.8. | Identification of the Reliability Coordinator as the primary contact for disseminating information regarding restoration to neighboring Reliability Coordinators, and to Transmission Operators, and Balancing Authorities within its Reliability Coordinator Area. | No Individual VRF Assigned | Retired | 2013-07-01 | 2019-03-31 | RC
EOP-006-2 | System Restoration Coordination | R1.9. | Criteria for transferring operations and authority back to the Balancing Authority. | No Individual VRF Assigned | Retired | 2013-07-01 | 2019-03-31 | RC
EOP-006-2 | System Restoration Coordination | R10. | Each Reliability Coordinator shall conduct two System restoration drills, exercises, or simulations per calendar year, which shall include the Transmission Operators and Generator Operators as dictated by the particular scope of the drill, exercise, or simulation that is being conducted. | MEDIUM | Retired | 2013-07-01 | 2019-03-31 | RC
EOP-006-2 | System Restoration Coordination | R10.1. | Each Reliability Coordinator shall request each Transmission Operator identified in its restoration plan and each Generator Operator identified in the Transmission Operators’ restoration plans to participate in a drill, exercise, or simulation at least every two calendar years. | No Individual VRF Assigned | Retired | 2013-07-01 | 2019-03-31 | RC
EOP-006-2 | System Restoration Coordination | R2. | The Reliability Coordinator shall distribute its most recent Reliability Coordinator Area restoration plan to each of its Transmission Operators and neighboring Reliability Coordinators within 30 calendar days of creation or revision. | LOWER | Retired | 2013-07-01 | 2019-03-31 | RC
EOP-006-2 | System Restoration Coordination | R3. | Each Reliability Coordinator shall review its restoration plan within 13 calendar months of the last review. | MEDIUM | Retired | 2013-07-01 | 2019-03-31 | RC
EOP-006-2 | System Restoration Coordination | R4. | Each Reliability Coordinator shall review their neighboring Reliability Coordinator’s restoration plans. | MEDIUM | Retired | 2013-07-01 | 2019-03-31 | RC
EOP-006-2 | System Restoration Coordination | R4.1. | If the Reliability Coordinator finds conflicts between its restoration plans and any of its neighbors, the conflicts shall be resolved in 30 calendar days. | No Individual VRF Assigned | Retired | 2013-07-01 | 2019-03-31 | RC
EOP-006-2 | System Restoration Coordination | R5. | Each Reliability Coordinator shall review the restoration plans required by EOP-005 of the Transmission Operators within its Reliability Coordinator Area. | MEDIUM | Retired | 2013-07-01 | 2019-03-31 | RC
EOP-006-2 | System Restoration Coordination | R5.1. | The Reliability Coordinator shall determine whether the Transmission Operator’s restoration plan is coordinated and compatible with the Reliability Coordinator’s restoration plan and other Transmission Operators’ restoration plans within its Reliability Coordinator Area. The Reliability Coordinator shall approve or disapprove, with stated reasons, the Transmission Operator’s submitted restoration plan within 30 calendar days following the receipt of the restoration plan from the Transmission Operator. | No Individual VRF Assigned | Retired | 2013-07-01 | 2019-03-31 | RC
EOP-006-2 | System Restoration Coordination | R6. | Each Reliability Coordinator shall have a copy of its latest restoration plan and copies of the latest approved restoration plan of each Transmission Operator in its Reliability Coordinator Area within its primary and backup control rooms so that it is available to all of its System Operators prior to the implementation date. | LOWER | Retired | 2013-07-01 | 2019-03-31 | RC
EOP-006-2 | System Restoration Coordination | R7. | Each Reliability Coordinator shall work with its affected Generator Operators, and Transmission Operators as well as neighboring Reliability Coordinators to monitor restoration progress, coordinate restoration, and take actions to restore the BES frequency within acceptable operating limits. If the restoration plan cannot be completed as expected the Reliability Coordinator shall utilize its restoration plan strategies to facilitate System restoration. | HIGH | Retired | 2013-07-01 | 2019-03-31 | RC
EOP-006-2 | System Restoration Coordination | R8. | The Reliability Coordinator shall coordinate or authorize resynchronizing islanded areas that bridge boundaries between Transmission Operators or Reliability Coordinators. If the resynchronization cannot be completed as expected the Reliability Coordinator shall utilize its restoration plan strategies to facilitate resynchronization. | HIGH | Retired | 2013-07-01 | 2019-03-31 | RC
EOP-006-2 | System Restoration Coordination | R9. | Each Reliability Coordinator shall include within its operations training program, annual System restoration training for its System Operators to assure the proper execution of its restoration plan. This training program shall address the following: | MEDIUM | Retired | 2013-07-01 | 2019-03-31 | RC
EOP-006-2 | System Restoration Coordination | R9.1. | The coordination role of the Reliability Coordinator. | No Individual VRF Assigned | Retired | 2013-07-01 | 2019-03-31 | RC
EOP-006-2 | System Restoration Coordination | R9.2. | Reestablishing the Interconnection. | No Individual VRF Assigned | Retired | 2013-07-01 | 2019-03-31 | RC
EOP-006-3 | System Restoration Coordination | R1. | Each Reliability Coordinator shall develop and implement a Reliability Coordinator Area restoration plan. The scope of the Reliability Coordinator’s restoration plan starts when Blackstart Resources are utilized to re-energize a shutdown area of the Bulk Electric System (BES), or separation has occurred between neighboring Reliability Coordinators, or an energized island has been formed on the BES within the Reliability Coordinator Area. The scope of the Reliability Coordinator’s restoration plan ends when all of its Transmission Operators are interconnected and its Reliability Coordinator Area is connected to all of its neighboring Reliability Coordinator Areas. The restoration plan shall include: [Violation Risk Factor = High] [Time Horizon = Operations Planning, Real-time Operations] | HIGH | Effective | 2019-04-01 |  | RC
EOP-006-3 | System Restoration Coordination | R1.1. | A description of the high-level strategy to be employed during restoration events for restoring the Interconnection, including minimum criteria for meeting the objectives of the Reliability Coordinator’s restoration plan. | No Individual VRF Assigned | Effective | 2019-04-01 |  | RC
EOP-006-3 | System Restoration Coordination | R1.2. | Criteria and conditions for re-establishing interconnections with other Transmission Operators within its Reliability Coordinator Area, with Transmission Operators in other Reliability Coordinator Areas, and with other Reliability Coordinators. | No Individual VRF Assigned | Effective | 2019-04-01 |  | RC
EOP-006-3 | System Restoration Coordination | R1.3. | Reporting requirements for the entities within the Reliability Coordinator Area during a restoration event. | No Individual VRF Assigned | Effective | 2019-04-01 |  | RC
EOP-006-3 | System Restoration Coordination | R1.4. | Criteria for sharing information regarding restoration with neighboring Reliability Coordinators and with Transmission Operators and Balancing Authorities within its Reliability Coordinator Area. | No Individual VRF Assigned | Effective | 2019-04-01 |  | RC
EOP-006-3 | System Restoration Coordination | R1.5. | Identification of the Reliability Coordinator as the primary contact for disseminating information regarding restoration to neighboring Reliability Coordinators, and to Transmission Operators, and Balancing Authorities within its Reliability Coordinator Area. | No Individual VRF Assigned | Effective | 2019-04-01 |  | RC
EOP-006-3 | System Restoration Coordination | R1.6. | Criteria for transferring operations and authority back to the Balancing Authority. | No Individual VRF Assigned | Effective | 2019-04-01 |  | RC
EOP-006-3 | System Restoration Coordination | R2. | The Reliability Coordinator shall distribute its most recent Reliability Coordinator Area restoration plan to each of its Transmission Operators and neighboring Reliability Coordinators within 30 calendar days of creation or revision. [Violation Risk Factor = Lower] [Time Horizon = Operations Planning] | LOWER | Effective | 2019-04-01 |  | RC
EOP-006-3 | System Restoration Coordination | R3. | Each Reliability Coordinator shall review its restoration plan within 13 calendar months of the last review. [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | MEDIUM | Effective | 2019-04-01 |  | RC
EOP-006-3 | System Restoration Coordination | R4. | Each Reliability Coordinator shall review its neighboring Reliability Coordinator’s restoration plans and provide written notification of any conflicts discovered during that review within 60 calendar days of receipt. [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | MEDIUM | Effective | 2019-04-01 |  | RC
EOP-006-3 | System Restoration Coordination | R4.1. | If a Reliability Coordinator finds conflicts between its restoration plans and any of its neighbors, the conflicts shall be resolved within 30 calendar days of receipt of written notification. | No Individual VRF Assigned | Effective | 2019-04-01 |  | RC
EOP-006-3 | System Restoration Coordination | R5. | Each Reliability Coordinator shall review the restoration plans required by EOP-005 of the Transmission Operators within its Reliability Coordinator Area. [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | MEDIUM | Effective | 2019-04-01 |  | RC
EOP-006-3 | System Restoration Coordination | R5.1. | The Reliability Coordinator shall determine whether the Transmission Operator’s restoration plan is coordinated and compatible with the Reliability Coordinator’s restoration plan and other Transmission Operators’ restoration plans within its Reliability Coordinator Area. The Reliability Coordinator shall provide notification to the Transmission Operator of approval or disapproval, with stated reasons, of the Transmission Operator’s submitted restoration plan within 30 calendar days following the receipt of the restoration plan from the Transmission Operator. | No Individual VRF Assigned | Effective | 2019-04-01 |  | RC
EOP-006-3 | System Restoration Coordination | R6. | Each Reliability Coordinator shall have a copy of its latest restoration plan and copies of the latest approved restoration plan of each Transmission Operator in its Reliability Coordinator Area within its primary and backup control rooms so that it is available to all of its System Operators prior to the effective date. [Violation Risk Factor = Lower] [Time Horizon = Operations Planning] | LOWER | Effective | 2019-04-01 |  | RC
EOP-006-3 | System Restoration Coordination | R7. | Each Reliability Coordinator shall include within its operations training program, annual System restoration training for its System Operators. This training program shall address the following: [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | MEDIUM | Effective | 2019-04-01 |  | RC
EOP-006-3 | System Restoration Coordination | R7.1. | The coordination role of the Reliability Coordinator; and | No Individual VRF Assigned | Effective | 2019-04-01 |  | RC
EOP-006-3 | System Restoration Coordination | R7.2. | Re-establishing the Interconnection. | No Individual VRF Assigned | Effective | 2019-04-01 |  | RC
EOP-006-3 | System Restoration Coordination | R8. | Each Reliability Coordinator shall conduct two System restoration drills, exercises, or simulations per calendar year, which shall include the Transmission Operators and Generator Operators as dictated by the particular scope of the drill, exercise, or simulation that is being conducted. [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | MEDIUM | Effective | 2019-04-01 |  | RC
EOP-006-3 | System Restoration Coordination | R8.1. | Each Reliability Coordinator shall request each Transmission Operator identified in its restoration plan and each Generator Operator identified in the Transmission Operators’ restoration plans to participate in a drill, exercise, or simulation at least once every two calendar years. | No Individual VRF Assigned | Effective | 2019-04-01 |  | RC
EOP-008-1 | Loss of Control Center Functionality | R1. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a current Operating Plan describing the manner in which it continues to meet its functional obligations with regard to the reliable operations of the BES in the event that its primary control center functionality is lost. This Operating Plan for backup functionality shall include the following, at a minimum: | MEDIUM | Retired | 2013-10-01 | 2019-03-31 | TOP, RC, BA
EOP-008-1 | Loss of Control Center Functionality | R1. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a current Operating Plan describing the manner in which it continues to meet its functional obligations with regard to the reliable operations of the BES in the event that its primary control center functionality is lost. This Operating Plan for backup functionality shall include the following, at a minimum: | MEDIUM | Retired | 2013-10-01 | 2019-03-31 | TOP, RC, BA
EOP-008-1 | Loss of Control Center Functionality | R1.1. | The location and method of implementation for providing backup functionality for the time it takes to restore the primary control center functionality. | MEDIUM | Retired | 2013-10-01 | 2019-03-31 | TOP, RC, BA
EOP-008-1 | Loss of Control Center Functionality | R1.2. | A summary description of the elements required to support the backup functionality. These elements shall include, at a minimum: | MEDIUM | Retired | 2013-10-01 | 2019-03-31 | TOP, RC, BA
EOP-008-1 | Loss of Control Center Functionality | R1.2.1. | Tools and applications to ensure that System Operators have situational awareness of the BES. | MEDIUM | Retired | 2013-10-01 | 2019-03-31 | TOP, RC, BA
EOP-008-1 | Loss of Control Center Functionality | R1.2.2. | Data communications. | MEDIUM | Retired | 2013-10-01 | 2019-03-31 | TOP, RC, BA
EOP-008-1 | Loss of Control Center Functionality | R1.2.3. | Voice communications. | MEDIUM | Retired | 2013-10-01 | 2019-03-31 | TOP, RC, BA
EOP-008-1 | Loss of Control Center Functionality | R1.2.4. | Power source(s). | MEDIUM | Retired | 2013-10-01 | 2019-03-31 | TOP, RC, BA
EOP-008-1 | Loss of Control Center Functionality | R1.2.5. | Physical and cyber security. | MEDIUM | Retired | 2013-10-01 | 2019-03-31 | TOP, RC, BA
EOP-008-1 | Loss of Control Center Functionality | R1.3. | An Operating Process for keeping the backup functionality consistent with the primary control center. | MEDIUM | Retired | 2013-10-01 | 2019-03-31 | TOP, RC, BA
EOP-008-1 | Loss of Control Center Functionality | R1.4. | Operating Procedures, including decision authority, for use in determining when to implement the Operating Plan for backup functionality. | MEDIUM | Retired | 2013-10-01 | 2019-03-31 | TOP, RC, BA
EOP-008-1 | Loss of Control Center Functionality | R1.5. | A transition period between the loss of primary control center functionality and the time to fully implement the backup functionality that is less than or equal to two hours. | MEDIUM | Retired | 2013-10-01 | 2019-03-31 | TOP, RC, BA
EOP-008-1 | Loss of Control Center Functionality | R1.6. | An Operating Process describing the actions to be taken during the transition period between the loss of primary control center functionality and the time to fully implement backup functionality elements identified in Requirement R1, Part 1.2. The Operating Process shall include at a minimum: | MEDIUM | Retired | 2013-10-01 | 2019-03-31 | TOP, RC, BA
EOP-008-1 | Loss of Control Center Functionality | R1.6.1. | A list of all entities to notify when there is a change in operating locations. | MEDIUM | Retired | 2013-10-01 | 2019-03-31 | TOP, RC, BA
EOP-008-1 | Loss of Control Center Functionality | R1.6.2. | Actions to manage the risk to the BES during the transition from primary to backup functionality as well as during outages of the primary or backup functionality. | MEDIUM | Retired | 2013-10-01 | 2019-03-31 | TOP, RC, BA
EOP-008-1 | Loss of Control Center Functionality | R1.6.3. | Identification of the roles for personnel involved during the initiation and implementation of the Operating Plan for backup functionality. | MEDIUM | Retired | 2013-10-01 | 2019-03-31 | TOP, RC, BA
EOP-008-1 | Loss of Control Center Functionality | R2. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a copy of its current Operating Plan for backup functionality available at its primary control center and at the location providing backup functionality. | LOWER | Retired | 2013-10-01 | 2019-03-31 | TOP, RC, BA
EOP-008-1 | Loss of Control Center Functionality | R3. | Each Reliability Coordinator shall have a backup control center facility (provided through its own dedicated backup facility or at another entity’s control center staffed with certified Reliability Coordinator operators when control has been transferred to the backup facility) that provides the functionality required for maintaining compliance with all Reliability Standards that depend on primary control center functionality. To avoid requiring a tertiary facility, a backup facility is not required during: • Planned outages of the primary or backup facilities of two weeks or less • Unplanned outages of the primary or backup facilities | HIGH | Retired | 2013-10-01 | 2019-03-31 | RC
EOP-008-1 | Loss of Control Center Functionality | R4. | Each Balancing Authority and Transmission Operator shall have backup functionality (provided either through a facility or contracted services staffed by applicable certified operators when control has been transferred to the backup functionality location) that includes monitoring, control, logging, and alarming sufficient for maintaining compliance with all Reliability Standards that depend on a Balancing Authority and Transmission Operator’s primary control center functionality respectively. To avoid requiring tertiary functionality, backup functionality is not required during: • Planned outages of the primary or backup functionality of two weeks or less • Unplanned outages of the primary or backup functionality | HIGH | Retired | 2013-10-01 | 2019-03-31 | TOP, BA
EOP-008-1 | Loss of Control Center Functionality | R5. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator, shall annually review and approve its Operating Plan for backup functionality. | MEDIUM | Retired | 2013-10-01 | 2019-03-31 | TOP, RC, BA
EOP-008-1 | Loss of Control Center Functionality | R5.1. | An update and approval of the Operating Plan for backup functionality shall take place within sixty calendar days of any changes to any part of the Operating Plan described in Requirement R1. | MEDIUM | Retired | 2013-10-01 | 2019-03-31 | TOP, RC, BA
EOP-008-1 | Loss of Control Center Functionality | R6. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have primary and backup functionality that do not depend on each other for the control center functionality required to maintain compliance with Reliability Standards. | MEDIUM | Retired | 2013-10-01 | 2019-03-31 | TOP, RC, BA
EOP-008-1 | Loss of Control Center Functionality | R7. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall conduct and document results of an annual test of its Operating Plan that demonstrates: | MEDIUM | Retired | 2013-10-01 | 2019-03-31 | TOP, RC, BA
EOP-008-1 | Loss of Control Center Functionality | R7.1. | The transition time between the simulated loss of primary control center functionality and the time to fully implement the backup functionality. | MEDIUM | Retired | 2013-10-01 | 2019-03-31 | TOP, RC, BA
EOP-008-1 | Loss of Control Center Functionality | R7.2. | The backup functionality for a minimum of two continuous hours. | MEDIUM | Retired | 2013-10-01 | 2019-03-31 | TOP, RC, BA
EOP-008-1 | Loss of Control Center Functionality | R8. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator that has experienced a loss of its primary or backup functionality and that anticipates that the loss of primary or backup functionality will last for more than six calendar months shall provide a plan to its Regional Entity within six calendar months of the date when the functionality is lost, showing how it will re-establish primary or backup functionality. | MEDIUM | Retired | 2013-10-01 | 2019-03-31 | TOP, RC, BA
EOP-008-2 | Loss of Control Center Functionality | R1. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a current Operating Plan describing the manner in which it continues to meet its functional obligations with regard to the reliable operations of the BES in the event that its primary control center functionality is lost. This Operating Plan for backup functionality shall include: [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | MEDIUM | Effective | 2019-04-01 |  | TOP, RC, BA
EOP-008-2 | Loss of Control Center Functionality | R1. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a current Operating Plan describing the manner in which it continues to meet its functional obligations with regard to the reliable operations of the BES in the event that its primary control center functionality is lost. This Operating Plan for backup functionality shall include: [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | MEDIUM | Effective | 2019-04-01 |  | TOP, RC, BA
EOP-008-2 | Loss of Control Center Functionality | R1.1. | The location and method of implementation for providing backup functionality. | No Individual VRF Assigned | Effective | 2019-04-01 |  | TOP, RC, BA
EOP-008-2 | Loss of Control Center Functionality | R1.2. | A summary description of the elements required to support the backup functionality. These elements shall include: | No Individual VRF Assigned | Effective | 2019-04-01 |  | TOP, RC, BA
EOP-008-2 | Loss of Control Center Functionality | R1.2.1. | Tools and applications to ensure that System Operators have situational awareness of the BES. | No Individual VRF Assigned | Effective | 2019-04-01 |  | TOP, RC, BA
EOP-008-2 | Loss of Control Center Functionality | R1.2.2. | Data exchange capabilities. | No Individual VRF Assigned | Effective | 2019-04-01 |  | TOP, RC, BA
EOP-008-2 | Loss of Control Center Functionality | R1.2.3. | Interpersonal Communications. | No Individual VRF Assigned | Effective | 2019-04-01 |  | TOP, RC, BA
EOP-008-2 | Loss of Control Center Functionality | R1.2.4. | Power source(s). | No Individual VRF Assigned | Effective | 2019-04-01 |  | TOP, RC, BA
EOP-008-2 | Loss of Control Center Functionality | R1.2.5. | Physical and cyber security. | No Individual VRF Assigned | Effective | 2019-04-01 |  | TOP, RC, BA
EOP-008-2 | Loss of Control Center Functionality | R1.3. | An Operating Process for keeping the backup functionality consistent with the primary control center. | No Individual VRF Assigned | Effective | 2019-04-01 |  | TOP, RC, BA
EOP-008-2 | Loss of Control Center Functionality | R1.4. | Operating Procedures, including decision authority, for use in determining when to implement the Operating Plan for backup functionality. | No Individual VRF Assigned | Effective | 2019-04-01 |  | TOP, RC, BA
EOP-008-2 | Loss of Control Center Functionality | R1.5. | A transition period between the loss of primary control center functionality and the time to fully implement the backup functionality that is less than or equal to two hours. | No Individual VRF Assigned | Effective | 2019-04-01 |  | TOP, RC, BA
EOP-008-2 | Loss of Control Center Functionality | R1.6. | An Operating Process describing the actions to be taken during the transition period between the loss of primary control center functionality and the time to fully implement backup functionality elements identified in Requirement R1, Part 1.2. The Operating Process shall include: | No Individual VRF Assigned | Effective | 2019-04-01 |  | TOP, RC, BA
EOP-008-2 | Loss of Control Center Functionality | R1.6.1. | A list of all entities to notify when there is a change in operating locations. | No Individual VRF Assigned | Effective | 2019-04-01 |  | TOP, RC, BA
EOP-008-2 | Loss of Control Center Functionality | R1.6.2. | Actions to manage the risk to the BES during the transition from primary to backup functionality, as well as during outages of the primary or backup functionality. | No Individual VRF Assigned | Effective | 2019-04-01 |  | TOP, RC, BA
EOP-008-2 | Loss of Control Center Functionality | R1.6.3. | Identification of the roles for personnel involved during the initiation and implementation of the Operating Plan for backup functionality. | No Individual VRF Assigned | Effective | 2019-04-01 |  | TOP, RC, BA
EOP-008-2 | Loss of Control Center Functionality | R2. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a copy of its current Operating Plan for backup functionality available at its primary control center and at the location providing backup functionality. [Violation Risk Factor = Lower] [Time Horizon = Operations Planning] | LOWER | Effective | 2019-04-01 |  | TOP, RC, BA
EOP-008-2 | Loss of Control Center Functionality | R3. | Each Reliability Coordinator shall have a backup control center facility (provided through its own dedicated backup facility or at another entity’s control center staffed with certified Reliability Coordinator operators when control has been transferred to the backup facility) that provides the functionality required for maintaining compliance with all Reliability Standards are applicable to the primary control center functionality. To avoid requiring a tertiary facility, a backup facility is not required during: [Violation Risk Factor = High] [Time Horizon = Operations Planning] • Planned outages of the primary or backup facilities of two weeks or less • Unplanned outages of the primary or backup facilities | HIGH | Effective | 2019-04-01 |  | TOP, RC, BA
EOP-008-2 | Loss of Control Center Functionality | R4. | Each Balancing Authority and Transmission Operator shall have backup functionality (provided either through a facility or contracted services staffed by applicable certified operators when control has been transferred to the backup functionality location) that includes monitoring, control, logging, and alarming sufficient for maintaining compliance with all Reliability Standards that are applicable to a Balancing Authority’s and Transmission Operator’s primary control center functionality. To avoid requiring tertiary functionality, backup functionality is not required during: [Violation Risk Factor = High] [Time Horizon = Operations Planning] • Planned outages of the primary or backup functionality of two weeks or less • Unplanned outages of the primary or backup functionality | HIGH | Effective | 2019-04-01 |  | TOP, BA
EOP-008-2 | Loss of Control Center Functionality | R5. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator, shall annually review and approve its Operating Plan for backup functionality. [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | MEDIUM | Effective | 2019-04-01 |  | TOP, RC, BA
EOP-008-2 | Loss of Control Center Functionality | R5.1. | An update and approval of the Operating Plan for backup functionality shall take place within sixty calendar days of any changes to any part of the Operating Plan described in Requirement R1. | No Individual VRF Assigned | Effective | 2019-04-01 |  | TOP, RC, BA
EOP-008-2 | Loss of Control Center Functionality | R6. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have primary and backup functionality that do not depend on each other for the control center functionality required to maintain compliance with Reliability Standards. [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | MEDIUM | Effective | 2019-04-01 |  | TOP, RC, BA
EOP-008-2 | Loss of Control Center Functionality | R7. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall conduct and document results of an annual test of its Operating Plan that demonstrates: [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | MEDIUM | Effective | 2019-04-01 |  | TOP, RC, BA
EOP-008-2 | Loss of Control Center Functionality | R7.1. | The transition time between the simulated loss of primary control center functionality and the time to fully implement the backup functionality. | No Individual VRF Assigned | Effective | 2019-04-01 |  | TOP, RC, BA
EOP-008-2 | Loss of Control Center Functionality | R7.2. | The backup functionality for a minimum of two continuous hours. | No Individual VRF Assigned | Effective | 2019-04-01 |  | TOP, RC, BA
EOP-008-2 | Loss of Control Center Functionality | R8. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator that has experienced a loss of its primary or backup functionality and that anticipates that the loss of primary or backup functionality will last for more than six calendar months shall provide a plan to its Regional Entity within six calendar months of the date when the functionality is lost, showing how it will re-establish primary or backup functionality. [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | MEDIUM | Effective | 2019-04-01 |  | TOP, RC, BA
EOP-010-1 | Geomagnetic Disturbance Operations | R1. | Each Reliability Coordinator shall develop, maintain, and implement a GMD Operating Plan that coordinates GMD Operating Procedures or Operating Processes within its Reliability Coordinator Area. At a minimum, the GMD Operating Plan shall include: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning, Operations Planning, Same-day Operations, Real-time Operations] | MEDIUM | Effective | 2015-04-01 |  | RC
EOP-010-1 | Geomagnetic Disturbance Operations | R1.1. | A description of activities designed to mitigate the effects of GMD events on the reliable operation of the interconnected transmission system within the Reliability Coordinator Area. | MEDIUM | Effective | 2015-04-01 |  | RC
EOP-010-1 | Geomagnetic Disturbance Operations | R1.2. | A process for the Reliability Coordinator to review the GMD Operating Procedures or Operating Processes of Transmission Operators within its Reliability Coordinator Area. | MEDIUM | Effective | 2015-04-01 |  | RC
EOP-010-1 | Geomagnetic Disturbance Operations | R2. | Each Reliability Coordinator shall disseminate forecasted and current space weather information to functional entities identified as recipients in the Reliability Coordinator's GMD Operating Plan. [Violation Risk Factor: Medium] [Time Horizon: Same-day Operations, Real-time Operations] | MEDIUM | Effective | 2017-04-01 |  | RC
EOP-010-1 | Geomagnetic Disturbance Operations | R3. | Each Transmission Operator shall develop, maintain, and implement a GMD Operating Procedure or Operating Process to mitigate the effects of GMD events on the reliable operation of its respective system. At a minimum, the Operating Procedure or Operating Process shall include: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning, Operations Planning, Same-day operations, Real-Time Operations] | MEDIUM | Effective | 2015-04-01 |  | TOP
EOP-010-1 | Geomagnetic Disturbance Operations | R3.1. | Steps or tasks to receive space weather information. | MEDIUM | Effective | 2015-04-01 |  | TOP
EOP-010-1 | Geomagnetic Disturbance Operations | R3.2. | System Operator actions to be initiated based on predetermined conditions. | MEDIUM | Effective | 2015-04-01 |  | TOP
EOP-010-1 | Geomagnetic Disturbance Operations | R3.3. | The conditions for terminating the Operating Procedure or Operating Process. | MEDIUM | Effective | 2015-04-01 |  | TOP
EOP-011-1 | Emergency Operations | R1. | Each Transmission Operator shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate operating Emergencies in its Transmission Operator Area. The Operating Plan(s) shall include the following, as applicable: [Violation Risk Factor: High] [Time Horizon: Real-Time Operations, Operations Planning, Long-term Planning] | HIGH | Retired | 2017-04-01 | 2023-09-30 | TOP
EOP-011-1 | Emergency Operations | R1. | Each Transmission Operator shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate operating Emergencies in its Transmission Operator Area. The Operating Plan(s) shall include the following, as applicable: [Violation Risk Factor: High] [Time Horizon: Real-Time Operations, Operations Planning, Long-term Planning] | HIGH | Retired | 2017-04-01 | 2023-09-30 | TOP
EOP-011-1 | Emergency Operations | R1. | Each Transmission Operator shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate operating Emergencies in its Transmission Operator Area. The Operating Plan(s) shall include the following, as applicable: [Violation Risk Factor: High] [Time Horizon: Real-Time Operations, Operations Planning, Long-term Planning] | HIGH | Retired | 2017-04-01 | 2023-09-30 | TOP
EOP-011-1 | Emergency Operations | R1.1. | Roles and responsibilities for activating the Operating Plan(s); | HIGH | Retired | 2017-04-01 | 2023-09-30 | TOP
EOP-011-1 | Emergency Operations | R1.2. | Processes to prepare for and mitigate Emergencies including: | HIGH | Retired | 2017-04-01 | 2023-09-30 | TOP
EOP-011-1 | Emergency Operations | R1.2. | Processes to prepare for and mitigate Emergencies including: | HIGH | Retired | 2017-04-01 | 2023-09-30 | TOP
EOP-011-1 | Emergency Operations | R1.2. | Processes to prepare for and mitigate Emergencies including: | HIGH | Retired | 2017-04-01 | 2023-09-30 | TOP
EOP-011-1 | Emergency Operations | R1.2.1. | Notification to its Reliability Coordinator, to include current and projected conditions, when experiencing an operating Emergency; | HIGH | Retired | 2017-04-01 | 2023-09-30 | TOP
EOP-011-1 | Emergency Operations | R1.2.1. | Notification to its Reliability Coordinator, to include current and projected conditions, when experiencing an operating Emergency; | HIGH | Retired | 2017-04-01 | 2023-09-30 | TOP
EOP-011-1 | Emergency Operations | R1.2.2. | Cancellation or recall of Transmission and generation outages; | HIGH | Retired | 2017-04-01 | 2023-09-30 | TOP
EOP-011-1 | Emergency Operations | R1.2.2. | Cancellation or recall of Transmission and generation outages; | HIGH | Retired | 2017-04-01 | 2023-09-30 | TOP
EOP-011-1 | Emergency Operations | R1.2.3. | Transmission system reconfiguration; | HIGH | Retired | 2017-04-01 | 2023-09-30 | TOP
EOP-011-1 | Emergency Operations | R1.2.4. | Redispatch of generation request; | HIGH | Retired | 2017-04-01 | 2023-09-30 | TOP
EOP-011-1 | Emergency Operations | R1.2.5. | Provisions for operator-controlled manual Load shedding that minimizes the overlap with automatic Load shedding and are capable of being implemented in a timeframe adequate for mitigating the Emergency; and | HIGH | Retired | 2017-04-01 | 2023-09-30 | TOP
EOP-011-1 | Emergency Operations | R1.2.6. | Reliability impacts of extreme weather conditions. | HIGH | Retired | 2017-04-01 | 2023-09-30 | TOP
EOP-011-1 | Emergency Operations | R1.2.6. | Reliability impacts of extreme weather conditions. | HIGH | Retired | 2017-04-01 | 2023-09-30 | TOP
EOP-011-1 | Emergency Operations | R2. | Each Balancing Authority shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate Capacity Emergencies and Energy Emergencies within its Balancing Authority Area. The Operating Plan(s) shall include the following, as applicable: [Violation Risk Factor: High] [Time Horizon: Real-Time Operations, Operations Planning, Long-term Planning] | HIGH | Retired | 2017-04-01 | 2023-09-30 | BA
EOP-011-1 | Emergency Operations | R2. | Each Balancing Authority shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate Capacity Emergencies and Energy Emergencies within its Balancing Authority Area. The Operating Plan(s) shall include the following, as applicable: [Violation Risk Factor: High] [Time Horizon: Real-Time Operations, Operations Planning, Long-term Planning] | HIGH | Retired | 2017-04-01 | 2023-09-30 | BA
EOP-011-1 | Emergency Operations | R2.1. | Roles and responsibilities for activating the Operating Plan(s); | HIGH | Retired | 2017-04-01 | 2023-09-30 | BA
EOP-011-1 | Emergency Operations | R2.1. | Roles and responsibilities for activating the Operating Plan(s); | HIGH | Retired | 2017-04-01 | 2023-09-30 | BA
EOP-011-1 | Emergency Operations | R2.2. | Processes to prepare for and mitigate Emergencies including: | HIGH | Retired | 2017-04-01 | 2023-09-30 | BA
EOP-011-1 | Emergency Operations | R2.2. | Processes to prepare for and mitigate Emergencies including: | HIGH | Retired | 2017-04-01 | 2023-09-30 | BA
EOP-011-1 | Emergency Operations | R2.2.1. | Notification to its Reliability Coordinator, to include current and projected conditions when experiencing a Capacity Emergency or Energy Emergency; | HIGH | Retired | 2017-04-01 | 2023-09-30 | BA
EOP-011-1 | Emergency Operations | R2.2.1. | Notification to its Reliability Coordinator, to include current and projected conditions when experiencing a Capacity Emergency or Energy Emergency; | HIGH | Retired | 2017-04-01 | 2023-09-30 | BA
EOP-011-1 | Emergency Operations | R2.2.2. | Requesting an Energy Emergency Alert, per Attachment 1; | HIGH | Retired | 2017-04-01 | 2023-09-30 | BA
EOP-011-1 | Emergency Operations | R2.2.2. | Requesting an Energy Emergency Alert, per Attachment 1; | HIGH | Retired | 2017-04-01 | 2023-09-30 | BA
EOP-011-1 | Emergency Operations | R2.2.3. | Managing generating resources in its Balancing Authority Area to address: | HIGH | Retired | 2017-04-01 | 2023-09-30 | BA
EOP-011-1 | Emergency Operations | R2.2.3. | Managing generating resources in its Balancing Authority Area to address: | HIGH | Retired | 2017-04-01 | 2023-09-30 | BA
EOP-011-1 | Emergency Operations | R2.2.3.1. | capability and availability; | HIGH | Retired | 2017-04-01 | 2023-09-30 | BA
EOP-011-1 | Emergency Operations | R2.2.3.1. | capability and availability; | HIGH | Retired | 2017-04-01 | 2023-09-30 | BA
EOP-011-1 | Emergency Operations | R2.2.3.2. | fuel supply and inventory concerns; | HIGH | Retired | 2017-04-01 | 2023-09-30 | BA
EOP-011-1 | Emergency Operations | R2.2.3.2. | fuel supply and inventory concerns; | HIGH | Retired | 2017-04-01 | 2023-09-30 | BA
EOP-011-1 | Emergency Operations | R2.2.3.3. | fuel switching capabilities; and | HIGH | Retired | 2017-04-01 | 2023-09-30 | BA
EOP-011-1 | Emergency Operations | R2.2.3.3. | fuel switching capabilities; and | HIGH | Retired | 2017-04-01 | 2023-09-30 | BA
EOP-011-1 | Emergency Operations | R2.2.3.4. | environmental constraints. | HIGH | Retired | 2017-04-01 | 2023-09-30 | BA
EOP-011-1 | Emergency Operations | R2.2.3.4. | environmental constraints. | HIGH | Retired | 2017-04-01 | 2023-09-30 | BA
EOP-011-1 | Emergency Operations | R2.2.4. | Public appeals for voluntary Load reductions; | HIGH | Retired | 2017-04-01 | 2023-09-30 | BA
EOP-011-1 | Emergency Operations | R2.2.4. | Public appeals for voluntary Load reductions; | HIGH | Retired | 2017-04-01 | 2023-09-30 | BA
EOP-011-1 | Emergency Operations | R2.2.5. | Requests to government agencies to implement their programs to achieve necessary energy reductions; | HIGH | Retired | 2017-04-01 | 2023-09-30 | BA
EOP-011-1 | Emergency Operations | R2.2.5. | Requests to government agencies to implement their programs to achieve necessary energy reductions; | HIGH | Retired | 2017-04-01 | 2023-09-30 | BA
EOP-011-1 | Emergency Operations | R2.2.6. | Reduction of internal utility energy use; | HIGH | Retired | 2017-04-01 | 2023-09-30 | BA
EOP-011-1 | Emergency Operations | R2.2.6. | Reduction of internal utility energy use; | HIGH | Retired | 2017-04-01 | 2023-09-30 | BA
EOP-011-1 | Emergency Operations | R2.2.7. | Use of Interruptible Load, curtailable Load and demand response; | HIGH | Retired | 2017-04-01 | 2023-09-30 | BA
EOP-011-1 | Emergency Operations | R2.2.7. | Use of Interruptible Load, curtailable Load and demand response; | HIGH | Retired | 2017-04-01 | 2023-09-30 | BA
EOP-011-1 | Emergency Operations | R2.2.8. | Provisions for operator-controlled manual Load shedding that minimizes the overlap with automatic Load shedding and are capable of being implemented in a timeframe adequate for mitigating the Emergency; and | HIGH | Retired | 2017-04-01 | 2023-09-30 | BA
EOP-011-1 | Emergency Operations | R2.2.8. | Provisions for operator-controlled manual Load shedding that minimizes the overlap with automatic Load shedding and are capable of being implemented in a timeframe adequate for mitigating the Emergency; and | HIGH | Retired | 2017-04-01 | 2023-09-30 | BA
EOP-011-1 | Emergency Operations | R2.2.9. | Reliability impacts of extreme weather conditions. | HIGH | Retired | 2017-04-01 | 2023-09-30 | BA
EOP-011-1 | Emergency Operations | R2.2.9. | Reliability impacts of extreme weather conditions. | HIGH | Retired | 2017-04-01 | 2023-09-30 | BA
EOP-011-1 | Emergency Operations | R3. | The Reliability Coordinator shall review the Operating Plan(s) to mitigate operating Emergencies submitted by a Transmission Operator or a Balancing Authority regarding any reliability risks that are identified between Operating Plans. [ViolationRisk Factor: High] [Time Horizon: Operations Planning] | HIGH | Retired | 2017-04-01 | 2023-09-30 | RC
EOP-011-1 | Emergency Operations | R3.1. | Within 30 calendar days of receipt, the Reliability Coordinator shall: | HIGH | Retired | 2017-04-01 | 2023-09-30 | RC
EOP-011-1 | Emergency Operations | R3.1.1. | Review each submitted Operating Plan(s) on the basis of compatibility and inter-dependency with other Balancing Authorities’ and Transmission Operators’ Operating Plans; | HIGH | Retired | 2017-04-01 | 2023-09-30 | RC
EOP-011-1 | Emergency Operations | R3.1.2. | Review each submitted Operating Plan(s) for coordination to avoid risk to Wide Area reliability; and | HIGH | Retired | 2017-04-01 | 2023-09-30 | RC
EOP-011-1 | Emergency Operations | R3.1.3. | Notify each Balancing Authority and Transmission Operator of the results of its review, specifying any time frame for resubmittal of its Operating Plan(s) if revisions are identified. | HIGH | Retired | 2017-04-01 | 2023-09-30 | RC
EOP-011-1 | Emergency Operations | R4. | Each Transmission Operator and Balancing Authority shall address any reliability risks identified by its Reliability Coordinator pursuant to Requirement R3 and resubmit its Operating Plan(s) to its Reliability Coordinator within a time period specified by its Reliability Coordinator. [Violation Risk Factor: High] [Time Horizon: Operation Planning] | HIGH | Retired | 2017-04-01 | 2023-09-30 | TOP, BA
EOP-011-1 | Emergency Operations | R5. | Each Reliability Coordinator that receives an Emergency notification from a Transmission Operator or Balancing Authority within its Reliability Coordinator Area shall notify, within 30 minutes from the time of receiving notification, other Balancing Authorities and Transmission Operators in its Reliability Coordinator Area, and neighboring Reliability Coordinators. [Violation Risk Factor: High] [Time Horizon: Real-Time Operations] | HIGH | Retired | 2017-04-01 | 2023-09-30 | RC
EOP-011-1 | Emergency Operations | R6. | Each Reliability Coordinator that has a Balancing Authority experiencing a potential or actual Energy Emergency within its Reliability Coordinator Area shall declare an Energy Emergency Alert, as detailed in Attachment 1. [Violation Risk Factor: High] [Time Horizon: Real-Time Operations] | HIGH | Retired | 2017-04-01 | 2023-09-30 | RC
EOP-011-2 | Emergency Preparedness and Operations | R1. | Each Transmission Operator shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate operating Emergencies in its Transmission Operator Area. The Operating Plan(s) shall include the following, as applicable: [Violation Risk Factor: High] [Time Horizon: Real-Time Operations, Operations Planning, Long-term Planning] | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R1. | Each Transmission Operator shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate operating Emergencies in its Transmission Operator Area. The Operating Plan(s) shall include the following, as applicable: [Violation Risk Factor: High] [Time Horizon: Real-Time Operations, Operations Planning, Long-term Planning] | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R1. | Each Transmission Operator shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate operating Emergencies in its Transmission Operator Area. The Operating Plan(s) shall include the following, as applicable: [Violation Risk Factor: High] [Time Horizon: Real-Time Operations, Operations Planning, Long-term Planning] | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R1.1. | Roles and responsibilities for activating the Operating Plan(s); | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R1.2. | Processes to prepare for and mitigate Emergencies including: | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R1.2. | Processes to prepare for and mitigate Emergencies including: | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R1.2. | Processes to prepare for and mitigate Emergencies including: | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R1.2.1. | Notification to its Reliability Coordinator, to include current and projected conditions, when experiencing an operating Emergency; | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R1.2.1. | Notification to its Reliability Coordinator, to include current and projected conditions, when experiencing an operating Emergency; | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R1.2.2. | Cancellation or recall of Transmission and generation outages; | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R1.2.2. | Cancellation or recall of Transmission and generation outages; | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R1.2.3. | Transmission system reconfiguration; | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R1.2.4. | Redispatch of generation request; | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R1.2.5. | Provisions for operator-controlled manual Load shedding that minimizes the overlap with automatic Load shedding and are capable of being implemented in a timeframe adequate for mitigating the Emergency; and | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R1.2.6. | Provisions to determine reliability impacts of | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R1.2.6. | Provisions to determine reliability impacts of: | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R1.2.6.1. | cold weather conditions; and | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R1.2.6.1. | cold weather conditions; and | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R1.2.6.2. | extreme weather conditions | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R1.2.6.2. | extreme weather conditions | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R2. | Each Balancing Authority shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate Capacity Emergencies and Energy Emergencies within its Balancing Authority Area. The Operating Plan(s) shall include the following, as applicable: [Violation Risk Factor: High] [Time Horizon: Real-Time Operations, Operations Planning, Long-term Planning] | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R2. | Each Balancing Authority shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate Capacity Emergencies and Energy Emergencies within its Balancing Authority Area. The Operating Plan(s) shall include the following, as applicable: [Violation Risk Factor: High] [Time Horizon: Real-Time Operations, Operations Planning, Long-term Planning] | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R2.1. | Roles and responsibilities for activating the Operating Plan(s); | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R2.1. | Roles and responsibilities for activating the Operating Plan(s); | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R2.2. | Processes to prepare for and mitigate Emergencies including: | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R2.2. | Processes to prepare for and mitigate Emergencies including: | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R2.2.1. | Notification to its Reliability Coordinator, to include current and projected conditions when experiencing a Capacity Emergency or Energy Emergency; | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R2.2.1. | Notification to its Reliability Coordinator, to include current and projected conditions when experiencing a Capacity Emergency or Energy Emergency; | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R2.2.2. | Requesting an Energy Emergency Alert, per Attachment 1; | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R2.2.2. | Requesting an Energy Emergency Alert, per Attachment 1; | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R2.2.3. | Managing generating resources in its Balancing Authority Area to address: | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R2.2.3. | Managing generating resources in its Balancing Authority Area to address: | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R2.2.3.1. | capability and availability; | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R2.2.3.1. | capability and availability; | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R2.2.3.2. | fuel supply and inventory concerns; | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R2.2.3.2. | fuel supply and inventory concerns; | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R2.2.3.3. | fuel switching capabilities; and | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R2.2.3.3. | fuel switching capabilities; and | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R2.2.3.4. | environmental constraints. | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R2.2.3.4. | environmental constraints. | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R2.2.4. | Public appeals for voluntary Load reductions; | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R2.2.4. | Public appeals for voluntary Load reductions; | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R2.2.5. | Requests to government agencies to implement their programs to achieve necessary energy reductions; | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R2.2.5. | Requests to government agencies to implement their programs to achieve necessary energy reductions; | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R2.2.6. | Reduction of internal utility energy use; | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R2.2.6. | Reduction of internal utility energy use; | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R2.2.7. | Use of Interruptible Load, curtailable Load and demand response; | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R2.2.7. | Use of Interruptible Load, curtailable Load and demand response; | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R2.2.8. | Provisions for operator-controlled manual Load shedding that minimizes the overlap with automatic Load shedding and are capable of being implemented in a timeframe adequate for mitigating the Emergency; and | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R2.2.8. | Provisions for operator-controlled manual Load shedding that minimizes the overlap with automatic Load shedding and are capable of being implemented in a timeframe adequate for mitigating the Emergency; and | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R2.2.9. | Provisions to determine reliability impacts of | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R2.2.9. | Provisions to determine reliability impacts of | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R2.2.9.1. | cold weather conditions; and | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R2.2.9.1. | cold weather conditions; and | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R2.2.9.2. | extreme weather conditions | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R2.2.9.2. | extreme weather conditions | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R3. | The Reliability Coordinator shall review the Operating Plan(s) to mitigate operating Emergencies submitted by a Transmission Operator or a Balancing Authority regarding any reliability risks that are identified between Operating Plans. [Violation Risk Factor: High] [Time Horizon: Operations Planning] | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R3.1. | Within 30 calendar days of receipt, the Reliability Coordinator shall: | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R3.1.1. | Review each submitted Operating Plan(s) on the basis of compatibility and inter-dependency with other Balancing Authorities’ and Transmission Operators’ Operating Plans; | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R3.1.2. | Review each submitted Operating Plan(s) for coordination to avoid risk to Wide Area reliability; and | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R3.1.3. | Notify each Balancing Authority and Transmission Operator of the results of its review, specifying any time frame for resubmittal of its Operating Plan(s) if revisions are identified. | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R4. | Each Transmission Operator and Balancing Authority shall address any reliability risks identified by its Reliability Coordinator pursuant to Requirement R3 and resubmit its Operating Plan(s) to its Reliability Coordinator within a time period specified by its Reliability Coordinator. [Violation Risk Factor: High] [Time Horizon: Operation Planning] | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R5. | Each Reliability Coordinator that receives an Emergency notification from a Transmission Operator or Balancing Authority within its Reliability Coordinator Area shall notify, within 30 minutes from the time of receiving notification, other Balancing Authorities and Transmission Operators in its Reliability Coordinator Area, and neighboring Reliability Coordinators. [Violation Risk Factor: High] [Time Horizon: Real-Time Operations] | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R6. | Each Reliability Coordinator that has a Balancing Authority experiencing a potential or actual Energy Emergency within its Reliability Coordinator Area shall declare an Energy Emergency Alert, as detailed in Attachment 1. [Violation Risk Factor: High] [Time Horizon: Real-Time Operations] | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R7. | Each Generator Owner shall implement and maintain one or more cold weather preparedness plan(s) for its generating units. The cold weather preparedness plan(s) shall include the following, at a minimum: | HIGH | Effective | 2023-10-01 |  | GO
EOP-011-2 | Emergency Preparedness and Operations | R7.1. | Generating unit(s) freeze protection measures based on geographical location and plant configuration; | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R7.2. | Annual inspection and maintenance of generating unit(s) freeze protection measures; | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R7.3. | Generating unit(s) cold weather data, to include: | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R7.3.1. | Generating unit(s) operating limitations in cold weather to include: | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R7.3.1.1. | capability and availability; | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R7.3.1.2. | fuel supply and inventory concerns; | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R7.3.1.3. | fuel switching capabilities; and | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R7.3.1.4. | environmental constraints. | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R7.3.2. | Generating unit(s) minimum: | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R7.3.2.1. | design temperature; or | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R7.3.2.2. | historical operating temperature; or | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R7.3.2.3. | current cold weather performance temperature determined by an engineering analysis. | HIGH | Effective | 2023-10-01
EOP-011-2 | Emergency Preparedness and Operations | R8. | Each Generator Owner in conjunction with its Generator Operator shall identify the entity responsible for providing the generating unit-specific training, and that identified entity shall provide the training to its maintenance or operations personnel responsible for implementing cold weather preparedness plan(s) developed pursuant to Requirement R7. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning, Operations Planning] | MEDIUM | Effective | 2023-10-01
EOP-011-3 | Emergency Operations | R1. | Each Transmission Operator shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate operating Emergencies in its Transmission Operator Area. The Operating Plan(s)shall include the following, as applicable: [Violation Risk Factor: High] [Time Horizon: Real-Time Operations, Operations Planning, Long-term Planning] | HIGH | Pending Approval |  |  | TOP
EOP-011-3 | Emergency Operations | R1.1. | Roles and responsibilitiesfor activating the Operating Plan(s) | HIGH | Pending Approval |  |  | TOP
EOP-011-3 | Emergency Operations | R1.2.1. | 1.2. Processes to prepare for and mitigate Emergencies including: 1.2.1. Notification to its Reliability Coordinator, to include current and projected conditions, when experiencing an operating Emergency | HIGH | Pending Approval |  |  | TOP
EOP-011-3 | Emergency Operations | R1.2.2. | 1.2. Processes to prepare for and mitigate Emergencies including: 1.2.2. Cancellation or recall of Transmission and generation outages | HIGH | Pending Approval |  |  | TOP
EOP-011-3 | Emergency Operations | R1.2.3. | R1. Each Transmission Operator shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate operating Emergencies in its Transmission Operator Area. The Operating Plan(s) shall include the following, as applicable: 1.2. Processes to prepare for and mitigate Emergencies including: 1.2.3. Transmission system reconfiguration |  | Pending Approval |  |  | TOP
EOP-011-3 | Emergency Operations | R1.2.3. | 1.2. Processes to prepare for and mitigate Emergencies including: 1.2.3. Transmission system reconfiguration | HIGH | Pending Approval |  |  | TOP
EOP-011-3 | Emergency Operations | R1.2.4. | 1.2. Processes to prepare for and mitigate Emergencies including: 1.2.4. Redispatch of generation request | HIGH | Pending Approval |  |  | TOP
EOP-011-3 | Emergency Operations | R1.2.5.1. | 1.2. Processes to prepare for and mitigate Emergencies including: 1.2.5. Operator-controlledmanual Load shedding during an Emergency that accounts for each of the following: 1.2.5.1. Provisions for manual Load shedding capable of being implemented in a timeframe adequate for mitigating the Emergency | HIGH | Pending Approval |  |  | TOP
EOP-011-3 | Emergency Operations | R1.2.5.2. | 1.2. Processes to prepare for and mitigate Emergencies including: 1.2.5. Operator-controlledmanual Load shedding during an Emergency that accounts for each of the following: 1.2.5.2. Provisions to minimize the overlap of circuits that are designated for manual Load shed and circuits that serve designated critical loads | HIGH | Pending Approval |  |  | TOP
EOP-011-3 | Emergency Operations | R1.2.5.3. | 1.2. Processes to prepare for and mitigate Emergencies including: 1.2.5. Operator-controlledmanual Load shedding during an Emergency that accounts for each of the following: 1.2.5.3. Provisions to minimize the overlap of circuits that are designated for manual Load shed and circuits that are utilized for underfrequency load shed (UFLS) or undervoltage load shed (UVLS) | HIGH | Pending Approval |  |  | TOP
EOP-011-3 | Emergency Operations | R1.2.5.4. | 1.2. Processes to prepare for and mitigate Emergencies including: 1.2.5. Operator-controlledmanual Load shedding during an Emergency that accounts for each of the following: 1.2.5.4. Provisionsfor limiting the utilization of UFLS or UVLS circuits for manual Load shed to situations where warranted by systemconditions. | HIGH | Pending Approval |  |  | TOP
EOP-011-3 | Emergency Operations | R1.2.6. | 1.2. Processes to prepare for and mitigate Emergencies including: 1.2.6. Provisions to determine reliability impacts of: 1.2.6.1. cold weather conditions; and 1.2.6.2. extreme weather conditions. | HIGH | Pending Approval |  |  | TOP
EOP-011-3 | Emergency Operations | R2. | Each Balancing Authority shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate Capacity Emergencies and Energy Emergencies within its Balancing Authority Area. The Operating Plan(s) shall include the following, as applicable: [Violation Risk Factor: High] [Time Horizon: Real-Time Operations, Operations Planning, Long-term Planning] | HIGH | Pending Approval |  |  | BA
EOP-011-3 | Emergency Operations | R2.1. | Roles and responsibilitiesfor activating the Operating Plan(s) | HIGH | Pending Approval |  |  | BA
EOP-011-3 | Emergency Operations | R2.2.1. | 2.2. Processes to prepare for and mitigate Emergencies including: 2.2.1. Notification to its Reliability Coordinator, to include current and projected conditions when experiencing a Capacity Emergency or Energy Emergency | HIGH | Pending Approval |  |  | BA
EOP-011-3 | Emergency Operations | R2.2.2. | 2.2. Processes to prepare for and mitigate Emergencies including: 2.2.2. Requesting an Energy Emergency Alert, per Attachment 1 | HIGH | Pending Approval |  |  | BA
EOP-011-3 | Emergency Operations | R2.2.3. | 2.2. Processes to prepare for and mitigate Emergencies including: 2.2.3. Managing generating resources in its Balancing Authority Area to address: 2.2.3.1. capability and availability 2.2.3.2. fuel supply and inventory concerns; 2.2.3.3. fuel switching capabilities; and 2.2.3.4. environmental constraints. | HIGH | Pending Approval |  |  | BA
EOP-011-3 | Emergency Operations | R2.2.4. | 2.2. Processes to prepare for and mitigate Emergencies including: 2.2.4. Public appealsfor voluntary Load reductions | HIGH | Pending Approval |  |  | BA
EOP-011-3 | Emergency Operations | R2.2.5. | 2.2. Processes to prepare for and mitigate Emergencies including: 2.2.5. Requeststo government agenciesto implementtheir programs to achieve necessary energy reductions | HIGH | Pending Approval |  |  | BA
EOP-011-3 | Emergency Operations | R2.2.6. | 2.2. Processes to prepare for and mitigate Emergencies including: 2.2.6. Reduction of internal utility energy use | HIGH | Pending Approval |  |  | BA
EOP-011-3 | Emergency Operations | R2.2.7. | 2.2. Processes to prepare for and mitigate Emergencies including: 2.2.7. Use of Interruptible Load, curtailable Load and demand response | HIGH | Pending Approval |  |  | BA
EOP-011-3 | Emergency Operations | R2.2.8. | 2.2. Processes to prepare for and mitigate Emergencies including: 2.2.8. Provisionsfor Transmission Operators to implement operator-controlled manual Load shed in accordance with Requirement R1 Part 1.2.5 | HIGH | Pending Approval |  |  | BA
EOP-011-3 | Emergency Operations | R2.2.9. | 2.2. Processes to prepare for and mitigate Emergencies including: 2.2.9. Provisions to determine reliability impacts of: 2.2.9.1. cold weather conditions; and 2.2.9.2. extreme weather conditions. | HIGH | Pending Approval |  |  | BA
EOP-011-3 | Emergency Operations | R3. | The Reliability Coordinatorshall review the Operating Plan(s) to mitigate operating Emergencies submitted by a Transmission Operator or a Balancing Authority regarding any reliability risksthat are identified betweenOperating Plans. [Violation Risk Factor: High] [Time Horizon: Operations Planning] | HIGH | Pending Approval |  |  | RC
EOP-011-3 | Emergency Operations | R3.1.1. | 3.1. Within 30 calendar days of receipt, the Reliability Coordinator shall: 3.1.1. Review each submitted Operating Plan(s) on the basis of compatibility and inter-dependency with other Balancing Authorities’ and Transmission Operators’ Operating Plans | HIGH | Pending Approval |  |  | RC
EOP-011-3 | Emergency Operations | R3.1.2. | 3.1. Within 30 calendar days of receipt, the Reliability Coordinator shall: 3.1.2. Review each submittedOperating Plan(s) for coordination to avoid risk to Wide Area reliability | HIGH | Pending Approval |  |  | RC
EOP-011-3 | Emergency Operations | R3.1.3. | 3.1. Within 30 calendar days of receipt, the Reliability Coordinator shall: 3.1.3. Notify each Balancing Authority and TransmissionOperator of the results of its review, specifying any time frame for resubmittal of its Operating Plan(s) if revisions are identified. | HIGH | Pending Approval |  |  | RC
EOP-011-3 | Emergency Operations | R4. | Each Transmission Operator and Balancing Authority shall address any reliability risks identified by its Reliability Coordinator pursuant to Requirement R3 and resubmit its Operating Plan(s) to its Reliability Coordinator within a time period specified by its Reliability Coordinator. [Violation Risk Factor: High] [Time Horizon: Operation Planning] | HIGH | Pending Approval |  |  | TOP, BA
EOP-011-3 | Emergency Operations | R5. | Each Reliability Coordinator that receives an Emergency notification from a Transmission Operator or Balancing Authority within its Reliability Coordinator Area shall notify, within 30 minutesfrom the time of receiving notification, other Balancing Authorities and Transmission Operators in its Reliability Coordinator Area, and neighboringReliability Coordinators. [Violation Risk Factor: High] [Time Horizon: RealTime Operations] | HIGH | Pending Approval |  |  | RC
EOP-011-3 | Emergency Operations | R6. | Each Reliability Coordinator that has a Balancing Authority experiencing a potential or actual Energy Emergency within its Reliability Coordinator Area shall declare an Energy Emergency Alert, as detailed in Attachment 1. [Violation Risk Factor: High] [Time Horizon: Real-Time Operations] | HIGH | Pending Approval |  |  | RC
EOP-011-4 | Emergency Operations | R1. | Each Transmission Operator shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate operating Emergencies in its Transmission Operator Area. The Operating Plan(s) shall include the following, as applicable: [Violation Risk Factor: High] [Time Horizon: Real-Time Operations, Operations Planning, Long-term Planning] | HIGH | Pending Approval |  |  | TOP
EOP-011-4 | Emergency Operations | R1.1. | R1. Each Transmission Operator shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate operating Emergencies in its Transmission Operator Area. The Operating Plan(s) shall include the following, as applicable: 1.1. Roles and responsibilities for activating the Operating Plan(s) | HIGH | Pending Approval |  |  | TOP
EOP-011-4 | Emergency Operations | R1.2.1. | R1. Each Transmission Operator shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate operating Emergencies in its Transmission Operator Area. The Operating Plan(s) shall include the following, as applicable: 1.2. Processes to prepare for and mitigate Emergencies including: 1.2.1. Notification to its Reliability Coordinator, to include current and projected conditions, when experiencing an operating Emergency | HIGH | Pending Approval |  |  | TOP
EOP-011-4 | Emergency Operations | R1.2.2. | R1. Each Transmission Operator shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate operating Emergencies in its Transmission Operator Area. The Operating Plan(s) shall include the following, as applicable: 1.2. Processes to prepare for and mitigate Emergencies including: 1.2.2. Cancellation or recall of Transmission and generation outages |  | Pending Approval |  |  | TOP
EOP-011-4 | Emergency Operations | R1.2.4. | R1. Each Transmission Operator shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate operating Emergencies in its Transmission Operator Area. The Operating Plan(s) shall include the following, as applicable: 1.2. Processes to prepare for and mitigate Emergencies including: 1.2.4. Redispatch of generation request | HIGH | Pending Approval |  |  | TOP
EOP-011-4 | Emergency Operations | R1.2.5.1. | R1. Each Transmission Operator shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate operating Emergencies in its Transmission Operator Area. The Operating Plan(s) shall include the following, as applicable: 1.2. Processes to prepare for and mitigate Emergencies including: 1.2.5. Operator-controlled manual Load shed, undervoltage load shed (UVLS), or underfrequency load shed (UFLS) during an Emergency that accounts for each of the following: 1.2.5.1. Provisions for manual Load shedding capable of being implemented in a timeframe adequate for mitigating the Emergency | HIGH | Pending Approval |  |  | TOP
EOP-011-4 | Emergency Operations | R1.2.5.2. | R1. Each Transmission Operator shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate operating Emergencies in its Transmission Operator Area. The Operating Plan(s) shall include the following, as applicable: 1.2. Processes to prepare for and mitigate Emergencies including: 1.2.5. Operator-controlled manual Load shed, undervoltage load shed (UVLS), or underfrequency load shed (UFLS) during an Emergency that accounts for each of the following: 1.2.5.2. Provisions to minimize the overlap of circuits that are designated for manual Load shed, UVLS, or UFLS and circuits that serve designated critical loads which are essential to the reliability of the BES | HIGH | Pending Approval |  |  | TOP
EOP-011-4 | Emergency Operations | R1.2.5.3. | R1. Each Transmission Operator shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate operating Emergencies in its Transmission Operator Area. The Operating Plan(s) shall include the following, as applicable: 1.2. Processes to prepare for and mitigate Emergencies including: 1.2.5. Operator-controlled manual Load shed, undervoltage load shed (UVLS), or underfrequency load shed (UFLS) during an Emergency that accounts for each of the following: 1.2.5.3. Provisions to minimize the overlap of circuits that are designated for manual Load shed and circuits that are utilized for UFLS or UVLS | HIGH | Pending Approval |  |  | TOP
EOP-011-4 | Emergency Operations | R1.2.5.4. | R1. Each Transmission Operator shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate operating Emergencies in its Transmission Operator Area. The Operating Plan(s) shall include the following, as applicable: 1.2. Processes to prepare for and mitigate Emergencies including: 1.2.5. Operator-controlled manual Load shed, undervoltage load shed (UVLS), or underfrequency load shed (UFLS) during an Emergency that accounts for each of the following: 1.2.5.4. Provisions for limiting the utilization of UFLS or UVLS circuits for manual Load shed to situations where warranted by system conditions | HIGH | Pending Approval |  |  | TOP
EOP-011-4 | Emergency Operations | R1.2.5.5. | R1. Each Transmission Operator shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate operating Emergencies in its Transmission Operator Area. The Operating Plan(s) shall include the following, as applicable: 1.2. Processes to prepare for and mitigate Emergencies including: 1.2.5. Operator-controlled manual Load shed, undervoltage load shed (UVLS), or underfrequency load shed (UFLS) during an Emergency that accounts for each of the following: 1.2.5.5. Provisions for the identification and prioritization of designated critical natural gas infrastructure loads which are essential to the reliability of the BES as defined by the Applicable Entity | HIGH | Pending Approval |  |  | TOP
EOP-011-4 | Emergency Operations | R1.2.6. | R1. Each Transmission Operator shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate operating Emergencies in its Transmission Operator Area. The Operating Plan(s) shall include the following, as applicable: 1.2. Processes to prepare for and mitigate Emergencies including: 1.2.6. Provisions to determine reliability impacts of: 1.2.6.1. Cold weather conditions; and 1.2.6.2. Extreme weather conditions |  | Pending Approval |  |  | TOP
EOP-011-4 | Emergency Operations | R2. | Each Balancing Authority shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate Capacity Emergencies and Energy Emergencies within its Balancing Authority Area. The Operating Plan(s) shall include the following, as applicable: [Violation Risk Factor: High] [Time Horizon: Real-Time Operations, Operations Planning, Long-term Planning] | HIGH | Pending Approval |  |  | BA
EOP-011-4 | Emergency Operations | R2.1. | R2. Each Balancing Authority shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate Capacity Emergencies and Energy Emergencies within its Balancing Authority Area. The Operating Plan(s) shall include the following, as applicable: 2.1. Roles and responsibilities for activating the Operating Plan(s) | HIGH | Pending Approval |  |  | BA
EOP-011-4 | Emergency Operations | R2.2.1. | R2. Each Balancing Authority shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate Capacity Emergencies and Energy Emergencies within its Balancing Authority Area. The Operating Plan(s) shall include the following, as applicable: 2.2. Processes to prepare for and mitigate Emergencies including: 2.2.1. Notification to its Reliability Coordinator to include current and projected conditions when experiencing a Capacity Emergency or Energy Emergency | HIGH | Pending Approval |  |  | BA
EOP-011-4 | Emergency Operations | R2.2.10. | R2. Each Balancing Authority shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate Capacity Emergencies and Energy Emergencies within its Balancing Authority Area. The Operating Plan(s) shall include the following, as applicable: 2.2. Processes to prepare for and mitigate Emergencies including: 2.2.10. Provisionsto determine reliability impacts of: 2.2.10.1. Cold weather conditions; and 2.2.10.2. Extreme weather conditions. | HIGH | Pending Approval |  |  | BA
EOP-011-4 | Emergency Operations | R2.2.2. | R2. Each Balancing Authority shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate Capacity Emergencies and Energy Emergencies within its Balancing Authority Area. The Operating Plan(s) shall include the following, as applicable: 2.2. Processes to prepare for and mitigate Emergencies including: 2.2.2. Requesting an Energy Emergency Alert, per Attachment 1 | HIGH | Pending Approval |  |  | BA
EOP-011-4 | Emergency Operations | R2.2.3. | R2. Each Balancing Authority shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate Capacity Emergencies and Energy Emergencies within its Balancing Authority Area. The Operating Plan(s) shall include the following, as applicable: 2.2. Processes to prepare for and mitigate Emergencies including: 2.2.3. Managing generating resources in its Balancing Authority Area to address: 2.2.3.1. Capability and availability; 2.2.3.2. Fuel supply and inventory concerns; 2.2.3.3. Fuel switching capabilities; and 2.2.3.4. Environmental constraints. | HIGH | Pending Approval |  |  | BA
EOP-011-4 | Emergency Operations | R2.2.4. | R2. Each Balancing Authority shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate Capacity Emergencies and Energy Emergencies within its Balancing Authority Area. The Operating Plan(s) shall include the following, as applicable: 2.2. Processes to prepare for and mitigate Emergencies including: 2.2.4. Public appeals for voluntary Load reductions | HIGH | Pending Approval |  |  | BA
EOP-011-4 | Emergency Operations | R2.2.5. | R2. Each Balancing Authority shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate Capacity Emergencies and Energy Emergencies within its Balancing Authority Area. The Operating Plan(s) shall include the following, as applicable: 2.2. Processes to prepare for and mitigate Emergencies including: 2.2.5. Requests to government agencies to implement their programs to achieve necessary energy reductions | HIGH | Pending Approval |  |  | BA
EOP-011-4 | Emergency Operations | R2.2.6. | R2. Each Balancing Authority shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate Capacity Emergencies and Energy Emergencies within its Balancing Authority Area. The Operating Plan(s) shall include the following, as applicable: 2.2. Processes to prepare for and mitigate Emergencies including: 2.2.6. Reduction of internal utility energy use | HIGH | Pending Approval |  |  | BA
EOP-011-4 | Emergency Operations | R2.2.7. | R2. Each Balancing Authority shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate Capacity Emergencies and Energy Emergencies within its Balancing Authority Area. The Operating Plan(s) shall include the following, as applicable: 2.2. Processes to prepare for and mitigate Emergencies including: 2.2.7. Use of Interruptible Load, curtailable Load, and demand response | HIGH | Pending Approval |  |  | BA
EOP-011-4 | Emergency Operations | R2.2.8. | R2. Each Balancing Authority shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate Capacity Emergencies and Energy Emergencies within its Balancing Authority Area. The Operating Plan(s) shall include the following, as applicable: 2.2. Processes to prepare for and mitigate Emergencies including: 2.2.8. Provisions for excluding critical natural gas infrastructure loads which are essential to the reliability of the BES, as defined by the Applicable Entity, as Interruptible Load, curtailable Load, and demand response during extreme cold weather periods within each Balancing Authority Area | HIGH | Pending Approval |  |  | BA
EOP-011-4 | Emergency Operations | R2.2.9. | R2. Each Balancing Authority shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate Capacity Emergencies and Energy Emergencies within its Balancing Authority Area. The Operating Plan(s) shall include the following, as applicable: 2.2. Processes to prepare for and mitigate Emergencies including: 2.2.9. Provisions for Transmission Operators to implement operator-controlled manual Load shedding, undervoltage Load shedding, or underfrequency Load shedding in accordance with Requirement R1 Part 1.2.5 | HIGH | Pending Approval |  |  | BA
EOP-011-4 | Emergency Operations | R3. | The Reliability Coordinator shall review the Operating Plan(s) to mitigate operating Emergencies submitted by a Transmission Operator or a Balancing Authority regarding any reliability risks that are identified between Operating Plans. [Violation Risk Factor: High] [Time Horizon: Operations Planning] | HIGH | Pending Approval |  |  | RC
EOP-011-4 | Emergency Operations | R3.1.1. | 3.1. Within 30 calendar days of receipt, the Reliability Coordinator shall: 3.1.1. Review each submitted Operating Plan(s) on the basis of compatibility and inter-dependency with other Balancing Authorities’ and Transmission Operators’ Operating Plans | HIGH | Pending Approval |  |  | RC
EOP-011-4 | Emergency Operations | R3.1.2. | 3.1. Within 30 calendar days of receipt, the Reliability Coordinator shall: 3.1.2. Review each submitted Operating Plan(s) for coordination to avoid risk to Wide Area reliability | HIGH | Pending Approval |  |  | RC
EOP-011-4 | Emergency Operations | R3.1.3. | 3.1. Within 30 calendar days of receipt, the Reliability Coordinator shall: 3.1.3. Notify each Balancing Authority and Transmission Operator of the results of its review, specifying any time frame for resubmittal of its Operating Plan(s) if revisions are identified. | HIGH | Pending Approval |  |  | RC
EOP-011-4 | Emergency Operations | R4. | Each Transmission Operator and Balancing Authority shall address any reliability risks identified by its Reliability Coordinator pursuant to Requirement R3 and resubmit its Operating Plan(s) to its Reliability Coordinator within a time period specified by its Reliability Coordinator. [Violation Risk Factor: High] [Time Horizon: Operation Planning] | HIGH | Pending Approval |  |  | TOP, BA
EOP-011-4 | Emergency Operations | R5. | Each Reliability Coordinator that receives an Emergency notification from a Transmission Operator or Balancing Authority within its Reliability Coordinator Area shall notify, within 30 minutes from the time of receiving notification, other Balancing Authorities and Transmission Operators in its Reliability Coordinator Area, and neighboring Reliability Coordinators. [Violation Risk Factor: High] [Time Horizon: RealTime Operations] | HIGH | Pending Approval |  |  | RC
EOP-011-4 | Emergency Operations | R6. | Each Reliability Coordinator that has a Balancing Authority experiencing a potential or actual Energy Emergency within its Reliability Coordinator Area shall declare an Energy Emergency Alert, as detailed in Attachment 1. [Violation Risk Factor: High] [Time Horizon: Real-Time Operations] | HIGH | Pending Approval |  |  | RC
EOP-011-4 | Emergency Operations | R7. | Each Transmission Operatorshall annually identify and notify Distribution Providers, UFLS-Only Distribution Providers and Transmission Owners that are required to assist with the mitigation of operating Emergencies in its Transmission Operator Area through operator-controlled manual Load shedding, undervoltage Load shedding, or underfrequency Load shedding. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning, Long-term Planning] | LOWER | Pending Approval |  |  | TOP
EOP-011-4 | Emergency Operations | R8. | Each Distribution Provider, UFLS-Only Distribution Provider, and Transmission Owner notified by a Transmission Operator per R7 to assist with the mitigation of operating Emergencies in its Transmission Operator Area shall develop, maintain, and implement a Load shedding plan. The Load shedding plan shall include the following, as applicable: [Violation Risk Factor: High] [Time Horizon: Real-Time Operations, Operations Planning, Long-term Planning] | HIGH | Pending Approval |  |  | TO, DP
EOP-011-4 | Emergency Operations | R8.1.1. | R8. Each Distribution Provider, UFLS-Only Distribution Provider, and Transmission Owner notified by a Transmission Operator per R7 to assist with the mitigation of operating Emergencies in its Transmission Operator Area shall develop, maintain, and implement a Load shedding plan. The Load shedding plan shall include the following, as applicable: 8.1. Operator-controlled manual Load shedding, undervoltage Load shedding, or underfrequency Load shedding during an Emergency that accounts for each of the following: 8.1.1. Provisions for manual Load shedding capable of being implemented in a timeframe adequate for mitigating the Emergency | HIGH | Pending Approval |  |  | TO, DP
EOP-011-4 | Emergency Operations | R8.1.2. | R8. Each Distribution Provider, UFLS-Only Distribution Provider, and Transmission Owner notified by a Transmission Operator per R7 to assist with the mitigation of operating Emergencies in its Transmission Operator Area shall develop, maintain, and implement a Load shedding plan. The Load shedding plan shall include the following, as applicable: 8.1. Operator-controlled manual Load shedding, undervoltage Load shedding, or underfrequency Load shedding during an Emergency that accounts for each of the following: 8.1.2. Provisions to minimize the overlap of circuits that are designated for manual, undervoltage, or underfrequency Load shed and circuits that serve designated critical loads which are essential to the reliability of the BES | HIGH | Pending Approval |  |  | TO, DP
EOP-011-4 | Emergency Operations | R8.1.3. | R8. Each Distribution Provider, UFLS-Only Distribution Provider, and Transmission Owner notified by a Transmission Operator per R7 to assist with the mitigation of operating Emergencies in its Transmission Operator Area shall develop, maintain, and implement a Load shedding plan. The Load shedding plan shall include the following, as applicable: 8.1. Operator-controlled manual Load shedding, undervoltage Load shedding, or underfrequency Load shedding during an Emergency that accounts for each of the following: 8.1.3. Provisions to minimize the overlap of circuits that are designated for manual Load shed and circuits that are utilized for UFLS or UVLS | HIGH | Pending Approval |  |  | TO, DP
EOP-011-4 | Emergency Operations | R8.1.4. | R8. Each Distribution Provider, UFLS-Only Distribution Provider, and Transmission Owner notified by a Transmission Operator per R7 to assist with the mitigation of operating Emergencies in its Transmission Operator Area shall develop, maintain, and implement a Load shedding plan. The Load shedding plan shall include the following, as applicable: 8.1. Operator-controlled manual Load shedding, undervoltage Load shedding, or underfrequency Load shedding during an Emergency that accounts for each of the following: 8.1.4. Provisions for limiting the utilization of UFLS or UVLS circuits for manual Load shed to situations where warranted by system conditions | HIGH | Pending Approval |  |  | TO, DP
EOP-011-4 | Emergency Operations | R8.1.5. | R8. Each Distribution Provider, UFLS-Only Distribution Provider, and Transmission Owner notified by a Transmission Operator per R7 to assist with the mitigation of operating Emergencies in its Transmission Operator Area shall develop, maintain, and implement a Load shedding plan. The Load shedding plan shall include the following, as applicable: 8.1. Operator-controlled manual Load shedding, undervoltage Load shedding, or underfrequency Load shedding during an Emergency that accounts for each of the following: 8.1.5. Provisions for the identification and prioritization of designated critical natural gas infrastructure loads which are essential to the reliability of the BES as defined by the Applicable Entity. | HIGH | Pending Approval |  |  | TO, DP
EOP-011-4 | Emergency Operations | R8.2. | R8. Each Distribution Provider, UFLS-Only Distribution Provider, and Transmission Owner notified by a Transmission Operator per R7 to assist with the mitigation of operating Emergencies in its Transmission Operator Area shall develop, maintain, and implement a Load shedding plan. The Load shedding plan shall include the following, as applicable: 8.2. Provisions to provide the Load shedding plan to the Transmission Operator for review. | HIGH | Pending Approval |  |  | TO, DP
EOP-012-1 | Extreme Cold Weather Preparedness and Operations | R1. | For each generating unit(s) with a commercial operation date subsequent to [Effective Date of this requirement], the Generator Owner shall: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning, Operations Planning] • Implement freeze protection measuresthat provide capability to operate for a period of not less than twelve (12) continuous hours at the Extreme Cold Weather Temperature for the unit(s), assuming a concurrent twenty (20) mph wind speed on any exposed Generator Cold Weather Critical Components; or • Explain in a declaration any technical, commercial, or operational constraints, as defined by the Generator Owner, that preclude the ability to implement appropriate freeze protection measures to provide capability of operating for twelve (12) hours at the documented Extreme Cold Weather Temperature. | MEDIUM | Future Effective |  |  | GO
EOP-012-1 | Extreme Cold Weather Preparedness and Operations | R2. | For each generating unit(s) in commercial operation prior to [Effective Date of this requirement], the Generator Owner shall ensure its generating unit(s) add new or modify existing freeze protection measures as needed to provide the capability to operate for a period of not lessthan one (1) hour at the unit(s) Extreme Cold Weather Temperature. Generating unit(s) that are not capable of operating for one (1) hour at its Extreme Cold Weather Temperature shall develop a Corrective Action Plan (CAP) for the identified issues, including identification of any needed modifications to the cold weather preparedness plan required under Requirement R3. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning, Operations Planning] | MEDIUM | Future Effective |  |  | GO
EOP-012-1 | Extreme Cold Weather Preparedness and Operations | R3. | Each Generator Owner shall implement and maintain one or more cold weather preparedness plan(s) for its generating units. The cold weather preparedness plan(s) shall include the following, at a minimum:[Violation Risk Factor: High] [Time Horizon: Operations Planning and Real-time Operations] | HIGH | Future Effective | 2025-01-01 |  | GO
EOP-012-1 | Extreme Cold Weather Preparedness and Operations | R3.1. | R3. Each Generator Owner shall implement and maintain one or more cold weather preparedness plan(s) for its generating units. The cold weather preparedness plan(s) shall include the following, at a minimum: 3.1 The Extreme Cold Weather Temperature for their unit(s) including the calculation date and source of temperature data | HIGH | Future Effective | 2025-01-01 |  | GO
EOP-012-1 | Extreme Cold Weather Preparedness and Operations | R3.2. | R3. Each Generator Owner shall implement and maintain one or more cold weather preparedness plan(s) for its generating units. The cold weather preparedness plan(s) shall include the following, at a minimum: 3.2 Documentation identifying the Generator Cold Weather Critical Components | HIGH | Future Effective | 2025-01-01 |  | GO
EOP-012-1 | Extreme Cold Weather Preparedness and Operations | R3.3. | R3. Each Generator Owner shall implement and maintain one or more cold weather preparedness plan(s) for its generating units. The cold weather preparedness plan(s) shall include the following, at a minimum: 3.3 Documentation of freeze protection measures implemented on Generator Cold Weather Critical Components which may include measures used to reduce the cooling effects of wind determined necessary by the Generator Owner to protect against heat loss, and where applicable, the effects of freezing precipitation (e.g., sleet, snow, ice, and freezing rain) | HIGH | Future Effective | 2025-01-01 |  | GO
EOP-012-1 | Extreme Cold Weather Preparedness and Operations | R3.4. | R3. Each Generator Owner shall implement and maintain one or more cold weather preparedness plan(s) for its generating units. The cold weather preparedness plan(s) shall include the following, at a minimum: 3.4 Annual inspection and maintenance of generating unit(s) freeze protection measures | HIGH | Future Effective | 2025-01-01 |  | GO
EOP-012-1 | Extreme Cold Weather Preparedness and Operations | R3.5.1. | R3. Each Generator Owner shall implement and maintain one or more cold weather preparedness plan(s) for its generating units. The cold weather preparedness plan(s) shall include the following, at a minimum: 3.5 Generating unit(s) cold weather data, to include: 3.5.1 Generating unit(s) operating limitations in cold weather to include: 3.5.1.1 Capability and availability; 3.5.1.2 Fuel supply and inventory concerns; 3.5.1.3 Fuel switching capabilities; and 3.5.1.4 Environmental constraints. | HIGH | Future Effective | 2025-01-01 |  | GO
EOP-012-1 | Extreme Cold Weather Preparedness and Operations | R3.5.2. | R3. Each Generator Owner shall implement and maintain one or more cold weather preparedness plan(s) for its generating units. The cold weather preparedness plan(s) shall include the following, at a minimum: 3.5 Generating unit(s) cold weather data, to include: 3.5.2 Generating unit(s) minimum: • Design temperature; • Historical operating temperature; or • Current cold weatherperformance temperature determined by an engineering analysis. |  | Future Effective | 2025-01-01 |  | GO
EOP-012-1 | Extreme Cold Weather Preparedness and Operations | R4.1. | R4. Once every five calendar years, each Generator Owner shall for each generating unit: 4.1 Calculate the Extreme Cold Weather Temperature, and update the cold weather preparedness plan if this temperature is now lower than the previous lowest calculation | LOW | Future Effective |  |  | GO
EOP-012-1 | Extreme Cold Weather Preparedness and Operations | R4.2. | R4. Once every five calendar years, each Generator Owner shall for each generating unit: 4.2 Review its documented generating unit(s) minimum temperature contained within its cold weather preparedness plan(s), pursuant to Part 3.5.2 |  | Future Effective |  |  | GO
EOP-012-1 | Extreme Cold Weather Preparedness and Operations | R4.3. | R4. Once every five calendar years, each Generator Owner shall for each generating unit: 4.3 Review whether its generating units have the freeze protection measures required to operate at the Extreme Cold Weather Temperature pursuant to R1 or R2 as applicable, and if not develop a CAP for the identified issues, including identification of any needed modifications to the cold weather preparedness plan required under Requirement R3. | LOW | Future Effective |  |  | GO
EOP-012-1 | Extreme Cold Weather Preparedness and Operations | R5. | Each Generator Owner in conjunction with its Generator Operator shall identify the entity responsible for providing the generating unit-specific training, and that identified entity shall provide annual training to its maintenance or operations personnel responsible for implementing the cold weather preparedness plan(s) developed pursuant to Requirement R3. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning, Operations Planning] | MEDIUM | Future Effective | 2025-01-01 |  | GOP, GO
EOP-012-1 | Extreme Cold Weather Preparedness and Operations | R6. | Each Generator Owner that owns a generating unit that experiences a Generator Cold Weather Reliability Eventshall develop a CAP, within 150 days or by July 1, whichever is earlier, that contains at a minimum: [Violation Risk Factor: High] [Time Horizon: Long-term Planning] | HIGH | Future Effective |  |  | GO
EOP-012-1 | Extreme Cold Weather Preparedness and Operations | R6.1. | R6. Each Generator Owner that owns a generating unit that experiences a Generator Cold Weather Reliability Eventshall develop a CAP, within 150 days or by July 1, whichever is earlier, that contains at a minimum: 6.1 A summary of the identified cause(s) for the Generator Cold Weather Reliability Event, where applicable, and any relevant associated data | HIGH | Future Effective |  |  | GO
EOP-012-1 | Extreme Cold Weather Preparedness and Operations | R6.2. | R6. Each Generator Owner that owns a generating unit that experiences a Generator Cold Weather Reliability Eventshall develop a CAP, within 150 days or by July 1, whichever is earlier, that contains at a minimum: 6.2 A review of applicability to similar equipment at other generating units owned by the Generator Owner | HIGH | Future Effective |  |  | GO
EOP-012-1 | Extreme Cold Weather Preparedness and Operations | R6.3. | R6. Each Generator Owner that owns a generating unit that experiences a Generator Cold Weather Reliability Eventshall develop a CAP, within 150 days or by July 1, whichever is earlier, that contains at a minimum: 6.3 An identification of any temporary operating limitations or impacts to the cold weather preparedness plan, that would apply until execution of the corrective action(s) identified in the CAP. | HIGH | Future Effective |  |  | GO
EOP-012-1 | Extreme Cold Weather Preparedness and Operations | R7.1. | R7. Each Generator Ownershall: 7.1 Implement each CAP developed pursuant to Requirements R2, R4, or R6, or explain in a declaration why corrective actions are not being implemented due to any technical, commercial, or operational constraints as defined by the Generator Owner. | MEDIUM | Future Effective |  |  | GO
EOP-012-1 | Extreme Cold Weather Preparedness and Operations | R7.2. | R7. Each Generator Ownershall: 7.2 Update each CAP if actions or timetables change, until completed | MEDIUM | Future Effective |  |  | GO
EOP-012-2 | Extreme Cold Weather Preparedness and Operations | R1.1. | R1. At least once every five calendar years, each Generator Owner shall, for each of its applicable generating unit(s): 1.1. Calculate the Extreme Cold Weather Temperature for each of its applicable unit(s) and identify the calculation date and source of temperature data | LOWER | Pending Approval |  |  | GO
EOP-012-2 | Extreme Cold Weather Preparedness and Operations | R1.1.1. | If the re-calculated Extreme Cold Weather Temperature is lower than the previous Extreme Cold Weather Temperature, the entity shall review and update its cold weather preparedness plan(s) under Requirement R4 within six (6) months of the recalculation. If new corrective actions are needed to provide the required operational capability under Requirement R2 or R3, the entity shall develop a Corrective Action Plan within 6 months of the recalculation. | LOWER | Pending Approval |  |  | GO
EOP-012-2 | Extreme Cold Weather Preparedness and Operations | R1.2.1. | R1. At least once every five calendar years, each Generator Owner shall, for each of its applicable generating unit(s): 1.2. Identify generating unit(s) cold weather data, to include: 1.2.1. Generating unit(s) operating limitations in cold weather to include: 1.2.1.1. Capability and availability; 1.2.1.2. Fuel supply and inventory concerns; 1.2.1.3. Start-up issues; 1.2.1.4. Fuel switching capabilities; and 1.2.1.5. Environmental constraints. | LOWER | Pending Approval |  |  | GO
EOP-012-2 | Extreme Cold Weather Preparedness and Operations | R1.2.2. | R1. At least once every five calendar years, each Generator Owner shall, for each of its applicable generating unit(s): 1.2. Identify generating unit(s) cold weather data, to include: 1.2.2. Generating unit(s) minimum: • Design temperature, and if available, the concurrent wind speed and precipitation; • Historical operating temperature at least one hour in duration, and if available, the concurrent wind speed and precipitation; or • Current cold weather performance temperature determined by an engineering analysis, which includes the concurrent wind speed and precipitation. | LOWER | Pending Approval |  |  | GO
EOP-012-2 | Extreme Cold Weather Preparedness and Operations | R2. | Applicable to generating units with a commercial operation date on or after October 1, 2027: Each Generator Owner, for each generating unit that has a calculated Extreme Cold Weather Temperature at or below 32 degrees Fahrenheit (zero degrees Celsius) as determined in Requirement R1, and that self-commits or is required to operate at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius), shall: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning, Operations Planning] • Implement freeze protection measures to protect Generator Cold Weather Critical Components that provide the capability to operate at the unit(s)’ Extreme Cold Weather Temperature with sustained concurrent twenty (20) mph wind speed for (i) a period of not less than twelve (12) continuous hours, or (ii) the maximum operational duration for intermittent energy resources if less than twelve (12) continuous hours; or • Develop a Corrective Action Plan(s) to add new or modify existing or previously planned freeze protection measures to provide the capability to operate at the unit(s)’ Extreme Cold Weather Temperature with a sustained concurrent twenty (20) mph wind speed for (i) a period of not less than twelve (12) continuous hours, or (ii) the maximum operational duration for intermittent energy resources if less than twelve (12) continuous hours. | MEDIUM | Pending Approval |  |  | GO
EOP-012-2 | Extreme Cold Weather Preparedness and Operations | R3. | Applicable to generating unit(s) in commercial operation prior to October 1, 2027: Each Generator Owner, for each generating unit that has a calculated Extreme Cold Weather Temperature at or below 32 degrees Fahrenheit (zero degrees Celsius) as determined in Requirement R1, and that self-commits or is required to operate at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius), shall: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning, Operations Planning] • Implement freeze protection measures to protect Generator Cold Weather Critical Components that provide the capability to operate at the unit(s)' Extreme Cold Weather Temperature; or • Develop a Corrective Action Plan to add new or modify existing freeze protection measures to provide the capability to operate at the unit(s)' Extreme Cold Weather Temperature. | MEDIUM | Pending Approval |  |  | GO
EOP-012-2 | Extreme Cold Weather Preparedness and Operations | R4. | Each Generator Owner shall implement and maintain one or more cold weather preparedness plan(s) for its generating units. The cold weather preparedness plan(s) shall include the following, at a minimum: [Violation Risk Factor: High] [Time Horizon: Operations Planning and Real-time Operations] | HIGH | Pending Approval |  |  | GO
EOP-012-2 | Extreme Cold Weather Preparedness and Operations | R4.1. | R4. Each Generator Owner shall implement and maintain one or more cold weather preparedness plan(s) for its generating units. The cold weather preparedness plan(s) shall include the following, at a minimum: 4.1. The lowest calculated Extreme Cold Weather Temperature for each unit, as determined in Requirement R1 | HIGH | Pending Approval |  |  | GO
EOP-012-2 | Extreme Cold Weather Preparedness and Operations | R4.2. | R4. Each Generator Owner shall implement and maintain one or more cold weather preparedness plan(s) for its generating units. The cold weather preparedness plan(s) shall include the following, at a minimum: 4.2. The generating unit cold weather data, as determined in Requirement R1.2 | HIGH | Pending Approval |  |  | GO
EOP-012-2 | Extreme Cold Weather Preparedness and Operations | R4.3. | R4. Each Generator Owner shall implement and maintain one or more cold weather preparedness plan(s) for its generating units. The cold weather preparedness plan(s) shall include the following, at a minimum: 4.3. Documentation identifying Generator Cold Weather Critical Components | HIGH | Pending Approval |  |  | GO
EOP-012-2 | Extreme Cold Weather Preparedness and Operations | R4.4. | R4. Each Generator Owner shall implement and maintain one or more cold weather preparedness plan(s) for its generating units. The cold weather preparedness plan(s) shall include the following, at a minimum: 4.4. Documentation of freeze protection measures implemented on Generator Cold Weather Critical Components which includes measures used to reduce the cooling effects of wind determined necessary by the Generator Owner to protect against heat loss, and where applicable, the effects of freezing precipitation (e.g., sleet, snow, ice, and freezing rain) | HIGH | Pending Approval |  |  | GO
EOP-012-2 | Extreme Cold Weather Preparedness and Operations | R4.5. | R4. Each Generator Owner shall implement and maintain one or more cold weather preparedness plan(s) for its generating units. The cold weather preparedness plan(s) shall include the following, at a minimum: 4.5. Annual inspection and maintenance of generating unit(s) freeze protection measures. | HIGH | Pending Approval |  |  | GO
EOP-012-2 | Extreme Cold Weather Preparedness and Operations | R5. | Each Generator Owner in conjunction with its Generator Operator shall identify the entity responsible for providing the generating unit-specific training, and that identified entity shall provide annual training to its maintenance or operations personnel responsible for implementing the cold weather preparedness plan(s) developed pursuant to Requirement R4. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning, Operations Planning] | MEDIUM | Pending Approval |  |  | GOP, GO
EOP-012-2 | Extreme Cold Weather Preparedness and Operations | R6. | Each Generator Owner shall, for each generating unit that has a calculated Extreme Cold Weather Temperature at or below 32 degrees Fahrenheit (zero degrees Celsius) as determined in Requirement R1 and that self-commits or is required to operate at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius), develop a Corrective Action Plan when the generating unit experiences a Generator Cold Weather Reliability Event. The Corrective Action Plan shall be developed within 150 days or by July 1, whichever is earlier, and contain at a minimum: [Violation Risk Factor: High] [Time Horizon: Long-term Planning] | HIGH | Pending Approval |  |  | GO
EOP-012-2 | Extreme Cold Weather Preparedness and Operations | R6.1. | R6. Each Generator Owner shall, for each generating unit that has a calculated Extreme Cold Weather Temperature at or below 32 degrees Fahrenheit (zero degrees Celsius) as determined in Requirement R1 and that self-commits or is required to operate at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius), develop a Corrective Action Plan when the generating unit experiences a Generator Cold Weather Reliability Event. The Corrective Action Plan shall be developed within 150 days or by July 1, whichever is earlier, and contain at a minimum: 6.1. A summary of the identified cause(s) for the Generator Cold Weather Reliability Event, where applicable, and any relevant associated data | HIGH | Pending Approval |  |  | GO
EOP-012-2 | Extreme Cold Weather Preparedness and Operations | R6.2. | R6. Each Generator Owner shall, for each generating unit that has a calculated Extreme Cold Weather Temperature at or below 32 degrees Fahrenheit (zero degrees Celsius) as determined in Requirement R1 and that self-commits or is required to operate at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius), develop a Corrective Action Plan when the generating unit experiences a Generator Cold Weather Reliability Event. The Corrective Action Plan shall be developed within 150 days or by July 1, whichever is earlier, and contain at a minimum: 6.2. A review of applicability to similar equipment at generating units owned by the Generator Owner | HIGH | Pending Approval |  |  | GO
EOP-012-2 | Extreme Cold Weather Preparedness and Operations | R6.3. | R6. Each Generator Owner shall, for each generating unit that has a calculated Extreme Cold Weather Temperature at or below 32 degrees Fahrenheit (zero degrees Celsius) as determined in Requirement R1 and that self-commits or is required to operate at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius), develop a Corrective Action Plan when the generating unit experiences a Generator Cold Weather Reliability Event. The Corrective Action Plan shall be developed within 150 days or by July 1, whichever is earlier, and contain at a minimum: 6.3. An identification of operating limitations or impacts to the cold weather preparedness plan that would apply until execution of the corrective action(s) identified in the Corrective Action Plan. | HIGH | Pending Approval |  |  | GO
EOP-012-2 | Extreme Cold Weather Preparedness and Operations | R7.1. | R7. Each Generator Owner, for each Corrective Action Plan developed pursuant to Requirements R1, R2, R3, or R6, shall: 7.1. Include a timetable for implementing the selected corrective action(s) that shall: 7.1.1. List the action(s) which address(es) existing equipment or freeze protection measures, if any, to be completed within 24 calendar monthsof completing development of the Corrective Action Plan; 7.1.2. List the action(s) which require(s) new equipment or freeze protection measures, if any, to be completed within 48 calendar months of completing development of the Corrective Action Plan; and 7.1.3. List the updates to the cold weather preparedness plan required under Requirement R4 to identify the updates or additions to the Generator Cold Weather Critical Components and their freeze protection measures | MEDIUM | Pending Approval |  |  | GO
EOP-012-2 | Extreme Cold Weather Preparedness and Operations | R7.2. | R7. Each Generator Owner, for each Corrective Action Plan developed pursuant to Requirements R1, R2, R3, or R6, shall: 7.2. Implement the Corrective Action Plan in accordance with the specified timetables in Requirement R7 Part 7.1 | MEDIUM | Pending Approval |  |  | GO
EOP-012-2 | Extreme Cold Weather Preparedness and Operations | R7.3. | R7. Each Generator Owner, for each Corrective Action Plan developed pursuant to Requirements R1, R2, R3, or R6, shall: 7.3. Update the Corrective Action Plan action(s) and timetable(s), with justification, if corrective action(s) change or timetable(s) exceed the timelines in Requirement R7 Part 7.1 | MEDIUM | Pending Approval |  |  | GO
EOP-012-2 | Extreme Cold Weather Preparedness and Operations | R7.4. | R7. Each Generator Owner, for each Corrective Action Plan developed pursuant to Requirements R1, R2, R3, or R6, shall: 7.4. Document in a declaration, with justification, any Generator Cold Weather Constraint that precludes the Generator Owner from implementing selected action(s) contained within the Corrective Action Plan. | MEDIUM | Pending Approval |  |  | GO
EOP-012-2 | Extreme Cold Weather Preparedness and Operations | R8.1. | R8. Each Generator Owner that creates a Generator Cold Weather Constraint declaration shall: 8.1. Review the Generator Cold Weather Constraint declaration at least every five calendar years or as needed when a change of status to the Generator Cold Weather Constraint occurs | MEDIUM | Pending Approval |  |  | GO
EOP-012-2 | Extreme Cold Weather Preparedness and Operations | R8.2. | R8. Each Generator Owner that creates a Generator Cold Weather Constraint declaration shall: 8.2. Update the operating limitations associated with capability and availability under Requirement R1 Part R1.2 if applicable. | MEDIUM | Pending Approval |  |  | GO
FAC-001-1 | Facility Connection Requirements | R1. | The Transmission Owner shall document, maintain, and publish Facility connection requirements to ensure compliance with NERC Reliability Standards and applicable Regional Entity, subregional, Power Pool, and individual Transmission Owner planning criteria and Facility connection requirements. The Transmission Owner’s Facility connection requirements shall address connection requirements for: | MEDIUM | Retired | 2013-11-25 | 2015-12-31 | TO
FAC-001-1 | Facility Connection Requirements | R1.1. | Generation Facilities, | MEDIUM | Retired | 2013-11-25 | 2015-12-31 | TO
FAC-001-1 | Facility Connection Requirements | R1.2. | Transmission Facilities, and | MEDIUM | Retired | 2013-11-25 | 2015-12-31 | TO
FAC-001-1 | Facility Connection Requirements | R1.3. | End-user Facilities | MEDIUM | Retired | 2013-11-25 | 2015-12-31 | TO
FAC-001-1 | Facility Connection Requirements | R2. | Each applicable Generator Owner shall, within 45 days of having an executed Agreement to evaluate the reliability impact of interconnecting a third party Facility to the Generator Owner’s existing Facility that is used to interconnect to the interconnected Transmission systems (under FAC-002-1), document and publish its Facility connection requirements to ensure compliance with NERC Reliability Standards and applicable Regional Entity, subregional, Power Pool, and individual Transmission Owner planning criteria and Facility connection requirements. | MEDIUM | Retired | 2013-11-25 | 2015-12-31 | TO
FAC-001-1 | Facility Connection Requirements | R3. | Each Transmission Owner and each applicable Generator Owner (in accordance with Requirement R2) shall address the following items in its Facility connection requirements: | MEDIUM | Retired | 2013-11-25 | 2015-12-31 | TO
FAC-001-1 | Facility Connection Requirements | R3.1. | Provide a written summary of its plans to achieve the required system performance as described in Requirements R1 or R2 throughout the planning horizon: | MEDIUM | Retired | 2013-11-25 | 2015-12-31 | TO
FAC-001-1 | Facility Connection Requirements | R3.1.1. | Procedures for coordinated joint studies of new Facilities and their impacts on the interconnected Transmission systems. | MEDIUM | Retired | 2013-11-25 | 2015-12-31 | TO
FAC-001-1 | Facility Connection Requirements | R3.1.10. | Power quality impacts. | MEDIUM | Retired | 2013-11-25 | 2015-12-31 | TO
FAC-001-1 | Facility Connection Requirements | R3.1.11. | Equipment Ratings. | MEDIUM | Retired | 2013-11-25 | 2015-12-31 | TO
FAC-001-1 | Facility Connection Requirements | R3.1.12. | Synchronizing of Facilities. | MEDIUM | Retired | 2013-11-25 | 2015-12-31 | TO
FAC-001-1 | Facility Connection Requirements | R3.1.13. | Maintenance coordination. | MEDIUM | Retired | 2013-11-25 | 2015-12-31 | TO
FAC-001-1 | Facility Connection Requirements | R3.1.14. | Operational issues (abnormal frequency and voltages). | MEDIUM | Retired | 2013-11-25 | 2015-12-31 | TO
FAC-001-1 | Facility Connection Requirements | R3.1.15. | Inspection requirements for existing or new Facilities. | MEDIUM | Retired | 2013-11-25 | 2015-12-31 | TO
FAC-001-1 | Facility Connection Requirements | R3.1.16. | Communications and procedures during normal and emergency operating conditions. | MEDIUM | Retired | 2013-11-25 | 2015-12-31 | TO
FAC-001-1 | Facility Connection Requirements | R3.1.2. | Procedures for notification of new or modified Facilities to others (those responsible for the reliability of the interconnected Transmission systems) as soon as feasible. | MEDIUM | Retired | 2013-11-25 | 2015-12-31 | TO
FAC-001-1 | Facility Connection Requirements | R3.1.3. | Voltage level and MW and MVAR capacity or demand at point of connection. | MEDIUM | Retired | 2013-11-25 | 2015-12-31 | TO
FAC-001-1 | Facility Connection Requirements | R3.1.4. | Breaker duty and surge protection. | MEDIUM | Retired | 2013-11-25 | 2015-12-31 | TO
FAC-001-1 | Facility Connection Requirements | R3.1.5. | System protection and coordination. | MEDIUM | Retired | 2013-11-25 | 2015-12-31 | TO
FAC-001-1 | Facility Connection Requirements | R3.1.6. | Metering and telecommunications. | MEDIUM | Retired | 2013-11-25 | 2015-12-31 | TO
FAC-001-1 | Facility Connection Requirements | R3.1.7. | Grounding and safety issues. | MEDIUM | Retired | 2013-11-25 | 2015-12-31 | TO
FAC-001-1 | Facility Connection Requirements | R3.1.8. | Insulation and insulation coordination. | MEDIUM | Retired | 2013-11-25 | 2015-12-31 | TO
FAC-001-1 | Facility Connection Requirements | R3.1.9. | Voltage, Reactive Power, and power factor control. | MEDIUM | Retired | 2013-11-25 | 2015-12-31 | TO
FAC-001-1 | Facility Connection Requirements | R4. | The Transmission Owner shall maintain and update its Facility connection requirements as required. The Transmission Owner shall make documentation of these requirements available to the users of the transmission system, the Regional Entity, and ERO on request (five business days). | MEDIUM | Retired | 2013-11-25 | 2015-12-31 | TO
FAC-001-2 | Facility Interconnection Requirements | R1. | Each Transmission Owner shall document Facility interconnection requirements, update them as needed, and make them available upon request. Each Transmission Owner’s Facility interconnection requirements shall address interconnection requirements for: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | Lower | Retired | 2016-01-01 | 2018-12-31 | TO
FAC-001-2 | Facility Interconnection Requirements | R1.1. | generation Facilities; | Lower | Retired | 2016-01-01 | 2018-12-31 | TO
FAC-001-2 | Facility Interconnection Requirements | R1.2. | transmission Facilities; and | Lower | Retired | 2016-01-01 | 2018-12-31 | TO
FAC-001-2 | Facility Interconnection Requirements | R1.3. | end-user Facilities. | Lower | Retired | 2016-01-01 | 2018-12-31 | TO
FAC-001-2 | Facility Interconnection Requirements | R2. | Each applicable Generator Owner shall document Facility interconnection requirements and make them available upon request within 45 calendar days of full execution of an Agreement to conduct a study on the reliability impact of interconnecting a third party Facility to the Generator Owner’s existing Facility that is used to interconnect to the Transmission system. [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | Lower | Retired | 2016-01-01 | 2018-12-31 | GO
FAC-001-2 | Facility Interconnection Requirements | R3. | Each Transmission Owner shall address the following items in its Facility interconnection requirements: [Violation Risk Factor: Lower] [Time Horizon: Long-Term Planning] | Lower | Retired | 2016-01-01 | 2018-12-31 | TO
FAC-001-2 | Facility Interconnection Requirements | R3.1. | Procedures for coordinated studies of new or materially modified existing interconnections and their impacts on affected system(s). | Lower | Retired | 2016-01-01 | 2018-12-31 | TO
FAC-001-2 | Facility Interconnection Requirements | R3.2. | Procedures for notifying those responsible for the reliability of affected system(s) of new or materially modified existing interconnections. | Lower | Retired | 2016-01-01 | 2018-12-31 | TO
FAC-001-2 | Facility Interconnection Requirements | R4. | Each applicable Generator Owner shall address the following items in its Facility interconnection requirements: [Violation Risk Factor: Lower] [Time Horizon: Long-Term Planning] | Lower | Retired | 2016-01-01 | 2018-12-31 | GO
FAC-001-2 | Facility Interconnection Requirements | R4.1. | Procedures for coordinated studies of new interconnections and their impacts on affected system(s). | Lower | Retired | 2016-01-01 | 2018-12-31 | GO
FAC-001-2 | Facility Interconnection Requirements | R4.2. | Procedures for notifying those responsible for the reliability of affected system(s) of new interconnections. | Lower | Retired | 2016-01-01 | 2018-12-31 | GO
FAC-001-3 | Facility Interconnection Requirements | R1. | Each Transmission Owner shall document Facility interconnection requirements, update them as needed, and make them available upon request. Each Transmission Owner’s Facility interconnection requirements shall address interconnection requirements for: | Lower | Effective | 2019-01-01 |  | TO
FAC-001-3 | Facility Interconnection Requirements | R1.1. | generation Facilities; | Lower | Effective | 2019-01-01 |  | TO
FAC-001-3 | Facility Interconnection Requirements | R1.2. | transmission Facilities; and | Lower | Effective | 2019-01-01 |  | TO
FAC-001-3 | Facility Interconnection Requirements | R1.3. | end-user Facilities. | Lower | Effective | 2019-01-01 |  | TO
FAC-001-3 | Facility Interconnection Requirements | R2. | Each applicable Generator Owner shall document Facility interconnection requirements and make them available upon request within 45 calendar days of full execution of an Agreement to conduct a study on the reliability impact of interconnecting a third party Facility to the Generator Owner’s existing Facility that is used to interconnect to the Transmission system. | Lower | Effective | 2019-01-01 |  | GO
FAC-001-3 | Facility Interconnection Requirements | R3. | Each Transmission Owner shall address the following items in its Facility interconnection requirements: | Lower | Effective | 2019-01-01 |  | TO
FAC-001-3 | Facility Interconnection Requirements | R3.1. | Procedures for coordinated studies of new or materially modified existing interconnections and their impacts on affected system(s). | Lower | Effective | 2019-01-01 |  | TO
FAC-001-3 | Facility Interconnection Requirements | R3.2. | Procedures for notifying those responsible for the reliability of affected system(s) of new or materially modified existing interconnections. | Lower | Effective | 2019-01-01 |  | TO
FAC-001-3 | Facility Interconnection Requirements | R3.3. | Procedures for confirming with those responsible for the reliability of affected systems that new or materially modified Facilities are within a Balancing Authority Area’s metered boundaries. | Lower | Effective | 2019-01-01 |  | TO
FAC-001-3 | Facility Interconnection Requirements | R4. | Each applicable Generator Owner shall address the following items in its Facility interconnection requirements: | Lower | Effective | 2019-01-01 |  | GO
FAC-001-3 | Facility Interconnection Requirements | R4.1. | Procedures for coordinated studies of new interconnections and their impacts on affected system(s). | Lower | Effective | 2019-01-01 |  | GO
FAC-001-3 | Facility Interconnection Requirements | R4.2. | Procedures for notifying those responsible for the reliability of affected system(s) of new interconnections. | Lower | Effective | 2019-01-01 |  | GO
FAC-001-3 | Facility Interconnection Requirements | R4.3. | Procedures for confirming with those responsible for the reliability of affected systems that new or materially modified Facilities are within a Balancing Authority Area’s metered boundaries. | Lower | Effective | 2019-01-01 |  | GO
FAC-001-4 | Facility Interconnection Requirements | R1. | Each Transmission Owner shall document Facility interconnection requirements, update them as needed, and make them available upon request. Each Transmission Owner’s Facility interconnection requirements shall address interconnection requirements for: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] 1.1. generation Facilities; 1.2. transmission Facilities; and 1.3. end-user Facilities. | LOWER | Effective | 2024-01-01 |  | TO
FAC-001-4 | Facility Interconnection Requirements | R2. | Each applicable Generator Owner shall document Facility interconnection requirements and make them available upon request within 45 calendar days of full execution of an Agreement to conduct a study on the reliability impact of interconnecting a third party Facility to the Generator Owner’s existing Facility that is used to interconnect to the Transmission system. [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | LOWER | Effective | 2024-01-01 |  | GO
FAC-001-4 | Facility Interconnection Requirements | R3.1. | R3. Each Transmission Owner shall address the following items in its Facility interconnection requirements: 3.1. Procedures for coordinated studies for new interconnections or existing interconnections seeking to make a qualified change as defined by the Planning Coordinator and their impacts on affected systems. | LOWER | Effective | 2024-01-01 |  | TO
FAC-001-4 | Facility Interconnection Requirements | R3.2. | R3. Each Transmission Owner shall address the following items in its Facility interconnection requirements: 3.2. Procedures for notifying those responsible for the reliability of affected system(s) of new interconnections or existing interconnections seeking to make a qualified change. | LOWER | Effective | 2024-01-01 |  | TO
FAC-001-4 | Facility Interconnection Requirements | R3.3. | R3. Each Transmission Owner shall address the following items in its Facility interconnection requirements: 3.3. Procedures for confirming with those responsible for the reliability of affected systems that new Facilities or existing Facilities seeking to make a qualified change are within a Balancing Authority Area. | LOWER | Effective | 2024-01-01 |  | TO
FAC-001-4 | Facility Interconnection Requirements | R4.1. | R4. Each applicable Generator Owner shall address the following items in its Facility interconnection requirements: 4.1. Procedures for coordinated studies of new interconnections and their impacts on affected system(s). | LOWER | Effective | 2024-01-01 |  | GO
FAC-001-4 | Facility Interconnection Requirements | R4.2. | R4. Each applicable Generator Owner shall address the following items in its Facility interconnection requirements: 4.2. Procedures for notifying those responsible for the reliability of affected system(s) of new interconnections. | LOWER | Effective | 2024-01-01 |  | GO
FAC-001-4 | Facility Interconnection Requirements | R4.3. | R4. Each applicable Generator Owner shall address the following items in its Facility interconnection requirements: 4.3. Procedures for confirming with those responsible for the reliability of affected systems that new Facilities or existing Facilities seeking to make a qualified change as defined by the Planning Coordinator are within a Balancing Authority Area. | LOWER | Effective | 2024-01-01 |  | GO
FAC-002-1 | Coordination of Plans For New Generation, Transmission, and End-User Facilities | R1. | The Generator Owner, Transmission Owner, Distribution Provider, and Load-Serving Entity seeking to integrate generation facilities, transmission facilities, and electricity end-user facilities shall each coordinate and cooperate on its assessments with its Transmission Planner and Planning Authority. The assessment shall include: | MEDIUM | Retired | 2012-04-01 | 2015-12-31 | TO, GO, DP
FAC-002-1 | Coordination of Plans For New Generation, Transmission, and End-User Facilities | R1.1. | Evaluation of the reliability impact of the new facilities and their connections on the interconnected transmission systems. | MEDIUM | Retired | 2012-04-01 | 2015-12-31 | TO, GO, DP
FAC-002-1 | Coordination of Plans For New Generation, Transmission, and End-User Facilities | R1.2. | Ensurance of compliance with NERC Reliability Standards and applicable Regional, subregional, Power Pool, and individual system planning criteria and facility connection requirements. | MEDIUM | Retired | 2012-04-01 | 2015-12-31 | TO, GO, DP
FAC-002-1 | Coordination of Plans For New Generation, Transmission, and End-User Facilities | R1.3. | Evidence that the parties involved in the assessment have coordinated and cooperated on the assessment of the reliability impacts of new facilities on the interconnected transmission systems. While these studies may be performed independently, the results shall be jointly evaluated and coordinated by the entities involved. | MEDIUM | Retired | 2012-04-01 | 2015-12-31 | TO, GO, DP
FAC-002-1 | Coordination of Plans For New Generation, Transmission, and End-User Facilities | R1.4. | Evidence that the assessment included steady-state, short-circuit, and dynamics studies as necessary to evaluate system performance under both normal and contingency conditions in accordance with Reliability Standards TPL-001-0, TPL-002-0, and TPL-003-0. | MEDIUM | Retired | 2012-04-01 | 2015-12-31 | TO, GO, DP
FAC-002-1 | Coordination of Plans For New Generation, Transmission, and End-User Facilities | R1.5. | Documentation that the assessment included study assumptions, system performance, alternatives considered, and jointly coordinated recommendations. | MEDIUM | Retired | 2012-04-01 | 2015-12-31 | TO, GO, DP
FAC-002-2 | Facility Interconnection Studies | R1. | Each Transmission Planner and each Planning Coordinator shall study the reliability impact of: (i) interconnecting new generation, transmission, or electricity end-user Facilities and (ii) materially modifying existing interconnections of generation, transmission, or electricity end-user Facilities. The following shall be studied: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Retired | 2016-01-01 | 2021-03-31 | TP, PC
FAC-002-2 | Facility Interconnection Studies | R1.1. | The reliability impact of the new interconnection, or materially modified existing interconnection, on affected system(s); | MEDIUM | Retired | 2016-01-01 | 2021-03-31 | TP, PC
FAC-002-2 | Facility Interconnection Studies | R1.2. | Adherence to applicable NERC Reliability Standards; regional and Transmission Owner planning criteria; and Facility interconnection requirements; | MEDIUM | Retired | 2016-01-01 | 2021-03-31 | TP, PC
FAC-002-2 | Facility Interconnection Studies | R1.3. | Steady-state, short-circuit, and dynamics studies, as necessary, to evaluate system performance under both normal and contingency conditions; and | MEDIUM | Retired | 2016-01-01 | 2021-03-31 | TP, PC
FAC-002-2 | Facility Interconnection Studies | R1.4. | Study assumptions, system performance, alternatives considered, and coordinated recommendations. While these studies may be performed independently, the results shall be evaluated and coordinated by the entities involved. | MEDIUM | Retired | 2016-01-01 | 2021-03-31 | TP, PC
FAC-002-2 | Facility Interconnection Studies | R2. | Each Generator Owner seeking to interconnect new generation Facilities, or to materially modify existing interconnections of generation Facilities, shall coordinate and cooperate on studies with its Transmission Planner or Planning Coordinator, including but not limited to the provision of data as described in R1, Parts 1.1-1.4. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Retired | 2016-01-01 | 2021-03-31 | GO
FAC-002-2 | Facility Interconnection Studies | R3. | Each Transmission Owner, each Distribution Provider, and each Load-Serving Entity seeking to interconnect new transmission Facilities or electricity end-user Facilities, or to materially modify existing interconnections of transmission Facilities or electricity end-user Facilities, shall coordinate and cooperate on studies with its Transmission Planner or Planning Coordinator, including but not limited to the provision of data as described in R1, Parts 1.1-1.4. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Retired | 2016-01-01 | 2021-03-31 | TO, DP
FAC-002-2 | Facility Interconnection Studies | R4. | Each Transmission Owner shall coordinate and cooperate with its Transmission Planner or Planning Coordinator on studies regarding requested new or materially modified interconnections to its Facilities, including but not limited to the provision of data as described in R1, Parts 1.1-1.4. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Retired | 2016-01-01 | 2021-03-31 | TO
FAC-002-2 | Facility Interconnection Studies | R5. | Each applicable Generator Owner shall coordinate and cooperate with its Transmission Planner or Planning Coordinator on studies regarding requested interconnections to its Facilities, including but not limited to the provision of data as described in R1, Parts 1.1-1.4. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Retired | 2016-01-01 | 2021-03-31 | GO
FAC-002-3 | Facility Interconnection Studies | R1. | Each Transmission Planner and each Planning Coordinator shall study the reliability impact of: (i) interconnecting new generation, transmission, or electricity end-user Facilities and (ii) materially modifying existing interconnections of generation, transmission, or electricity end-user Facilities. The following shall be studied: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2021-04-01 |  | GO, DP, TP, TO, PC
FAC-002-3 | Facility Interconnection Studies | R1.1. | The reliability impact of the new interconnection, or materially modified existing interconnection, on affected system(s); | MEDIUM | Effective | 2021-04-01 |  | GO, DP, TO, TP, PC
FAC-002-3 | Facility Interconnection Studies | R1.2. | Adherence to applicable NERC Reliability Standards; regional and Transmission Owner planning criteria; and Facility interconnection requirements; | MEDIUM | Effective | 2021-04-01 |  | GO, DP, TO, TP, PC
FAC-002-3 | Facility Interconnection Studies | R1.3. | Steady-state, short-circuit, and dynamics studies, as necessary, to evaluate system performance under both normal and contingency conditions; and | MEDIUM | Effective | 2021-04-01 |  | GO, DP, TO, TP, PC
FAC-002-3 | Facility Interconnection Studies | R1.4. | Study assumptions, system performance, alternatives considered, and coordinated recommendations. While these studies may be performed independently, the results shall be evaluated and coordinated by the entities involved. | MEDIUM | Effective | 2021-04-01 |  | GO, DP, TO, TP, PC
FAC-002-3 | Facility Interconnection Studies | R2. | Each Generator Owner seeking to interconnect new generation Facilities, or to materially modify existing interconnections of generation Facilities, shall coordinate and cooperate on studies with its Transmission Planner or Planning Coordinator, including but not limited to the provision of data as described in R1, Parts 1.1-1.4. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2021-04-01 |  | GO, DP, TO, TP, PC
FAC-002-3 | Facility Interconnection Studies | R3. | Each Transmission Owner and each Distribution Provider seeking to interconnect new transmission Facilities or electricity end-user Facilities, or to materially modify existing interconnections of transmission Facilities or electricity end-user Facilities, shall coordinate and cooperate on studies with its Transmission Planner or Planning Coordinator, including but not limited to the provision of data as described in R1, Parts 1.1-1.4. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2021-04-01 |  | GO, DP, TO, TP, PC
FAC-002-3 | Facility Interconnection Studies | R4. | Each Transmission Owner shall coordinate and cooperate with its Transmission Planner or Planning Coordinator on studies regarding requested new or materially modified interconnections to its Facilities, including but not limited to the provision of data as described in R1, Parts 1.1-1.4. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2021-04-01 |  | GO, DP, TO, TP, PC
FAC-002-3 | Facility Interconnection Studies | R5. | Each applicable Generator Owner shall coordinate and cooperate with its Transmission Planner or Planning Coordinator on studies regarding requested interconnections to its Facilities, including but not limited to the provision of data as described in R1, Parts 1.1-1.4. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2021-04-01 |  | GO, DP, TO, TP, PC
FAC-002-4 | Facility Interconnection Studies | R1. | Each Transmission Planner and each Planning Coordinator shall study the reliability impact of: (i) interconnecting new generation, transmission, or electricity end-user Facilities and (ii) existing interconnections of generation, transmission, or electricity end-user Facilities seeking to make a qualified change as defined by the Planning Coordinator under Requirement R6. The following shall be studied: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2024-01-01 |  | PC, TP
FAC-002-4 | Facility Interconnection Studies | R1.1. | R1. Each Transmission Planner and each Planning Coordinator shall study the reliability impact of: (i) interconnecting new generation, transmission, or electricity end-user Facilities and (ii) existing interconnections of generation, transmission, or electricity end-user Facilities seeking to make a qualified change as defined by the Planning Coordinator under Requirement R6. The following shall be studied: 1.1. The reliability impact of the new interconnection, or existing interconnection seeking to make a qualified change as defined by the Planning Coordinator under Requirement R6, on affected system(s) | MEDIUM | Effective | 2024-01-01 |  | PC, TP
FAC-002-4 | Facility Interconnection Studies | R1.2. | R1. Each Transmission Planner and each Planning Coordinator shall study the reliability impact of: (i) interconnecting new generation, transmission, or electricity end-user Facilities and (ii) existing interconnections of generation, transmission, or electricity end-user Facilities seeking to make a qualified change as defined by the Planning Coordinator under Requirement R6. The following shall be studied: 1.2. Adherence to applicable NERC Reliability Standards; regional and Transmission Owner planning criteria; and Facility interconnection requirements | MEDIUM | Effective | 2024-01-01 |  | PC, TP
FAC-002-4 | Facility Interconnection Studies | R1.3. | R1. Each Transmission Planner and each Planning Coordinator shall study the reliability impact of: (i) interconnecting new generation, transmission, or electricity end-user Facilities and (ii) existing interconnections of generation, transmission, or electricity end-user Facilities seeking to make a qualified change as defined by the Planning Coordinator under Requirement R6. The following shall be studied: 1.3. Steady-state, short-circuit, and dynamics studies, as necessary, to evaluate system performance under both normal and contingency conditions | MEDIUM | Effective | 2024-01-01 |  | PC, TP
FAC-002-4 | Facility Interconnection Studies | R1.4. | R1. Each Transmission Planner and each Planning Coordinator shall study the reliability impact of: (i) interconnecting new generation, transmission, or electricity end-user Facilities and (ii) existing interconnections of generation, transmission, or electricity end-user Facilities seeking to make a qualified change as defined by the Planning Coordinator under Requirement R6. The following shall be studied: 1.4. Study assumptions, system performance, alternatives considered, and coordinated recommendations. While these studies may be performed independently, the results shall be evaluated and coordinated by the entities involved. | MEDIUM | Effective | 2024-01-01 |  | PC, TP
FAC-002-4 | Facility Interconnection Studies | R2. | Each Generator Owner seeking to interconnect new generation Facilities, or existing interconnections of generation Facilities seeking to make a qualified change as defined by the Planning Coordinator under Requirement R6, shall coordinate and cooperate on studies with its Transmission Planner or Planning Coordinator, including but not limited to the provision of data as described in R1, Parts 1.1-1.4. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2024-01-01 |  | GO
FAC-002-4 | Facility Interconnection Studies | R3. | Each Transmission Owner and each Distribution Provider seeking to interconnect new transmission Facilities or electricity end-user Facilities, or existing interconnections of transmission Facilities or electricity end-user Facilities seeking to make a qualified change as defined by the Planning Coordinator under Requirement R6, shall coordinate and cooperate on studies with its Transmission Planner or Planning Coordinator, including but not limited to the provision of data as described in R1, Parts 1.1-1.4. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2024-01-01 |  | DP, TO
FAC-002-4 | Facility Interconnection Studies | R4. | Each Transmission Owner shall coordinate and cooperate with its Transmission Planner or Planning Coordinator on studies regarding requested new or existing interconnections seeking to make a qualified change as defined by the Planning Coordinator under Requirement R6, to its Facilities, including but not limited to the provision of data as described in R1, Parts 1.1-1.4. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2024-01-01 |  | TO
FAC-002-4 | Facility Interconnection Studies | R5. | Each applicable Generator Owner shall coordinate and cooperate with its Transmission Planner or Planning Coordinator on studies regarding requested interconnections to its Facilities, including but not limited to the provision of data as described in R1, Parts 1.1-1.4. [Violation Risk Factor: Medium] [Time Horizon: Longterm Planning] | MEDIUM | Effective | 2024-01-01 |  | GO
FAC-002-4 | Facility Interconnection Studies | R6. | Each Planning Coordinator shall maintain a publicly available definition of qualified change for the purposes of facility interconnection. [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | LOWER | Effective | 2024-01-01 |  | PC
FAC-003-2 | Transmission Vegetation Management | R1. | Each Transmission Owner shall manage vegetation to prevent encroachments into the MVCD of its applicable line(s) which are either an element of an IROL, or an element of a Major WECC Transfer Path; operating within their Rating and all Rated Electrical Operating Conditions of the types shown below2. 1. An encroachment into the MVCD as shown in FAC-003-Table 2, observed in Real-time, absent a Sustained Outage, [Violation Risk Factor: High] [Time Horizon: Real-time]: 2. An encroachment due to a fall-in from inside the ROW that caused a vegetation-related Sustained Outage, 3. An encroachment due to the blowing together of applicable lines and vegetation located inside the ROW that caused a vegetation-related Sustained Outage,4 4. An encroachment due to vegetation growth into the MVCD that caused a vegetation-related Sustained Outage.4 | HIGH | Retired |  |  | TO
FAC-003-2 | Transmission Vegetation Management | R2. | Each Transmission Owner shall manage vegetation to prevent encroachments into the MVCD of its applicable line(s) which are not either an element of an IROL, or an element of a Major WECC Transfer Path; operating within its Rating and all Rated Electrical Operating Conditions of the types shown below2 [Violation Risk Factor: Medium] [Time Horizon: Real-time]: 1. An encroachment into the MVCD, observed in Real-time, absent a Sustained Outage,3 2. An encroachment due to a fall-in from inside the ROW that caused a vegetation-related Sustained Outage,4 3. An encroachment due to blowing together of applicable lines and vegetation located inside the ROW that caused a vegetation-related Sustained Outage,4 4. An encroachment due to vegetation growth into the line MVCD that caused a vegetation-related Sustained Outage4 | HIGH | Retired |  |  | TO
FAC-003-2 | Transmission Vegetation Management | R3. | Each Transmission Owner shall have documented maintenance strategies or procedures or processes or specifications it uses to prevent the encroachment of vegetation into the MVCD of its applicable lines that accounts for the following: | LOWER | Retired |  |  | TO
FAC-003-2 | Transmission Vegetation Management | R3.1. | Movement of applicable line conductors under their Rating and all Rated Electrical Operating Conditions; | LOWER | Retired |  |  | TO
FAC-003-2 | Transmission Vegetation Management | R3.2. | Inter-relationships between vegetation growth rates, vegetation control methods, and inspection frequency. [Violation Risk Factor: Lower] [Time Horizon: Long Term Planning]: | LOWER | Retired |  |  | TO
FAC-003-2 | Transmission Vegetation Management | R4. | Each Transmission Owner, without any intentional time delay, shall notify the control center holding switching authority for the associated applicable line when the Transmission Owner has confirmed the existence of a vegetation condition that is likely to cause a Fault at any moment [Violation Risk Factor: Medium] [Time Horizon: Real-time]. | MEDIUM | Retired |  |  | TO
FAC-003-2 | Transmission Vegetation Management | R5. | When a Transmission Owner is constrained from performing vegetation work on an applicable line operating within its Rating and all Rated Electrical Operating Conditions, and the constraint may lead to a vegetation encroachment into the MVCD prior to the implementation of the next annual work plan, then the Transmission Owner shall take corrective action to ensure continued vegetation management to prevent encroachments [Violation Risk Factor: Medium] [Time Horizon: Operations Planning]. | MEDIUM | Retired |  |  | TO
FAC-003-2 | Transmission Vegetation Management | R6. | Each Transmission Owner shall perform a Vegetation Inspection of 100% of its applicable transmission lines (measured in units of choice - circuit, pole line, line miles or kilometers, etc.) at least once per calendar year and with no more than 18 calendar months between inspections on the same ROW5. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning]. | MEDIUM | Retired |  |  | TO
FAC-003-2 | Transmission Vegetation Management | R7. | Each Transmission Owner shall complete 100% of its annual vegetation work plan of applicable lines to ensure no vegetation encroachments occur within the MVCD. Modifications to the work plan in response to changing conditions or to findings from vegetation inspections may be made (provided they do not allow encroachment of vegetation into the MVCD) and must be documented. The percent completed calculation is based on the number of units actually completed divided by the number of units in the final amended plan (measured in units of choice - circuit, pole line, line miles or kilometers, etc.) Examples of reasons for modification to annual plan may include [Violation Risk Factor: Medium] [Time Horizon: Operations Planning]: • Change in expected growth rate/ environmental factors • Circumstances that are beyond the control of a Transmission Owner6 • Rescheduling work between growing seasons • Crew or contractor availability/ Mutual assistance agreements • Identified unanticipated high priority work • Weather conditions/Accessibility • Permitting delays • Land ownership changes/Change in land use by the landowner • Emerging technologies | MEDIUM | Retired |  |  | TO
FAC-003-3 | Transmission Vegetation Management | R1. | Each applicable Transmission Owner and applicable Generator Owner shall manage vegetation to prevent encroachments into the MVCD of its applicable line(s) which are either an element of an IROL, or an element of a Major WECC Transfer Path; operating within their Rating and all Rated Electrical Operating Conditions of the types shown below4 1. An encroachment into the MVCD as shown in FAC-003-Table 2, observed in Real-time, absent a Sustained Outage, [Violation Risk Factor: High] [Time Horizon: Real-time]: 2. An encroachment due to a fall-in from inside the ROW that caused a vegetation-related Sustained Outage, 3. An encroachment due to the blowing together of applicable lines and vegetation located inside the ROW that caused a vegetation-related Sustained Outage 4. An encroachment due to vegetation growth into the MVCD that caused a vegetation-related Sustained Outage., | HIGH | Retired | 2014-07-01 | 2016-09-30 | TO, GO
FAC-003-3 | Transmission Vegetation Management | R2. | Each applicable Transmission Owner and applicable Generator Owner shall manage vegetation to prevent encroachments into the MVCD of its applicable line(s) which are not either an element of an IROL, or an element of a Major WECC Transfer Path; operating within its Rating and all Rated Electrical Operating Conditions of the types shown below9 1. An encroachment into the MVCD, observed in Real-time, absent a Sustained Outage, [Violation Risk Factor: Medium] [Time Horizon: Real-time]: 2. An encroachment due to a fall-in from inside the ROW that caused a vegetation-related Sustained Outage, 3. An encroachment due to blowing together of applicable lines and vegetation located inside the ROW that caused a vegetation-related Sustained Outage, 4. An encroachment due to vegetation growth into the line MVCD that caused a vegetation-related Sustained Outage | HIGH | Retired | 2014-07-01 | 2016-09-30 | TO, GO
FAC-003-3 | Transmission Vegetation Management | R3. | Each applicable Transmission Owner and applicable Generator Owner shall have documented maintenance strategies or procedures or processes or specifications it uses to prevent the encroachment of vegetation into the MVCD of its applicable lines that accounts for the following: | LOWER | Retired | 2014-07-01 | 2016-09-30 | TO, GO
FAC-003-3 | Transmission Vegetation Management | R3.1. | Movement of applicable line conductors under their Rating and all Rated Electrical Operating Conditions; | LOWER | Retired | 2014-07-01 | 2016-09-30 | TO, GO
FAC-003-3 | Transmission Vegetation Management | R3.2. | Inter-relationships between vegetation growth rates, vegetation control methods, and inspection frequency. | LOWER | Retired | 2014-07-01 | 2016-09-30 | TO, GO
FAC-003-3 | Transmission Vegetation Management | R4. | Each applicable Transmission Owner and applicable Generator Owner, without any intentional time delay, shall notify the control center holding switching authority for the associated applicable line when the applicable Transmission Owner and applicable Generator Owner has confirmed the existence of a vegetation condition that is likely to cause a Fault at any moment | MEDIUM | Retired | 2014-07-01 | 2016-09-30 | TO, GO
FAC-003-3 | Transmission Vegetation Management | R5. | When a applicable Transmission Owner and applicable Generator Owner is constrained from performing vegetation work on an applicable line operating within its Rating and all Rated Electrical Operating Conditions, and the constraint may lead to a vegetation encroachment into the MVCD prior to the implementation of the next annual work plan, then the applicable Transmission Owner or applicable Generator Owner shall take corrective action to ensure continued vegetation management to prevent encroachments | MEDIUM | Retired | 2014-07-01 | 2016-09-30 | TO, GO
FAC-003-3 | Transmission Vegetation Management | R6. | Each applicable Transmission Owner and applicable Generator Owner shall perform a Vegetation Inspection of 100% of its applicable transmission lines (measured in units of choice - circuit, pole line, line miles or kilometers, etc.) at least once per calendar year and with no more than 18 calendar months between inspections on the same ROW14 | MEDIUM | Retired | 2014-07-01 | 2016-09-30 | TO, GO
FAC-003-3 | Transmission Vegetation Management | R7. | Each applicable Transmission Owner and applicable Generator Owner shall complete 100% of its annual vegetation work plan of applicable lines to ensure no vegetation encroachments occur within the MVCD. Modifications to the work plan in response to changing conditions or to findings from vegetation inspections may be made (provided they do not allow encroachment of vegetation into the MVCD) and must be documented. The percent completed calculation is based on the number of units actually completed divided by the number of units in the final amended plan (measured in units of choice - circuit, pole line, line miles or kilometers, etc.) Examples of reasons for modification to annual plan may include | MEDIUM | Retired | 2014-07-01 | 2016-09-30 | TO, GO
FAC-003-4 | Transmission Vegetation Management | R1. | Each applicable Transmission Owner and applicable Generator Owner shall manage vegetation to prevent encroachments into the Minimum Vegetation Clearance Distance (MVCD) of its applicable line(s) which are either an element of an IROL, or an element of a Major WECC Transfer Path; operating within their Rating and all Rated Electrical Operating Conditions of the types shown below4 : | HIGH | Effective | 2016-10-01 |  | TO, GO
FAC-003-4 | Transmission Vegetation Management | R1.1. | An encroachment into the MVCD as shown in FAC-003-Table 2, observed in Real-time, absent a Sustained Outage, | HIGH | Effective | 2016-10-01 |  | TO, GO
FAC-003-4 | Transmission Vegetation Management | R1.2. | An encroachment due to a fall-in from inside the ROW that caused a vegetation-related Sustained Outage, | HIGH | Effective | 2016-10-01 |  | TO, GO
FAC-003-4 | Transmission Vegetation Management | R1.3. | An encroachment due to the blowing together of applicable lines and vegetation located inside the ROW that caused a vegetation-related Sustained Outage | HIGH | Effective | 2016-10-01 |  | TO, GO
FAC-003-4 | Transmission Vegetation Management | R1.4. | An encroachment due to vegetation growth into the MVCD that caused a vegetation-related Sustained Outage. | HIGH | Effective | 2016-10-01 |  | TO, GO
FAC-003-4 | Transmission Vegetation Management | R2. | Each applicable Transmission Owner and applicable Generator Owner shall manage vegetation to prevent encroachments into the MVCD of its applicable line(s) which are not either an element of an IROL, or an element of a Major WECC Transfer Path; operating within its Rating and all Rated Electrical Operating Conditions of the types shown below | HIGH | Effective | 2016-10-01 |  | TO, GO
FAC-003-4 | Transmission Vegetation Management | R2.1. | An encroachment into the MVCD, observed in Real-time, absent a Sustained Outage | HIGH | Effective | 2016-10-01 |  | TO, GO
FAC-003-4 | Transmission Vegetation Management | R2.2. | An encroachment due to a fall-in from inside the ROW that caused a vegetation-related Sustained Outage, | HIGH | Effective | 2016-10-01 |  | TO, GO
FAC-003-4 | Transmission Vegetation Management | R2.3. | An encroachment due to the blowing together of applicable lines and vegetation located inside the ROW that caused a vegetation-related Sustained Outage, | HIGH | Effective | 2016-10-01 |  | TO, GO
FAC-003-4 | Transmission Vegetation Management | R2.4. | An encroachment due to vegetation growth into the line MVCD that caused a vegetation-related Sustained Outage. | HIGH | Effective | 2016-10-01 |  | TO, GO
FAC-003-4 | Transmission Vegetation Management | R3. | Each applicable Transmission Owner and applicable Generator Owner shall have documented maintenance strategies or procedures or processes or specifications it uses to prevent the encroachment of vegetation into the MVCD of its applicable lines that accounts for the following: | LOWER | Effective | 2016-10-01 |  | TO, GO
FAC-003-4 | Transmission Vegetation Management | R3.1. | Movement of applicable line conductors under their Rating and all Rated Electrical Operating Conditions; | LOWER | Effective | 2016-10-01 |  | TO, GO
FAC-003-4 | Transmission Vegetation Management | R3.2. | Inter-relationships between vegetation growth rates, vegetation control methods, and inspection frequency. | LOWER | Effective | 2016-10-01 |  | TO, GO
FAC-003-4 | Transmission Vegetation Management | R4. | Each applicable Transmission Owner and applicable Generator Owner, without any intentional time delay, shall notify the control center holding switching authority for the associated applicable line when the applicable Transmission Owner and applicable Generator Owner has confirmed the existence of a vegetation condition that is likely to cause a Fault at any moment | MEDIUM | Effective | 2016-10-01 |  | TO, GO
FAC-003-4 | Transmission Vegetation Management | R5. | When an applicable Transmission Owner and an applicable Generator Owner are constrained from performing vegetation work on an applicable line operating within its Rating and all Rated Electrical Operating Conditions, and the constraint may lead to a vegetation encroachment into the MVCD prior to the implementation of the next annual work plan, then the applicable Transmission Owner or applicable Generator Owner shall take corrective action to ensure continued vegetation management to prevent encroachments | MEDIUM | Effective | 2016-10-01 |  | TO, GO
FAC-003-4 | Transmission Vegetation Management | R6. | Each applicable Transmission Owner and applicable Generator Owner shall perform a Vegetation Inspection of 100% of its applicable transmission lines (measured in units of choice - circuit, pole line, line miles or kilometers, etc.) at least once per calendar year and with no more than 18 calendar months between inspections on the same ROW14 | MEDIUM | Effective | 2016-10-01 |  | TO, GO
FAC-003-4 | Transmission Vegetation Management | R7. | Each applicable Transmission Owner and applicable Generator Owner shall complete 100% of its annual vegetation work plan of applicable lines to ensure no vegetation encroachments occur within the MVCD. Modifications to the work plan in response to changing conditions or to findings from vegetation inspections may be made (provided they do not allow encroachment of vegetation into the MVCD) and must be documented. The percent completed calculation is based on the number of units actually completed divided by the number of units in the final amended plan (measured in units of choice - circuit, pole line, line miles or kilometers, etc.). Examples of reasons for modification to annual plan may include | MEDIUM | Effective | 2016-10-01 |  | TO, GO
FAC-003-4 | Transmission Vegetation Management | R7.1. | Change in expected growth rate/environmental factors | MEDIUM | Effective | 2016-10-01 |  | TO, GO
FAC-003-4 | Transmission Vegetation Management | R7.10. | Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. | MEDIUM | Effective | 2016-10-01 |  | TO, GO
FAC-003-4 | Transmission Vegetation Management | R7.2. | Circumstances that are beyond the control of an applicable Transmission Owner or applicable Generator Owner15 | MEDIUM | Effective | 2016-10-01 |  | TO, GO
FAC-003-4 | Transmission Vegetation Management | R7.3. | Rescheduling work between growing seasons | MEDIUM | Effective | 2016-10-01 |  | TO, GO
FAC-003-4 | Transmission Vegetation Management | R7.4. | Crew or contractor availability/Mutual assistance agreements | MEDIUM | Effective | 2016-10-01 |  | TO, GO
FAC-003-4 | Transmission Vegetation Management | R7.5. | Identified unanticipated high priority work | MEDIUM | Effective | 2016-10-01 |  | TO, GO
FAC-003-4 | Transmission Vegetation Management | R7.6. | Weather conditions/Accessibility | MEDIUM | Effective | 2016-10-01 |  | TO, GO
FAC-003-4 | Transmission Vegetation Management | R7.7. | Permitting delays | MEDIUM | Effective | 2016-10-01 |  | TO, GO
FAC-003-4 | Transmission Vegetation Management | R7.8. | Land ownership changes/Change in land use by the landowner | MEDIUM | Effective | 2016-10-01 |  | TO, GO
FAC-003-4 | Transmission Vegetation Management | R7.9. | Emerging technologies | MEDIUM | Effective | 2016-10-01 |  | TO, GO
FAC-003-5 | Transmission Vegetation Management | R1. | Each applicable Transmission Owner and applicable Generator Owner shall manage vegetation to prevent encroachments into the Minimum Vegetation Clearance Distance (MVCD) of its applicable line(s); operating within their Rating and all Rated Electrical Operating Conditions of the types shown below4 : | HIGH | Effective | 2024-04-01 |  | TO, GO
FAC-003-5 | Transmission Vegetation Management | R1.1. | An encroachment into the MVCD as shown in FAC-003-Table 2, observed in Real-time, absent a Sustained Outage, | HIGH | Effective | 2024-04-01 |  | TO, GO
FAC-003-5 | Transmission Vegetation Management | R1.2. | An encroachment due to a fall-in from inside the ROW that caused a vegetation-related Sustained Outage, | HIGH | Effective | 2024-04-01 |  | TO, GO
FAC-003-5 | Transmission Vegetation Management | R1.3. | An encroachment due to the blowing together of applicable lines and vegetation located inside the ROW that caused a vegetation-related Sustained Outage | HIGH | Effective | 2024-04-01 |  | TO, GO
FAC-003-5 | Transmission Vegetation Management | R1.4. | An encroachment due to vegetation growth into the MVCD that caused a vegetation-related Sustained Outage. | HIGH | Effective | 2024-04-01 |  | TO, GO
FAC-003-5 | Transmission Vegetation Management | R2. | Reserved for future use | HIGH | Effective | 2024-04-01 |  | TO, GO
FAC-003-5 | Transmission Vegetation Management | R3. | Each applicable Transmission Owner and applicable Generator Owner shall have documented maintenance strategies or procedures or processes or specifications it uses to prevent the encroachment of vegetation into the MVCD of its applicable lines that accounts for the following: | LOWER | Effective | 2024-04-01 |  | TO, GO
FAC-003-5 | Transmission Vegetation Management | R3.1. | Movement of applicable line conductors under their Rating and all Rated Electrical Operating Conditions; | LOWER | Effective | 2024-04-01 |  | TO, GO
FAC-003-5 | Transmission Vegetation Management | R3.2. | Inter-relationships between vegetation growth rates, vegetation control methods, and inspection frequency. | LOWER | Effective | 2024-04-01 |  | TO, GO
FAC-003-5 | Transmission Vegetation Management | R4. | Each applicable Transmission Owner and applicable Generator Owner, without any intentional time delay, shall notify the control center holding switching authority for the associated applicable line when the applicable Transmission Owner and applicable Generator Owner has confirmed the existence of a vegetation condition that is likely to cause a Fault at any moment | MEDIUM | Effective | 2024-04-01 |  | TO, GO
FAC-003-5 | Transmission Vegetation Management | R5. | When an applicable Transmission Owner and an applicable Generator Owner are constrained from performing vegetation work on an applicable line operating within its Rating and all Rated Electrical Operating Conditions, and the constraint may lead to a vegetation encroachment into the MVCD prior to the implementation of the next annual work plan, then the applicable Transmission Owner or applicable Generator Owner shall take corrective action to ensure continued vegetation management to prevent encroachments | MEDIUM | Effective | 2024-04-01 |  | TO, GO
FAC-003-5 | Transmission Vegetation Management | R6. | Each applicable Transmission Owner and applicable Generator Owner shall perform a Vegetation Inspection of 100% of its applicable transmission lines (measured in units of choice - circuit, pole line, line miles or kilometers, etc.) at least once per calendar year and with no more than 18 calendar months between inspections on the same ROW14 | MEDIUM | Effective | 2024-04-01 |  | TO, GO
FAC-003-5 | Transmission Vegetation Management | R7. | Each applicable Transmission Owner and applicable Generator Owner shall complete 100% of its annual vegetation work plan of applicable lines to ensure no vegetation encroachments occur within the MVCD. Modifications to the work plan in response to changing conditions or to findings from vegetation inspections may be made (provided they do not allow encroachment of vegetation into the MVCD) and must be documented. The percent completed calculation is based on the number of units actually completed divided by the number of units in the final amended plan (measured in units of choice - circuit, pole line, line miles or kilometers, etc.). Examples of reasons for modification to annual plan may include | MEDIUM | Effective | 2024-04-01 |  | TO, GO
FAC-003-5 | Transmission Vegetation Management | R7.1. | Change in expected growth rate/environmental factors | MEDIUM | Effective | 2024-04-01 |  | TO, GO
FAC-003-5 | Transmission Vegetation Management | R7.10. | Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. | MEDIUM | Effective | 2024-04-01 |  | TO, GO
FAC-003-5 | Transmission Vegetation Management | R7.2. | Circumstances that are beyond the control of an applicable Transmission Owner or applicable Generator Owner15 | MEDIUM | Effective | 2024-04-01 |  | TO, GO
FAC-003-5 | Transmission Vegetation Management | R7.3. | Rescheduling work between growing seasons | MEDIUM | Effective | 2024-04-01 |  | TO, GO
FAC-003-5 | Transmission Vegetation Management | R7.4. | Crew or contractor availability/Mutual assistance agreements | MEDIUM | Effective | 2024-04-01 |  | TO, GO
FAC-003-5 | Transmission Vegetation Management | R7.5. | Identified unanticipated high priority work | MEDIUM | Effective | 2024-04-01 |  | TO, GO
FAC-003-5 | Transmission Vegetation Management | R7.6. | Weather conditions/Accessibility | MEDIUM | Effective | 2024-04-01 |  | TO, GO
FAC-003-5 | Transmission Vegetation Management | R7.7. | Permitting delays | MEDIUM | Effective | 2024-04-01 |  | TO, GO
FAC-003-5 | Transmission Vegetation Management | R7.8. | Land ownership changes/Change in land use by the landowner | MEDIUM | Effective | 2024-04-01 |  | TO, GO
FAC-003-5 | Transmission Vegetation Management | R7.9. | Emerging technologies | MEDIUM | Effective | 2024-04-01 |  | TO, GO
FAC-008-2 | Facility Ratings | R1. | Each Generator Owner shall have documentation for determining the Facility Ratings of its solely and jointly owned generator Facility(ies) up to the low side terminals of the main step up transformer if the Generator Owner does not own the main step up transformer and the high side terminals of the main step up transformer if the Generator Owner owns the main step up transformer. |  | Never Came Into Effect in Ontario |  |  | GO
FAC-008-2 | Facility Ratings | R1.1. | The documentation shall contain assumptions used to rate the generator and at least one of the following: • Design or construction information such as design criteria, ratings provided by equipment manufacturers, equipment drawings and/or specifications, engineering analyses, method(s) consistent with industry standards (e.g. ANSI and IEEE), or an established engineering practice that has been verified by testing or engineering analysis. • Operational information such as commissioning test results, performance testing or historical performance records, any of which may be supplemented by engineering analyses. |  | Never Came Into Effect in Ontario |  |  | GO
FAC-008-2 | Facility Ratings | R1.2. | The documentation shall be consistent with the principle that the Facility Ratings do not exceed the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. |  | Never Came Into Effect in Ontario |  |  | GO
FAC-008-2 | Facility Ratings | R2. | Each Generator Owner shall have a documented methodology for determining Facility Ratings (Facility Ratings methodology) of its solely and jointly owned equipment connected between the location specified in R1 and the point of interconnection with the Transmission Owner that contains all of the following. |  | Never Came Into Effect in Ontario |  |  | GO
FAC-008-2 | Facility Ratings | R2.1. | The methodology used to establish the Ratings of the equipment that comprises the Facility(ies) shall be consistent with at least one of the following: • Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating. • One or more industry standards developed through an open process such as Institute of Electrical and Electronic Engineers (IEEE) or International Council on Large Electric Systems (CIGRE). • A practice that has been verified by testing, performance history or engineering analysis. |  | Never Came Into Effect in Ontario |  |  | GO
FAC-008-2 | Facility Ratings | R2.2. | The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R2, Part 2.1 including identification of how each of the following were considered: |  | Never Came Into Effect in Ontario |  |  | GO
FAC-008-2 | Facility Ratings | R2.2.1. | Equipment Rating standard(s) used in development of this methodology. |  | Never Came Into Effect in Ontario |  |  | GO
FAC-008-2 | Facility Ratings | R2.2.2. | Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. |  | Never Came Into Effect in Ontario |  |  | GO
FAC-008-2 | Facility Ratings | R2.2.3. | Ambient conditions (for particular or average conditions or as they vary in real-time). |  | Never Came Into Effect in Ontario |  |  | GO
FAC-008-2 | Facility Ratings | R2.2.4. | Operating limitations. |  | Never Came Into Effect in Ontario |  |  | GO
FAC-008-2 | Facility Ratings | R2.3. | A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. |  | Never Came Into Effect in Ontario |  |  | GO
FAC-008-2 | Facility Ratings | R2.4. | The process by which the Rating of equipment that comprises a Facility is determined. |  | Never Came Into Effect in Ontario |  |  | GO
FAC-008-2 | Facility Ratings | R2.4.1. | The scope of equipment addressed shall include, but not be limited to, conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. |  | Never Came Into Effect in Ontario |  |  | GO
FAC-008-2 | Facility Ratings | R2.4.2. | The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. |  | Never Came Into Effect in Ontario |  |  | GO
FAC-008-2 | Facility Ratings | R3. | Each Transmission Owner shall have a documented methodology for determining Facility Ratings (Facility Ratings methodology) of its solely and jointly owned Facilities (except for those generating unit Facilities addressed in R1 and R2) that contains all of the following: |  | Never Came Into Effect in Ontario |  |  | TO
FAC-008-2 | Facility Ratings | R3.1. | The methodology used to establish the Ratings of the equipment that comprises the Facility shall be consistent with at least one of the following: • Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating. • One or more industry standards developed through an open process such as Institute of Electrical and Electronics Engineers (IEEE) or International Council on Large Electric Systems (CIGRE). • A practice that has been verified by testing, performance history or engineering analysis. |  | Never Came Into Effect in Ontario |  |  | TO
FAC-008-2 | Facility Ratings | R3.2. | The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R3, Part 3.1 including identification of how each of the following were considered: |  | Never Came Into Effect in Ontario |  |  | TO
FAC-008-2 | Facility Ratings | R3.2.1. | Equipment Rating standard(s) used in development of this methodology. |  | Never Came Into Effect in Ontario |  |  | TO
FAC-008-2 | Facility Ratings | R3.2.2. | Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. |  | Never Came Into Effect in Ontario |  |  | TO
FAC-008-2 | Facility Ratings | R3.2.3. | Ambient conditions (for particular or average conditions or as they vary in real-time). |  | Never Came Into Effect in Ontario |  |  | TO
FAC-008-2 | Facility Ratings | R3.2.4. | Operating limitations. |  | Never Came Into Effect in Ontario |  |  | TO
FAC-008-2 | Facility Ratings | R3.3. | A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. |  | Never Came Into Effect in Ontario |  |  | TO
FAC-008-2 | Facility Ratings | R3.4. | The process by which the Rating of equipment that comprises a Facility is determined. |  | Never Came Into Effect in Ontario |  |  | TO
FAC-008-2 | Facility Ratings | R3.4.1. | The scope of equipment addressed shall include, but not be limited to, transmission conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. |  | Never Came Into Effect in Ontario |  |  | TO
FAC-008-2 | Facility Ratings | R3.4.2. | The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. |  | Never Came Into Effect in Ontario |  |  | TO
FAC-008-2 | Facility Ratings | R4. | Each Transmission Owner shall make its Facility Ratings methodology and each Generator Owner shall each make its documentation for determining its Facility Ratings and its Facility Ratings methodology available for inspection and technical review by those Reliability Coordinators, Transmission Operators, Transmission Planners and Planning Coordinators that have responsibility for the area in which the associated Facilities are located, within 21 calendar days of receipt of a request. |  | Never Came Into Effect in Ontario |  |  | TO, GO
FAC-008-2 | Facility Ratings | R5. | If a Reliability Coordinator, Transmission Operator, Transmission Planner or Planning Coordinator provides documented comments on its technical review of a Transmission Owner’s Facility Ratings methodology or Generator Owner’s documentation for determining its Facility Ratings and its Facility Rating methodology, the Transmission Owner or Generator Owner shall provide a response to that commenting entity within 45 calendar days of receipt of those comments. The response shall indicate whether a change will be made to the Facility Ratings methodology and, if no change will be made to that Facility Ratings methodology, the reason why. |  | Never Came Into Effect in Ontario |  |  | TO, GO
FAC-008-2 | Facility Ratings | R6. | Each Transmission Owner and Generator Owner shall have Facility Ratings for its solely and jointly owned Facilities that are consistent with the associated Facility Ratings methodology or documentation for determining its Facility Ratings. |  | Never Came Into Effect in Ontario |  |  | TO, GO
FAC-008-2 | Facility Ratings | R7. | Each Transmission Owner and Generator Owner shall provide Facility Ratings for its solely and jointly owned Facilities that are existing Facilities, new Facilities, modifications to existing Facilities and re-ratings of existing Facilities to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) as scheduled by such requesting entities. |  | Never Came Into Effect in Ontario |  |  | TO, GO
FAC-008-3 | Facility Ratings | R1. | Each Generator Owner shall have documentation for determining the Facility Ratings of its solely and jointly owned generator Facility(ies) up to the low side terminals of the main step up transformer if the Generator Owner does not own the main step up transformer and the high side terminals of the main step up transformer if the Generator Owner owns the main step up transformer. | LOWER | Retired | 2013-01-01 | 2021-09-30 | GO
FAC-008-3 | Facility Ratings | R1.1. | The documentation shall contain assumptions used to rate the generator and at least one of the following:• Design or construction information such as design criteria, ratings provided by equipment manufacturers, equipment drawings and/or specifications, engineering analyses, method(s) consistent with industry standards (e.g. ANSI and IEEE), or an established engineering practice that has been verified by testing or engineering analysis.• Operational information such as commissioning test results, performance testing or historical performance records, any of which may be supplemented by engineering analyses. | LOWER | Retired | 2013-01-01 | 2021-09-30 | GO
FAC-008-3 | Facility Ratings | R1.2. | The documentation shall be consistent with the principle that the Facility Ratings do not exceed the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. | LOWER | Retired | 2013-01-01 | 2021-09-30 | GO
FAC-008-3 | Facility Ratings | R2. | Each Generator Owner shall have a documented methodology for determining Facility Ratings (Facility Ratings methodology) of its solely and jointly owned equipment connected between the location specified in R1 and the point of interconnection with the Transmission Owner that contains all of the following. | MEDIUM | Retired | 2013-01-01 | 2021-09-30 | GO
FAC-008-3 | Facility Ratings | R2.1. | The methodology used to establish the Ratings of the equipment that comprises the Facility(ies) shall be consistent with at least one of the following:• Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating. • One or more industry standards developed through an open process such as Institute of Electrical and Electronic Engineers (IEEE) or International Council on Large Electric Systems (CIGRE).• A practice that has been verified by testing, performance history or engineering analysis. | MEDIUM | Retired | 2013-01-01 | 2021-09-30 | GO
FAC-008-3 | Facility Ratings | R2.2. | The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R2, Part 2.1 including identification of how each of the following were considered: | MEDIUM | Retired | 2013-01-01 | 2021-09-30 | GO
FAC-008-3 | Facility Ratings | R2.2.1. | Equipment Rating standard(s) used in development of this methodology. | MEDIUM | Retired | 2013-01-01 | 2021-09-30 | GO
FAC-008-3 | Facility Ratings | R2.2.2. | Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. | MEDIUM | Retired | 2013-01-01 | 2021-09-30 | GO
FAC-008-3 | Facility Ratings | R2.2.3. | Ambient conditions (for particular or average conditions or as they vary in real-time). | MEDIUM | Retired | 2013-01-01 | 2021-09-30 | GO
FAC-008-3 | Facility Ratings | R2.2.4. | Operating limitations.1 | MEDIUM | Retired | 2013-01-01 | 2021-09-30 | GO
FAC-008-3 | Facility Ratings | R2.3. | A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. | MEDIUM | Retired | 2013-01-01 | 2021-09-30 | GO
FAC-008-3 | Facility Ratings | R2.4. | The process by which the Rating of equipment that comprises a Facility is determined. | MEDIUM | Retired | 2013-01-01 | 2021-09-30 | GO
FAC-008-3 | Facility Ratings | R2.4.1. | The scope of equipment addressed shall include, but not be limited to, conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. | MEDIUM | Retired | 2013-01-01 | 2021-09-30 | GO
FAC-008-3 | Facility Ratings | R2.4.2. | The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. | MEDIUM | Retired | 2013-01-01 | 2021-09-30 | GO
FAC-008-3 | Facility Ratings | R3. | Each Transmission Owner shall have a documented methodology for determining Facility Ratings (Facility Ratings methodology) of its solely and jointly owned Facilities (except for those generating unit Facilities addressed in R1 and R2) that contains all of the following: | MEDIUM | Retired | 2013-01-01 | 2021-09-30 | TO
FAC-008-3 | Facility Ratings | R3.1. | The methodology used to establish the Ratings of the equipment that comprises the Facility shall be consistent with at least one of the following:• Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating.• One or more industry standards developed through an open process such as Institute of Electrical and Electronics Engineers (IEEE) or International Council on Large Electric Systems (CIGRE).• A practice that has been verified by testing, performance history or engineering analysis. | MEDIUM | Retired | 2013-01-01 | 2021-09-30 | TO
FAC-008-3 | Facility Ratings | R3.2. | The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R3, Part 3.1 including identification of how each of the following were considered: | MEDIUM | Retired | 2013-01-01 | 2021-09-30 | TO
FAC-008-3 | Facility Ratings | R3.2.1. | Equipment Rating standard(s) used in development of this methodology. | MEDIUM | Retired | 2013-01-01 | 2021-09-30 | TO
FAC-008-3 | Facility Ratings | R3.2.2. | Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. | MEDIUM | Retired | 2013-01-01 | 2021-09-30 | TO
FAC-008-3 | Facility Ratings | R3.2.3. | Ambient conditions (for particular or average conditions or as they vary in real-time). | MEDIUM | Retired | 2013-01-01 | 2021-09-30 | TO
FAC-008-3 | Facility Ratings | R3.2.4. | Operating limitations.2 | MEDIUM | Retired | 2013-01-01 | 2021-09-30 | TO
FAC-008-3 | Facility Ratings | R3.3. | A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. | MEDIUM | Retired | 2013-01-01 | 2021-09-30 | TO
FAC-008-3 | Facility Ratings | R3.4. | The process by which the Rating of equipment that comprises a Facility is determined. | MEDIUM | Retired | 2013-01-01 | 2021-09-30 | TO
FAC-008-3 | Facility Ratings | R3.4.1. | The scope of equipment addressed shall include, but not be limited to, transmission conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. | MEDIUM | Retired | 2013-01-01 | 2021-09-30 | TO
FAC-008-3 | Facility Ratings | R3.4.2. | The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. | MEDIUM | Retired | 2013-01-01 | 2021-09-30 | TO
FAC-008-3 | Facility Ratings | R6. | Each Transmission Owner and Generator Owner shall have Facility Ratings for its solely and jointly owned Facilities that are consistent with the associated Facility Ratings methodology or documentation for determining its Facility Ratings. | MEDIUM | Retired | 2013-01-01 | 2021-09-30 | TO, GO
FAC-008-3 | Facility Ratings | R7. | Each Generator Owner shall provide Facility Ratings (for its solely and jointly owned Facilities that are existing Facilities, new Facilities, modifications to existing Facilities and re-ratings of existing Facilities) to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) as scheduled by such requesting entities. | MEDIUM | Retired | 2013-01-01 | 2021-09-30 | GO
FAC-008-3 | Facility Ratings | R8. | Each Transmission Owner (and each Generator Owner subject to Requirement R2) shall provide requested information as specified below (for its solely and jointly owned Facilities that are existing Facilities, new Facilities, modifications to existing Facilities and re-ratings of existing Facilities) to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s): | MEDIUM | Retired | 2013-01-01 | 2021-09-30 | TO, GO
FAC-008-3 | Facility Ratings | R8.1. | As scheduled by the requesting entities: | MEDIUM | Retired | 2013-01-01 | 2021-09-30 | TO, GO
FAC-008-3 | Facility Ratings | R8.1.1. | Facility Ratings | MEDIUM | Retired | 2013-01-01 | 2021-09-30 | TO, GO
FAC-008-3 | Facility Ratings | R8.1.2. | Identity of the most limiting equipment of the Facilities | MEDIUM | Retired | 2013-01-01 | 2021-09-30 | TO, GO
FAC-008-3 | Facility Ratings | R8.2. | Within 30 calendar days (or a later date if specified by the requester), for any requested Facility with a Thermal Rating that limits the use of Facilities under the requester’s authority by causing any of the following: 1) An Interconnection Reliability Operating Limit, 2) A limitation of Total Transfer Capability, 3) An impediment to generator deliverability, or 4) An impediment to service to a major load center: | MEDIUM | Retired | 2013-01-01 | 2021-09-30 | TO, GO
FAC-008-3 | Facility Ratings | R8.2.1. | Identity of the existing next most limiting equipment of the Facility | MEDIUM | Retired | 2013-01-01 | 2021-09-30 | TO, GO
FAC-008-3 | Facility Ratings | R8.2.2. | The Thermal Rating for the next most limiting equipment identified in Requirement R8, Part 8.2.1. | MEDIUM | Retired | 2013-01-01 | 2021-09-30 | TO, GO
FAC-008-5 | Facility Ratings | R1. | Each Generator Owner shall have documentation for determining the Facility Ratings of its solely and jointly owned generator Facility(ies) up to the low side terminals of the main step up transformer if the Generator Owner does not own the main step up transformer and the high side terminals of the main step up transformer if the Generator Owner owns the main step up transformer. | LOWER | Effective | 2021-10-01 |  | GO
FAC-008-5 | Facility Ratings | R1.1. | The documentation shall contain assumptions used to rate the generator and at least one of the following:• Design or construction information such as design criteria, ratings provided by equipment manufacturers, equipment drawings and/or specifications, engineering analyses, method(s) consistent with industry standards (e.g. ANSI and IEEE), or an established engineering practice that has been verified by testing or engineering analysis.• Operational information such as commissioning test results, performance testing or historical performance records, any of which may be supplemented by engineering analyses. | LOWER | Effective | 2021-10-01 |  | GO
FAC-008-5 | Facility Ratings | R1.2. | The documentation shall be consistent with the principle that the Facility Ratings do not exceed the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. | LOWER | Effective | 2021-10-01 |  | GO
FAC-008-5 | Facility Ratings | R2. | Each Generator Owner shall have a documented methodology for determining Facility Ratings (Facility Ratings methodology) of its solely and jointly owned equipment connected between the location specified in R1 and the point of interconnection with the Transmission Owner that contains all of the following. | MEDIUM | Effective | 2021-10-01 |  | GO
FAC-008-5 | Facility Ratings | R2.1. | The methodology used to establish the Ratings of the equipment that comprises the Facility(ies) shall be consistent with at least one of the following:• Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating. • One or more industry standards developed through an open process such as Institute of Electrical and Electronic Engineers (IEEE) or International Council on Large Electric Systems (CIGRE).• A practice that has been verified by testing, performance history or engineering analysis. | MEDIUM | Effective | 2021-10-01 |  | GO
FAC-008-5 | Facility Ratings | R2.2. | The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R2, Part 2.1 including identification of how each of the following were considered: | MEDIUM | Effective | 2021-10-01 |  | GO
FAC-008-5 | Facility Ratings | R2.2.1. | Equipment Rating standard(s) used in development of this methodology. | MEDIUM | Effective | 2021-10-01 |  | GO
FAC-008-5 | Facility Ratings | R2.2.2. | Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. | MEDIUM | Effective | 2021-10-01 |  | GO
FAC-008-5 | Facility Ratings | R2.2.3. | Ambient conditions (for particular or average conditions or as they vary in real-time). | MEDIUM | Effective | 2021-10-01 |  | GO
FAC-008-5 | Facility Ratings | R2.2.4. | Operating limitations.1 | MEDIUM | Effective | 2021-10-01 |  | GO
FAC-008-5 | Facility Ratings | R2.3. | A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. | MEDIUM | Effective | 2021-10-01 |  | GO
FAC-008-5 | Facility Ratings | R2.4. | The process by which the Rating of equipment that comprises a Facility is determined. | MEDIUM | Effective | 2021-10-01 |  | GO
FAC-008-5 | Facility Ratings | R2.4.1. | The scope of equipment addressed shall include, but not be limited to, conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. | MEDIUM | Effective | 2021-10-01 |  | GO
FAC-008-5 | Facility Ratings | R2.4.2. | The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. | MEDIUM | Effective | 2021-10-01 |  | GO
FAC-008-5 | Facility Ratings | R3. | Each Transmission Owner shall have a documented methodology for determining Facility Ratings (Facility Ratings methodology) of its solely and jointly owned Facilities (except for those generating unit Facilities addressed in R1 and R2) that contains all of the following: | MEDIUM | Effective | 2021-10-01 |  | TO
FAC-008-5 | Facility Ratings | R3.1. | The methodology used to establish the Ratings of the equipment that comprises the Facility shall be consistent with at least one of the following:• Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating.• One or more industry standards developed through an open process such as Institute of Electrical and Electronics Engineers (IEEE) or International Council on Large Electric Systems (CIGRE).• A practice that has been verified by testing, performance history or engineering analysis. | MEDIUM | Effective | 2021-10-01 |  | TO
FAC-008-5 | Facility Ratings | R3.2. | The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R3, Part 3.1 including identification of how each of the following were considered: | MEDIUM | Effective | 2021-10-01 |  | TO
FAC-008-5 | Facility Ratings | R3.2.1. | Equipment Rating standard(s) used in development of this methodology. | MEDIUM | Effective | 2021-10-01 |  | TO
FAC-008-5 | Facility Ratings | R3.2.2. | Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. | MEDIUM | Effective | 2021-10-01 |  | TO
FAC-008-5 | Facility Ratings | R3.2.3. | Ambient conditions (for particular or average conditions or as they vary in real-time). | MEDIUM | Effective | 2021-10-01 |  | TO
FAC-008-5 | Facility Ratings | R3.2.4. | Operating limitations.2 | MEDIUM | Effective | 2021-10-01 |  | TO
FAC-008-5 | Facility Ratings | R3.3. | A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. | MEDIUM | Effective | 2021-10-01 |  | TO
FAC-008-5 | Facility Ratings | R3.4. | The process by which the Rating of equipment that comprises a Facility is determined. | MEDIUM | Effective | 2021-10-01 |  | TO
FAC-008-5 | Facility Ratings | R3.4.1. | The scope of equipment addressed shall include, but not be limited to, transmission conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. | MEDIUM | Effective | 2021-10-01 |  | TO
FAC-008-5 | Facility Ratings | R3.4.2. | The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. | MEDIUM | Effective | 2021-10-01 |  | TO
FAC-008-5 | Facility Ratings | R6. | Each Transmission Owner and Generator Owner shall have Facility Ratings for its solely and jointly owned Facilities that are consistent with the associated Facility Ratings methodology or documentation for determining its Facility Ratings. | MEDIUM | Effective | 2021-10-01 |  | TO, GO
FAC-008-5 | Facility Ratings | R8. | Each Transmission Owner (and each Generator Owner subject to Requirement R2) shall provide requested information as specified below (for its solely and jointly owned Facilities that are existing Facilities, new Facilities, modifications to existing Facilities and re-ratings of existing Facilities) to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s): | MEDIUM | Effective | 2021-10-01 |  | TO, GO
FAC-008-5 | Facility Ratings | R8.1. | As scheduled by the requesting entities: | MEDIUM | Effective | 2021-10-01 |  | TO, GO
FAC-008-5 | Facility Ratings | R8.1.1. | Facility Ratings | MEDIUM | Effective | 2021-10-01 |  | TO, GO
FAC-008-5 | Facility Ratings | R8.1.2. | Identity of the most limiting equipment of the Facilities | MEDIUM | Effective | 2021-10-01 |  | TO, GO
FAC-008-5 | Facility Ratings | R8.2. | Within 30 calendar days (or a later date if specified by the requester), for any requested Facility with a Thermal Rating that limits the use of Facilities under the requester’s authority by causing any of the following: 1) An Interconnection Reliability Operating Limit, 2) A limitation of Total Transfer Capability, 3) An impediment to generator deliverability, or 4) An impediment to service to a major load center: | MEDIUM | Effective | 2021-10-01 |  | TO, GO
FAC-008-5 | Facility Ratings | R8.2.1. | Identity of the existing next most limiting equipment of the Facility | MEDIUM | Effective | 2021-10-01 |  | TO, GO
FAC-008-5 | Facility Ratings | R8.2.2. | The Thermal Rating for the next most limiting equipment identified in Requirement R8, Part 8.2.1. | MEDIUM | Effective | 2021-10-01 |  | TO, GO
FAC-010-2.1 | System Operating Limits Methodology for the Planning Horizon | R1. | The Planning Authority shall have a documented SOL Methodology for use in developing SOLs within its Planning Authority Area. This SOL Methodology shall: | LOWER | Retired | 2010-04-11 | 2017-03-31 | PA
FAC-010-2.1 | System Operating Limits Methodology for the Planning Horizon | R1.1. | Be applicable for developing SOLs used in the planning horizon. | LOWER | Retired | 2010-04-11 | 2017-03-31 | PA
FAC-010-2.1 | System Operating Limits Methodology for the Planning Horizon | R1.2. | State that SOLs shall not exceed associated Facility Ratings. | LOWER | Retired | 2010-04-11 | 2017-03-31 | PA
FAC-010-2.1 | System Operating Limits Methodology for the Planning Horizon | R1.3. | Include a description of how to identify the subset of SOLs that qualify as IROLs. | LOWER | Retired | 2010-04-11 | 2017-03-31 | PA
FAC-010-2.1 | System Operating Limits Methodology for the Planning Horizon | R2. | The Planning Authority’s SOL Methodology shall include a requirement that SOLs provide BES performance consistent with the following: | No Individual VRF Assigned | Retired | 2010-04-11 | 2017-03-31 | PA
FAC-010-2.1 | System Operating Limits Methodology for the Planning Horizon | R2.1. | In the pre-contingency state and with all Facilities in service, the BES shall demonstrate transient, dynamic and voltage stability; all Facilities shall be within their Facility Ratings and within their thermal, voltage and stability limits. In the determination of SOLs, the BES condition used shall reflect expected system conditions and shall reflect changes to system topology such as Facility outages. | HIGH | Retired | 2010-04-11 | 2017-03-31 | PA
FAC-010-2.1 | System Operating Limits Methodology for the Planning Horizon | R2.2. | Following the single Contingencies identified in Requirement 2.2.1 through Requirement 2.2.3, the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading or uncontrolled separation shall not occur. | HIGH | Retired | 2010-04-11 | 2017-03-31 | PA
FAC-010-2.1 | System Operating Limits Methodology for the Planning Horizon | R2.2.1. | Single line to ground or three-phase Fault (whichever is more severe), with Normal Clearing, on any Faulted generator, line, transformer, or shunt device. | MEDIUM | Retired | 2010-04-11 | 2017-03-31 | PA
FAC-010-2.1 | System Operating Limits Methodology for the Planning Horizon | R2.2.2. | Loss of any generator, line, transformer, or shunt device without a Fault. | MEDIUM | Retired | 2010-04-11 | 2017-03-31 | PA
FAC-010-2.1 | System Operating Limits Methodology for the Planning Horizon | R2.2.3. | Single pole block, with Normal Clearing, in a monopolar or bipolar high voltage direct current system. | MEDIUM | Retired | 2010-04-11 | 2017-03-31 | PA
FAC-010-2.1 | System Operating Limits Methodology for the Planning Horizon | R2.3. | Starting with all Facilities in service, the system’s response to a single Contingency, may include any of the following: | MEDIUM | Retired | 2010-04-11 | 2017-03-31 | PA
FAC-010-2.1 | System Operating Limits Methodology for the Planning Horizon | R2.3.1. | Planned or controlled interruption of electric supply to radial customers or some local network customers connected to or supplied by the Faulted Facility or by the affected area. | MEDIUM | Retired | 2010-04-11 | 2017-03-31 | PA
FAC-010-2.1 | System Operating Limits Methodology for the Planning Horizon | R2.3.2. | System reconfiguration through manual or automatic control or protection actions. | MEDIUM | Retired | 2010-04-11 | 2017-03-31 | PA
FAC-010-2.1 | System Operating Limits Methodology for the Planning Horizon | R2.4. | To prepare for the next Contingency, system adjustments may be made, including changes to generation, uses of the transmission system, and the transmission system topology. | MEDIUM | Retired | 2010-04-11 | 2017-03-31 | PA
FAC-010-2.1 | System Operating Limits Methodology for the Planning Horizon | R2.5. | Starting with all Facilities in service and following any of the multiple Contingencies identified in Reliability Standard TPL-003 the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading or uncontrolled separation shall not occur. | MEDIUM | Retired | 2010-04-11 | 2017-03-31 | PA
FAC-010-2.1 | System Operating Limits Methodology for the Planning Horizon | R2.6. | In determining the system’s response to any of the multiple Contingencies, identified in Reliability Standard TPL-003, in addition to the actions identified in R2.3.1 and R2.3.2, the following shall be acceptable: | MEDIUM | Retired | 2010-04-11 | 2017-03-31 | PA
FAC-010-2.1 | System Operating Limits Methodology for the Planning Horizon | R2.6.1. | Planned or controlled interruption of electric supply to customers (load shedding), the planned removal from service of certain generators, and/or the curtailment of contracted Firm (non-recallable reserved) electric power Transfers. | MEDIUM | Retired | 2010-04-11 | 2017-03-31 | PA
FAC-010-2.1 | System Operating Limits Methodology for the Planning Horizon | R3. | The Planning Authority’s methodology for determining SOLs, shall include, as a minimum, a description of the following, along with any reliability margins applied for each: | LOWER | Retired | 2010-04-11 | 2017-03-31 | PA
FAC-010-2.1 | System Operating Limits Methodology for the Planning Horizon | R3.1. | Study model (must include at least the entire Planning Authority Area as well as the critical Real-Time Applications details from other Planning Authority Areas that would impact the Facility or Facilities under study). | LOWER | Retired | 2010-04-11 | 2017-03-31 | PA
FAC-010-2.1 | System Operating Limits Methodology for the Planning Horizon | R3.2. | Selection of applicable Contingencies. | LOWER | Retired | 2010-04-11 | 2017-03-31 | PA
FAC-010-2.1 | System Operating Limits Methodology for the Planning Horizon | R3.3. | Level of detail of system models used to determine SOLs. | LOWER | Retired | 2010-04-11 | 2017-03-31 | PA
FAC-010-2.1 | System Operating Limits Methodology for the Planning Horizon | R3.4. | Allowed uses of Special Protection Systems or Remedial Action Plans. | MEDIUM | Retired | 2010-04-11 | 2017-03-31 | PA
FAC-010-2.1 | System Operating Limits Methodology for the Planning Horizon | R3.5. | Anticipated transmission system configuration, generation dispatch and Load level. | LOWER | Retired | 2010-04-11 | 2017-03-31 | PA
FAC-010-2.1 | System Operating Limits Methodology for the Planning Horizon | R3.6. | Criteria for determining when violating a SOL qualifies as an Interconnection Reliability Operating Limit (IROL) and criteria for developing any associated IROL Tv. | MEDIUM | Retired | 2010-04-11 | 2017-03-31 | PA
FAC-010-2.1 | System Operating Limits Methodology for the Planning Horizon | R4. | The Planning Authority shall issue its SOL Methodology, and any change to that methodology, to all of the following prior to the effectiveness of the change: | LOWER | Retired | 2010-04-11 | 2017-03-31 | PA
FAC-010-2.1 | System Operating Limits Methodology for the Planning Horizon | R4.1. | Each adjacent Planning Authority and each Planning Authority that indicated it has a reliability-related need for the methodology. | LOWER | Retired | 2010-04-11 | 2017-03-31 | PA
FAC-010-2.1 | System Operating Limits Methodology for the Planning Horizon | R4.2. | Each Reliability Coordinator and Transmission Operator that operates any portion of the Planning Authority’s Planning Authority Area. | LOWER | Retired | 2010-04-11 | 2017-03-31 | PA
FAC-010-2.1 | System Operating Limits Methodology for the Planning Horizon | R4.3. | Each Transmission Planner that works in the Planning Authority’s Planning Authority Area. | LOWER | Retired | 2010-04-11 | 2017-03-31 | PA
FAC-010-3 | System Operating Limits Methodology for the Planning Horizon | R1. | The Planning Authority shall have a documented SOL Methodology for use in developing SOLs within its Planning Authority Area. This SOL Methodology shall: | LOWER | Effective | 2017-04-01 |  | PA
FAC-010-3 | System Operating Limits Methodology for the Planning Horizon | R1.1. | Be applicable for developing SOLs used in the planning horizon. | LOWER | Effective | 2017-04-01 |  | PA
FAC-010-3 | System Operating Limits Methodology for the Planning Horizon | R1.2. | State that SOLs shall not exceed associated Facility Ratings. | LOWER | Effective | 2017-04-01 |  | PA
FAC-010-3 | System Operating Limits Methodology for the Planning Horizon | R1.3. | Include a description of how to identify the subset of SOLs that qualify as IROLs. | LOWER | Effective | 2017-04-01 |  | PA
FAC-010-3 | System Operating Limits Methodology for the Planning Horizon | R2. | The Planning Authority’s SOL Methodology shall include a requirement that SOLs provide BES performance consistent with the following: | No Individual VRF Assigned | Effective | 2017-04-01 |  | PA
FAC-010-3 | System Operating Limits Methodology for the Planning Horizon | R2.1. | In the pre-contingency state and with all Facilities in service, the BES shall demonstrate transient, dynamic and voltage stability; all Facilities shall be within their Facility Ratings and within their thermal, voltage and stability limits. In the determination of SOLs, the BES condition used shall reflect expected system conditions and shall reflect changes to system topology such as Facility outages. | HIGH | Effective | 2017-04-01 |  | PA
FAC-010-3 | System Operating Limits Methodology for the Planning Horizon | R2.2. | Following the single Contingencies1 identified in Requirement 2.2.1 through Requirement 2.2.3, the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading or uncontrolled separation shall not occur. | HIGH | Effective | 2017-04-01 |  | PA
FAC-010-3 | System Operating Limits Methodology for the Planning Horizon | R2.2.1. | Single line to ground or three-phase Fault (whichever is more severe), with Normal Clearing, on any Faulted generator, line, transformer, or shunt device. | MEDIUM | Effective | 2017-04-01 |  | PA
FAC-010-3 | System Operating Limits Methodology for the Planning Horizon | R2.2.2. | Loss of any generator, line, transformer, or shunt device without a Fault. | MEDIUM | Effective | 2017-04-01 |  | PA
FAC-010-3 | System Operating Limits Methodology for the Planning Horizon | R2.2.3. | Single pole block, with Normal Clearing, in a monopolar or bipolar high voltage direct current system. | MEDIUM | Effective | 2017-04-01 |  | PA
FAC-010-3 | System Operating Limits Methodology for the Planning Horizon | R2.3. | Starting with all Facilities in service, the system’s response to a single Contingency, may include any of the following: | MEDIUM | Effective | 2017-04-01 |  | PA
FAC-010-3 | System Operating Limits Methodology for the Planning Horizon | R2.3.1. | Planned or controlled interruption of electric supply to radial customers or some local network customers connected to or supplied by the Faulted Facility or by the affected area. | MEDIUM | Effective | 2017-04-01 |  | PA
FAC-010-3 | System Operating Limits Methodology for the Planning Horizon | R2.3.2. | System reconfiguration through manual or automatic control or protection actions. | MEDIUM | Effective | 2017-04-01 |  | PA
FAC-010-3 | System Operating Limits Methodology for the Planning Horizon | R2.4. | To prepare for the next Contingency, system adjustments may be made, including changes to generation, uses of the transmission system, and the transmission system topology. | MEDIUM | Effective | 2017-04-01 |  | PA
FAC-010-3 | System Operating Limits Methodology for the Planning Horizon | R2.5. | Starting with all Facilities in service and following any of the multiple Contingencies identified in Reliability Standard TPL-003 the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading or uncontrolled separation shall not occur. | MEDIUM | Effective | 2017-04-01 |  | PA
FAC-010-3 | System Operating Limits Methodology for the Planning Horizon | R2.6. | In determining the system’s response to any of the multiple Contingencies, identified in Reliability Standard TPL-003, in addition to the actions identified in R2.3.1 and R2.3.2, the following shall be acceptable: | MEDIUM | Effective | 2017-04-01 |  | PA
FAC-010-3 | System Operating Limits Methodology for the Planning Horizon | R2.6.1. | Planned or controlled interruption of electric supply to customers (load shedding), the planned removal from service of certain generators, and/or the curtailment of contracted Firm (non-recallable reserved) electric power Transfers. | MEDIUM | Effective | 2017-04-01 |  | PA
FAC-010-3 | System Operating Limits Methodology for the Planning Horizon | R3. | The Planning Authority’s methodology for determining SOLs, shall include, as a minimum, a description of the following, along with any reliability margins applied for each: | LOWER | Effective | 2017-04-01 |  | PA
FAC-010-3 | System Operating Limits Methodology for the Planning Horizon | R3.1. | Study model (must include at least the entire Planning Authority Area as well as the critical Real-Time Applications details from other Planning Authority Areas that would impact the Facility or Facilities under study). | LOWER | Effective | 2017-04-01 |  | PA
FAC-010-3 | System Operating Limits Methodology for the Planning Horizon | R3.2. | Selection of applicable Contingencies. | LOWER | Effective | 2017-04-01 |  | PA
FAC-010-3 | System Operating Limits Methodology for the Planning Horizon | R3.3. | Level of detail of system models used to determine SOLs. | LOWER | Effective | 2017-04-01 |  | PA
FAC-010-3 | System Operating Limits Methodology for the Planning Horizon | R3.4. | Allowed uses of Remedial Action Schemes. | MEDIUM | Effective | 2017-04-01 |  | PA
FAC-010-3 | System Operating Limits Methodology for the Planning Horizon | R3.5. | Anticipated transmission system configuration, generation dispatch and Load level. | LOWER | Effective | 2017-04-01 |  | PA
FAC-010-3 | System Operating Limits Methodology for the Planning Horizon | R3.6. | Criteria for determining when violating a SOL qualifies as an Interconnection Reliability Operating Limit (IROL) and criteria for developing any associated IROL Tv. | MEDIUM | Effective | 2017-04-01 |  | PA
FAC-010-3 | System Operating Limits Methodology for the Planning Horizon | R4. | The Planning Authority shall issue its SOL Methodology, and any change to that methodology, to all of the following prior to the effectiveness of the change: | LOWER | Effective | 2017-04-01 |  | PA
FAC-010-3 | System Operating Limits Methodology for the Planning Horizon | R4.1. | Each adjacent Planning Authority and each Planning Authority that indicated it has a reliability-related need for the methodology. | LOWER | Effective | 2017-04-01 |  | PA
FAC-010-3 | System Operating Limits Methodology for the Planning Horizon | R4.2. | Each Reliability Coordinator and Transmission Operator that operates any portion of the Planning Authority’s Planning Authority Area. | LOWER | Effective | 2017-04-01 |  | PA
FAC-010-3 | System Operating Limits Methodology for the Planning Horizon | R4.3. | Each Transmission Planner that works in the Planning Authority’s Planning Authority Area. | LOWER | Effective | 2017-04-01 |  | PA
FAC-011-2 | System Operating Limits Methodology for the Operations Horizon | R1. | The Reliability Coordinator shall have a documented methodology for use in developing SOLs (SOL Methodology) within its Reliability Coordinator Area. This SOL Methodology shall: | LOWER | Retired | 2008-11-15 | 2017-03-31 | RC
FAC-011-2 | System Operating Limits Methodology for the Operations Horizon | R1.1. | Be applicable for developing SOLs used in the operations horizon. | LOWER | Retired | 2008-11-15 | 2017-03-31 | RC
FAC-011-2 | System Operating Limits Methodology for the Operations Horizon | R1.2. | State that SOLs shall not exceed associated Facility Ratings. | LOWER | Retired | 2008-11-15 | 2017-03-31 | RC
FAC-011-2 | System Operating Limits Methodology for the Operations Horizon | R1.3. | Include a description of how to identify the subset of SOLs that qualify as IROLs. | LOWER | Retired | 2008-11-15 | 2017-03-31 | RC
FAC-011-2 | System Operating Limits Methodology for the Operations Horizon | R2. | The Reliability Coordinator’s SOL Methodology shall include a requirement that SOLs provide BES performance consistent with the following: | No Individual VRF Assigned | Retired | 2008-11-15 | 2017-03-31 | RC
FAC-011-2 | System Operating Limits Methodology for the Operations Horizon | R2.1. | In the pre-contingency state, the BES shall demonstrate transient, dynamic and voltage stability; all Facilities shall be within their Facility Ratings and within their thermal, voltage and stability limits. In the determination of SOLs, the BES condition used shall reflect current or expected system conditions and shall reflect changes to system topology such as Facility outages. | HIGH | Retired | 2008-11-15 | 2017-03-31 | RC
FAC-011-2 | System Operating Limits Methodology for the Operations Horizon | R2.2. | Following the single Contingencies identified in Requirement 2.2.1 through Requirement 2.2.3, the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading or uncontrolled separation shall not occur. | HIGH | Retired | 2008-11-15 | 2017-03-31 | RC
FAC-011-2 | System Operating Limits Methodology for the Operations Horizon | R2.2.1. | Single line to ground or 3-phase Fault (whichever is more severe), with Normal Clearing, on any Faulted generator, line, transformer, or shunt device. | MEDIUM | Retired | 2008-11-15 | 2017-03-31 | RC
FAC-011-2 | System Operating Limits Methodology for the Operations Horizon | R2.2.2. | Loss of any generator, line, transformer, or shunt device without a Fault. | MEDIUM | Retired | 2008-11-15 | 2017-03-31 | RC
FAC-011-2 | System Operating Limits Methodology for the Operations Horizon | R2.2.3. | Single pole block, with Normal Clearing, in a monopolar or bipolar high voltage direct current system. | MEDIUM | Retired | 2008-11-15 | 2017-03-31 | RC
FAC-011-2 | System Operating Limits Methodology for the Operations Horizon | R2.3. | In determining the system’s response to a single Contingency, the following shall be acceptable: | MEDIUM | Retired | 2008-11-15 | 2017-03-31 | RC
FAC-011-2 | System Operating Limits Methodology for the Operations Horizon | R2.3.1. | Planned or controlled interruption of electric supply to radial customers or some local network customers connected to or supplied by the Faulted Facility or by the affected area. | MEDIUM | Retired | 2008-11-15 | 2017-03-31 | RC
FAC-011-2 | System Operating Limits Methodology for the Operations Horizon | R2.3.2. | Interruption of other network customers, (a) only if the system has already been adjusted, or is being adjusted, following at least one prior outage, or (b) if the real-time operating conditions are more adverse than anticipated in the corresponding studies | MEDIUM | Retired | 2008-11-15 | 2017-03-31 | RC
FAC-011-2 | System Operating Limits Methodology for the Operations Horizon | R2.3.3. | System reconfiguration through manual or automatic control or protection actions. | MEDIUM | Retired | 2008-11-15 | 2017-03-31 | RC
FAC-011-2 | System Operating Limits Methodology for the Operations Horizon | R2.4. | To prepare for the next Contingency, system adjustments may be made, including changes to generation, uses of the transmission system, and the transmission system topology. | MEDIUM | Retired | 2008-11-15 | 2017-03-31 | RC
FAC-011-2 | System Operating Limits Methodology for the Operations Horizon | R3. | The Reliability Coordinator’s methodology for determining SOLs, shall include, as a minimum, a description of the following, along with any reliability margins applied for each: | MEDIUM | Retired | 2008-11-15 | 2017-03-31 | RC
FAC-011-2 | System Operating Limits Methodology for the Operations Horizon | R3.1. | Study model (must include at least the entire Reliability Coordinator Area as well as the critical Real-Time Applications details from other Reliability Coordinator Areas that would impact the Facility or Facilities under study.) | MEDIUM | Retired | 2008-11-15 | 2017-03-31 | RC
FAC-011-2 | System Operating Limits Methodology for the Operations Horizon | R3.2. | Selection of applicable Contingencies | MEDIUM | Retired | 2008-11-15 | 2017-03-31 | RC
FAC-011-2 | System Operating Limits Methodology for the Operations Horizon | R3.3. | A process for determining which of the stability limits associated with the list of multiple contingencies (provided by the Planning Authority in accordance with FAC-014 Requirement 6) are applicable for use in the operating horizon given the actual or expected system conditions. | MEDIUM | Retired | 2008-11-15 | 2017-03-31 | RC
FAC-011-2 | System Operating Limits Methodology for the Operations Horizon | R3.3.1. | This process shall address the need to modify these limits, to modify the list of limits, and to modify the list of associated multiple contingencies. | No Individual VRF Assigned | Retired | 2008-11-15 | 2017-03-31 | RC
FAC-011-2 | System Operating Limits Methodology for the Operations Horizon | R3.4. | Level of detail of system models used to determine SOLs. | LOWER | Retired | 2008-11-15 | 2017-03-31 | RC
FAC-011-2 | System Operating Limits Methodology for the Operations Horizon | R3.5. | Allowed uses of Special Protection Systems or Remedial Action Plans. | MEDIUM | Retired | 2008-11-15 | 2017-03-31 | RC
FAC-011-2 | System Operating Limits Methodology for the Operations Horizon | R3.6. | Anticipated transmission system configuration, generation dispatch and Load level | MEDIUM | Retired | 2008-11-15 | 2017-03-31 | RC
FAC-011-2 | System Operating Limits Methodology for the Operations Horizon | R3.7. | Criteria for determining when violating a SOL qualifies as an Interconnection Reliability Operating Limit (IROL) and criteria for developing any associated IROL Tv. | MEDIUM | Retired | 2008-11-15 | 2017-03-31 | RC
FAC-011-2 | System Operating Limits Methodology for the Operations Horizon | R4. | The Reliability Coordinator shall issue its SOL Methodology and any changes to that methodology, prior to the effectiveness of the Methodology or of a change to the Methodology, to all of the following: | LOWER | Retired | 2008-11-15 | 2017-03-31 | RC
FAC-011-2 | System Operating Limits Methodology for the Operations Horizon | R4.1. | Each adjacent Reliability Coordinator and each Reliability Coordinator that indicated it has a reliability-related need for the methodology. | LOWER | Retired | 2008-11-15 | 2017-03-31 | RC
FAC-011-2 | System Operating Limits Methodology for the Operations Horizon | R4.2. | Each Planning Authority and Transmission Planner that models any portion of the Reliability Coordinator’s Reliability Coordinator Area. | LOWER | Retired | 2008-11-15 | 2017-03-31 | RC
FAC-011-2 | System Operating Limits Methodology for the Operations Horizon | R4.3. | Each Transmission Operator that operates in the Reliability Coordinator Area. | LOWER | Retired | 2008-11-15 | 2017-03-31 | RC
FAC-011-3 | System Operating Limits Methodology for the Operations Horizon | R1. | The Reliability Coordinator shall have a documented methodology for use in developing SOLs (SOL Methodology) within its Reliability Coordinator Area. This SOL Methodology shall: | LOWER | Effective | 2017-04-01 |  | RC
FAC-011-3 | System Operating Limits Methodology for the Operations Horizon | R1.1. | Be applicable for developing SOLs used in the operations horizon. | LOWER | Effective | 2017-04-01 |  | RC
FAC-011-3 | System Operating Limits Methodology for the Operations Horizon | R1.2. | State that SOLs shall not exceed associated Facility Ratings. | LOWER | Effective | 2017-04-01 |  | RC
FAC-011-3 | System Operating Limits Methodology for the Operations Horizon | R1.3. | Include a description of how to identify the subset of SOLs that qualify as IROLs. | LOWER | Effective | 2017-04-01 |  | RC
FAC-011-3 | System Operating Limits Methodology for the Operations Horizon | R2. | The Reliability Coordinator’s SOL Methodology shall include a requirement that SOLs provide BES performance consistent with the following: | No Individual VRF Assigned | Effective | 2017-04-01 |  | RC
FAC-011-3 | System Operating Limits Methodology for the Operations Horizon | R2.1. | In the pre-contingency state, the BES shall demonstrate transient, dynamic and voltage stability; all Facilities shall be within their Facility Ratings and within their thermal, voltage and stability limits. In the determination of SOLs, the BES condition used shall reflect current or expected system conditions and shall reflect changes to system topology such as Facility outages. | HIGH | Effective | 2017-04-01 |  | RC
FAC-011-3 | System Operating Limits Methodology for the Operations Horizon | R2.2. | Following the single Contingencies identified in Requirement 2.2.1 through Requirement 2.2.3, the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading or uncontrolled separation shall not occur. | HIGH | Effective | 2017-04-01 |  | RC
FAC-011-3 | System Operating Limits Methodology for the Operations Horizon | R2.2.1. | Single line to ground or 3-phase Fault (whichever is more severe), with Normal Clearing, on any Faulted generator, line, transformer, or shunt device. | MEDIUM | Effective | 2017-04-01 |  | RC
FAC-011-3 | System Operating Limits Methodology for the Operations Horizon | R2.2.2. | Loss of any generator, line, transformer, or shunt device without a Fault. | MEDIUM | Effective | 2017-04-01 |  | RC
FAC-011-3 | System Operating Limits Methodology for the Operations Horizon | R2.2.3. | Single pole block, with Normal Clearing, in a monopolar or bipolar high voltage direct current system. | MEDIUM | Effective | 2017-04-01 |  | RC
FAC-011-3 | System Operating Limits Methodology for the Operations Horizon | R2.3. | In determining the system’s response to a single Contingency, the following shall be acceptable: | MEDIUM | Effective | 2017-04-01 |  | RC
FAC-011-3 | System Operating Limits Methodology for the Operations Horizon | R2.3.1. | Planned or controlled interruption of electric supply to radial customers or some local network customers connected to or supplied by the Faulted Facility or by the affected area. | MEDIUM | Effective | 2017-04-01 |  | RC
FAC-011-3 | System Operating Limits Methodology for the Operations Horizon | R2.3.2. | Interruption of other network customers, (a) only if the system has already been adjusted, or is being adjusted, following at least one prior outage, or (b) if the real-time operating conditions are more adverse than anticipated in the corresponding studies | MEDIUM | Effective | 2017-04-01 |  | RC
FAC-011-3 | System Operating Limits Methodology for the Operations Horizon | R2.3.3. | System reconfiguration through manual or automatic control or protection actions. | MEDIUM | Effective | 2017-04-01 |  | RC
FAC-011-3 | System Operating Limits Methodology for the Operations Horizon | R2.4. | To prepare for the next Contingency, system adjustments may be made, including changes to generation, uses of the transmission system, and the transmission system topology. | MEDIUM | Effective | 2017-04-01 |  | RC
FAC-011-3 | System Operating Limits Methodology for the Operations Horizon | R3. | The Reliability Coordinator’s methodology for determining SOLs, shall include, as a minimum, a description of the following, along with any reliability margins applied for each: | MEDIUM | Effective | 2017-04-01 |  | RC
FAC-011-3 | System Operating Limits Methodology for the Operations Horizon | R3.1. | Study model (must include at least the entire Reliability Coordinator Area as well as the critical Real-Time Applications details from other Reliability Coordinator Areas that would impact the Facility or Facilities under study.) | MEDIUM | Effective | 2017-04-01 |  | RC
FAC-011-3 | System Operating Limits Methodology for the Operations Horizon | R3.2. | Selection of applicable Contingencies | MEDIUM | Effective | 2017-04-01 |  | RC
FAC-011-3 | System Operating Limits Methodology for the Operations Horizon | R3.3. | A process for determining which of the stability limits associated with the list of multiple contingencies (provided by the Planning Authority in accordance with FAC-014 Requirement 6) are applicable for use in the operating horizon given the actual or expected system conditions. | MEDIUM | Effective | 2017-04-01 |  | RC
FAC-011-3 | System Operating Limits Methodology for the Operations Horizon | R3.3.1. | This process shall address the need to modify these limits, to modify the list of limits, and to modify the list of associated multiple contingencies. | No Individual VRF Assigned | Effective | 2017-04-01 |  | RC
FAC-011-3 | System Operating Limits Methodology for the Operations Horizon | R3.4. | Level of detail of system models used to determine SOLs. | LOWER | Effective | 2017-04-01 |  | RC
FAC-011-3 | System Operating Limits Methodology for the Operations Horizon | R3.5. | Allowed uses of Remedial Action Plans. | MEDIUM | Effective | 2017-04-01 |  | RC
FAC-011-3 | System Operating Limits Methodology for the Operations Horizon | R3.6. | Anticipated transmission system configuration, generation dispatch and Load level | MEDIUM | Effective | 2017-04-01 |  | RC
FAC-011-3 | System Operating Limits Methodology for the Operations Horizon | R3.7. | Criteria for determining when violating a SOL qualifies as an Interconnection Reliability Operating Limit (IROL) and criteria for developing any associated IROL Tv. | MEDIUM | Effective | 2017-04-01 |  | RC
FAC-011-3 | System Operating Limits Methodology for the Operations Horizon | R4. | The Reliability Coordinator shall issue its SOL Methodology and any changes to that methodology, prior to the effectiveness of the Methodology or of a change to the Methodology, to all of the following: | LOWER | Effective | 2017-04-01 |  | RC
FAC-011-3 | System Operating Limits Methodology for the Operations Horizon | R4.1. | Each adjacent Reliability Coordinator and each Reliability Coordinator that indicated it has a reliability-related need for the methodology. | LOWER | Effective | 2017-04-01 |  | RC
FAC-011-3 | System Operating Limits Methodology for the Operations Horizon | R4.2. | Each Planning Authority and Transmission Planner that models any portion of the Reliability Coordinator’s Reliability Coordinator Area. | LOWER | Effective | 2017-04-01 |  | RC
FAC-011-3 | System Operating Limits Methodology for the Operations Horizon | R4.3. | Each Transmission Operator that operates in the Reliability Coordinator Area. | LOWER | Effective | 2017-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R1. | Each Reliability Coordinator shall have a documented methodology for establishing SOLs (i.e., SOL methodology) within its Reliability Coordinator Area. | MEDIUM | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R1. | Each Reliability Coordinator shall have a documented methodology for establishing SOLs (i.e., SOL methodology) within its Reliability Coordinator Area. | MEDIUM | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R2. | Each Reliability Coordinator shall include in its SOL methodology the method for Transmission Operators to determine which owner-provided Facility Ratings are to be used in operations such that the Transmission Operator and its Reliability Coordinator use common Facility Ratings | MEDIUM | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R3. | Each Reliability Coordinator shall include in its SOL methodology the method for Transmission Operators to determine the System Voltage Limits to be used in operations. The method shall: | MEDIUM | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R3.1. | Require that each BES bus/station have an associated System Voltage Limits, unless its SOL methodology specifically allows the exclusion of BES buses/stations from the requirement to have an associated System Voltage Limit; | MEDIUM | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R3.2. | Require that System Voltage Limits respect voltage-based Facility Ratings; | MEDIUM | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R3.3. | Require that System Voltage Limits are greater than or equal to in-service BES relay settings for undervoltage load shedding systems and Undervoltage Load Shedding Programs; | MEDIUM | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R3.4. | Identify the minimum allowable System Voltage Limit; | MEDIUM | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R3.5. | Define the method for determining common System Voltage Limits between the Reliability Coordinator and its Transmission Operators, between adjacent Transmission Operators, and between adjacent Reliability Coordinators within an Interconnection | MEDIUM | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R4. | Each Reliability Coordinator shall include in its SOL methodology the method for determining the stability limits to be used in operations. The method shall: | MEDIUM | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R4.1. | Specify stability performance criteria, including any margins applied. The criteria shall, at a minimum, include the following: | MEDIUM | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R4.1.1. | steady-state voltage stability; | MEDIUM | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R4.1.2. | transient voltage response; | MEDIUM | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R4.1.3. | angular stability; and | MEDIUM | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R4.1.4. | System damping. | MEDIUM | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R4.2. | Require that stability limits are established to meet the criteria specified in Part 4.1 for the Contingencies identified in Requirement R5 applicable to the establishment of stability limits that are expected to produce more severe System impacts on its portion of the BES. | MEDIUM | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R4.3. | Describe how the Reliability Coordinator establishes stability limits when there is an impact to more than one Transmission Operator in its Reliability Coordinator Area or other Reliability Coordinator Areas. | MEDIUM | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R4.4. | Describe how stability limits are determined, considering levels of transfers, Load and generation dispatch, and System conditions including any changes to System topology such as Facility outages. | MEDIUM | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R4.5. | Describe the level of detail that is required for the study model(s), including the portion modeled of the Reliability Coordinator Area, and the critical modeling details from other Reliability Coordinator Areas, necessary to determine different types of stability limits. | MEDIUM | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R4.6. | Describe the allowed uses of Remedial Action Schemes and other automatic post-Contingency mitigation actions in establishing stability limits used in operations. | MEDIUM | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R4.7. | State that the use of underfrequency load shedding (UFLS) programs and Undervoltage Load Shedding (UVLS) Programs are not allowed in the establishment of stability limits. | MEDIUM | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R5. | Each Reliability Coordinator shall identify in its SOL methodology the set of Contingency events for use in determining stability limits and the set of Contingency events for use in performing Operational Planning Analysis (OPAs) and Real-time Assessments (RTAs). The SOL methodology for each set shall: | MEDIUM | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R5.1. | Specify the following single Contingency events | MEDIUM | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R5.1.1. | Loss of any of the following either by single phase to ground or three phase Fault (whichever is more severe) with Normal Clearing, or without a Fault: • generator; • transmission circuit; • transformer; • shunt device; or • single pole block in a monopolar or bipolar high voltage direct current system. | MEDIUM | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R5.2. | Specify additional single or multiple Contingency events or types of Contingency events, if any. | MEDIUM | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R5.3. | Describe the method(s) for identifying which, if any, of the Contingency events provided by the Planning Coordinator or Transmission Planner in accordance with FAC-014-3, Requirement R7, to use in determining stability limits. | MEDIUM | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R6. | Each Reliability Coordinator shall include the following performance framework in its SOL methodology to determine SOL exceedances when performing Real-time monitoring, Real-time Assessments, and Operational Planning Analyses: | HIGH | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R6.1. | System performance for no Contingencies demonstrates the following: | HIGH | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R6.1.1. | Steady state flow through Facilities are within Normal Ratings; however, Emergency Ratings may be used when System adjustments to return the flow within its Normal Rating could be executed and completed within the specified time duration of those Emergency Ratings. | HIGH | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R6.1.2. | Steady state voltages are within normal System Voltage Limits; however, emergency System Voltage Limits may be used when System adjustments to return the voltage within its normal System Voltage Limits could be executed and completed within the specified time duration of those emergency System Voltage Limits. | HIGH | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R6.1.3. | Predetermined stability limits are not exceeded. | HIGH | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R6.1.4. | Instability, Cascading or uncontrolled separation that adversely impact the reliability of the Bulk Electric System does not occur. 1 | HIGH | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R6.2. | System performance for the single Contingencies listed in Part 5.1 demonstrates the following: | HIGH | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R6.2.1. | Steady state post-Contingency flow through Facilities within applicable Emergency Ratings. Steady state post-Contingency flow through a Facility must not be above the Facility’s highest Emergency Rating. | HIGH | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R6.2.2. | Steady state post-Contingency voltages are within emergency System Voltage Limits. | HIGH | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R6.2.3. | The stability performance criteria defined in the Reliability Coordinator’s SOL methodology are met1 . | HIGH | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R6.2.4. | Instability, Cascading or uncontrolled separation that adversely impact the reliability of the Bulk Electric System does not occur1 . | HIGH | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R6.3. | System performance for applicable Contingencies identified in Part 5.2 demonstrates that: instability, Cascading, or uncontrolled separation that adversely impact the reliability of the Bulk Electric System does not occur. | HIGH | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R6.4. | In determining the System’s response to any Contingency identified in Requirement R5, planned manual load shedding is acceptable only after all other available System adjustments have been made. | HIGH | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R7. | Each Reliability Coordinator shall include in its SOL methodology a risk-based approach for determining how SOL exceedances identified as part of Real-time monitoring and Real-time Assessments must be communicated and if so, the timeframe that communication must occur. The approach shall include: | HIGH | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R7.1. | A requirement that the following SOL exceedances will always be communicated, within a timeframe identified by the Reliability Coordinator. | HIGH | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R7.1.1. | IROL exceedances; | HIGH | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R7.1.2. | SOL exceedances of stability limits; | HIGH | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R7.1.3. | Post Contingency SOL exceedances that are identified to have a validated risk of instability, Cascading, and uncontrolled separation; | HIGH | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R7.1.4. | Pre-Contingency SOL exceedances of Facility Ratings; and | HIGH | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R7.1.5. | Pre-Contingency SOL exceedances of normal minimum System Voltage Limits. | HIGH | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R7.2. | A requirement that the following SOL exceedances must be communicated, if not resolved within 30 minutes, within a timeframe identified by the Reliability Coordinator. | HIGH | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R7.2.1. | Post-Contingency SOL exceedances of Facility Ratings and emergency System Voltage Limits, and | HIGH | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R7.2.2. | Pre-Contingency SOL exceedances of normal maximum System Voltage Limits. | HIGH | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R8. | Each Reliability Coordinator shall include in its SOL methodology: | HIGH | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R8.1. | A description of how to identify the subset of SOLs that qualify as Interconnection Reliability Operating Limits (IROLs). | HIGH | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R8.2. | Criteria for determining when exceeding a SOL qualifies as exceeding an IROL and criteria for developing any associated IROL Tv. | HIGH | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R9. | Each Reliability Coordinator shall provide its SOL methodology to: | LOWER | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R9.1. | Each Reliability Coordinator that requests and indicates it has a reliability-related need within 30 days of a request. | LOWER | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R9.2. | Each of the following entities prior to the effective date of the SOL methodology: | LOWER | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R9.2.1. | Each adjacent Reliability Coordinator within the same; Interconnection; | LOWER | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R9.2.2. | Each Planning Coordinator and Transmission Planner that is responsible for planning any portion of the Reliability Coordinator Area; | LOWER | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R9.2.3. | Each Transmission Operator within its Reliability Coordinator Area; and | LOWER | Effective | 2024-04-01 |  | RC
FAC-011-4 | System Operating Limits Methodology for the Operations Horizon | R9.2.4. | Each Reliability Coordinator that has requested to receive updates and indicated it had a reliability-related need. | LOWER | Effective | 2024-04-01 |  | RC
FAC-013-2 | Assessment of Transfer Capability for the Near-Term Transmission Planning Horizon | R1. | Each Planning Coordinator shall have a documented methodology it uses to perform an annual assessment of Transfer Capability in the Near-Term Transmission Planning Horizon (Transfer Capability methodology). The Transfer Capability methodology shall include, at a minimum, the following information: | MEDIUM | Retired | 2013-04-01 | 2020-12-24 | PC
FAC-013-2 | Assessment of Transfer Capability for the Near-Term Transmission Planning Horizon | R1.1. | Criteria for the selection of the transfers to be assessed. | No Individual VRF Assigned | Retired | 2013-04-01 | 2020-12-24 | PC
FAC-013-2 | Assessment of Transfer Capability for the Near-Term Transmission Planning Horizon | R1.2. | A statement that the assessment shall respect known System Operating Limits (SOLs). | No Individual VRF Assigned | Retired | 2013-04-01 | 2020-12-24 | PC
FAC-013-2 | Assessment of Transfer Capability for the Near-Term Transmission Planning Horizon | R1.3. | A statement that the assumptions and criteria used to perform the assessment are consistent with the Planning Coordinator’s planning practices. | No Individual VRF Assigned | Retired | 2013-04-01 | 2020-12-24 | PC
FAC-013-2 | Assessment of Transfer Capability for the Near-Term Transmission Planning Horizon | R1.4. | A description of how each of the following assumptions and criteria used in performing the assessment are addressed: | No Individual VRF Assigned | Retired | 2013-04-01 | 2020-12-24 | PC
FAC-013-2 | Assessment of Transfer Capability for the Near-Term Transmission Planning Horizon | R1.4.1. | Generation dispatch, including but not limited to long term planned outages, additions and retirements. | No Individual VRF Assigned | Retired | 2013-04-01 | 2020-12-24 | PC
FAC-013-2 | Assessment of Transfer Capability for the Near-Term Transmission Planning Horizon | R1.4.2. | Transmission system topology, including but not limited to long term planned Transmission outages, additions, and retirements. | No Individual VRF Assigned | Retired | 2013-04-01 | 2020-12-24 | PC
FAC-013-2 | Assessment of Transfer Capability for the Near-Term Transmission Planning Horizon | R1.4.3. | System demand. | No Individual VRF Assigned | Retired | 2013-04-01 | 2020-12-24 | PC
FAC-013-2 | Assessment of Transfer Capability for the Near-Term Transmission Planning Horizon | R1.4.4. | Current approved and projected Transmission uses. | No Individual VRF Assigned | Retired | 2013-04-01 | 2020-12-24 | PC
FAC-013-2 | Assessment of Transfer Capability for the Near-Term Transmission Planning Horizon | R1.4.5. | Parallel path (loop flow) adjustments. | No Individual VRF Assigned | Retired | 2013-04-01 | 2020-12-24 | PC
FAC-013-2 | Assessment of Transfer Capability for the Near-Term Transmission Planning Horizon | R1.4.6. | Contingencies | No Individual VRF Assigned | Retired | 2013-04-01 | 2020-12-24 | PC
FAC-013-2 | Assessment of Transfer Capability for the Near-Term Transmission Planning Horizon | R1.4.7. | Monitored Facilities. | No Individual VRF Assigned | Retired | 2013-04-01 | 2020-12-24 | PC
FAC-013-2 | Assessment of Transfer Capability for the Near-Term Transmission Planning Horizon | R1.5. | A description of how simulations of transfers are performed through the adjustment of generation, Load or both. | No Individual VRF Assigned | Retired | 2013-04-01 | 2020-12-24 | PC
FAC-013-2 | Assessment of Transfer Capability for the Near-Term Transmission Planning Horizon | R2. | Each Planning Coordinator shall issue its Transfer Capability methodology, and any revisions to the Transfer Capability methodology, to the following entities subject to the following: | LOWER | Retired | 2013-04-01 | 2020-12-24 | PC
FAC-013-2 | Assessment of Transfer Capability for the Near-Term Transmission Planning Horizon | R2.1. | Distribute to the following prior to the effectiveness of such revisions: | No Individual VRF Assigned | Retired | 2013-04-01 | 2020-12-24 | PC
FAC-013-2 | Assessment of Transfer Capability for the Near-Term Transmission Planning Horizon | R2.1.1. | Each Planning Coordinator adjacent to the Planning Coordinator’s Planning Coordinator area or overlapping the Planning Coordinator’s area. | No Individual VRF Assigned | Retired | 2013-04-01 | 2020-12-24 | PC
FAC-013-2 | Assessment of Transfer Capability for the Near-Term Transmission Planning Horizon | R2.1.2. | Each Transmission Planner within the Planning Coordinator’s Planning Coordinator area. | No Individual VRF Assigned | Retired | 2013-04-01 | 2020-12-24 | PC
FAC-013-2 | Assessment of Transfer Capability for the Near-Term Transmission Planning Horizon | R2.2. | Distribute to each functional entity that has a reliability-related need for the Transfer Capability methodology and submits a request for that methodology within 30 calendar days of receiving that written request. | No Individual VRF Assigned | Retired | 2013-04-01 | 2020-12-24 | PC
FAC-013-2 | Assessment of Transfer Capability for the Near-Term Transmission Planning Horizon | R4. | During each calendar year, each Planning Coordinator shall conduct simulations and document an assessment based on those simulations in accordance with its Transfer Capability methodology for at least one year in the Near-Term Transmission Planning Horizon. | MEDIUM | Retired | 2013-04-01 | 2020-12-24 | PC
FAC-013-2 | Assessment of Transfer Capability for the Near-Term Transmission Planning Horizon | R5. | Each Planning Coordinator shall make the documented Transfer Capability assessment results available within 45 calendar days of the completion of the assessment to the recipients of its Transfer Capability methodology pursuant to Requirement R2, Parts 2.1 and Part 2.2. However, if a functional entity that has a reliability related need for the results of the annual assessment of the Transfer Capabilities makes a written request for such an assessment after the completion of the assessment, the Planning Coordinator shall make the documented Transfer Capability assessment results available to that entity within 45 calendar days of receipt of the request | LOWER | Retired | 2013-04-01 | 2020-12-24 | PC
FAC-013-2 | Assessment of Transfer Capability for the Near-Term Transmission Planning Horizon | R6. | If a recipient of a documented Transfer Capability assessment requests data to support the assessment results, the Planning Coordinator shall provide such data to that entity within 45 calendar days of receipt of the request. The provision of such data shall be subject to the legal and regulatory obligations of the Planning Coordinator’s area regarding the disclosure of confidential and/or sensitive information. | LOWER | Retired | 2013-04-01 | 2020-12-24 | PC
FAC-014-2 | Establish and Communicate System Operating Limits | R1. | The Reliability Coordinator shall ensure that SOLs, including Interconnection Reliability Operating Limits (IROLs), for its Reliability Coordinator Area are established and that the SOLs (including Interconnection Reliability Operating Limits) are consistent with its SOL Methodology. | MEDIUM | Effective | 2008-11-16 |  | RC
FAC-014-2 | Establish and Communicate System Operating Limits | R1. | The Reliability Coordinator shall ensure that SOLs, including Interconnection Reliability Operating Limits (IROLs), for its Reliability Coordinator Area are established and that the SOLs (including Interconnection Reliability Operating Limits) are consistent with its SOL Methodology. | MEDIUM | Effective | 2008-11-16 |  | RC
FAC-014-2 | Establish and Communicate System Operating Limits | R2. | The Transmission Operator shall establish SOLs (as directed by its Reliability Coordinator) for its portion of the Reliability Coordinator Area that are consistent with its Reliability Coordinator’s SOL Methodology. | MEDIUM | Effective | 2008-11-16 |  | TOP, RC
FAC-014-2 | Establish and Communicate System Operating Limits | R2. | The Transmission Operator shall establish SOLs (as directed by its Reliability Coordinator) for its portion of the Reliability Coordinator Area that are consistent with its Reliability Coordinator’s SOL Methodology. | MEDIUM | Effective | 2008-11-16 |  | TOP, RC
FAC-014-2 | Establish and Communicate System Operating Limits | R3. | The Planning Authority shall establish SOLs, including IROLs, for its Planning Authority Area that are consistent with its SOL Methodology. | MEDIUM | Effective | 2008-11-16 |  | PA
FAC-014-2 | Establish and Communicate System Operating Limits | R3. | The Planning Authority shall establish SOLs, including IROLs, for its Planning Authority Area that are consistent with its SOL Methodology. | MEDIUM | Effective | 2008-11-16 |  | PA
FAC-014-2 | Establish and Communicate System Operating Limits | R4. | The Transmission Planner shall establish SOLs, including IROLs, for its Transmission Planning Area that are consistent with its Planning Authority’s SOL Methodology. | MEDIUM | Effective | 2008-11-16 |  | TP
FAC-014-2 | Establish and Communicate System Operating Limits | R4. | The Transmission Planner shall establish SOLs, including IROLs, for its Transmission Planning Area that are consistent with its Planning Authority’s SOL Methodology. | MEDIUM | Effective | 2008-11-16 |  | TP
FAC-014-2 | Establish and Communicate System Operating Limits | R5. | The Reliability Coordinator, Planning Authority and Transmission Planner shall each provide its SOLs and IROLs to those entities that have a reliability-related need for those limits and provide a written request that includes a schedule for delivery of those limits as follows: | HIGH | Effective | 2008-11-16 |  | TP, RC, PA
FAC-014-2 | Establish and Communicate System Operating Limits | R5.1. | The Reliability Coordinator shall provide its SOLs (including the subset of SOLs that are IROLs) to adjacent Reliability Coordinators and Reliability Coordinators who indicate a reliability-related need for those limits, and to the Transmission Operators, Transmission Planners, Transmission Service Providers and Planning Authorities within its Reliability Coordinator Area. For each IROL, the Reliability Coordinator shall provide the following supporting information: | HIGH | Effective | 2008-11-16 |  | RC
FAC-014-2 | Establish and Communicate System Operating Limits | R5.1.1. | Identification and status of the associated Facility (or group of Facilities) that is (are) critical to the derivation of the IROL. | MEDIUM | Effective | 2008-11-16 |  | RC
FAC-014-2 | Establish and Communicate System Operating Limits | R5.1.1. | Identification and status of the associated Facility (or group of Facilities) that is (are) critical to the derivation of the IROL. | MEDIUM | Effective | 2008-11-16 |  | RC
FAC-014-2 | Establish and Communicate System Operating Limits | R5.1.2. | The value of the IROL and its associated Tv. | MEDIUM | Effective | 2008-11-16 |  | RC
FAC-014-2 | Establish and Communicate System Operating Limits | R5.1.3. | The associated Contingency(ies). | MEDIUM | Effective | 2008-11-16 |  | RC
FAC-014-2 | Establish and Communicate System Operating Limits | R5.1.4. | The type of limitation represented by the IROL (e.g., voltage collapse, angular stability). | MEDIUM | Effective | 2008-11-16 |  | RC
FAC-014-2 | Establish and Communicate System Operating Limits | R5.2. | The Transmission Operator shall provide any SOLs it developed to its Reliability Coordinator and to the Transmission Service Providers that share its portion of the Reliability Coordinator Area. | MEDIUM | Effective | 2008-11-16 |  | TOP
FAC-014-2 | Establish and Communicate System Operating Limits | R5.3. | The Planning Authority shall provide its SOLs (including the subset of SOLs that are IROLs) to adjacent Planning Authorities, and to Transmission Planners, Transmission Service Providers, Transmission Operators and Reliability Coordinators that work within its Planning Authority Area. | MEDIUM | Effective | 2008-11-16 |  | PA
FAC-014-2 | Establish and Communicate System Operating Limits | R5.4. | The Transmission Planner shall provide its SOLs (including the subset of SOLs that are IROLs) to its Planning Authority, Reliability Coordinators, Transmission Operators, and Transmission Service Providers that work within its Transmission Planning Area and to adjacent Transmission Planners. | MEDIUM | Effective | 2008-11-16 |  | TP
FAC-014-2 | Establish and Communicate System Operating Limits | R6. | The Planning Authority shall identify the subset of multiple contingencies (if any), from Reliability Standard TPL-003 which result in stability limits. | MEDIUM | Effective | 2008-11-16 |  | PA
FAC-014-2 | Establish and Communicate System Operating Limits | R6.1. | The Planning Authority shall provide this list of multiple contingencies and the associated stability limits to the Reliability Coordinators that monitor the facilities associated with these contingencies and limits. | MEDIUM | Effective | 2008-11-16 |  | PA
FAC-014-2 | Establish and Communicate System Operating Limits | R6.2. | If the Planning Authority does not identify any stability-related multiple contingencies, the Planning Authority shall so notify the Reliability Coordinator. | MEDIUM | Effective | 2008-11-16 |  | PA
FAC-014-3 | Establish and Communicate System Operating Limits | R1. | Each Reliability Coordinator shall establish Interconnection Reliability Operating Limits (IROLs) for its Reliability Coordinator Area in accordance with its System Operating Limit methodology (SOL methodology). | HIGH | Effective | 2024-04-01 |  | TOP, TP, RC, PC
FAC-014-3 | Establish and Communicate System Operating Limits | R1. | Each Reliability Coordinator shall establish Interconnection Reliability Operating Limits (IROLs) for its Reliability Coordinator Area in accordance with its System Operating Limit methodology (SOL methodology). | HIGH | Effective | 2024-04-01 |  | TOP, TP, RC, PC
FAC-014-3 | Establish and Communicate System Operating Limits | R2. | Each Transmission Operator shall establish System Operating Limits SOLs for its portion of the Reliability Coordinator Area in accordance with its Reliability Coordinator's SOL methodology. | MEDIUM | Effective | 2024-04-01 |  | TOP, TP, RC, PC
FAC-014-3 | Establish and Communicate System Operating Limits | R2. | Each Transmission Operator shall establish System Operating Limits SOLs for its portion of the Reliability Coordinator Area in accordance with its Reliability Coordinator's SOL methodology. | MEDIUM | Effective | 2024-04-01 |  | TOP, TP, RC, PC
FAC-014-3 | Establish and Communicate System Operating Limits | R3. | Each Transmission Operator shall provide its SOLs to its Reliability Coordinator. | MEDIUM | Effective | 2024-04-01 |  | TOP, TP, RC, PC
FAC-014-3 | Establish and Communicate System Operating Limits | R3. | Each Transmission Operator shall provide its SOLs to its Reliability Coordinator. | MEDIUM | Effective | 2024-04-01 |  | TOP, TP, RC, PC
FAC-014-3 | Establish and Communicate System Operating Limits | R4. | Each Reliability Coordinator shall establish stability limits when an identified instability impacts adjacent Reliability Coordinator Areas or more than one Transmission Operator in its Reliability Coordinator Area in accordance with its SOL methodology. | HIGH | Effective | 2024-04-01 |  | TOP, TP, RC, PC
FAC-014-3 | Establish and Communicate System Operating Limits | R4. | Each Reliability Coordinator shall establish stability limits when an identified instability impacts adjacent Reliability Coordinator Areas or more than one Transmission Operator in its Reliability Coordinator Area in accordance with its SOL methodology. | HIGH | Effective | 2024-04-01 |  | TOP, TP, RC, PC
FAC-014-3 | Establish and Communicate System Operating Limits | R5. | Each Reliability Coordinator shall provide: | HIGH | Effective | 2024-04-01 |  | TOP, TP, RC, PC
FAC-014-3 | Establish and Communicate System Operating Limits | R5.1. | Each Planning Coordinator and each Transmission Planner within its Reliability Coordinator Area, the SOLs for its Reliability Coordinator Area (including the subset of SOLs that are IROLs) at least once every twelve calendar months. [Time Horizon: Operati | MEDIUM | Effective | 2024-04-01 |  | TOP, TP, RC, PC
FAC-014-3 | Establish and Communicate System Operating Limits | R5.2. | Each impacted Planning Coordinator and each impacted Transmission Planner within its Reliability Coordinator Area, the following information for each established stability limit and each established IROL at least once every twelve calendar months: [Time H | HIGH | Effective | 2024-04-01 |  | TOP, TP, RC, PC
FAC-014-3 | Establish and Communicate System Operating Limits | R5.2.1. | The value of the stability limit or IROL; | MEDIUM | Effective | 2024-04-01 |  | TOP, TP, RC, PC
FAC-014-3 | Establish and Communicate System Operating Limits | R5.2.2. | Identification of the Facilities that are critical to the derivation of the stability limit or the IROL; | MEDIUM | Effective | 2024-04-01 |  | TOP, TP, RC, PC
FAC-014-3 | Establish and Communicate System Operating Limits | R5.2.2. | Identification of the Facilities that are critical to the derivation of the stability limit or the IROL; | MEDIUM | Effective | 2024-04-01 |  | TOP, TP, RC, PC
FAC-014-3 | Establish and Communicate System Operating Limits | R5.2.3. | The associated IROL Tv for any IROL; | MEDIUM | Effective | 2024-04-01 |  | TOP, TP, RC, PC
FAC-014-3 | Establish and Communicate System Operating Limits | R5.2.4. | The associated critical Contingency(ies); | MEDIUM | Effective | 2024-04-01 |  | TOP, TP, RC, PC
FAC-014-3 | Establish and Communicate System Operating Limits | R5.2.5. | A description of system conditions associated with the stability limit or IROL; and | MEDIUM | Effective | 2024-04-01 |  | TOP, TP, RC, PC
FAC-014-3 | Establish and Communicate System Operating Limits | R5.2.6. | The type of limitation represented by the stability limit or IROL (e.g., voltage collapse, angular stability). | MEDIUM | Effective | 2024-04-01 |  | TOP, TP, RC, PC
FAC-014-3 | Establish and Communicate System Operating Limits | R5.3. | Each impacted Transmission Operator within its Reliability Coordinator Area, the value of the stability limits established pursuant to Requirement R4 and each IROL established pursuant to Requirement R1, in an agreed upon time frame necessary for inclusio | MEDIUM | Effective | 2024-04-01 |  | TOP, TP, RC, PC
FAC-014-3 | Establish and Communicate System Operating Limits | R5.4. | Each impacted Transmission Operator within its Reliability Coordinator Area, the information identified in Requirement R5 Parts 5.2.2 – 5.2.6 for each established stability limit and each established IROL, and any updates to that information within an agr | MEDIUM | Effective | 2024-04-01 |  | TOP, TP, RC, PC
FAC-014-3 | Establish and Communicate System Operating Limits | R5.5. | Each requesting Transmission Operator within its Reliability Coordinator Area, requested SOL information for its Reliability Coordinator Area, on a mutually agreed upon schedule. [Time Horizon: Operations Planning] | MEDIUM | Effective | 2024-04-01 |  | TOP, TP, RC, PC
FAC-014-3 | Establish and Communicate System Operating Limits | R5.6. | Each impacted Generator Owner or Transmission Owner, within its Reliability Coordinator Area, with a list of their Facilities that have been identified as critical to the derivation of an IROL and its associated critical contingencies at least once every | MEDIUM | Effective | 2024-04-01 |  | TOP, TP, RC, PC
FAC-014-3 | Establish and Communicate System Operating Limits | R6. | Each Planning Coordinator and each Transmission Planner shall implement a documented process to use Facility Ratings, System steady-state voltage limits and stability criteria in its Planning Assessment of Near-Term Transmission Planning Horizon that are | MEDIUM | Effective | 2024-04-01 |  | TOP, TP, RC, PC
FAC-014-3 | Establish and Communicate System Operating Limits | R7. | Each Planning Coordinator and each Transmission Planner shall annually communicate the following information for Corrective Action Plans developed to address any instability identified in its Planning Assessment of the Near-Term Transmission Planning Hori | MEDIUM | Effective | 2024-04-01 |  | TOP, TP, RC, PC
FAC-014-3 | Establish and Communicate System Operating Limits | R7.1. | The Corrective Action Plan developed to mitigate the identified instability, including any automatic control or operator-assisted actions (such as Remedial Action Schemes, under voltage load shedding, or any Operating Procedures); | MEDIUM | Effective | 2024-04-01 |  | TOP, TP, RC, PC
FAC-014-3 | Establish and Communicate System Operating Limits | R7.2. | The type of instability addressed by the Corrective Action Plan (e.g. steady-state and/or transient voltage instability, angular instability including generating unit loss of synchronism and/or unacceptable damping); | MEDIUM | Effective | 2024-04-01 |  | TOP, TP, RC, PC
FAC-014-3 | Establish and Communicate System Operating Limits | R7.3. | The associated stability criteria violation requiring the Corrective Action Plan (e.g. violation of transient voltage response criteria or damping rate criteria); | MEDIUM | Effective | 2024-04-01 |  | TOP, TP, RC, PC
FAC-014-3 | Establish and Communicate System Operating Limits | R7.4. | The planning event Contingency(ies) associated with the identified instability requiring the Corrective Action Plan; | MEDIUM | Effective | 2024-04-01 |  | TOP, TP, RC, PC
FAC-014-3 | Establish and Communicate System Operating Limits | R7.5. | The System conditions and Facilities associated with the identified instability requiring the Corrective Action Plan. | MEDIUM | Effective | 2024-04-01 |  | TOP, TP, RC, PC
FAC-014-3 | Establish and Communicate System Operating Limits | R8. | Each Planning Coordinator and each Transmission Planner shall annually communicate to each impacted Transmission Owner and Generation Owner a list of their Facilities that comprise the planning event Contingency(ies) that would cause instability, Cascadin | MEDIUM | Effective | 2024-04-01 |  | TOP, TP, RC, PC
INT-004-3.1 | Dynamic Interchange Transaction Modifications | R1. | Each Purchasing-Selling Entity that secures energy to serve Load via a Dynamic Schedule or Pseudo-Tie shall ensure that a Request for Interchange is submitted as an on-time1 Arranged Interchange to the Sink Balancing Authority for that Dynamic Schedule or Pseudo-Tie, unless the information about the Pseudo-Tie is included in congestion management procedure(s) via an alternate method. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning, Same-day Operations] | LOWER | Effective | 2015-01-01
INT-004-3.1 | Dynamic Interchange Transaction Modifications | R2. | The Purchasing-Selling Entity that submits a Request for Interchange in accordance with Requirement R1 shall ensure the Confirmed Interchange associated with that Dynamic Schedule or Pseudo-Tie is updated for future hours in order to support congestion management procedures if any one of the following occurs: [Violation Risk Factor: Lower] [Time Horizon: Operations Planning, Same Day Operations, Real Time Operations] | LOWER | Effective | 2015-01-01
INT-004-3.1 | Dynamic Interchange Transaction Modifications | R2.1. | For Confirmed Interchange greater than 250 MW for the last hour, the actual hourly integrated energy deviates from the Confirmed Interchange by more than 10% for that hour and that deviation is expected to persist. | LOWER | Effective | 2015-01-01
INT-004-3.1 | Dynamic Interchange Transaction Modifications | R2.2. | For Confirmed Interchange less than or equal to 250 MW for the last hour, the actual hourly integrated energy deviates from the Confirmed Interchange by more than 25 MW for that hour and that deviation is expected to persist. | LOWER | Effective | 2015-01-01
INT-004-3.1 | Dynamic Interchange Transaction Modifications | R2.3. | The Purchasing-Selling Entity receives notification from a Reliability Coordinator or Transmission Operator to update the Confirmed Interchange. | LOWER | Effective | 2015-01-01
INT-004-3.1 | Dynamic Interchange Transaction Modifications | R3. | Each Balancing Authority shall only implement or operate a Pseudo-Tie that is included in the NAESB Electric Industry Registry publication in order to support congestion management procedures. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Effective | 2015-01-01 |  | BA
INT-006-4 | Evaluation of Interchange Transactions | R1. | Each Balancing Authority shall approve or deny each on-time Arranged Interchange or emergency Arranged Interchange that it receives and shall do so prior to the expiration of the time period defined in Attachment 1, Column B. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning, Same-day Operations, Real-time Operations] | LOWER | Retired | 2015-01-01 | 2021-03-31 | BA
INT-006-4 | Evaluation of Interchange Transactions | R1.1. | Each Source and Sink Balancing Authority shall deny the Arranged Interchange or curtail Confirmed Interchange if it does not expect to be capable of supporting the magnitude of the Interchange, including ramping, throughout the duration of the Arranged Interchange. | LOWER | Retired | 2015-01-01 | 2021-03-31 | BA
INT-006-4 | Evaluation of Interchange Transactions | R1.2. | Each Balancing Authority shall deny the Arranged Interchange or curtail Confirmed Interchange if the Scheduling Path (proper connectivity of Adjacent Balancing Authorities) between it and its Adjacent Balancing Authorities is invalid. | LOWER | Retired | 2015-01-01 | 2021-03-31 | BA
INT-006-4 | Evaluation of Interchange Transactions | R2. | Each Transmission Service Provider shall approve or deny each on-time Arranged Interchange or emergency Arranged Interchange that it receives and shall do so prior to the expiration of the time period defined in Attachment 1, Column B. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning, Same-day Operations, Real-time Operations] | LOWER | Retired | 2015-01-01 | 2021-03-31 | TSP
INT-006-4 | Evaluation of Interchange Transactions | R2.1. | Each Transmission Service Provider shall deny the Arranged Interchange or curtail Confirmed Interchange if the transmission path (proper connectivity of adjacent Transmission Service Providers) between it and its adjacent Transmission Service Providers is invalid. | LOWER | Retired | 2015-01-01 | 2021-03-31 | TSP
INT-006-4 | Evaluation of Interchange Transactions | R3. | The Source Balancing Authority and the Sink Balancing Authority receiving a Reliability Adjustment Arranged Interchange shall approve or deny it prior to the expiration of the time period defined in Attachment 1, Column B. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning, Same-day Operations, Real-time Operations] | LOWER | Retired | 2015-01-01 | 2021-03-31 | BA
INT-006-4 | Evaluation of Interchange Transactions | R3.1. | If a Balancing Authority denies a Reliability Adjustment Arranged Interchange, the Balancing Authority must communicate that fact to its Reliability Coordinator no more than 10 minutes after the denial. | LOWER | Retired | 2015-01-01 | 2021-03-31 | BA
INT-006-4 | Evaluation of Interchange Transactions | R4. | Each Sink Balancing Authority shall confirm that none of the following conditions exist prior to transitioning an Arranged Interchange to Confirmed Interchange: [Violation Risk Factor: Lower] [Time Horizon: Operations Planning, Same-day Operations, Real-time Operations]  It is a Reliability Adjustment Arranged Interchange, the time period specified in Attachment 1, Column B has elapsed, and the Source Balancing Authority or the Sink Balancing Authority associated with the Arranged Interchange has not communicated its approval of the transition.  It is not a Reliability Adjustment Arranged Interchange, the time period specified in Attachment 1, Column B, has elapsed, and not all Balancing Authorities and Transmission Service Providers associated with the Arranged Interchange have communicated their approval of the transition.  It is not a Reliability Adjustment Arranged Interchange, the time period specified in Attachment 1, Column B, has elapsed, and any entity associated with the Arranged Interchange has communicated its denial of the transition. | LOWER | Retired | 2015-01-01 | 2021-03-31 | BA
INT-006-4 | Evaluation of Interchange Transactions | R5. | For each Arranged Interchange that is transitioned to Confirmed Interchange, the Sink Balancing Authority shall notify the following entities of the on-time Confirmed Interchange such that the notification is delivered in time to be incorporated into scheduling systems prior to ramp start as specified in Attachment 1, Column D: [Violation Risk Factor: Lower] [Time Horizon: Operations Planning, Same-day Operations, Real-time Operations] | LOWER | Retired | 2015-01-01 | 2021-03-31 | BA
INT-006-4 | Evaluation of Interchange Transactions | R5.1. | The Source Balancing Authority, | LOWER | Retired | 2015-01-01 | 2021-03-31 | BA
INT-006-4 | Evaluation of Interchange Transactions | R5.2. | Each Intermediate Balancing Authority, | LOWER | Retired | 2015-01-01 | 2021-03-31 | BA
INT-006-4 | Evaluation of Interchange Transactions | R5.3. | Each Reliability Coordinator associated with each Balancing Authority included in the Arranged Interchange, | LOWER | Retired | 2015-01-01 | 2021-03-31 | BA
INT-006-4 | Evaluation of Interchange Transactions | R5.4. | Each Transmission Service Provider included in the Arranged Interchange, and | LOWER | Retired | 2015-01-01 | 2021-03-31 | BA
INT-006-4 | Evaluation of Interchange Transactions | R5.5. | Each Purchasing Selling Entity included in the Arranged Interchange. | LOWER | Retired | 2015-01-01 | 2021-03-31 | BA
INT-006-5 | Evaluation of Interchange Transactions | R1. | Each Balancing Authority shall approve or deny each on-time Arranged Interchange or emergency Arranged Interchange that it receives and shall do so prior to the expiration of the time period defined in Attachment 1, Column B. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning, Same-day Operations, Real-time Operations] | LOWER | Effective | 2021-04-01 |  | TSP, BA
INT-006-5 | Evaluation of Interchange Transactions | R1.1. | Each Source and Sink Balancing Authority shall deny the Arranged Interchange or curtail Confirmed Interchange if it does not expect to be capable of supporting the magnitude of the Interchange, including ramping, throughout the duration of the Arranged Interchange. | LOWER | Effective | 2021-04-01 |  | TSP, BA
INT-006-5 | Evaluation of Interchange Transactions | R1.2. | Each Balancing Authority shall deny the Arranged Interchange or curtail Confirmed Interchange if the Scheduling Path (proper connectivity of Adjacent Balancing Authorities) between it and its Adjacent Balancing Authorities is invalid. | LOWER | Effective | 2021-04-01 |  | TSP, BA
INT-006-5 | Evaluation of Interchange Transactions | R2. | Each Transmission Service Provider shall approve or deny each on-time Arranged Interchange or emergency Arranged Interchange that it receives and shall do so prior to the expiration of the time period defined in Attachment 1, Column B. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning, Same-day Operations, Real-time Operations] | LOWER | Effective | 2021-04-01 |  | TSP, BA
INT-006-5 | Evaluation of Interchange Transactions | R2.1. | Each Transmission Service Provider shall deny the Arranged Interchange or curtail Confirmed Interchange if the transmission path (proper connectivity of adjacent Transmission Service Providers) between it and its adjacent Transmission Service Providers is invalid. | LOWER | Effective | 2021-04-01 |  | TSP, BA
INT-006-5 | Evaluation of Interchange Transactions | R3. | The Source Balancing Authority and the Sink Balancing Authority receiving a Reliability Adjustment Arranged Interchange shall approve or deny it prior to the expiration of the time period defined in Attachment 1, Column B. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning, Same-day Operations, Real-time Operations] | LOWER | Effective | 2021-04-01 |  | TSP, BA
INT-006-5 | Evaluation of Interchange Transactions | R3.1. | Reserved | LOWER | Effective | 2021-04-01 |  | TSP, BA
INT-006-5 | Evaluation of Interchange Transactions | R4. | Reserved | LOWER | Effective | 2021-04-01 |  | TSP, BA
INT-006-5 | Evaluation of Interchange Transactions | R5. | Reserved | LOWER | Effective | 2021-04-01 |  | TSP, BA
INT-006-5 | Evaluation of Interchange Transactions | R5.1. | The Source Balancing Authority, | LOWER | Effective | 2021-04-01 |  | TSP, BA
INT-006-5 | Evaluation of Interchange Transactions | R5.2. | Each Intermediate Balancing Authority, | LOWER | Effective | 2021-04-01 |  | TSP, BA
INT-006-5 | Evaluation of Interchange Transactions | R5.3. | Each Reliability Coordinator associated with each Balancing Authority included in the Arranged Interchange, | LOWER | Effective | 2021-04-01 |  | TSP, BA
INT-006-5 | Evaluation of Interchange Transactions | R5.4. | Each Transmission Service Provider included in the Arranged Interchange, and | LOWER | Effective | 2021-04-01 |  | TSP, BA
INT-006-5 | Evaluation of Interchange Transactions | R5.5. | Each Purchasing Selling Entity included in the Arranged Interchange. | LOWER | Effective | 2021-04-01 |  | TSP, BA
INT-009-2.1 | Implementation of Interchange | R1. | Each Balancing Authority shall agree with each of its Adjacent Balancing Authorities that its Composite Confirmed Interchange with that Adjacent Balancing Authority, at mutually agreed upon time intervals, excluding Dynamic Schedules and Pseudo-Ties and including any Interchange per INT-010-2 not yet captured in the Composite Confirmed Interchange, is: [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | MEDIUM | Retired | 2015-01-01 | 2021-03-31 | BA
INT-009-2.1 | Implementation of Interchange | R1.1. | Identical in magnitude to that of the Adjacent Balancing Authority, and | MEDIUM | Retired | 2015-01-01 | 2021-03-31 | BA
INT-009-2.1 | Implementation of Interchange | R1.2. | Opposite in sign or direction to that of the Adjacent Balancing Authority. | MEDIUM | Retired | 2015-01-01 | 2021-03-31 | BA
INT-009-2.1 | Implementation of Interchange | R2. | The Attaining Balancing Authority and the Native Balancing Authority shall use a dynamic value emanating from an agreed upon common source to account for the Pseudo-Tie in the Actual Net Interchange (NIA) term of their respective control ACE (or alternate control process). [Violation Risk Factor: Medium] [Time Horizon: Realtime Operations] | MEDIUM | Retired | 2015-01-01 | 2021-03-31 | BA
INT-009-2.1 | Implementation of Interchange | R3. | Each Balancing Authority in whose area the high-voltage direct current tie is controlled shall coordinate the Confirmed Interchange prior to its implementation with the Transmission Operator of the high-voltage direct current tie. [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations, Operations Planning] | MEDIUM | Retired | 2015-01-01 | 2021-03-31 | BA
INT-009-3 | Implementation of Interchange | R1. | Each Balancing Authority shall agree with each of its Adjacent Balancing Authorities that its Composite Confirmed Interchange with that Adjacent Balancing Authority, at mutually agreed upon time intervals, excluding Dynamic Schedules and Pseudo‐Ties and including any Interchange not yet captured in the Composite Confirmed Interchange, is: [Violation Risk Factor: Medium] [Time Horizon: Real‐time Operations] | MEDIUM | Effective | 2021-04-01 |  | BA
INT-009-3 | Implementation of Interchange | R1.1. | Identical in magnitude to that of the Adjacent Balancing Authority, and | MEDIUM | Effective | 2021-04-01 |  | BA
INT-009-3 | Implementation of Interchange | R1.2. | Opposite in sign or direction to that of the Adjacent Balancing Authority. | MEDIUM | Effective | 2021-04-01 |  | BA
INT-009-3 | Implementation of Interchange | R2. | Reserved | MEDIUM | Effective | 2021-04-01 |  | BA
INT-009-3 | Implementation of Interchange | R3. | Each Balancing Authority in whose area the high-voltage direct current tie is controlled shall coordinate the Confirmed Interchange prior to its implementation with the Transmission Operator of the high-voltage direct current tie. [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations, Operations Planning] | MEDIUM | Effective | 2021-04-01 |  | BA
INT-010-2.1 | Interchange Initiation and Modification for Reliability | R1. | The Balancing Authority that experiences a loss of resources covered by an energy sharing agreement or other reliability needs covered by an energy sharing agreement shall ensure that a Request for Interchange (RFI) is submitted with a start time no more than 60 minutes beyond the resource loss. If the use of the energy sharing agreement does not exceed 60 minutes from the time of the resource loss, no RFI is required. [Violation Risk Factor: Lower] [Time Horizon: Real Time Operations] | LOWER | Retired | 2015-01-01 | 2020-12-31 | BA
INT-010-2.1 | Interchange Initiation and Modification for Reliability | R2. | Each Sink Balancing Authority shall ensure that a Reliability Adjustment Arranged Interchange reflecting a modification is submitted within 60 minutes of the start of the modification if a Reliability Coordinator directs the modification of a Confirmed Interchange or Implemented Interchange for actual or anticipated reliability-related reasons. [Violation Risk Factor: Lower] [Time Horizon: Real Time Operations] | LOWER | Retired | 2015-01-01 | 2020-12-31 | BA
INT-010-2.1 | Interchange Initiation and Modification for Reliability | R3. | Each Sink Balancing Authority shall ensure that a Request for Interchange is submitted reflecting that Interchange Schedule within 60 minutes of the start of the scheduled Interchange if a Reliability Coordinator directs the scheduling of Interchange for actual or anticipated reliability-related reasons. [Violation Risk Factor: Lower] [Time Horizon: Real Time Operations] | LOWER | Retired | 2015-01-01 | 2020-12-31 | BA
INT-011-1.1 | Intra-Balancing Authority Transaction Identification | R1. | Each Load-Serving Entity that uses Point to Point Transmission Service for intra-Balancing Authority Area transfers shall submit a Request for Interchange unless the information about intra-Balancing Authority transfers is included in congestion management procedure(s) via an alternate method. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning, Same-day Operations] | LOWER | Effective | 2015-01-01
IRO-001-1.1 | Reliability Coordination - Responsibilities and Authorities | R1. | Each Regional Reliability Organization, subregion, or interregional coordinating group shall establish one or more Reliability Coordinators to continuously assess transmission reliability and coordinate emergency operations among the operating entities within the region and across the regional boundaries. | HIGH | Retired | 2008-10-29 | 2017-03-31
IRO-001-1.1 | Reliability Coordination - Responsibilities and Authorities | R2. | The Reliability Coordinator shall comply with a regional reliability plan approved by the NERC Operating Committee. | HIGH | Retired | 2008-10-29 | 2017-03-31 | RC
IRO-001-1.1 | Reliability Coordination - Responsibilities and Authorities | R3. | The Reliability Coordinator shall have clear decision-making authority to act and to direct actions to be taken by Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities within its Reliability Coordinator Area to preserve the integrity and reliability of the Bulk Electric System. These actions shall be taken without delay, but no longer than 30 minutes. | HIGH | Retired | 2008-10-29 | 2017-03-31 | RC
IRO-001-1.1 | Reliability Coordination - Responsibilities and Authorities | R4. | Reliability Coordinators that delegate tasks to other entities shall have formal operating agreements with each entity to which tasks are delegated. The Reliability Coordinator shall verify that all delegated tasks are understood, communicated, and addressed within its Reliability Coordinator Area. All responsibilities for complying with NERC and regional standards applicable to Reliability Coordinators shall remain with the Reliability Coordinator. | MEDIUM | Retired | 2008-10-29 | 2017-03-31 | RC
IRO-001-1.1 | Reliability Coordination - Responsibilities and Authorities | R5. | The Reliability Coordinator shall list within its reliability plan all entities to which the Reliability Coordinator has delegated required tasks. | LOWER | Retired | 2008-10-29 | 2017-03-31 | RC
IRO-001-1.1 | Reliability Coordination - Responsibilities and Authorities | R6. | The Reliability Coordinator shall verify that all delegated tasks are carried out by NERC-certified Reliability Coordinator operating personnel. | MEDIUM | Retired | 2008-10-29 | 2017-03-31 | RC
IRO-001-1.1 | Reliability Coordination - Responsibilities and Authorities | R7. | The Reliability Coordinator shall have clear, comprehensive coordination agreements with adjacent Reliability Coordinators to ensure that System Operating Limit or Interconnection Reliability Operating Limit violation mitigation requiring actions in adjacent Reliability Coordinator Areas are coordinated. | HIGH | Retired | 2008-10-29 | 2017-03-31 | RC
IRO-001-1.1 | Reliability Coordination - Responsibilities and Authorities | R8. | Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities shall comply with Reliability Coordinator directives unless such actions would violate safety, equipment, or regulatory or statutory requirements. Under these circumstances, the Transmission Operator, Balancing Authority, Generator Operator, Transmission Service Provider, Load-Serving Entity, or Purchasing-Selling Entity shall immediately inform the Reliability Coordinator of the inability to perform the directive so that the Reliability Coordinator may implement alternate remedial actions. | HIGH | Retired | 2008-10-29 | 2017-03-31 | TSP, TOP, GOP, BA
IRO-001-1.1 | Reliability Coordination - Responsibilities and Authorities | R9. | The Reliability Coordinator shall act in the interests of reliability for the overall Reliability Coordinator Area and the Interconnection before the interests of any other entity. | HIGH | Retired | 2008-10-29 | 2017-03-31 | RC
IRO-001-2 | Reliability Coordination - Responsibilities and Authorities | R1. | Each Regional Reliability Organization, subregion, or interregional coordinating group shall establish one or more Reliability Coordinators to continuously assess transmission reliability and coordinate emergency operations among the operating entities within the region and across the regional boundaries. | HIGH | Never Came Into Effect in Ontario
IRO-001-2 | Reliability Coordination - Responsibilities and Authorities | R2. | The Reliability Coordinator shall comply with a regional reliability plan approved by the NERC Operating Committee. | HIGH | Never Came Into Effect in Ontario |  |  | RC
IRO-001-2 | Reliability Coordination - Responsibilities and Authorities | R3. | The Reliability Coordinator shall have clear decision-making authority to act and to direct actions to be taken by Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities within its Reliability Coordinator Area to preserve the integrity and reliability of the Bulk Electric System. These actions shall be taken without delay, but no longer than 30 minutes. | HIGH | Never Came Into Effect in Ontario |  |  | RC
IRO-001-2 | Reliability Coordination - Responsibilities and Authorities | R4. | Reliability Coordinators that delegate tasks to other entities shall have formal operating agreements with each entity to which tasks are delegated. The Reliability Coordinator shall verify that all delegated tasks are understood, communicated, and addressed within its Reliability Coordinator Area. All responsibilities for complying with NERC and regional standards applicable to Reliability Coordinators shall remain with the Reliability Coordinator. | MEDIUM | Never Came Into Effect in Ontario |  |  | RC
IRO-001-2 | Reliability Coordination - Responsibilities and Authorities | R5. | The Reliability Coordinator shall list within its reliability plan all entities to which the Reliability Coordinator has delegated required tasks. | LOWER | Never Came Into Effect in Ontario |  |  | RC
IRO-001-2 | Reliability Coordination - Responsibilities and Authorities | R6. | The Reliability Coordinator shall verify that all delegated tasks are carried out by NERC-certified Reliability Coordinator operating personnel. | MEDIUM | Never Came Into Effect in Ontario |  |  | RC
IRO-001-2 | Reliability Coordination - Responsibilities and Authorities | R7. | Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities shall comply with Reliability Coordinator directives unless such actions would violate safety, equipment, or regulatory or statutory requirements. Under these circumstances, the Transmission Operator, Balancing Authority, Generator Operator, Transmission Service Provider, Load-Serving Entity, or Purchasing-Selling Entity shall immediately inform the Reliability Coordinator of the inability to perform the directive so that the Reliability Coordinator may implement alternate remedial actions. | HIGH | Never Came Into Effect in Ontario |  |  | TSP, TOP, GOP, BA
IRO-001-2 | Reliability Coordination - Responsibilities and Authorities | R8. | The Reliability Coordinator shall act in the interests of reliability for the overall Reliability Coordinator Area and the Interconnection before the interests of any other entity. | HIGH | Never Came Into Effect in Ontario |  |  | RC
IRO-001-3 | Reliability Coordination - Responsibilities and Authorities | R1. | Each Reliability Coordinator shall have the authority to act or direct others to act (which could include issuing Reliability Directives) to prevent identified events or mitigate the magnitude or duration of actual events that result in an Emergency or Adverse Reliability Impact. [Violation Risk Factor: High][Time Horizon: Real-time Operations, Same Day Operations and Operations Planning] | HIGH | Never Came Into Effect in Ontario |  |  | RC
IRO-001-3 | Reliability Coordination - Responsibilities and Authorities | R2. | Each Transmission Operator, Balancing Authority, Generator Operator, and Distribution Provider shall comply with its Reliability Coordinator’s direction unless compliance with the direction cannot be physically implemented or unless such actions would violate safety, equipment, regulatory, or statutory requirements. [Violation Risk Factor: High] [Time Horizon: Real-time Operations, Same Day Operations and Operations Planning] | HIGH | Never Came Into Effect in Ontario |  |  | TOP, GOP, DP, BA
IRO-001-3 | Reliability Coordination - Responsibilities and Authorities | R3. | Each Transmission Operator, Balancing Authority, Generator Operator, and Distribution Provider shall inform its Reliability Coordinator upon recognition of its inability to perform as directed in accordance with Requirement R2. [Violation Risk Factor: High] [Time Horizon: Real-time Operations, Same Day Operations and Operations Planning] | HIGH | Never Came Into Effect in Ontario |  |  | TOP, GOP, DP, BA
IRO-001-4 | Reliability Coordination – Responsibilities | R1. | Each Reliability Coordinator shall act to address the reliability of its Reliability Coordinator Area via direct actions or by issuing Operating Instructions. [Violation Risk Factor: High][Time Horizon: Same-Day Operations, Real-time Operations] | HIGH | Effective | 2017-04-01 |  | RC
IRO-001-4 | Reliability Coordination – Responsibilities | R2. | Each Transmission Operator, Balancing Authority, Generator Operator, and Distribution Provider shall comply with its Reliability Coordinator’s Operating Instructions unless compliance with the Operating Instructions cannot be physically implemented or unless such actions would violate safety, equipment, regulatory, or statutory requirements. [Violation Risk Factor: High] [Time Horizon: Same-Day Operations, Real-time Operations] | HIGH | Effective | 2017-04-01 |  | TOP, GOP, DP, BA
IRO-001-4 | Reliability Coordination – Responsibilities | R3. | Each Transmission Operator, Balancing Authority, Generator Operator, and Distribution Provider shall inform its Reliability Coordinator of its inability to perform the Operating Instruction issued by its Reliability Coordinator in Requirement R1. [Violation Risk Factor: High] [Time Horizon: Same-Day Operations, Real-time Operations] | HIGH | Effective | 2017-04-01 |  | TOP, GOP, DP, BA
IRO-002-2 | Reliability Coordination - Facilities | R1. | Each Reliability Coordinator shall have adequate communications facilities (voice and data links) to appropriate entities within its Reliability Coordinator Area. These communications facilities shall be staffed and available to act in addressing a real-time emergency condition. | HIGH | Retired | 2011-10-01 | 2017-03-31 | RC
IRO-002-2 | Reliability Coordination - Facilities | R2. | Each Reliability Coordinator — or its Transmission Operators and Balancing Authorities — shall provide, or arrange provisions for, data exchange to other Reliability Coordinators or Transmission Operators and Balancing Authorities via a secure network. | MEDIUM | Retired | 2011-10-01 | 2017-03-31 | TOP, RC, BA
IRO-002-2 | Reliability Coordination - Facilities | R3. | Each Reliability Coordinator shall have multi-directional communications capabilities with its Transmission Operators and Balancing Authorities, and with neighboring Reliability Coordinators, for both voice and data exchange as required to meet reliability needs of the Interconnection. | MEDIUM | Retired | 2011-10-01 | 2017-03-31 | RC
IRO-002-2 | Reliability Coordination - Facilities | R4. | Each Reliability Coordinator shall have detailed real-time monitoring capability of its Reliability Coordinator Area and sufficient monitoring capability of its surrounding Reliability Coordinator Areas to ensure that potential or actual System Operating Limit or Interconnection Reliability Operating Limit violations are identified. Each Reliability Coordinator shall have monitoring systems that provide information that can be easily understood and interpreted by the Reliability Coordinator’s operating personnel, giving particular emphasis to alarm management and awareness systems, automated data transfers, and synchronized information systems, over a redundant and highly reliable infrastructure. | HIGH | Retired | 2011-10-01 | 2017-03-31 | RC
IRO-002-2 | Reliability Coordination - Facilities | R5. | Each Reliability Coordinator shall monitor Bulk Electric System elements (generators, transmission lines, buses, transformers, breakers, etc.) that could result in SOL or IROL violations within its Reliability Coordinator Area. Each Reliability Coordinator shall monitor both real and reactive power system flows, and operating reserves, and the status of Bulk Electric System elements that are or could be critical to SOLs and IROLs and system restoration requirements within its Reliability Coordinator Area. | HIGH | Retired | 2011-10-01 | 2017-03-31 | RC
IRO-002-2 | Reliability Coordination - Facilities | R6. | Each Reliability Coordinator shall have adequate analysis tools such as state estimation, pre- and post-contingency analysis capabilities (thermal, stability, and voltage), and wide-area overview displays. | HIGH | Retired | 2011-10-01 | 2017-03-31 | RC
IRO-002-2 | Reliability Coordination - Facilities | R7. | Each Reliability Coordinator shall continuously monitor its Reliability Coordinator Area. Each Reliability Coordinator shall have provisions for backup facilities that shall be exercised if the main monitoring system is unavailable. Each Reliability Coordinator shall ensure SOL and IROL monitoring and derivations continue if the main monitoring system is unavailable. | HIGH | Retired | 2011-10-01 | 2017-03-31 | RC
IRO-002-2 | Reliability Coordination - Facilities | R8. | Each Reliability Coordinator shall control its Reliability Coordinator analysis tools, including approvals for planned maintenance. Each Reliability Coordinator shall have procedures in place to mitigate the effects of analysis tool outages. | HIGH | Retired | 2011-10-01 | 2017-03-31 | RC
IRO-002-3 | Reliability Coordination – Analysis Tools | R1. | Each Reliability Coordinator shall provide its System Operators with the authority to approve, deny or cancel planned outages of its own analysis tools. | MEDIUM | Never Came Into Effect in Ontario |  |  | RC
IRO-002-3 | Reliability Coordination – Analysis Tools | R2. | Each Reliability Coordinator shall have procedures in place to mitigate the effects of analysis tool outages. | MEDIUM | Never Came Into Effect in Ontario |  |  | RC
IRO-002-4 | Reliability Coordination — Monitoring and Analysis | R1. | Each Reliability Coordinator shall have data exchange capabilities with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, for it to perform its Operational Planning Analyses, Real-time monitoring, and Realtime Assessments. [Violation Risk Factor: High] [Time Horizon: Operations Planning, Same-Day Operations, Real-time Operations] | HIGH | Retired | 2017-04-01 | 2017-12-31 | RC
IRO-002-4 | Reliability Coordination — Monitoring and Analysis | R2. | Each Reliability Coordinator shall provide its System Operators with the authority to approve planned outages and maintenance of its telecommunication, monitoring and analysis capabilities. [Violation Risk Factor: High] [Time Horizon: Operations Planning, Same-Day Operations, Real-time Operations] | HIGH | Retired | 2017-04-01 | 2017-12-31 | RC
IRO-002-4 | Reliability Coordination — Monitoring and Analysis | R3. | Each Reliability Coordinator shall monitor Facilities, the status of Special Protection Systems, and non-BES facilities identified as necessary by the Reliability Coordinator, within its Reliability Coordinator Area and neighboring Reliability Coordinator Areas to identify any System Operating Limit exceedances and to determine any Interconnection Reliability Operating Limit exceedances within its Reliability Coordinator Area. [Violation Risk Factor: High] [Time Horizon: Real-Time Operations] | HIGH | Retired | 2017-04-01 | 2017-12-31 | RC
IRO-002-4 | Reliability Coordination — Monitoring and Analysis | R4. | Each Reliability Coordinator shall have monitoring systems that provide information utilized by the Reliability Coordinator’s operating personnel, giving particular emphasis to alarm management and awareness systems, automated data transfers, and synchronized information systems, over a redundant infrastructure. [Violation Risk Factor: High] [Time Horizon: Real-time Operations] | HIGH | Retired | 2017-04-01 | 2017-12-31 | RC
IRO-002-5 | Reliability Coordination — Monitoring and Analysis | R1. | Each Reliability Coordinator shall have data exchange capabilities with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, for it to perform its Operational Planning Analyses. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Retired | 2018-01-01 | 2019-12-31 | RC
IRO-002-5 | Reliability Coordination — Monitoring and Analysis | R2. | Each Reliability Coordinator shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Reliability Coordinator's primary Control Center, for the exchange of Real-time data with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, for performing its Real-time monitoring and Real-time Assessments. [Violation Risk Factor: High] [Time Horizon: Same-Day Operations, Real-time Operations] | HIGH | Retired | 2018-01-01 | 2019-12-31 | RC
IRO-002-5 | Reliability Coordination — Monitoring and Analysis | R3. | Each Reliability Coordinator shall test its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Reliability Coordinator shall initiate action within two hours to restore redundant functionality. [Violation Risk Factor: Medium ] [Time Horizon: Operations Planning] | MEDIUM | Retired | 2018-01-01 | 2019-12-31 | RC
IRO-002-5 | Reliability Coordination — Monitoring and Analysis | R4. | Each Reliability Coordinator shall provide its System Operators with the authority to approve planned outages and maintenance of its telecommunication, monitoring and analysis capabilities. [Violation Risk Factor: High] [Time Horizon: Operations Planning, Same-Day Operations, Real-time Operations] | HIGH | Retired | 2018-01-01 | 2019-12-31 | RC
IRO-002-5 | Reliability Coordination — Monitoring and Analysis | R5. | Each Reliability Coordinator shall monitor Facilities, the status of Remedial Action Schemes, and non-BES facilities identified as necessary by the Reliability Coordinator, within its Reliability Coordinator Area and neighboring Reliability Coordinator Areas to identify any System Operating Limit exceedances and to determine any Interconnection Reliability Operating Limit exceedances within its Reliability Coordinator Area. [Violation Risk Factor: High] [Time Horizon: Real-Time Operations] | HIGH | Retired | 2018-01-01 | 2019-12-31 | RC
IRO-002-5 | Reliability Coordination — Monitoring and Analysis | R6. | Each Reliability Coordinator shall have monitoring systems that provide information utilized by the Reliability Coordinator’s operating personnel, giving particular emphasis to alarm management and awareness systems, automated data transfers, and synchronized information systems, over a redundant infrastructure. [Violation Risk Factor: High] [Time Horizon: Real-time Operations] | HIGH | Retired | 2018-01-01 | 2019-12-31 | RC
IRO-002-6 | Reliability Coordination – Monitoring and Analysis | R1. | Each Reliability Coordinator shall have data exchange capabilities with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, for it to perform its Operational Planning Analyses. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Retired | 2020-01-01 | 2021-03-31 | RC
IRO-002-6 | Reliability Coordination – Monitoring and Analysis | R2. | Each Reliability Coordinator shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Reliability Coordinator's primary Control Center, for the exchange of Real-time data with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, for performing its Real-time monitoring and Real-time Assessments. [Violation Risk Factor: High] [Time Horizon: Same-Day Operations, Real-time Operations] | HIGH | Retired | 2020-01-01 | 2021-03-31 | RC
IRO-002-6 | Reliability Coordination – Monitoring and Analysis | R3. | Each Reliability Coordinator shall test its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Reliability Coordinator shall initiate action within two hours to restore redundant functionality. [Violation Risk Factor: Medium ] [Time Horizon: Operations Planning] | MEDIUM | Retired | 2020-01-01 | 2021-03-31 | RC
IRO-002-6 | Reliability Coordination – Monitoring and Analysis | R4. | Each Reliability Coordinator shall provide its System Operators with the authority to approve planned outages and maintenance of its telecommunication, monitoring and analysis capabilities. [Violation Risk Factor: High] [Time Horizon: Operations Planning, Same-Day Operations, Real-time Operations] | HIGH | Retired | 2020-01-01 | 2021-03-31 | RC
IRO-002-6 | Reliability Coordination – Monitoring and Analysis | R5. | Each Reliability Coordinator shall monitor Facilities, the status of Remedial Action Schemes, and non-BES facilities identified as necessary by the Reliability Coordinator, within its Reliability Coordinator Area and neighboring Reliability Coordinator Areas to identify any System Operating Limit exceedances and to determine any Interconnection Reliability Operating Limit exceedances within its Reliability Coordinator Area. [Violation Risk Factor: High] [Time Horizon: Real-Time Operations] | HIGH | Retired | 2020-01-01 | 2021-03-31 | RC
IRO-002-6 | Reliability Coordination – Monitoring and Analysis | R6. | Each Reliability Coordinator shall have monitoring systems that provide information utilized by the Reliability Coordinator’s operating personnel, giving particular emphasis to alarm management and awareness systems, automated data transfers, and synchronized information systems, over a redundant infrastructure. [Violation Risk Factor: High] [Time Horizon: Real-time Operations] | HIGH | Retired | 2020-01-01 | 2021-03-31 | RC
IRO-002-7 | Reliability Coordination - Monitoring and Analysis | R1. | Reserved. (retired in SAR) | HIGH | Effective | 2021-04-01 |  | RC
IRO-002-7 | Reliability Coordination - Monitoring and Analysis | R2. | Each Reliability Coordinator shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Reliability Coordinator's primary Control Center, for the exchange of Real-time data with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, for performing its Real-time monitoring and Real-time Assessments. [Violation Risk Factor: High] [Time Horizon: Same-Day Operations, Real-time Operations] | HIGH | Effective | 2021-04-01 |  | RC
IRO-002-7 | Reliability Coordination - Monitoring and Analysis | R3. | Each Reliability Coordinator shall test its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Reliability Coordinator shall initiate action within two hours to restore redundant functionality. [Violation Risk Factor: Medium ] [Time Horizon: Operations Planning] | MEDIUM | Effective | 2021-04-01 |  | RC
IRO-002-7 | Reliability Coordination - Monitoring and Analysis | R4. | Each Reliability Coordinator shall provide its System Operators with the authority to approve planned outages and maintenance of its telecommunication, monitoring and analysis capabilities. [Violation Risk Factor: High] [Time Horizon: Operations Planning, Same-Day Operations, Real-time Operations] | HIGH | Effective | 2021-04-01 |  | RC
IRO-002-7 | Reliability Coordination - Monitoring and Analysis | R5. | Each Reliability Coordinator shall monitor Facilities, the status of Remedial Action Schemes, and non-BES facilities identified as necessary by the Reliability Coordinator, within its Reliability Coordinator Area and neighboring Reliability Coordinator Areas to identify any System Operating Limit exceedances and to determine any Interconnection Reliability Operating Limit exceedances within its Reliability Coordinator Area. [Violation Risk Factor: High] [Time Horizon: Real-Time Operations] | HIGH | Effective | 2021-04-01 |  | RC
IRO-002-7 | Reliability Coordination - Monitoring and Analysis | R6. | Each Reliability Coordinator shall have monitoring systems that provide information utilized by the Reliability Coordinator’s operating personnel, giving particular emphasis to alarm management and awareness systems, automated data transfers, and synchronized information systems, over a redundant infrastructure. [Violation Risk Factor: High] [Time Horizon: Real-time Operations] | HIGH | Effective | 2021-04-01 |  | RC
IRO-003-2 | Reliability Coordination - Wide-Area View | R1. | Each Reliability Coordinator shall monitor all Bulk Electric System facilities, which may include sub-transmission information, within its Reliability Coordinator Area and adjacent Reliability Coordinator Areas, as necessary to ensure that, at any time, regardless of prior planned or unplanned events, the Reliability Coordinator is able to determine any potential System Operating Limit and Interconnection Reliability Operating Limit violations within its Reliability Coordinator Area. | HIGH | Retired | 2006-11-01 | 2017-03-31 | RC
IRO-003-2 | Reliability Coordination - Wide-Area View | R2. | Each Reliability Coordinator shall know the current status of all critical facilities whose failure, degradation or disconnection could result in an SOL or IROL violation. Reliability Coordinators shall also know the status of any facilities that may be required to assist area restoration objectives. | HIGH | Retired | 2006-11-01 | 2017-03-31 | RC
IRO-004-2 | Reliability Coordination - Operations Planning | R1. | Each Transmission Operator, Balancing Authority, and Transmission Service Provider shall comply with the directives of its Reliability Coordinator based on the next day assessments in the same manner in which it would comply during real time operating events. | HIGH | Retired | 2011-10-01 | 2017-03-31 | TSP, TOP, BA
IRO-005-3.1(i)a | Reliability Coordination — Current Day Operations | R1. | Each Reliability Coordinator shall monitor its Reliability Coordinator Area parameters, including but not limited to the following: | N/A | Never Came Into Effect in Ontario |  |  | RC
IRO-005-3.1(i)a | Reliability Coordination — Current Day Operations | R1.1. | Current status of Bulk Electric System elements (transmission or generation including critical auxiliaries such as Automatic Voltage Regulators and Remedial Action Schemes) and system loading. | N/A | Never Came Into Effect in Ontario |  |  | RC
IRO-005-3.1(i)a | Reliability Coordination — Current Day Operations | R1.10. | Contingency events. | N/A | Never Came Into Effect in Ontario |  |  | RC
IRO-005-3.1(i)a | Reliability Coordination — Current Day Operations | R1.2. | Current pre-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. | N/A | Never Came Into Effect in Ontario |  |  | RC
IRO-005-3.1(i)a | Reliability Coordination — Current Day Operations | R1.3. | Current post-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. | N/A | Never Came Into Effect in Ontario |  |  | RC
IRO-005-3.1(i)a | Reliability Coordination — Current Day Operations | R1.4. | System real and reactive reserves (actual versus required). | N/A | Never Came Into Effect in Ontario |  |  | RC
IRO-005-3.1(i)a | Reliability Coordination — Current Day Operations | R1.5. | Capacity and energy adequacy conditions. | N/A | Never Came Into Effect in Ontario |  |  | RC
IRO-005-3.1(i)a | Reliability Coordination — Current Day Operations | R1.6. | Current ACE for all its Balancing Authorities. | N/A | Never Came Into Effect in Ontario |  |  | RC
IRO-005-3.1(i)a | Reliability Coordination — Current Day Operations | R1.7. | Current local or Transmission Loading Relief procedures in effect. | N/A | Never Came Into Effect in Ontario |  |  | RC
IRO-005-3.1(i)a | Reliability Coordination — Current Day Operations | R1.8. | Planned generation dispatches. | N/A | Never Came Into Effect in Ontario |  |  | RC
IRO-005-3.1(i)a | Reliability Coordination — Current Day Operations | R1.9. | Planned transmission or generation outages. | N/A | Never Came Into Effect in Ontario |  |  | RC
IRO-005-3.1(i)a | Reliability Coordination — Current Day Operations | R10. | In instances where there is a difference in derived limits, the Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities shall always operate the Bulk Electric System to the most limiting parameter. | N/A | Never Came Into Effect in Ontario |  |  | TSP, TOP, GOP, BA
IRO-005-3.1(i)a | Reliability Coordination — Current Day Operations | R11. | The Transmission Service Provider shall respect SOLs and IROLs in accordance with filed tariffs and regional Total Transfer Calculation and Available Transfer Calculation processes. | N/A | Never Came Into Effect in Ontario |  |  | TSP
IRO-005-3.1(i)a | Reliability Coordination — Current Day Operations | R12. | Each Reliability Coordinator who foresees a transmission problem (such as an SOL or IROL violation, loss of reactive reserves, etc.) within its Reliability Coordinator Area shall issue an alert to all impacted Transmission Operators and Balancing Authorities in its Reliability Coordinator Area without delay. The receiving Reliability Coordinator shall disseminate this information to its impacted Transmission Operators and Balancing Authorities. The Reliability Coordinator shall notify all impacted Transmission Operators, Balancing Authorities, when the transmission problem has been mitigated. | N/A | Never Came Into Effect in Ontario |  |  | RC
IRO-005-3.1(i)a | Reliability Coordination — Current Day Operations | R2. | Each Reliability Coordinator shall monitor its Balancing Authorities’ parameters to ensure that the required amount of operating reserves is provided and available as required to meet the Control Performance Standard and Disturbance Control Standard requirements. If necessary, the Reliability Coordinator shall direct the Balancing Authorities in the Reliability Coordinator Area to arrange for assistance from neighboring Balancing Authorities. The Reliability Coordinator shall issue Energy Emergency Alerts as needed and at the request of its Balancing Authorities and Load-Serving Entities. | N/A | Never Came Into Effect in Ontario |  |  | RC
IRO-005-3.1(i)a | Reliability Coordination — Current Day Operations | R3. | Each Reliability Coordinator shall ensure its Transmission Operators and Balancing Authorities are aware of Geo-Magnetic Disturbance (GMD) forecast information and assist as needed in the development of any required response plans. | N/A | Never Came Into Effect in Ontario |  |  | RC
IRO-005-3.1(i)a | Reliability Coordination — Current Day Operations | R4. | The Reliability Coordinator shall disseminate information within its Reliability Coordinator Area, as required. | N/A | Never Came Into Effect in Ontario |  |  | RC
IRO-005-3.1(i)a | Reliability Coordination — Current Day Operations | R5. | Each Reliability Coordinator shall monitor system frequency and its Balancing Authorities’ performance and direct any necessary rebalancing to return to CPS and DCS compliance. The Transmission Operators and Balancing Authorities shall utilize all resources, including firm load shedding, as directed by its Reliability Coordinator to relieve the emergent condition. | N/A | Never Came Into Effect in Ontario |  |  | TOP, RC, BA
IRO-005-3.1(i)a | Reliability Coordination — Current Day Operations | R6. | The Reliability Coordinator shall coordinate with Transmission Operators, Balancing Authorities, and Generator Operators as needed to develop and implement action plans to mitigate potential or actual SOL, CPS, or DCS violations. The Reliability Coordinator shall coordinate pending generation and transmission maintenance outages with Transmission Operators, Balancing Authorities, and Generator Operators as needed in both the real time and next-day reliability analysis timeframes. | N/A | Never Came Into Effect in Ontario |  |  | RC
IRO-005-3.1(i)a | Reliability Coordination — Current Day Operations | R7. | As necessary, the Reliability Coordinator shall assist the Balancing Authorities in its Reliability Coordinator Area in arranging for assistance from neighboring Reliability Coordinator Areas or Balancing Authorities. | N/A | Never Came Into Effect in Ontario |  |  | RC
IRO-005-3.1(i)a | Reliability Coordination — Current Day Operations | R8. | The Reliability Coordinator shall identify sources of large Area Control Errors that may be contributing to Frequency Error, Time Error, or Inadvertent Interchange and shall discuss corrective actions with the appropriate Balancing Authority. The Reliability Coordinator shall direct its Balancing Authority to comply with CPS and DCS. | N/A | Never Came Into Effect in Ontario |  |  | RC
IRO-005-3.1(i)a | Reliability Coordination — Current Day Operations | R9. | Whenever a Remedial Action Scheme that may have an inter-Balancing Authority, or inter-Transmission Operator impact (e.g., could potentially affect transmission flows resulting in a SOL or IROL violation) is armed, the Reliability Coordinators shall be aware of the impact of the operation of that Remedial Action Scheme on inter-area flows. The Transmission Operator shall immediately inform the Reliability Coordinator of the status of the Remedial Action Scheme including any degradation or potential failure to operate as expected. | N/A | Never Came Into Effect in Ontario |  |  | TOP, RC
IRO-005-3.1a | Reliability Coordination — Current Day Operations | R1. | Each Reliability Coordinator shall monitor its Reliability Coordinator Area parameters, including but not limited to the following: | N/A | Retired | 2012-10-10 | 2017-03-31 | RC
IRO-005-3.1a | Reliability Coordination — Current Day Operations | R1.1. | Current status of Bulk Electric System elements (transmission or generation including critical auxiliaries such as Automatic Voltage Regulators and Special Protection Systems) and system loading. | N/A | Retired | 2012-10-10 | 2017-03-31 | RC
IRO-005-3.1a | Reliability Coordination — Current Day Operations | R1.10. | Contingency events. | N/A | Retired | 2012-10-10 | 2017-03-31 | RC
IRO-005-3.1a | Reliability Coordination — Current Day Operations | R1.2. | Current pre-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. | N/A | Retired | 2012-10-10 | 2017-03-31 | RC
IRO-005-3.1a | Reliability Coordination — Current Day Operations | R1.3. | Current post-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. | N/A | Retired | 2012-10-10 | 2017-03-31 | RC
IRO-005-3.1a | Reliability Coordination — Current Day Operations | R1.4. | System real and reactive reserves (actual versus required). | N/A | Retired | 2012-10-10 | 2017-03-31 | RC
IRO-005-3.1a | Reliability Coordination — Current Day Operations | R1.5. | Capacity and energy adequacy conditions. | N/A | Retired | 2012-10-10 | 2017-03-31 | RC
IRO-005-3.1a | Reliability Coordination — Current Day Operations | R1.6. | Current ACE for all its Balancing Authorities. | N/A | Retired | 2012-10-10 | 2017-03-31 | RC
IRO-005-3.1a | Reliability Coordination — Current Day Operations | R1.7. | Current local or Transmission Loading Relief procedures in effect. | N/A | Retired | 2012-10-10 | 2017-03-31 | RC
IRO-005-3.1a | Reliability Coordination — Current Day Operations | R1.8. | Planned generation dispatches. | N/A | Retired | 2012-10-10 | 2017-03-31 | RC
IRO-005-3.1a | Reliability Coordination — Current Day Operations | R1.9. | Planned transmission or generation outages. | N/A | Retired | 2012-10-10 | 2017-03-31 | RC
IRO-005-3.1a | Reliability Coordination — Current Day Operations | R10. | In instances where there is a difference in derived limits, the Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities shall always operate the Bulk Electric System to the most limiting parameter. | N/A | Retired | 2012-10-10 | 2017-03-31 | TSP, TOP, GOP, BA
IRO-005-3.1a | Reliability Coordination — Current Day Operations | R11. | The Transmission Service Provider shall respect SOLs and IROLs in accordance with filed tariffs and regional Total Transfer Calculation and Available Transfer Calculation processes. | N/A | Retired | 2012-10-10 | 2017-03-31 | TSP
IRO-005-3.1a | Reliability Coordination — Current Day Operations | R12. | Each Reliability Coordinator who foresees a transmission problem (such as an SOL or IROL violation, loss of reactive reserves, etc.) within its Reliability Coordinator Area shall issue an alert to all impacted Transmission Operators and Balancing Authorities in its Reliability Coordinator Area without delay. The receiving Reliability Coordinator shall disseminate this information to its impacted Transmission Operators and Balancing Authorities. The Reliability Coordinator shall notify all impacted Transmission Operators, Balancing Authorities, when the transmission problem has been mitigated. | N/A | Retired | 2012-10-10 | 2017-03-31 | RC
IRO-005-3.1a | Reliability Coordination — Current Day Operations | R2. | Each Reliability Coordinator shall monitor its Balancing Authorities’ parameters to ensure that the required amount of operating reserves is provided and available as required to meet the Control Performance Standard and Disturbance Control Standard requirements. If necessary, the Reliability Coordinator shall direct the Balancing Authorities in the Reliability Coordinator Area to arrange for assistance from neighboring Balancing Authorities. The Reliability Coordinator shall issue Energy Emergency Alerts as needed and at the request of its Balancing Authorities and Load-Serving Entities. | N/A | Retired | 2012-10-10 | 2017-03-31 | RC
IRO-005-3.1a | Reliability Coordination — Current Day Operations | R3. | Each Reliability Coordinator shall ensure its Transmission Operators and Balancing Authorities are aware of Geo-Magnetic Disturbance (GMD) forecast information and assist as needed in the development of any required response plans. | N/A | Retired | 2012-10-10 | 2017-03-31 | RC
IRO-005-3.1a | Reliability Coordination — Current Day Operations | R4. | The Reliability Coordinator shall disseminate information within its Reliability Coordinator Area, as required. | N/A | Retired | 2012-10-10 | 2017-03-31 | RC
IRO-005-3.1a | Reliability Coordination — Current Day Operations | R5. | Each Reliability Coordinator shall monitor system frequency and its Balancing Authorities’ performance and direct any necessary rebalancing to return to CPS and DCS compliance. The Transmission Operators and Balancing Authorities shall utilize all resources, including firm load shedding, as directed by its Reliability Coordinator to relieve the emergent condition. | N/A | Retired | 2012-10-10 | 2017-03-31 | TOP, RC, BA
IRO-005-3.1a | Reliability Coordination — Current Day Operations | R6. | The Reliability Coordinator shall coordinate with Transmission Operators, Balancing Authorities, and Generator Operators as needed to develop and implement action plans to mitigate potential or actual SOL, CPS, or DCS violations. The Reliability Coordinator shall coordinate pending generation and transmission maintenance outages with Transmission Operators, Balancing Authorities, and Generator Operators as needed in both the real time and next-day reliability analysis timeframes. | N/A | Retired | 2012-10-10 | 2017-03-31 | RC
IRO-005-3.1a | Reliability Coordination — Current Day Operations | R7. | As necessary, the Reliability Coordinator shall assist the Balancing Authorities in its Reliability Coordinator Area in arranging for assistance from neighboring Reliability Coordinator Areas or Balancing Authorities. | N/A | Retired | 2012-10-10 | 2017-03-31 | RC
IRO-005-3.1a | Reliability Coordination — Current Day Operations | R8. | The Reliability Coordinator shall identify sources of large Area Control Errors that may be contributing to Frequency Error, Time Error, or Inadvertent Interchange and shall discuss corrective actions with the appropriate Balancing Authority. The Reliability Coordinator shall direct its Balancing Authority to comply with CPS and DCS. | N/A | Retired | 2012-10-10 | 2017-03-31 | RC
IRO-005-3.1a | Reliability Coordination — Current Day Operations | R9. | Whenever a Special Protection System that may have an inter-Balancing Authority, or inter-Transmission Operator impact (e.g., could potentially affect transmission flows resulting in a SOL or IROL violation) is armed, the Reliability Coordinators shall be aware of the impact of the operation of that Special Protection System on inter-area flows. The Transmission Operator shall immediately inform the Reliability Coordinator of the status of the Special Protection System including any degradation or potential failure to operate as expected. | N/A | Retired | 2012-10-10 | 2017-03-31 | TOP, RC
IRO-005-4 | Reliability Coordination — Current Day Operations | R1. | When the results of an Operational Planning Analysis or Real-time Assessment indicate an anticipated or actual condition with Adverse Reliability Impacts within its Reliability Coordinator Area, each Reliability Coordinator shall notify all impacted Transmission Operators and Balancing Authorities in its Reliability Coordinator Area. | HIGH | Never Came Into Effect in Ontario |  |  | RC
IRO-005-4 | Reliability Coordination — Current Day Operations | R1. | When the results of an Operational Planning Analysis or Real-time Assessment indicate an anticipated or actual condition with Adverse Reliability Impacts within its Reliability Coordinator Area, each Reliability Coordinator shall notify all impacted Transmission Operators and Balancing Authorities in its Reliability Coordinator Area. | HIGH | Never Came Into Effect in Ontario |  |  | RC
IRO-005-4 | Reliability Coordination — Current Day Operations | R2. | Each Reliability Coordinator that identifies an anticipated or actual condition with Adverse Reliability Impacts within its Reliability Coordinator Area shall notify all impacted Transmission Operators and Balancing Authorities in its Reliability Coordinator Area when the problem has been mitigated. | MEDIUM | Never Came Into Effect in Ontario |  |  | RC
IRO-005-4 | Reliability Coordination — Current Day Operations | R2. | Each Reliability Coordinator that identifies an anticipated or actual condition with Adverse Reliability Impacts within its Reliability Coordinator Area shall notify all impacted Transmission Operators and Balancing Authorities in its Reliability Coordinator Area when the problem has been mitigated. | MEDIUM | Never Came Into Effect in Ontario |  |  | RC
IRO-006-5 | Reliability Coordination - Transmission Loading Relief (TLR) | R1. | Each Reliability Coordinator and Balancing Authority that receives a request pursuant to an Interconnection-wide transmission loading relief procedure (such as Eastern Interconnection TLR, WECC Unscheduled Flow Mitigation, or congestion management procedures from the ERCOT Protocols) from any Reliability Coordinator, Balancing Authority, or Transmission Operator in another Interconnection to curtail an Interchange Transaction that crosses an Interconnection boundary shall comply with the request, unless it provides a reliability reason to the requestor why it cannot comply with the request. | HIGH | Effective | 2011-10-01 |  | RC, BA
IRO-006-EAST-1 | Transmission Loading Relief Procedure for the Eastern Interconnection | R1. | When acting or instructing others to act to mitigate the magnitude and duration of the instance of exceeding an IROL within that IROL’s TV • Inter-area redispatch of generation , each Reliability Coordinator shall initiate, prior to or concurrently with the initiation of the Eastern Interconnection TLR procedure (or continuing management of this procedure if already initiated), one or more of the following actions: • Intra-area redispatch of generation • Reconfiguration of the transmission system • Voluntary load reductions (e.g., Demand-side Management) • Controlled load reductions (e.g., load shedding) | HIGH | Retired | 2011-01-01 | 2016-06-30 | RC
IRO-006-EAST-1 | Transmission Loading Relief Procedure for the Eastern Interconnection | R2. | To ensure operating entities are provided with information needed to maintain an awareness of changes to the Transmission System, when initiating the Eastern Interconnection TLR procedure to prevent or mitigate an SOL or IROL exceedance, and at least every clock hour (with the exception of TLR-1, where an hourly update is not required) after initiation up to and including the hour when the TLR level has been identified as TLR Level 0, the Reliability Coordinator shall identify: | MEDIUM | Retired | 2011-01-01 | 2016-06-30 | RC
IRO-006-EAST-1 | Transmission Loading Relief Procedure for the Eastern Interconnection | R2.1. | A list of congestion management actions to be implemented, and | No Individual VRF Assigned | Retired | 2011-01-01 | 2016-06-30 | RC
IRO-006-EAST-1 | Transmission Loading Relief Procedure for the Eastern Interconnection | R2.2. | One of the following TLR levels: TLR-1, TLR-2, TLR-3A, TLR-3B, TLR-4, TLR-5A, TLR-5B, TLR-6, TLR-0 | No Individual VRF Assigned | Retired | 2011-01-01 | 2016-06-30 | RC
IRO-006-EAST-1 | Transmission Loading Relief Procedure for the Eastern Interconnection | R3. | Upon the identification of the TLR level and a list of congestion management actions to be implemented, the Reliability Coordinator initiating this TLR procedure shall: | MEDIUM | Retired | 2011-01-01 | 2016-06-30 | RC
IRO-006-EAST-1 | Transmission Loading Relief Procedure for the Eastern Interconnection | R3.1. | Notify all Reliability Coordinators in the Eastern Interconnection of the identified TLR level | No Individual VRF Assigned | Retired | 2011-01-01 | 2016-06-30 | RC
IRO-006-EAST-1 | Transmission Loading Relief Procedure for the Eastern Interconnection | R3.2. | Communicate the list of congestion management actions to be implemented to 1.) all Reliability Coordinators in the Eastern Interconnection, and 2.) those Reliability Coordinators in other Interconnections responsible for curtailing Interchange Transactions crossing Interconnection boundaries identified in the list of congestion management actions. | No Individual VRF Assigned | Retired | 2011-01-01 | 2016-06-30 | RC
IRO-006-EAST-1 | Transmission Loading Relief Procedure for the Eastern Interconnection | R3.3. | Request that the congestion management actions identified in Requirement R2, Part 2.1 be implemented by: 1.) Each Reliability Coordinator associated with a Sink Balancing Authority for which Interchange Transactions are to be curtailed, 2.) Each Reliability Coordinator associated with a Balancing Authority in the Eastern Interconnection for which Network Integration Transmission Service or Native Load is to be curtailed, and 3.) Each Reliability Coordinator associated with a Balancing Authority in the Eastern Interconnection for which its Market Flow is to be curtailed. | No Individual VRF Assigned | Retired | 2011-01-01 | 2016-06-30 | RC
IRO-006-EAST-1 | Transmission Loading Relief Procedure for the Eastern Interconnection | R4. | Each Reliability Coordinator that receives a request as described in Requirement R3, Part 3.3. shall, within 15 minutes of receiving the request, implement the congestion management actions requested by the issuing Reliability Coordinator as follows: • Instruct its Balancing Authorities to implement the Interchange Transaction schedule change requests. • Instruct its Balancing Authorities to implement the Network Integration Transmission Service and Native Load schedule changes for which the Balancing Authorities are responsible. • Instruct its Balancing Authorities to implement the Market Flow schedule changes for which the Balancing Authorities are responsible. • If an assessment shows that one or more of the congestion management actions communicated in Requirement R3, Part 3.3 will result in a reliability concern or will be ineffective, the Reliability Coordinator may replace those specific actions with alternate congestion management actions, provided that: o The alternate congestion management actions have been agreed to by the initiating Reliability Coordinator, and o The assessment shows that the alternate congestion management actions will not adversely affect reliability. | HIGH | Retired | 2011-01-01 | 2016-06-30 | RC
IRO-006-EAST-2 | Transmission Loading Relief Procedure for the Eastern Interconnection | R1. | Each Reliability Coordinator that initiates the Eastern Interconnection TLR procedure to prevent or mitigate an SOL or IROL exceedance shall identify the TLR level and the congestion management actions to be implemented, and shall update this information at least every clock hour (except TLR-1) after initiation up to and including the hour when the TLR level has been identified as TLR Level 0.1 [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | MEDIUM | Effective | 2016-07-01 |  | RC
IRO-006-EAST-2 | Transmission Loading Relief Procedure for the Eastern Interconnection | R2. | Each Reliability Coordinator with a Sink Balancing Authority that must implement congestion management actions pursuant to the Eastern Interconnection TLR procedure shall, within 15 minutes of receiving the request from the issuing Reliability Coordinator, instruct the Sink Balancing Authority to implement the congestion management actions, subject to the following exception: [Violation Risk Factor: High] [Time Horizon: Real-time Operations ] ● Should an assessment determine that one or more of the congestion management actions communicated will result in a reliability concern or will be ineffective, the Reliability Coordinator with a Sink Balancing Authority shall coordinate alternate congestion management actions with the issuing Reliability Coordinator. | HIGH | Effective | 2016-07-01 |  | RC
IRO-008-1 | Reliability Coordinator Operational Analyses and Real-time Assessments | R1. | Each Reliability Coordinator shall perform an Operational Planning Analysis to assess whether the planned operations for the next day within its Wide Area, will exceed any of its Interconnection Reliability Operating Limits (IROLs) during anticipated normal and Contingency event conditions. (Time Horizon: Operations Planning) | HIGH | Retired | 2011-10-01 | 2017-03-31 | RC
IRO-008-1 | Reliability Coordinator Operational Analyses and Real-time Assessments | R1. | Each Reliability Coordinator shall perform an Operational Planning Analysis to assess whether the planned operations for the next day within its Wide Area, will exceed any of its Interconnection Reliability Operating Limits (IROLs) during anticipated normal and Contingency event conditions. (Time Horizon: Operations Planning) | HIGH | Retired | 2011-10-01 | 2017-03-31 | RC
IRO-008-1 | Reliability Coordinator Operational Analyses and Real-time Assessments | R2. | Each Reliability Coordinator shall perform a Real-Time Assessment at least once every 30 minutes to determine if its Wide Area is exceeding any IROLs or is expected to exceed any IROLs. (Time Horizon: Real-time Operations) | HIGH | Retired | 2011-10-01 | 2017-03-31 | RC
IRO-008-1 | Reliability Coordinator Operational Analyses and Real-time Assessments | R3. | When a Reliability Coordinator determines that the results of an Operational Planning Analysis or Real-Time Assessment indicates the need for specific operational actions to prevent or mitigate an instance of exceeding an IROL, the Reliability Coordinator shall share its results with those entities that are expected to take those actions. (Time Horizon: Real-time Operations or Same Day Operations) | MEDIUM | Retired | 2011-10-01 | 2017-03-31 | RC
IRO-008-2 | Reliability Coordinator Operational Analyses and Real-time Assessments | R1. | Each Reliability Coordinator shall perform an Operational Planning Analysis that will allow it to assess whether the planned operations for the next-day will exceed System Operating Limits (SOLs) and Interconnection Operating Reliability Limits (IROLs) within its Wide Area. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Effective | 2017-04-01 |  | RC
IRO-008-2 | Reliability Coordinator Operational Analyses and Real-time Assessments | R2. | Each Reliability Coordinator shall have a coordinated Operating Plan(s) for next-day operations to address potential System Operating Limit (SOL) and Interconnection Reliability Operating Limit (IROL) exceedances identified as a result of its Operational Planning Analysis as performed in Requirement R1 while considering the Operating Plans for the next-day provided by its Transmission Operators and Balancing Authorities. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Effective | 2017-04-01 |  | RC
IRO-008-2 | Reliability Coordinator Operational Analyses and Real-time Assessments | R3. | Each Reliability Coordinator shall notify impacted entities identified in its Operating Plan(s) cited in Requirement R2 as to their role in such plan(s). [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Effective | 2017-04-01 |  | RC
IRO-008-2 | Reliability Coordinator Operational Analyses and Real-time Assessments | R4. | Each Reliability Coordinator shall ensure that a Real-time Assessment is performed at least once every 30 minutes. [Violation Risk Factor: High] [Time Horizon: Sameday Operations, Real-time Operations] | HIGH | Effective | 2017-04-01 |  | RC
IRO-008-2 | Reliability Coordinator Operational Analyses and Real-time Assessments | R5. | Each Reliability Coordinator shall notify impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area, and other impacted Reliability Coordinators as indicated in its Operating Plan, when the results of a Realtime Assessment indicate an actual or expected condition that results in, or could result in, a System Operating Limit (SOL) or Interconnection Reliability Operating Limit (IROL) exceedance within its Wide Area. [Violation Risk Factor: High] [Time Horizon: Same-Day Operations, Real-time Operations] | HIGH | Effective | 2017-04-01 |  | RC
IRO-008-2 | Reliability Coordinator Operational Analyses and Real-time Assessments | R6. | Each Reliability Coordinator shall notify impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area, and other impacted Reliability Coordinators as indicated in its Operating Plan, when the System Operating Limit (SOL) or Interconnection Reliability Operating Limit (IROL) exceedance identified in Requirement R5 has been prevented or mitigated. [Violation Risk Factor: Medium] [Time Horizon: Same-Day Operations, Real-time Operations] | MEDIUM | Effective | 2017-04-01 |  | RC
IRO-008-3 | Reliability Coordinator Operational Analyses and Real-time Assessments | R1. | Each Reliability Coordinator shall perform an Operational Planning Analysis that will allow it to assess whether the planned operations for the next-day will exceed System Operating Limits (SOLs) and Interconnection Reliability Operating Limits (IROLs) within its Wide Area. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Effective | 2024-04-01 |  | RC
IRO-008-3 | Reliability Coordinator Operational Analyses and Real-time Assessments | R2. | Each Reliability Coordinator shall have a coordinated Operating Plan(s) for next-day operations to address potential System Operating Limit (SOL) and Interconnection Reliability Operating Limit (IROL) exceedances identified as a result of its Operational Planning Analysis as performed in Requirement R1 while considering the Operating Plans for the next-day provided by its Transmission Operators and Balancing Authorities. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Effective | 2024-04-01 |  | RC
IRO-008-3 | Reliability Coordinator Operational Analyses and Real-time Assessments | R3. | Each Reliability Coordinator shall notify impacted entities identified in its Operating Plan(s) cited in Requirement R2 as to their role in such plan(s). [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Effective | 2024-04-01 |  | RC
IRO-008-3 | Reliability Coordinator Operational Analyses and Real-time Assessments | R4. | Each Reliability Coordinator shall ensure that a Real-time Assessment is performed at least once every 30 minutes. [Violation Risk Factor: High] [Time Horizon: Sameday Operations, Real-time Operations] | HIGH | Effective | 2024-04-01 |  | RC
IRO-008-3 | Reliability Coordinator Operational Analyses and Real-time Assessments | R5. | Each Reliability Coordinator shall notify, in accordance with its SOL methodology, impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area, and other impacted Reliability Coordinators as indicated in its Operating Plan, when the results of a Realtime Assessment indicate an actual or expected condition that results in, or could result in, a System Operating Limit (SOL) exceedance or an Interconnection Reliability Operating Limit (IROL) exceedance within its Wide Area. [Violation Risk Factor: High] [Time Horizon: Same-Day Operations, Real-time Operations] | HIGH | Effective | 2024-04-01 |  | RC
IRO-008-3 | Reliability Coordinator Operational Analyses and Real-time Assessments | R6. | Each Reliability Coordinator shall notifyy, in accordance with SOL methodology, impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area, and other impacted Reliability Coordinators as indicated in its Operating Plan, when the System Operating Limit (SOL) exceedance or an Interconnection Reliability Operating Limit (IROL) exceedance identified in Requirement R5 has been prevented or mitigated.[Violation Risk Factor: Medium] [Time Horizon: Same-Day Operations, Real-time Operations] | MEDIUM | Effective | 2024-04-01 |  | RC
IRO-008-3 | Reliability Coordinator Operational Analyses and Real-time Assessments | R7. | Each Reliability Coordinator shall use its SOL methodology when determining SOL exceedances for Real-time Assessments, Real-time monitoring, and Operational Planning Analysis. [Violation Risk Factor: Medium ] [Time Horizon: Same-Day Operations, Real-time Operations, Operations Planning] | MEDIUM | Effective | 2024-04-01 |  | RC
IRO-009-2 | Reliability Coordinator Actions to Operate Within IROLs | R1. | For each IROL (in its Reliability Coordinator Area) that the Reliability Coordinator identifies one or more days prior to the current day, the Reliability Coordinator shall have one or more Operating Processes, Procedures, or Plans that identify actions the Reliability Coordinator shall take or actions the Reliability Coordinator shall direct others to take (up to and including load shedding): [Violation Risk Factor: Medium] [Time Horizon: Operations Planning or Same Day Operations] | MEDIUM | Effective | 2016-04-01 |  | RC
IRO-009-2 | Reliability Coordinator Actions to Operate Within IROLs | R1.1. | That can be implemented in time to prevent the identified IROL exceedance. | MEDIUM | Effective | 2016-04-01 |  | RC
IRO-009-2 | Reliability Coordinator Actions to Operate Within IROLs | R1.2. | To mitigate the magnitude and duration of an IROL exceedance such that the IROL exceedance is relieved within the IROL’s Tv. | MEDIUM | Effective | 2016-04-01 |  | RC
IRO-009-2 | Reliability Coordinator Actions to Operate Within IROLs | R2. | Each Reliability Coordinator shall initiate one or more Operating Processes, Procedures, or Plans (not limited to the Operating Processes, Procedures, or Plans developed for Requirement R1) that are intended to prevent an IROL exceedance, as identified in the Reliability Coordinator’s Real-time monitoring or Real-time Assessment. [Violation Risk Factor: High] [Time Horizon: Real-time Operations] | HIGH | Effective | 2016-04-01 |  | RC
IRO-009-2 | Reliability Coordinator Actions to Operate Within IROLs | R3. | Each Reliability Coordinator shall act or direct others to act so that the magnitude and duration of an IROL exceedance is mitigated within the IROL’s Tv, as identified in the Reliability Coordinator’s Real-time monitoring or Real-time Assessment. [Violation Risk Factor: High] [Time Horizon: Real-time Operations] | HIGH | Effective | 2016-04-01 |  | RC
IRO-009-2 | Reliability Coordinator Actions to Operate Within IROLs | R4. | Each Reliability Coordinator shall operate to the most limiting IROL and Tv in instances where there is a difference in an IROL or its Tv between Reliability Coordinators that are responsible for that Facility (or group of Facilities). [Violation Risk Factor: High] [Time Horizon: Real-time Operations] | HIGH | Effective | 2016-04-01 |  | RC
IRO-010-1a | Reliability Coordinator Data Specification and Collection | R1. | The Reliability Coordinator shall have a documented specification for data and information to build and maintain models to support Real-time monitoring, Operational Planning Analyses, and Real-time Assessments of its Reliability Coordinator Area to prevent instability, uncontrolled separation, and cascading outages. The specification shall include the following: (Time Horizon: Operations Planning) | MEDIUM | Retired | 2011-10-01 | 2016-12-31 | RC
IRO-010-1a | Reliability Coordinator Data Specification and Collection | R1.1. | List of required data and information needed by the Reliability Coordinator to support Real-Time Monitoring, Operational Planning Analyses, and Real-Time Assessments. | No Individual VRF Assigned | Retired | 2011-10-01 | 2016-12-31 | RC
IRO-010-1a | Reliability Coordinator Data Specification and Collection | R1.2. | Mutually agreeable format. | No Individual VRF Assigned | Retired | 2011-10-01 | 2016-12-31 | RC
IRO-010-1a | Reliability Coordinator Data Specification and Collection | R1.3. | Timeframe and periodicity for providing data and information (based on its hardware and software requirements, and the time needed to do its Operational Planning Analyses). | No Individual VRF Assigned | Retired | 2011-10-01 | 2016-12-31 | RC
IRO-010-1a | Reliability Coordinator Data Specification and Collection | R1.4. | Process for data provision when automated Real-Time system operating data is unavailable. | No Individual VRF Assigned | Retired | 2011-10-01 | 2016-12-31 | RC
IRO-010-1a | Reliability Coordinator Data Specification and Collection | R2. | The Reliability Coordinator shall distribute its data specification to entities that have Facilities monitored by the Reliability Coordinator and to entities that provide Facility status to the Reliability Coordinator. (Violation Risk Factor: Low) (Time Horizon: Operations Planning) | MEDIUM | Retired | 2011-10-01 | 2016-12-31 | RC
IRO-010-1a | Reliability Coordinator Data Specification and Collection | R3. | Each Balancing Authority, Generator Owner, Generator Operator, Interchange Authority, Load-serving Entity, Reliability Coordinator, Transmission Operator, and Transmission Owner shall provide data and information, as specified, to the Reliability Coordinator(s) with which it has a reliability relationship. (Violation Risk Factor: Medium) (Time Horizon: Operations Planning; Same-day Operations; Real-time Operations) | MEDIUM | Retired | 2011-10-01 | 2017-03-31 | TOP, TO, RC, GOP, GO, BA
IRO-010-2 | Reliability Coordinator Data Specification and Collection | R1. | The Reliability Coordinator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The data specification shall include but not be limited to: (Violation Risk Factor: Low) (Time Horizon: Operations Planning) | LOWER | Retired | 2017-01-01 | 2021-03-31 | RC
IRO-010-2 | Reliability Coordinator Data Specification and Collection | R1.1. | A list of data and information needed by the Reliability Coordinator to support its Operational Planning Analyses, Real-time monitoring, and Realtime Assessments including non-BES data and external network data, as deemed necessary by the Reliability Coordinator. | LOWER | Retired | 2017-01-01 | 2021-03-31 | RC
IRO-010-2 | Reliability Coordinator Data Specification and Collection | R1.2. | Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability. | LOWER | Retired | 2017-01-01 | 2021-03-31 | RC
IRO-010-2 | Reliability Coordinator Data Specification and Collection | R1.3. | A periodicity for providing data. | LOWER | Retired | 2017-01-01 | 2021-03-31 | RC
IRO-010-2 | Reliability Coordinator Data Specification and Collection | R1.4. | The deadline by which the respondent is to provide the indicated data. | LOWER | Retired | 2017-01-01 | 2021-03-31 | RC
IRO-010-2 | Reliability Coordinator Data Specification and Collection | R2. | The Reliability Coordinator shall distribute its data specification to entities that have data required by the Reliability Coordinator’s Operational Planning Analyses, Realtime monitoring, and Real-time Assessments. (Violation Risk Factor: Low) (Time Horizon: Operations Planning) | LOWER | Retired | 2017-01-01 | 2021-03-31 | RC
IRO-010-2 | Reliability Coordinator Data Specification and Collection | R3. | Each Reliability Coordinator, Balancing Authority, Generator Owner, Generator Operator, Load-Serving Entity, Transmission Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R2 shall satisfy the obligations of the documented specifications using: (Violation Risk Factor: Medium) (Time Horizon: Operations Planning, Same-Day Operations, Real-time Operations) | MEDIUM | Retired | 2017-04-01 | 2021-03-31 | TOP, TO, RC, GOP, GO, DP, BA
IRO-010-2 | Reliability Coordinator Data Specification and Collection | R3.1. | A mutually agreeable format | MEDIUM | Retired | 2017-04-01 | 2021-03-31 | TOP, TO, RC, GOP, GO, DP, BA
IRO-010-2 | Reliability Coordinator Data Specification and Collection | R3.2. | A mutually agreeable process for resolving data conflicts | MEDIUM | Retired | 2017-04-01 | 2021-03-31 | TOP, TO, RC, GOP, GO, DP, BA
IRO-010-2 | Reliability Coordinator Data Specification and Collection | R3.3. | A mutually agreeable security protocol | MEDIUM | Retired | 2017-04-01 | 2021-03-31 | TOP, TO, RC, GOP, GO, DP, BA
IRO-010-3 | Reliability Coordinator Data Specification and Collection | R1. | The Reliability Coordinator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The data specification shall include but not be limited to: (Violation Risk Factor: Low) (Time Horizon: Operations Planning) | LOWER | Retired | 2021-04-01 | 2023-09-30 | DP, TOP, TO, GOP, GO, BA, RC
IRO-010-3 | Reliability Coordinator Data Specification and Collection | R1. | The Reliability Coordinator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The data specification shall include but not be limited to: (Violation Risk Factor: Low) (Time Horizon: Operations Planning) | LOWER | Retired | 2021-04-01 | 2023-09-30 | DP, TOP, TO, GOP, GO, BA, RC
IRO-010-3 | Reliability Coordinator Data Specification and Collection | R1.1. | A list of data and information needed by the Reliability Coordinator to support its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments including non-BES data and external network data, as deemed necessary by the Reliability Coordinator. | LOWER | Retired | 2021-04-01 | 2023-09-30 | DP, TOP, TO, GOP, GO, BA, RC
IRO-010-3 | Reliability Coordinator Data Specification and Collection | R1.2. | Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability. | LOWER | Retired | 2021-04-01 | 2023-09-30 | DP, TOP, TO, GOP, GO, BA, RC
IRO-010-3 | Reliability Coordinator Data Specification and Collection | R1.3. | A periodicity for providing data. | LOWER | Retired | 2021-04-01 | 2023-09-30 | DP, TOP, TO, GOP, GO, BA, RC
IRO-010-3 | Reliability Coordinator Data Specification and Collection | R1.4. | The deadline by which the respondent is to provide the indicated data. | LOWER | Retired | 2021-04-01 | 2023-09-30 | DP, TOP, TO, GOP, GO, BA, RC
IRO-010-3 | Reliability Coordinator Data Specification and Collection | R2. | The Reliability Coordinator shall distribute its data specification to entities that have data required by the Reliability Coordinator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. (Violation Risk Factor: Low) (Time Horizon: Operations Planning) | LOWER | Retired | 2021-04-01 | 2023-09-30 | DP, TOP, TO, GOP, GO, BA, RC
IRO-010-3 | Reliability Coordinator Data Specification and Collection | R3. | Each Reliability Coordinator, Balancing Authority, Generator Owner, Generator Operator, Transmission Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R2 shall satisfy the obligations of the documented specifications using: (Violation Risk Factor: Medium) (Time Horizon: Operations Planning, Same-Day Operations, Real-time Operations) | MEDIUM | Retired | 2021-04-01 | 2023-09-30 | DP, TOP, TO, GOP, GO, BA, RC
IRO-010-3 | Reliability Coordinator Data Specification and Collection | R3.1. | A mutually agreeable format | MEDIUM | Retired | 2021-04-01 | 2023-09-30 | DP, GOP, GO, TOP, TO, BA, RC
IRO-010-3 | Reliability Coordinator Data Specification and Collection | R3.2. | A mutually agreeable process for resolving data conflicts | MEDIUM | Retired | 2021-04-01 | 2023-09-30 | DP, TOP, TO, GOP, GO, BA, RC
IRO-010-4 | Reliability Coordinator Data Specification and Collection | R1. | The Reliability Coordinator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The data specification shall include but not be limited to: (Violation Risk Factor: Low) (Time Horizon: Operations Planning) | LOWER | Effective | 2023-10-01
IRO-010-4 | Reliability Coordinator Data Specification and Collection | R1.1. | A list of data and information needed by the Reliability Coordinator to support its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments including non-BES data and external network data, as deemed necessary by the Reliability Coordinator. | LOWER | Effective | 2023-10-01
IRO-010-4 | Reliability Coordinator Data Specification and Collection | R1.2. | Provisions for notification of current Protection System and Remedial Action Scheme (RAS) status or degradation that impacts System reliability. | LOWER | Effective | 2023-10-01
IRO-010-4 | Reliability Coordinator Data Specification and Collection | R1.3. | Provisions for notification of BES generating unit(s) during local forecasted cold weather to include: | LOWER | Effective | 2023-10-01
IRO-010-4 | Reliability Coordinator Data Specification and Collection | R1.3.1. | Operating limitations based on: | LOWER | Effective | 2023-10-01
IRO-010-4 | Reliability Coordinator Data Specification and Collection | R1.3.1.1. | capability and availability; | LOWER | Effective | 2023-10-01
IRO-010-4 | Reliability Coordinator Data Specification and Collection | R1.3.1.2. | fuel supply and inventory concerns; | LOWER | Effective | 2023-10-01
IRO-010-4 | Reliability Coordinator Data Specification and Collection | R1.3.1.3. | fuel switching capabilities; and | LOWER | Effective | 2023-10-01
IRO-010-4 | Reliability Coordinator Data Specification and Collection | R1.3.1.4. | environmental constraints | LOWER | Effective | 2023-10-01
IRO-010-4 | Reliability Coordinator Data Specification and Collection | R1.3.2. | Generating unit(s) minimum | LOWER | Effective | 2023-10-01
IRO-010-4 | Reliability Coordinator Data Specification and Collection | R1.4. | A periodicity for providing data | LOWER | Effective | 2023-10-01
IRO-010-4 | Reliability Coordinator Data Specification and Collection | R1.5. | The deadline by which the respondent is to provide the indicated data. | LOWER | Effective | 2023-10-01
IRO-010-4 | Reliability Coordinator Data Specification and Collection | R2. | The Reliability Coordinator shall distribute its data specification to entities that have data required by the Reliability Coordinator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. (Violation Risk Factor: Low) (Time Horizon: Operations Planning) | LOWER | Effective | 2023-10-01
IRO-010-4 | Reliability Coordinator Data Specification and Collection | R3. | Each Reliability Coordinator, Balancing Authority, Generator Owner, Generator Operator, Transmission Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R2 shall satisfy the obligations of the documented specifications using: (Violation Risk Factor: Medium) (Time Horizon: Operations Planning, Same-Day Operations, Real-time Operations) | MEDIUM | Effective | 2023-10-01
IRO-010-4 | Reliability Coordinator Data Specification and Collection | R3.1. | A mutually agreeable format | MEDIUM | Effective | 2023-10-01
IRO-010-4 | Reliability Coordinator Data Specification and Collection | R3.2. | A mutually agreeable process for resolving data conflicts | MEDIUM | Effective | 2023-10-01
IRO-010-4 | Reliability Coordinator Data Specification and Collection | R3.3. | A mutually agreeable security protocol | MEDIUM | Effective | 2023-10-01
IRO-010-5 | Reliability Coordinator Data and information Specification and Collection | R1. | The Reliability Coordinator shall maintain documented specification(s) for the data and information necessary for it to perform its Operational Planning Analyses, Realtime monitoring, and Real-time Assessments. The specification shall include but not be limited to: (Violation Risk Factor: Low) (Time Horizon: Operations Planning) | LOW | Future Effective | 2025-10-01 |  | RC
IRO-010-5 | Reliability Coordinator Data and information Specification and Collection | R1.1. | A list of data and information needed by the Reliability Coordinator to support its Operational Planning Analyses, Real-time monitoring, and Real- time Assessments including non-BES data and information, external network data and information, and identification of the entities responsible for responding to the specification as deemed necessary by the Reliability Coordinator | LOW | Future Effective | 2025-10-01 |  | RC
IRO-010-5 | Reliability Coordinator Data and information Specification and Collection | R1.2. | Provisions for notification of current Protection System and Remedial Action Scheme (RAS) status or degradation that impacts System reliability. | LOW | Future Effective | 2025-10-01 |  | RC
IRO-010-5 | Reliability Coordinator Data and information Specification and Collection | R1.3. | Provisions for notification of BES generating unit(s) during local forecasted cold weather to include: | LOW | Future Effective | 2025-10-01 |  | RC
IRO-010-5 | Reliability Coordinator Data and information Specification and Collection | R1.3.1. | Operating limitations based on: | LOW | Future Effective | 2025-10-01 |  | RC
IRO-010-5 | Reliability Coordinator Data and information Specification and Collection | R1.3.1.1. | capability and availability; | LOW | Future Effective | 2025-10-01 |  | RC
IRO-010-5 | Reliability Coordinator Data and information Specification and Collection | R1.3.1.2. | fuel supply and inventory concerns; | LOW | Future Effective | 2025-10-01 |  | RC
IRO-010-5 | Reliability Coordinator Data and information Specification and Collection | R1.3.1.3. | fuel switching capabilities; and | LOW | Future Effective | 2025-10-01 |  | RC
IRO-010-5 | Reliability Coordinator Data and information Specification and Collection | R1.3.1.4. | environmental constraints | LOW | Future Effective | 2025-10-01 |  | RC
IRO-010-5 | Reliability Coordinator Data and information Specification and Collection | R1.3.2. | Generating unit(s) minimum: | LOW | Future Effective | 2025-10-01 |  | RC
IRO-010-5 | Reliability Coordinator Data and information Specification and Collection | R1.3.2.1. | design temperature; or | LOW | Future Effective | 2025-10-01 |  | RC
IRO-010-5 | Reliability Coordinator Data and information Specification and Collection | R1.3.2.2. | historical operating temperature; or | LOW | Future Effective | 2025-10-01 |  | RC
IRO-010-5 | Reliability Coordinator Data and information Specification and Collection | R1.3.2.3. | current cold weather performance temperature determined by an engineering analysis. | LOW | Future Effective | 2025-10-01 |  | RC
IRO-010-5 | Reliability Coordinator Data and information Specification and Collection | R1.4. | Identification of a mutually agreeable process for resolving conflicts. | LOW | Future Effective | 2025-10-01 |  | RC
IRO-010-5 | Reliability Coordinator Data and information Specification and Collection | R1.5. | Method(s) for the entity identified in Part 1.1 to provide data and information that includes, but is not limited to. | LOW | Future Effective | 2025-10-01 |  | RC
IRO-010-5 | Reliability Coordinator Data and information Specification and Collection | R1.5.1. | Specific deadlines or periodicity in which data and information is to be provided; | LOW | Future Effective | 2025-10-01 |  | RC
IRO-010-5 | Reliability Coordinator Data and information Specification and Collection | R1.5.2. | Performance criteria for the availability and accuracy of data and information, as applicable; | LOW | Future Effective | 2025-10-01 |  | RC
IRO-010-5 | Reliability Coordinator Data and information Specification and Collection | R1.5.3. | Provisions to update or correct data and information, as applicable or necessary. | LOW | Future Effective | 2025-10-01 |  | RC
IRO-010-5 | Reliability Coordinator Data and information Specification and Collection | R1.5.4. | A mutually agreeable format. | LOW | Future Effective | 2025-10-01 |  | RC
IRO-010-5 | Reliability Coordinator Data and information Specification and Collection | R1.5.5. | A mutually agreeable method(s) for securely transferring data and information. | LOW | Future Effective | 2025-10-01 |  | RC
IRO-010-5 | Reliability Coordinator Data and information Specification and Collection | R2. | The Reliability Coordinator shall distribute its data and information specification(s) to entities that have data required by the Reliability Coordinator’s Operational Planning Analyses, Real- time monitoring, and Real-time Assessments. (Violation Risk Factor: Low) (Time Horizon: Operations Planning) | LOW | Future Effective | 2025-10-01 |  | RC
IRO-010-5 | Reliability Coordinator Data and information Specification and Collection | R3. | Each Reliability Coordinator, Balancing Authority, Generator Owner, Generator Operator, Transmission Operator, Transmission Owner, and Distribution Provider receiving a specification(s) in Requirement R2 shall satisfy the obligations of the documented specifications . (Violation Risk Factor: Medium) (Time Horizon: Operations Planning, Same-Day Operations, Real-time Operations) | MEDIUM | Future Effective | 2025-10-01 |  | DP, TOP, TO, GOP, GO, BA, RC
IRO-014-1 | Procedures, Processes, or Plans to Support Coordination Between Reliability Coordinators | R1. | The Reliability Coordinator shall have Operating Procedures, Processes, or Plans in place for activities that require notification, exchange of information or coordination of actions with one or more other Reliability Coordinators to support Interconnection reliability. These Operating Procedures, Processes, or Plans shall address Scenarios that affect other Reliability Coordinator Areas as well as those developed in coordination with other Reliability Coordinators. | MEDIUM | Retired | 2006-02-07 | 2017-03-31 | RC
IRO-014-1 | Procedures, Processes, or Plans to Support Coordination Between Reliability Coordinators | R1.1. | These Operating Procedures, Processes, or Plans shall collectively address, as a minimum, the following: | LOWER | Retired | 2006-02-07 | 2017-03-31 | RC
IRO-014-1 | Procedures, Processes, or Plans to Support Coordination Between Reliability Coordinators | R1.1.1. | Communications and notifications, including the conditions under which one Reliability Coordinator notifies other Reliability Coordinators; the process to follow in making those notifications; and the data and information to be exchanged with other Reliability Coordinators. | MEDIUM | Retired | 2006-02-07 | 2017-03-31 | RC
IRO-014-1 | Procedures, Processes, or Plans to Support Coordination Between Reliability Coordinators | R1.1.2. | Energy and capacity shortages. | MEDIUM | Retired | 2006-02-07 | 2017-03-31 | RC
IRO-014-1 | Procedures, Processes, or Plans to Support Coordination Between Reliability Coordinators | R1.1.3. | Planned or unplanned outage information. | MEDIUM | Retired | 2006-02-07 | 2017-03-31 | RC
IRO-014-1 | Procedures, Processes, or Plans to Support Coordination Between Reliability Coordinators | R1.1.4. | Voltage control, including the coordination of reactive resources for voltage control. | MEDIUM | Retired | 2006-02-07 | 2017-03-31 | RC
IRO-014-1 | Procedures, Processes, or Plans to Support Coordination Between Reliability Coordinators | R1.1.5. | Coordination of information exchange to support reliability assessments. | LOWER | Retired | 2006-02-07 | 2017-03-31 | RC
IRO-014-1 | Procedures, Processes, or Plans to Support Coordination Between Reliability Coordinators | R1.1.6. | Authority to act to prevent and mitigate instances of causing Adverse Reliability Impacts to other Reliability Coordinator Areas. | LOWER | Retired | 2006-02-07 | 2017-03-31 | RC
IRO-014-1 | Procedures, Processes, or Plans to Support Coordination Between Reliability Coordinators | R2. | Each Reliability Coordinator’s Operating Procedure, Process, or Plan that requires one or more other Reliability Coordinators to take action (e.g., make notifications, exchange information, or coordinate actions) shall be: | LOWER | Retired | 2006-02-07 | 2017-03-31 | RC
IRO-014-1 | Procedures, Processes, or Plans to Support Coordination Between Reliability Coordinators | R2.1. | Agreed to by all the Reliability Coordinators required to take the indicated action(s). | LOWER | Retired | 2006-02-07 | 2017-03-31 | RC
IRO-014-1 | Procedures, Processes, or Plans to Support Coordination Between Reliability Coordinators | R2.2. | Distributed to all Reliability Coordinators that are required to take the indicated action(s). | LOWER | Retired | 2006-02-07 | 2017-03-31 | RC
IRO-014-1 | Procedures, Processes, or Plans to Support Coordination Between Reliability Coordinators | R3. | A Reliability Coordinator’s Operating Procedures, Processes, or Plans developed to support a Reliability Coordinator-to-Reliability Coordinator Operating Procedure, Process, or Plan shall include: | MEDIUM | Retired | 2006-02-07 | 2017-03-31 | RC
IRO-014-1 | Procedures, Processes, or Plans to Support Coordination Between Reliability Coordinators | R3.1. | A reference to the associated Reliability Coordinator-to-Reliability Coordinator Operating Procedure, Process, or Plan. | MEDIUM | Retired | 2006-02-07 | 2017-03-31 | RC
IRO-014-1 | Procedures, Processes, or Plans to Support Coordination Between Reliability Coordinators | R3.2. | The agreed-upon actions from the associated Reliability Coordinator-to-Reliability Coordinator Operating Procedure, Process, or Plan. | LOWER | Retired | 2006-02-07 | 2017-03-31 | RC
IRO-014-1 | Procedures, Processes, or Plans to Support Coordination Between Reliability Coordinators | R4. | Each of the Operating Procedures, Processes, and Plans addressed in Reliability Standard IRO-014 Requirement 1 and Requirement 3 shall: | LOWER | Retired | 2006-02-07 | 2017-03-31 | RC
IRO-014-1 | Procedures, Processes, or Plans to Support Coordination Between Reliability Coordinators | R4.1. | Include version control number or date | LOWER | Retired | 2006-02-07 | 2017-03-31 | RC
IRO-014-1 | Procedures, Processes, or Plans to Support Coordination Between Reliability Coordinators | R4.2. | Include a distribution list. | LOWER | Retired | 2006-02-07 | 2017-03-31 | RC
IRO-014-1 | Procedures, Processes, or Plans to Support Coordination Between Reliability Coordinators | R4.3. | Be reviewed, at least once every three years, and updated if needed. | LOWER | Retired | 2006-02-07 | 2017-03-31 | RC
IRO-014-2 | Coordination Among Reliability Coordinators | R1. | Each Reliability Coordinator shall have Operating Procedures, Operating Processes, or Operating Plans for activities that require notification, exchange of information or coordination of actions that may impact other Reliability Coordinator Areas to support Interconnection reliability. These Operating Procedures, Processes, or Plans shall collectively address the following: | MEDIUM | Never Came Into Effect in Ontario |  |  | RC
IRO-014-2 | Coordination Among Reliability Coordinators | R1.1. | Communications and notifications, including the mutually agreed to conditions under which one Reliability Coordinator notifies other Reliability Coordinators; the process to follow in making those notifications; and the data and information to be exchanged with other Reliability Coordinators. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | RC
IRO-014-2 | Coordination Among Reliability Coordinators | R1.2. | Energy and capacity shortages. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | RC
IRO-014-2 | Coordination Among Reliability Coordinators | R1.3. | Planned or unplanned outage information. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | RC
IRO-014-2 | Coordination Among Reliability Coordinators | R1.4. | Control of voltage, including the coordination of reactive resources. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | RC
IRO-014-2 | Coordination Among Reliability Coordinators | R1.5. | Coordination of information exchange to support reliability assessments. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | RC
IRO-014-2 | Coordination Among Reliability Coordinators | R1.6. | Authority to act to prevent and mitigate system conditions which could cause Adverse Reliability Impacts to other Reliability Coordinator Areas. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | RC
IRO-014-2 | Coordination Among Reliability Coordinators | R1.7. | Weekly conference calls | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | RC
IRO-014-2 | Coordination Among Reliability Coordinators | R2. | Each Reliability Coordinator shall maintain its Operating Procedures, Operating Processes, or Operating Plans identified in Requirement R1 as follows: | LOWER | Never Came Into Effect in Ontario |  |  | RC
IRO-014-2 | Coordination Among Reliability Coordinators | R2.1. | Review and update annually with no more that 15 months between reviews. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | RC
IRO-014-2 | Coordination Among Reliability Coordinators | R2.2. | Obtain written agreement from all of the Reliability Coordinators required to take the indicated action(s) for each update. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | RC
IRO-014-2 | Coordination Among Reliability Coordinators | R2.3. | Distribute to all Reliability Coordinators that are required to take the indicated action(s) within 30 days of an update. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | RC
IRO-014-2 | Coordination Among Reliability Coordinators | R3. | Each Reliability Coordinator shall make notifications and exchange reliability–related information with other Reliability Coordinators in accordance with the Operating Procedures, Operating Processes, or Operating Plans identified in Requirement R1. | MEDIUM | Never Came Into Effect in Ontario |  |  | RC
IRO-014-2 | Coordination Among Reliability Coordinators | R4. | Each Reliability Coordinator shall participate in agreed upon conference calls, at least weekly (per Requirement 1, Part 1.7) with other Reliability Coordinators within the same Interconnection. | LOWER | Never Came Into Effect in Ontario |  |  | RC
IRO-014-2 | Coordination Among Reliability Coordinators | R5. | Each Reliability Coordinator, upon identification of an Adverse Reliability Impact, shall notify all other Reliability Coordinators. | MEDIUM | Never Came Into Effect in Ontario |  |  | RC
IRO-014-2 | Coordination Among Reliability Coordinators | R6. | During each instance where Reliability Coordinators disagree on the existence of an Adverse Reliability Impact each impacted Reliability Coordinator shall operate as though the problem exists. | HIGH | Never Came Into Effect in Ontario |  |  | RC
IRO-014-2 | Coordination Among Reliability Coordinators | R7. | During those instances where Reliability Coordinators disagree on the existence of an Adverse Reliability Impact, the Reliability Coordinator that identified the Adverse Reliability Impact shall develop an action plan to resolve the Adverse Reliability Impact. [Violation Risk Factor: | HIGH | Never Came Into Effect in Ontario |  |  | RC
IRO-014-2 | Coordination Among Reliability Coordinators | R8. | During those instances where Reliability Coordinators disagree on the existence of an Adverse Reliability Impact, each Reliability Coordinator shall implement the action plan developed by the Reliability Coordinator that identified the Adverse Reliability Impact unless such actions would violate safety, equipment, regulatory or statutory requirements. | HIGH | Never Came Into Effect in Ontario |  |  | RC
IRO-014-3 | Coordination Among Reliability Coordinators | R1. | Each Reliability Coordinator shall have and implement Operating Procedures, Operating Processes, or Operating Plans, for activities that require notification or coordination of actions that may impact adjacent Reliability Coordinator Areas, to support Interconnection reliability. These Operating Procedures, Operating Processes, or Operating Plans shall include, but are not limited to, the following: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning, Same-Day Operations] | MEDIUM | Effective | 2017-04-01 |  | RC
IRO-014-3 | Coordination Among Reliability Coordinators | R1.1. | Criteria and processes for notifications. | MEDIUM | Effective | 2017-04-01 |  | RC
IRO-014-3 | Coordination Among Reliability Coordinators | R1.2. | Energy and capacity shortages. | MEDIUM | Effective | 2017-04-01 |  | RC
IRO-014-3 | Coordination Among Reliability Coordinators | R1.3. | Control of voltage, including the coordination of reactive resources. | MEDIUM | Effective | 2017-04-01 |  | RC
IRO-014-3 | Coordination Among Reliability Coordinators | R1.4. | Exchange of information including planned and unplanned outage information to support its Operational Planning Analyses and Real-time Assessments. | MEDIUM | Effective | 2017-04-01 |  | RC
IRO-014-3 | Coordination Among Reliability Coordinators | R1.5. | Provisions for periodic communications to support reliable operations. | MEDIUM | Effective | 2017-04-01 |  | RC
IRO-014-3 | Coordination Among Reliability Coordinators | R2. | Each Reliability Coordinator shall maintain its Operating Procedures, Operating Processes, or Operating Plans identified in Requirement R1 as follows: [Violation Risk Factor: Low] [Time Horizon: Operations Planning, Same-Day Operations] | LOWER | Effective | 2017-04-01 |  | RC
IRO-014-3 | Coordination Among Reliability Coordinators | R2.1. | Review and update annually with no more than 15 months between reviews. | LOWER | Effective | 2017-04-01 |  | RC
IRO-014-3 | Coordination Among Reliability Coordinators | R2.2. | Obtain written agreement from all of the Reliability Coordinators required to take the indicated action(s) for each update. | LOWER | Effective | 2017-04-01 |  | RC
IRO-014-3 | Coordination Among Reliability Coordinators | R2.3. | Distribute to all Reliability Coordinators that are required to take the indicated action(s) within 30 days of an update. | LOWER | Effective | 2017-04-01 |  | RC
IRO-014-3 | Coordination Among Reliability Coordinators | R3. | Each Reliability Coordinator, upon identification of an expected or actual Emergency in its Reliability Coordinator Area, shall notify other impacted Reliability Coordinators. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning, Same Day Operations, Real-time Operations] | MEDIUM | Effective | 2017-04-01 |  | RC
IRO-014-3 | Coordination Among Reliability Coordinators | R4. | Each impacted Reliability Coordinator shall operate as though the Emergency exists during each instance where Reliability Coordinators disagree on the existence of an Emergency. [Violation Risk Factor: High] [Time Horizon: Operations Planning, Same- Day Operations, Real-time Operations] | HIGH | Effective | 2017-04-01 |  | RC
IRO-014-3 | Coordination Among Reliability Coordinators | R5. | Each Reliability Coordinator that Identifies an Emergency in its Reliability Coordinator Area shall develop an action plan to resolve the Emergency during those instances where impacted Reliability Coordinators disagree on the existence of an Emergency. [Violation Risk Factor: High][Time Horizon: Operations Planning, Same-Day Operations, Real-time Operations] | HIGH | Effective | 2017-04-01 |  | RC
IRO-014-3 | Coordination Among Reliability Coordinators | R6. | Each impacted Reliability Coordinator shall implement the action plan developed by the Reliability Coordinator that identifies the Emergency during those instances where Reliability Coordinators disagree on the existence of an Emergency, unless such actions would violate safety, equipment, regulatory, or statutory requirements. [Violation Risk Factor: High][Time Horizon: Operations Planning, Same-Day Operations, Real-time Operations] | HIGH | Effective | 2017-04-01 |  | RC
IRO-014-3 | Coordination Among Reliability Coordinators | R7. | Each Reliability Coordinator shall assist Reliability Coordinators, if requested and able, provided that the requesting Reliability Coordinator has implemented its emergency procedures, unless such actions cannot be physically implemented or would violate safety, equipment, regulatory, or statutory requirements. [Violation Risk Factor: High] [Time Horizon: Real-time Operations] | HIGH | Effective | 2017-04-01 |  | RC
IRO-015-1 | Notifications and Information Exchange Between Reliability Coordinators | R1. | The Reliability Coordinator shall follow its Operating Procedures, Processes, or Plans for making notifications and exchanging reliability-related information with other Reliability Coordinators. | MEDIUM | Retired | 2006-02-07 | 2017-03-31 | RC
IRO-015-1 | Notifications and Information Exchange Between Reliability Coordinators | R1.1. | The Reliability Coordinator shall make notifications to other Reliability Coordinators of conditions in its Reliability Coordinator Area that may impact other Reliability Coordinator Areas. | MEDIUM | Retired | 2006-02-07 | 2017-03-31 | RC
IRO-015-1 | Notifications and Information Exchange Between Reliability Coordinators | R2. | The Reliability Coordinator shall participate in agreed upon conference calls and other communication forums with adjacent Reliability Coordinators. | LOWER | Retired | 2006-02-07 | 2017-03-31 | RC
IRO-015-1 | Notifications and Information Exchange Between Reliability Coordinators | R2.1. | The frequency of these conference calls shall be agreed upon by all involved Reliability Coordinators and shall be at least weekly. | LOWER | Retired | 2006-02-07 | 2017-03-31 | RC
IRO-015-1 | Notifications and Information Exchange Between Reliability Coordinators | R3. | The Reliability Coordinator shall provide reliability-related information as requested by other Reliability Coordinators. | MEDIUM | Retired | 2006-02-07 | 2017-03-31 | RC
IRO-016-1 | Coordination of Real-time Activities Between Reliability Coordinators | R1. | The Reliability Coordinator that identifies a potential, expected, or actual problem that requires the actions of one or more other Reliability Coordinators shall contact the other Reliability Coordinator(s) to confirm that there is a problem and then discuss options and decide upon a solution to prevent or resolve the identified problem. | MEDIUM | Retired | 2006-02-07 | 2017-03-31 | RC
IRO-016-1 | Coordination of Real-time Activities Between Reliability Coordinators | R1.1. | If the involved Reliability Coordinators agree on the problem and the actions to take to prevent or mitigate the system condition, each involved Reliability Coordinator shall implement the agreed-upon solution, and notify the involved Reliability Coordinators of the action(s) taken. | MEDIUM | Retired | 2006-02-07 | 2017-03-31 | RC
IRO-016-1 | Coordination of Real-time Activities Between Reliability Coordinators | R1.2. | If the involved Reliability Coordinators cannot agree on the problem(s) each Reliability Coordinator shall re-evaluate the causes of the disagreement (bad data, status, study results, tools, etc.). | MEDIUM | Retired | 2006-02-07 | 2017-03-31 | RC
IRO-016-1 | Coordination of Real-time Activities Between Reliability Coordinators | R1.2.1. | If time permits, this re-evaluation shall be done before taking corrective actions. | MEDIUM | Retired | 2006-02-07 | 2017-03-31 | RC
IRO-016-1 | Coordination of Real-time Activities Between Reliability Coordinators | R1.2.2. | If time does not permit, then each Reliability Coordinator shall operate as though the problem(s) exist(s) until the conflicting system status is resolved. | MEDIUM | Retired | 2006-02-07 | 2017-03-31 | RC
IRO-016-1 | Coordination of Real-time Activities Between Reliability Coordinators | R1.3. | If the involved Reliability Coordinators cannot agree on the solution, the more conservative solution shall be implemented. | MEDIUM | Retired | 2006-02-07 | 2017-03-31 | RC
IRO-017-1 | Outage Coordination | R1. | Each Reliability Coordinator shall develop, implement, and maintain an outage coordination process for generation and Transmission outages within its Reliability Coordinator Area. The outage coordination process shall: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Effective | 2017-04-01 |  | RC
IRO-017-1 | Outage Coordination | R1.1. | Identify applicable roles and reporting responsibilities including: | MEDIUM | Effective | 2017-04-01 |  | RC
IRO-017-1 | Outage Coordination | R1.1.1. | Development and communication of outage schedules. | MEDIUM | Effective | 2017-04-01 |  | RC
IRO-017-1 | Outage Coordination | R1.1.2. | Assignment of coordination responsibilities for outage schedules between Transmission Operator(s) and Balancing Authority(s). | MEDIUM | Effective | 2017-04-01 |  | RC
IRO-017-1 | Outage Coordination | R1.2. | Specify outage submission timing requirements. | MEDIUM | Effective | 2017-04-01 |  | RC
IRO-017-1 | Outage Coordination | R1.3. | Define the process to evaluate the impact of Transmission and generation outages within its Wide Area. | MEDIUM | Effective | 2017-04-01 |  | RC
IRO-017-1 | Outage Coordination | R1.4. | Define the process to coordinate the resolution of identified outage conflicts with its Transmission Operators and Balancing Authorities, and other Reliability Coordinators. | MEDIUM | Effective | 2017-04-01 |  | RC
IRO-017-1 | Outage Coordination | R2. | Each Transmission Operator and Balancing Authority shall perform the functions specified in its Reliability Coordinator’s outage coordination process. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Effective | 2017-04-01 |  | TOP, BA
IRO-017-1 | Outage Coordination | R2. | Each Transmission Operator and Balancing Authority shall perform the functions specified in its Reliability Coordinator’s outage coordination process. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Effective | 2017-04-01 |  | TOP, BA
IRO-017-1 | Outage Coordination | R3. | Each Planning Coordinator and Transmission Planner shall provide its Planning Assessment to impacted Reliability Coordinators. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2017-04-01 |  | TP, PC
IRO-017-1 | Outage Coordination | R3. | Each Planning Coordinator and Transmission Planner shall provide its Planning Assessment to impacted Reliability Coordinators. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2017-04-01 |  | TP, PC
IRO-017-1 | Outage Coordination | R3. | Each Planning Coordinator and Transmission Planner shall provide its Planning Assessment to impacted Reliability Coordinators. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2017-04-01 |  | TP, PC
IRO-017-1 | Outage Coordination | R3. | Each Planning Coordinator and Transmission Planner shall provide its Planning Assessment to impacted Reliability Coordinators. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2017-04-01 |  | TP, PC
IRO-017-1 | Outage Coordination | R4. | Each Planning Coordinator and Transmission Planner shall jointly develop solutions with its respective Reliability Coordinator(s) for identified issues or conflicts with planned outages in its Planning Assessment for the Near-Term Transmission Planning Horizon. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2017-04-01 |  | TP, PC
IRO-017-1 | Outage Coordination | R4. | Each Planning Coordinator and Transmission Planner shall jointly develop solutions with its respective Reliability Coordinator(s) for identified issues or conflicts with planned outages in its Planning Assessment for the Near-Term Transmission Planning Horizon. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2017-04-01 |  | TP, PC
IRO-017-1 | Outage Coordination | R4. | Each Planning Coordinator and Transmission Planner shall jointly develop solutions with its respective Reliability Coordinator(s) for identified issues or conflicts with planned outages in its Planning Assessment for the Near-Term Transmission Planning Horizon. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2017-04-01 |  | TP, PC
IRO-018-1 | Reliability Coordinator Real-time Reliability Monitoring and Analysis Capabilities | R1. | Each Reliability Coordinator shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. The Operating Process or Operating Procedure shall include: | HIGH | Retired | 2018-04-01 | 2018-03-31 | RC
IRO-018-1 | Reliability Coordinator Real-time Reliability Monitoring and Analysis Capabilities | R1.1. | Criteria for evaluating potential Real-time data quality discrepancies including, but not limited to: | HIGH | Retired | 2018-04-01 | 2018-03-31 | RC
IRO-018-1 | Reliability Coordinator Real-time Reliability Monitoring and Analysis Capabilities | R1.1.1. | Data outside of a prescribed data range; | HIGH | Retired | 2018-04-01 | 2018-03-31 | RC
IRO-018-1 | Reliability Coordinator Real-time Reliability Monitoring and Analysis Capabilities | R1.1.2. | Analog data not updated within a predetermined time period; | HIGH | Retired | 2018-04-01 | 2018-03-31 | RC
IRO-018-1 | Reliability Coordinator Real-time Reliability Monitoring and Analysis Capabilities | R1.1.3. | Data entered manually to override telemetered information; and | HIGH | Retired | 2018-04-01 | 2018-03-31 | RC
IRO-018-1 | Reliability Coordinator Real-time Reliability Monitoring and Analysis Capabilities | R1.1.4. | Data otherwise identified as invalid or suspect. | HIGH | Retired | 2018-04-01 | 2018-03-31 | RC
IRO-018-1 | Reliability Coordinator Real-time Reliability Monitoring and Analysis Capabilities | R1.2. | Actions to coordinate resolution of Real-time data quality discrepancies with the entity(ies) responsible for providing the data. | HIGH | Retired | 2018-04-01 | 2018-03-31 | RC
IRO-018-1 | Reliability Coordinator Real-time Reliability Monitoring and Analysis Capabilities | R2. | Each Reliability Coordinator shall provide its System Operators with indication(s) of the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. | MEDIUM | Retired | 2018-04-01 | 2018-03-31 | RC
IRO-018-1 | Reliability Coordinator Real-time Reliability Monitoring and Analysis Capabilities | R3. | Each Reliability Coordinator shall implement an Operating Process or Operating Procedure to maintain the quality of any analysis used in its Real-time Assessments. The Operating Process or Operating Procedure shall include: | MEDIUM | Retired | 2018-04-01 | 2018-03-31 | RC
IRO-018-1 | Reliability Coordinator Real-time Reliability Monitoring and Analysis Capabilities | R3.1. | Criteria for evaluating the quality of any analysis used in its Real-time Assessments; and | MEDIUM | Retired | 2018-04-01 | 2018-03-31 | RC
IRO-018-1 | Reliability Coordinator Real-time Reliability Monitoring and Analysis Capabilities | R3.2. | Actions to resolve quality deficiencies in any analysis used in its Real-time Assessments. | MEDIUM | Retired | 2018-04-01 | 2018-03-31 | RC
IRO-018-1 | Reliability Coordinator Real-time Reliability Monitoring and Analysis Capabilities | R4. | Each Reliability Coordinator shall provide its System Operators with indication(s) of the quality of any analysis used in its Real-time Assessments. | MEDIUM | Retired | 2018-04-01 | 2018-03-31 | RC
IRO-018-1 | Reliability Coordinator Real-time Reliability Monitoring and Analysis Capabilities | R5. | Each Reliability Coordinator shall utilize an independent alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. | MEDIUM | Retired | 2018-04-01 | 2018-03-31 | RC
IRO-018-1(i) | Reliability Coordinator Real-time Reliability Monitoring and Analysis Capabilities | R1. | Each Reliability Coordinator shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. The Operating Process or Operating Procedure shall include: [Violation Risk Factor: High ] [Time Horizon: Real-time Operations] | HIGH | Effective | 2018-04-01 |  | RC
IRO-018-1(i) | Reliability Coordinator Real-time Reliability Monitoring and Analysis Capabilities | R1.1. | Criteria for evaluating the quality of Real-time data; | HIGH | Effective | 2018-04-01 |  | RC
IRO-018-1(i) | Reliability Coordinator Real-time Reliability Monitoring and Analysis Capabilities | R1.2. | Provisions to indicate the quality of Real-time data to the System Operator; and | HIGH | Effective | 2018-04-01 |  | RC
IRO-018-1(i) | Reliability Coordinator Real-time Reliability Monitoring and Analysis Capabilities | R1.3. | Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects Real-time Assessments. | HIGH | Effective | 2018-04-01 |  | RC
IRO-018-1(i) | Reliability Coordinator Real-time Reliability Monitoring and Analysis Capabilities | R2. | Each Reliability Coordinator shall implement an Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments. The Operating Process or Operating Procedure shall include: [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | MEDIUM | Effective | 2018-04-01 |  | RC
IRO-018-1(i) | Reliability Coordinator Real-time Reliability Monitoring and Analysis Capabilities | R2.1. | Criteria for evaluating the quality of analysis used in its Real-time Assessments; | MEDIUM | Effective | 2018-04-01 |  | RC
IRO-018-1(i) | Reliability Coordinator Real-time Reliability Monitoring and Analysis Capabilities | R2.2. | Provisions to indicate the quality of analysis used in its Real-time Assessments; and | MEDIUM | Effective | 2018-04-01 |  | RC
IRO-018-1(i) | Reliability Coordinator Real-time Reliability Monitoring and Analysis Capabilities | R2.3. | Actions to address analysis quality issues affecting its Real-time Assessments. | MEDIUM | Effective | 2018-04-01 |  | RC
IRO-018-1(i) | Reliability Coordinator Real-time Reliability Monitoring and Analysis Capabilities | R3. | Each Reliability Coordinator shall have an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | MEDIUM | Effective | 2018-04-01 |  | RC
MOD-001-0 | Available Transmission System Capability | R1. | Each Regional Reliability Organization, in conjunction with its members, shall develop and document a Regional TTC and ATC methodology. (Certain systems that are not required to post ATC values are exempt from this standard.) The Regional Reliability Organization’s TTC and ATC methodology shall include each of the following nine items, and shall explain its use in determining TTC and ATC values: | N/A | Never Came Into Effect in Ontario
MOD-001-0 | Available Transmission System Capability | R1.1. | A narrative explaining how TTC and ATC values are determined. | N/A | Never Came Into Effect in Ontario
MOD-001-0 | Available Transmission System Capability | R1.2. | An accounting for how the reservations and schedules for firm (non-recallable) and non-firm (recallable) transfers, both within and outside the Transmission Service Provider’s system, are included. | N/A | Never Came Into Effect in Ontario
MOD-001-0 | Available Transmission System Capability | R1.3. | An accounting for the ultimate points of power injection (sources) and power extraction (sinks) in TTC and ATC calculations. | N/A | Never Came Into Effect in Ontario
MOD-001-0 | Available Transmission System Capability | R1.4. | A description of how incomplete or so-called partial path transmission reservations are addressed. (Incomplete or partial path transmission reservations are those for which all transmission reservations necessary to complete the transmission path from ultimate source to ultimate sink are not identifiable due to differing reservation priorities, durations, or because the reservations have not all been made.) | N/A | Never Came Into Effect in Ontario
MOD-001-0 | Available Transmission System Capability | R1.5. | A requirement that TTC and ATC values shall be determined and posted as follows: | N/A | Never Came Into Effect in Ontario
MOD-001-0 | Available Transmission System Capability | R1.5.1. | Daily values for current week at least once per day. | N/A | Never Came Into Effect in Ontario
MOD-001-0 | Available Transmission System Capability | R1.5.2. | Daily values for day 8 through the first month at least once per week. | N/A | Never Came Into Effect in Ontario
MOD-001-0 | Available Transmission System Capability | R1.5.3. | Monthly values for months 2 through 13 at least once per month. | N/A | Never Came Into Effect in Ontario
MOD-001-0 | Available Transmission System Capability | R1.6. | Indication of the treatment and level of customer demands, including interruptible demands. | N/A | Never Came Into Effect in Ontario
MOD-001-0 | Available Transmission System Capability | R1.7. | A specification of how system conditions, limiting facilities, contingencies, transmission reservations, energy schedules, and other data needed by Transmission Service Providers for the calculation of TTC and ATC values are shared and used within the Regional Reliability Organization and with neighboring interconnected electric systems, including adjacent systems, subregions, and Regional Reliability Organizations. In addition, specify how this information is to be used to determine TTC and ATC values. If some data is not used, provide an explanation. | N/A | Never Came Into Effect in Ontario
MOD-001-0 | Available Transmission System Capability | R1.8. | A description of how the assumptions for and the calculations of TTC and ATC values change over different time (such as hourly, daily, and monthly) horizons. | N/A | Never Came Into Effect in Ontario
MOD-001-0 | Available Transmission System Capability | R1.9. | A description of the Regional Reliability Organization’s practice on the netting of transmission reservations for purposes of TTC and ATC determination. | N/A | Never Came Into Effect in Ontario
MOD-001-0 | Available Transmission System Capability | R2. | The Regional Reliability Organization shall make the most recent version of the documentation of its TTC and ATC methodology available on a Web site accessible by NERC, the Regional Reliability Organizations, and transmission users. | N/A | Never Came Into Effect in Ontario
MOD-001-1a | Available Transmission System Capability | R1. | Each Transmission Operator shall select one of the methodologies listed below for calculating Available Transfer Capability (ATC) or Available Flowgate Capability (AFC) for each ATC Path per time period identified in R2 for those Facilities within its Transmission operating area: [Time Horizon: Operations Planning]  The Area Interchange Methodology, as described in MOD-028  The Rated System Path Methodology, as described in MOD-029  The Flowgate Methodology, as described in MOD-030 | MEDIUM | Effective | 2010-04-18 |  | TOP
MOD-001-1a | Available Transmission System Capability | R2. | Each Transmission Service Provider shall calculate ATC or AFC values as listed below using the methodology or methodologies selected by its Transmission Operator(s): [Time Horizon: Operations Planning] | MEDIUM | Effective | 2010-04-18 |  | TSP
MOD-001-1a | Available Transmission System Capability | R2. | Each Transmission Service Provider shall calculate ATC or AFC values as listed below using the methodology or methodologies selected by its Transmission Operator(s): [Time Horizon: Operations Planning] | MEDIUM | Effective | 2010-04-18 |  | TSP
MOD-001-1a | Available Transmission System Capability | R2.1. | Hourly values for at least the next 48 hours. | No Individual VRF Assigned | Effective | 2010-04-18 |  | TSP
MOD-001-1a | Available Transmission System Capability | R2.1. | Hourly values for at least the next 48 hours. | No Individual VRF Assigned | Effective | 2010-04-18 |  | TSP
MOD-001-1a | Available Transmission System Capability | R2.2. | Daily values for at least the next 31 calendar days. | No Individual VRF Assigned | Effective | 2010-04-18 |  | TSP
MOD-001-1a | Available Transmission System Capability | R2.2. | Daily values for at least the next 31 calendar days. | No Individual VRF Assigned | Effective | 2010-04-18 |  | TSP
MOD-001-1a | Available Transmission System Capability | R2.3. | Monthly values for at least the next 12 months (months 2-13). | No Individual VRF Assigned | Effective | 2010-04-18 |  | TSP
MOD-001-1a | Available Transmission System Capability | R3. | Each Transmission Service Provider shall prepare and keep current an Available Transfer Capability Implementation Document (ATCID) that includes, at a minimum, the following information: [Time Horizon: Operations Planning] | MEDIUM | Effective | 2010-04-18 |  | TSP
MOD-001-1a | Available Transmission System Capability | R3.1. | Information describing how the selected methodology (or methodologies) has been implemented, in such detail that, given the same information used by the Transmission Service Provider, the results of the ATC or AFC calculations can be validated. | No Individual VRF Assigned | Effective | 2010-04-18 |  | TSP
MOD-001-1a | Available Transmission System Capability | R3.2. | A description of the manner in which the Transmission Service Provider will account for counterflows including: | No Individual VRF Assigned | Effective | 2010-04-18 |  | TSP
MOD-001-1a | Available Transmission System Capability | R3.2.1. | How confirmed Transmission reservations, expected Interchange and internal counterflow are addressed in firm and non-firm ATC or AFC calculations. | No Individual VRF Assigned | Effective | 2010-04-18 |  | TSP
MOD-001-1a | Available Transmission System Capability | R3.2.2. | A rationale for that accounting specified in R3.2. | No Individual VRF Assigned | Effective | 2010-04-18 |  | TSP
MOD-001-1a | Available Transmission System Capability | R3.3. | The identity of the Transmission Operators and Transmission Service Providers from which the Transmission Service Provider receives data for use in calculating ATC or AFC. | No Individual VRF Assigned | Effective | 2010-04-18 |  | TSP
MOD-001-1a | Available Transmission System Capability | R3.4. | The identity of the Transmission Service Providers and Transmission Operators to which it provides data for use in calculating transfer or Flowgate capability. | No Individual VRF Assigned | Effective | 2010-04-18 |  | TSP
MOD-001-1a | Available Transmission System Capability | R3.5. | A description of the allocation processes listed below that are applicable to the Transmission Service Provider: • Processes used to allocate transfer or Flowgate capability among multiple lines or sub-paths within a larger ATC Path or Flowgate. • Processes used to allocate transfer or Flowgate capabilities among multiple owners or users of an ATC Path or Flowgate. • Processes used to allocate transfer or Flowgate capabilities between Transmission Service Providers to address issues such as forward looking congestion management and seams coordination. | No Individual VRF Assigned | Effective | 2010-04-18 |  | TSP
MOD-001-1a | Available Transmission System Capability | R3.6. | A description of how generation and transmission outages are considered in transfer or Flowgate capability calculations, including: | No Individual VRF Assigned | Effective | 2010-04-18 |  | TSP
MOD-001-1a | Available Transmission System Capability | R3.6.1. | The criteria used to determine when an outage that is in effect part of a day impacts a daily calculation. | No Individual VRF Assigned | Effective | 2010-04-18 |  | TSP
MOD-001-1a | Available Transmission System Capability | R3.6.2. | The criteria used to determine when an outage that is in effect part of a month impacts a monthly calculation. | No Individual VRF Assigned | Effective | 2010-04-18 |  | TSP
MOD-001-1a | Available Transmission System Capability | R3.6.3. | How outages from other Transmission Service Providers that can not be mapped to the Transmission model used to calculate transfer or Flowgate capability are addressed. | No Individual VRF Assigned | Effective | 2010-04-18 |  | TSP
MOD-001-1a | Available Transmission System Capability | R4. | The Transmission Service Provider shall notify the following entities before implementing a new or revised ATCID: [Time Horizon: Operations Planning] | LOWER | Effective | 2010-04-18 |  | TSP
MOD-001-1a | Available Transmission System Capability | R4.1. | Each Planning Coordinator associated with the Transmission Service Provider’s area. | No Individual VRF Assigned | Effective | 2010-04-18 |  | TSP
MOD-001-1a | Available Transmission System Capability | R4.2. | Each Reliability Coordinator associated with the Transmission Service Provider’s area. | No Individual VRF Assigned | Effective | 2010-04-18 |  | TSP
MOD-001-1a | Available Transmission System Capability | R4.3. | Each Transmission Operator associated with the Transmission Service Provider’s area. | No Individual VRF Assigned | Effective | 2010-04-18 |  | TSP
MOD-001-1a | Available Transmission System Capability | R4.4. | Each Planning Coordinator adjacent to the Transmission Service Provider’s area. | No Individual VRF Assigned | Effective | 2010-04-18 |  | TSP
MOD-001-1a | Available Transmission System Capability | R4.5. | Each Reliability Coordinator adjacent to the Transmission Service Provider’s area. | No Individual VRF Assigned | Effective | 2010-04-18 |  | TSP
MOD-001-1a | Available Transmission System Capability | R4.6. | Each Transmission Service Provider whose area is adjacent to the Transmission Service Provider’s area. | No Individual VRF Assigned | Effective | 2010-04-18 |  | TSP
MOD-001-1a | Available Transmission System Capability | R5. | The Transmission Service Provider shall make available the current ATCID to all of the entities specified in R4. [Time Horizon: Operations Planning] | LOWER | Effective | 2010-04-18 |  | TSP
MOD-001-1a | Available Transmission System Capability | R6. | When calculating Total Transfer Capability (TTC) or Total Flowgate Capability (TFC) the Transmission Operator shall use assumptions no more limiting than those used in the planning of operations for the corresponding time period studied, providing such planning of operations has been performed for that time period. [Time Horizon: Operations Planning] | MEDIUM | Effective | 2010-04-18 |  | TOP
MOD-001-1a | Available Transmission System Capability | R7. | When calculating ATC or AFC the Transmission Service Provider shall use assumptions no more limiting than those used in the planning of operations for the corresponding time period studied, providing such planning of operations has been performed for that time period. [Time Horizon: Operations Planning] | MEDIUM | Effective | 2010-04-18 |  | TSP
MOD-001-1a | Available Transmission System Capability | R7. | When calculating ATC or AFC the Transmission Service Provider shall use assumptions no more limiting than those used in the planning of operations for the corresponding time period studied, providing such planning of operations has been performed for that time period. [Time Horizon: Operations Planning] | MEDIUM | Effective | 2010-04-18 |  | TSP
MOD-001-1a | Available Transmission System Capability | R8. | Each Transmission Service Provider that calculates ATC shall recalculate ATC at a minimum on the following frequency, unless none of the calculated values identified in the ATC equation have changed: [Time Horizon: Operations Planning] | MEDIUM | Effective | 2010-04-18 |  | TSP
MOD-001-1a | Available Transmission System Capability | R8. | Each Transmission Service Provider that calculates ATC shall recalculate ATC at a minimum on the following frequency, unless none of the calculated values identified in the ATC equation have changed: [Time Horizon: Operations Planning] | MEDIUM | Effective | 2010-04-18 |  | TSP
MOD-001-1a | Available Transmission System Capability | R8.1. | Hourly values, once per hour. Transmission Service Providers are allowed up to 175 hours per calendar year during which calculations are not required to be performed, despite a change in a calculated value identified in the ATC equation. | No Individual VRF Assigned | Effective | 2010-04-18 |  | TSP
MOD-001-1a | Available Transmission System Capability | R8.1. | Hourly values, once per hour. Transmission Service Providers are allowed up to 175 hours per calendar year during which calculations are not required to be performed, despite a change in a calculated value identified in the ATC equation. | No Individual VRF Assigned | Effective | 2010-04-18 |  | TSP
MOD-001-1a | Available Transmission System Capability | R8.2. | Daily values, once per day. | No Individual VRF Assigned | Effective | 2010-04-18 |  | TSP
MOD-001-1a | Available Transmission System Capability | R8.2. | Daily values, once per day. | No Individual VRF Assigned | Effective | 2010-04-18 |  | TSP
MOD-001-1a | Available Transmission System Capability | R8.3. | Monthly values, once per week. | No Individual VRF Assigned | Effective | 2010-04-18 |  | TSP
MOD-001-1a | Available Transmission System Capability | R9. | Within thirty calendar days of receiving a request by any Transmission Service Provider, Planning Coordinator, Reliability Coordinator, or Transmission Operator for data from the list below solely for use in the requestor’s ATC or AFC calculations, each Transmission Service Provider receiving said request shall begin to make the requested data available to the requestor, subject to the conditions specified in R9.1 and R9.2: [Time Horizon: Operations Planning] • Expected generation and Transmission outages, additions, and retirements. • Load forecasts. • Unit commitments and order of dispatch, to include all designated network resources and other resources that are committed or have the legal obligation to run, as they are expected to run, in one of the following formats chosen by the data provider:  Dispatch Order  Participation Factors  Block Dispatch • Aggregated firm capacity set-aside for Network Integration Transmission Service and aggregated non-firm capacity set aside for Network Integration Transmission Service (i.e. Secondary Service). • Firm and non-firm Transmission reservations. • Aggregated capacity set-aside for Grandfathered obligations • Firm roll-over rights. • Any firm and non-firm adjustments applied by the Transmission Service Provider to reflect parallel path impacts. • Power flow models and underlying assumptions. • Contingencies, provided in one or more of the following formats: A list of Elements  A list of Flowgates  A set of selection criteria that can be applied to the Transmission model used by the Transmission Operator and/or Transmission Service Provider • Facility Ratings. • Any other services that impact Existing Transmission Commitments (ETCs). • Values of Capacity Benefit Margin (CBM) and Transmission Reliability Margin (TRM) for all ATC Paths or Flowgates. • Values of Total Flowgate Capability (TFC) and AFC for any Flowgates considered by the Transmission Service Provider receiving the request when selling Transmission service. • Values of TTC and ATC for all ATC Paths for those Transmission Service Providers receiving the request that do not consider Flowgates when selling Transmission Service. • Source and sink identification and mapping to the model. | MEDIUM | Effective | 2010-04-18 |  | TSP
MOD-001-1a | Available Transmission System Capability | R9. | Within thirty calendar days of receiving a request by any Transmission Service Provider, Planning Coordinator, Reliability Coordinator, or Transmission Operator for data from the list below solely for use in the requestor’s ATC or AFC calculations, each Transmission Service Provider receiving said request shall begin to make the requested data available to the requestor, subject to the conditions specified in R9.1 and R9.2: [Time Horizon: Operations Planning] • Expected generation and Transmission outages, additions, and retirements. • Load forecasts. • Unit commitments and order of dispatch, to include all designated network resources and other resources that are committed or have the legal obligation to run, as they are expected to run, in one of the following formats chosen by the data provider:  Dispatch Order  Participation Factors  Block Dispatch • Aggregated firm capacity set-aside for Network Integration Transmission Service and aggregated non-firm capacity set aside for Network Integration Transmission Service (i.e. Secondary Service). • Firm and non-firm Transmission reservations. • Aggregated capacity set-aside for Grandfathered obligations • Firm roll-over rights. • Any firm and non-firm adjustments applied by the Transmission Service Provider to reflect parallel path impacts. • Power flow models and underlying assumptions. • Contingencies, provided in one or more of the following formats: A list of Elements  A list of Flowgates  A set of selection criteria that can be applied to the Transmission model used by the Transmission Operator and/or Transmission Service Provider • Facility Ratings. • Any other services that impact Existing Transmission Commitments (ETCs). • Values of Capacity Benefit Margin (CBM) and Transmission Reliability Margin (TRM) for all ATC Paths or Flowgates. • Values of Total Flowgate Capability (TFC) and AFC for any Flowgates considered by the Transmission Service Provider receiving the request when selling Transmission service. • Values of TTC and ATC for all ATC Paths for those Transmission Service Providers receiving the request that do not consider Flowgates when selling Transmission Service. • Source and sink identification and mapping to the model. | MEDIUM | Effective | 2010-04-18 |  | TSP
MOD-001-1a | Available Transmission System Capability | R9.1. | The Transmission Service Provider shall make its own current data available, in the format maintained by the Transmission Service Provider, for up to 13 months into the future (subject to confidentiality and security requirements). | No Individual VRF Assigned | Effective | 2010-04-18 |  | TSP
MOD-001-1a | Available Transmission System Capability | R9.1. | The Transmission Service Provider shall make its own current data available, in the format maintained by the Transmission Service Provider, for up to 13 months into the future (subject to confidentiality and security requirements). | No Individual VRF Assigned | Effective | 2010-04-18 |  | TSP
MOD-001-1a | Available Transmission System Capability | R9.1.1. | If the Transmission Service Provider uses the data requested in its transfer or Flowgate capability calculations, it shall make the data used available | No Individual VRF Assigned | Effective | 2010-04-18 |  | TSP
MOD-001-1a | Available Transmission System Capability | R9.1.1. | If the Transmission Service Provider uses the data requested in its transfer or Flowgate capability calculations, it shall make the data used available | No Individual VRF Assigned | Effective | 2010-04-18 |  | TSP
MOD-001-1a | Available Transmission System Capability | R9.1.2. | If the Transmission Service Provider does not use the data requested in its transfer or Flowgate capability calculations, but maintains that data, it shall make that data available | No Individual VRF Assigned | Effective | 2010-04-18 |  | TSP
MOD-001-1a | Available Transmission System Capability | R9.1.2. | If the Transmission Service Provider does not use the data requested in its transfer or Flowgate capability calculations, but maintains that data, it shall make that data available | No Individual VRF Assigned | Effective | 2010-04-18 |  | TSP
MOD-001-1a | Available Transmission System Capability | R9.1.3. | If the Transmission Service Provider does not use the data requested in its transfer or Flowgate capability calculations, and does not maintain that data, it shall not be required to make that data available | No Individual VRF Assigned | Effective | 2010-04-18 |  | TSP
MOD-001-1a | Available Transmission System Capability | R9.1.3. | If the Transmission Service Provider does not use the data requested in its transfer or Flowgate capability calculations, and does not maintain that data, it shall not be required to make that data available | No Individual VRF Assigned | Effective | 2010-04-18 |  | TSP
MOD-001-1a | Available Transmission System Capability | R9.2. | This data shall be made available by the Transmission Provider on the schedule specified by the requestor (but no more frequently than once per hour, unless mutually agreed to by the requester and the provider). | No Individual VRF Assigned | Effective | 2010-04-18 |  | TSP
MOD-001-1a | Available Transmission System Capability | R9.2. | This data shall be made available by the Transmission Provider on the schedule specified by the requestor (but no more frequently than once per hour, unless mutually agreed to by the requester and the provider). | No Individual VRF Assigned | Effective | 2010-04-18 |  | TSP
MOD-001-2 | Available Transmission System Capability | R1. | Each Transmission Operator that determines Total Flowgate Capability (TFC) or Total Transfer Capability (TTC) shall develop a written methodology (or methodologies) for determining TFC or TTC values. The methodology (or methodologies) shall reflect the Transmission Operator’s current practices for determining TFC or TTC values. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Never Came Into Effect in Ontario |  |  | TOP
MOD-001-2 | Available Transmission System Capability | R1.1. | Each methodology shall describe the method used to account for the following limitations in both the pre‐ and post‐contingency state: | LOWER | Never Came Into Effect in Ontario |  |  | TOP
MOD-001-2 | Available Transmission System Capability | R1.1.1. | Facility ratings; | LOWER | Never Came Into Effect in Ontario |  |  | TOP
MOD-001-2 | Available Transmission System Capability | R1.1.2. | System voltage limits; | LOWER | Never Came Into Effect in Ontario |  |  | TOP
MOD-001-2 | Available Transmission System Capability | R1.1.3. | Transient stability limits; | LOWER | Never Came Into Effect in Ontario |  |  | TOP
MOD-001-2 | Available Transmission System Capability | R1.1.4. | Voltage stability limits; and | LOWER | Never Came Into Effect in Ontario |  |  | TOP
MOD-001-2 | Available Transmission System Capability | R1.1.5. | Other System Operating Limits (SOLs). | LOWER | Never Came Into Effect in Ontario |  |  | TOP
MOD-001-2 | Available Transmission System Capability | R1.2. | Each methodology shall describe the method used to account for each of the following elements, provided such elements impact the determination of TFC or TTC: | LOWER | Never Came Into Effect in Ontario |  |  | TOP
MOD-001-2 | Available Transmission System Capability | R1.2.1. | The simulation of transfers performed through the adjustment of generation, Load, or both; | LOWER | Never Came Into Effect in Ontario |  |  | TOP
MOD-001-2 | Available Transmission System Capability | R1.2.2. | Transmission topology, including, but not limited to, additions and retirements; | LOWER | Never Came Into Effect in Ontario |  |  | TOP
MOD-001-2 | Available Transmission System Capability | R1.2.3. | Expected transmission uses; | LOWER | Never Came Into Effect in Ontario |  |  | TOP
MOD-001-2 | Available Transmission System Capability | R1.2.4. | Planned outages; | LOWER | Never Came Into Effect in Ontario |  |  | TOP
MOD-001-2 | Available Transmission System Capability | R1.2.5. | Parallel path (loop flow) adjustments; | LOWER | Never Came Into Effect in Ontario |  |  | TOP
MOD-001-2 | Available Transmission System Capability | R1.2.6. | Load forecast; and | LOWER | Never Came Into Effect in Ontario |  |  | TOP
MOD-001-2 | Available Transmission System Capability | R1.2.7. | Generator dispatch, including, but not limited to, additions and retirements. | LOWER | Never Came Into Effect in Ontario |  |  | TOP
MOD-001-2 | Available Transmission System Capability | R1.3. | Each methodology shall describe the process for including any reliability‐related constraints that are requested to be included by another Transmission Operator, provided that (1) the request references this specific requirement, and (2) the requesting Transmission Operator includes those constraints in its TFC or TTC determination. | LOWER | Never Came Into Effect in Ontario |  |  | TOP
MOD-001-2 | Available Transmission System Capability | R1.3.1. | Each Transmission Operator that uses the Flowgate Methodology shall include in its methodology an impact test process for including requested constraints. If a generator to Load transfer in a registered entity’s area or a transfer to a neighboring registered entity impacts the requested constraint by five percent or greater, the requested constraint shall be included in the TFC determination, otherwise the requested constraint is not required to be included. | LOWER | Never Came Into Effect in Ontario |  |  | TOP
MOD-001-2 | Available Transmission System Capability | R1.3.2. | Each Transmission Operator that uses the Area Interchange or Rated System Path Methodology shall describe in its methodology the process it uses to account for requested constraints that have a five percent or greater distribution factor for a transfer between areas in the TTC determination; otherwise the requested constraint is not required to be included. When testing transfers involving the requesting Transmission Operator’s area, the requested constraint may be excluded. | LOWER | Never Came Into Effect in Ontario |  |  | TOP
MOD-001-2 | Available Transmission System Capability | R1.3.3. | A different method for determining whether requested constraints need to be included in the TFC or TTC determination may be used if agreed to by the Transmission Operators. | LOWER | Never Came Into Effect in Ontario |  |  | TOP
MOD-001-2 | Available Transmission System Capability | R2. | Each Transmission Service Provider that determines Available Flowgate Capability (AFC) or Available Transfer Capability (ATC) shall develop an Available Transfer Capability Implementation Document (ATCID) that describes the methodology (or methodologies) for determining AFC or ATC values. The methodology (or methodologies) shall reflect the Transmission Service Provider’s current practices for determining AFC or ATC values. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Never Came Into Effect in Ontario |  |  | TSP
MOD-001-2 | Available Transmission System Capability | R2. | Each Transmission Service Provider that determines Available Flowgate Capability (AFC) or Available Transfer Capability (ATC) shall develop an Available Transfer Capability Implementation Document (ATCID) that describes the methodology (or methodologies) for determining AFC or ATC values. The methodology (or methodologies) shall reflect the Transmission Service Provider’s current practices for determining AFC or ATC values. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Never Came Into Effect in Ontario |  |  | TSP
MOD-001-2 | Available Transmission System Capability | R2.1. | Each methodology shall describe the method used to account for the following elements, provided such elements impact the determination of AFC or ATC: | LOWER | Never Came Into Effect in Ontario |  |  | TSP
MOD-001-2 | Available Transmission System Capability | R2.1.1. | The simulation of transfers performed through the adjustment of generation, Load, or both; | LOWER | Never Came Into Effect in Ontario |  |  | TSP
MOD-001-2 | Available Transmission System Capability | R2.1.2. | Transmission topology, including, but not limited to, additions and retirements; | LOWER | Never Came Into Effect in Ontario |  |  | TSP
MOD-001-2 | Available Transmission System Capability | R2.1.3. | Expected transmission uses; | LOWER | Never Came Into Effect in Ontario |  |  | TSP
MOD-001-2 | Available Transmission System Capability | R2.1.4. | Planned outages; | LOWER | Never Came Into Effect in Ontario |  |  | TSP
MOD-001-2 | Available Transmission System Capability | R2.1.5. | Parallel path (loop flow) adjustments; | LOWER | Never Came Into Effect in Ontario |  |  | TSP
MOD-001-2 | Available Transmission System Capability | R2.1.6. | Load forecast; and | LOWER | Never Came Into Effect in Ontario |  |  | TSP
MOD-001-2 | Available Transmission System Capability | R2.1.7. | Generator dispatch, including, but not limited to, additions and retirements. | LOWER | Never Came Into Effect in Ontario |  |  | TSP
MOD-001-2 | Available Transmission System Capability | R2.2. | Each Transmission Service Provider that uses the Flowgate Methodology shall, for reliabilityrelated constraints identified in part 1.3, use the AFC determined by the Transmission Service Provider for that constraint. | LOWER | Never Came Into Effect in Ontario |  |  | TSP
MOD-001-2 | Available Transmission System Capability | R3. | Each Transmission Service Provider that determines Capacity Benefit Margin (CBM) values shall develop a Capacity Benefit Margin Implementation Document (CBMID) that describes its method for determining CBM values. The method described in the CBMID shall reflect the Transmission Service Provider’s current practices for determining CBM values. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Never Came Into Effect in Ontario |  |  | TSP
MOD-001-2 | Available Transmission System Capability | R4. | Each Transmission Operator that determines Transmission Reliability Margin (TRM) values shall develop a Transmission Reliability Margin Implementation Document (TRMID) that describes its method for determining TRM values. The method described in the TRMID shall reflect the Transmission Operator’s current practices for determining TRM values. [Violation Risk Factor: Lower][Time Horizon: Operations Planning] | LOWER | Never Came Into Effect in Ontario |  |  | TOP
MOD-001-2 | Available Transmission System Capability | R5. | Within 45 calendar days of receiving a written request that references this specific requirement from a Planning Coordinator, Reliability Coordinator, Transmission Operator, Transmission Planner, Transmission Service Provider, or any other registered entity that demonstrates a reliability need, each Transmission Operator or Transmission Service Provider shall provide: [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP
MOD-001-2 | Available Transmission System Capability | R5.1. | A written response to any request for clarification of its TFC or TTC methodology, ATCID, CBMID, or TRMID. If the request for clarification is contrary to the Transmission Operator’s or Transmission Service Provider’s confidentiality, regulatory, or security requirements then a written response shall be provided explaining the clarifications not provided, on what basis and whether there are any options for resolving any of the confidentiality, regulatory, or security concerns. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP
MOD-001-2 | Available Transmission System Capability | R5.2. | If not publicly posted on OASIS or its company website, the Transmission Operator’s effective: | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP
MOD-001-2 | Available Transmission System Capability | R5.2.1. | TRMID; and | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP
MOD-001-2 | Available Transmission System Capability | R5.2.2. | TFC or TTC methodology. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP
MOD-001-2 | Available Transmission System Capability | R5.3. | If not publicly posted on OASIS or its company website, the Transmission Service Provider’s effective: | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP
MOD-001-2 | Available Transmission System Capability | R5.3.1. | ATCID; and | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP
MOD-001-2 | Available Transmission System Capability | R5.3.2. | CBMID. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP
MOD-001-2 | Available Transmission System Capability | R6. | Each Transmission Operator or Transmission Service Provider that receives a written request from another Transmission Operator or Transmission Service Provider for data related to AFC, ATC, TFC, or TTC determinations that (1) references this specific requirement, and (2) specifies that the requested data is for use in the requesting party’s AFC, ATC, TFC, or TTC determination shall take one of the actions below. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP
MOD-001-2 | Available Transmission System Capability | R6.1. | In responding to a written request for data on an ongoing basis, the Transmission Service Provider or Transmission Operator shall make available its data on an ongoing basis no later than 45 calendar days from receipt of the written request. Unless otherwise agreed upon, the Transmission Operator or Transmission Service Provider is not required to: | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP
MOD-001-2 | Available Transmission System Capability | R6.1.1. | Alter the format in which it maintains or uses the data; or | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP
MOD-001-2 | Available Transmission System Capability | R6.1.2. | Make available the requested data on a more frequent basis than it produces the data and in no event shall it be required to provide the data more frequently than once an hour. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP
MOD-001-2 | Available Transmission System Capability | R6.2. | In responding to all other data requests, each Transmission Operator or Transmission Service Provider shall make available the requested data within 45 calendar days of receipt of the written request. Unless otherwise agreed upon, the Transmission Operator or Transmission Service Provider is not required to alter the format in which it maintains or uses the data. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP
MOD-001-2 | Available Transmission System Capability | R6.3. | If making available any requested data under parts 6.1 or 6.2 of this requirement is contrary to the Transmission Operator’s or Transmission Service Provider’s confidentiality, regulatory, or security requirements, the Transmission Operator or Transmission Service Provider shall not be required to make available that data; provided that, within 45 calendar days of the written request, it responds to the requesting registered entity specifying the data that is not being provided, on what basis and whether there are any options for resolving any of the confidentiality, regulatory or security concerns. | LOWER | Never Came Into Effect in Ontario |  |  | TSP, TOP
MOD-004-0 | Capacity Benefit Margin | R1. | Each Regional Reliability Organization, in conjunction with its members, shall develop and document a Regional CBM methodology. The Regional Reliability Organization’s CBM methodology shall include each of the following ten items, and shall explain its use in determining CBM value. Other items that are Regional Reliability Organization specific or that are considered in each respective Regional Reliability Organization methodology shall also be explained along with their use in determining CBM values. | N/A | Never Came Into Effect in Ontario
MOD-004-0 | Capacity Benefit Margin | R1.1. | Specify that the method used by each Regional Reliability Organization member to determine its generation reliability requirements as the basis for CBM shall be consistent with its generation planning criteria. | N/A | Never Came Into Effect in Ontario
MOD-004-0 | Capacity Benefit Margin | R1.10. | Describe the inclusion or exclusion rationale for generation reserve sharing arrangements in the CBM values. | N/A | Never Came Into Effect in Ontario
MOD-004-0 | Capacity Benefit Margin | R1.2. | Specify the frequency of calculation of the generation reliability requirement and associated CBM values. | N/A | Never Came Into Effect in Ontario
MOD-004-0 | Capacity Benefit Margin | R1.3. | Require that generation unit outages considered in a Transmission Service Provider’s CBM calculation be restricted to those units within the Transmission Service Provider’s system. | N/A | Never Came Into Effect in Ontario
MOD-004-0 | Capacity Benefit Margin | R1.4. | Require that CBM be preserved only on the Transmission Service Provider’s System where the Load-Serving Entity’s Load is located (i.e., CBM is an import quantity only). | N/A | Never Came Into Effect in Ontario
MOD-004-0 | Capacity Benefit Margin | R1.5. | Describe the inclusion or exclusion rationale for generation resources of each Load-Serving Entity including those generation resources not directly connected to the Transmission Service Provider’s system but serving Load-Serving Entity loads connected to the Transmission Service Provider’s system. | N/A | Never Came Into Effect in Ontario
MOD-004-0 | Capacity Benefit Margin | R1.6. | Describe the inclusion or exclusion rationale for generation connected to the Transmission Service Provider’s system but not obligated to serve Native/Network Load connected to the Transmission Service Provider’s system. | N/A | Never Came Into Effect in Ontario
MOD-004-0 | Capacity Benefit Margin | R1.7. | Describe the formal process and rationale for the Regional Reliability Organization to grant any variances to individual Transmission Service Providers from the Regional Reliability Organization’s CBM methodology. | N/A | Never Came Into Effect in Ontario
MOD-004-0 | Capacity Benefit Margin | R1.8. | Specify the relationship of CBM to the generation reliability requirement and the allocation of the CBM values to the appropriate transmission facilities. The sum of the CBM values allocated to all interfaces shall not exceed that portion of the generation reliability requirement that is to be provided by outside resources. | N/A | Never Came Into Effect in Ontario
MOD-004-0 | Capacity Benefit Margin | R1.9. | Describe the inclusion or exclusion rationale for the loads of each Load-Serving Entity, including interruptible demands and buy-through contracts (type of service contract that offers the customer the option to be interrupted or to accept a higher rate for service under certain conditions). | N/A | Never Came Into Effect in Ontario
MOD-004-0 | Capacity Benefit Margin | R2. | The Regional Reliability Organization shall make the most recent version of the documentation of its CBM methodology available on a website accessible by NERC, the Regional Reliability Organizations, and transmission users. | N/A | Never Came Into Effect in Ontario
MOD-004-1 | Capacity Benefit Margin | R1. | The Transmission Service Provider that maintains CBM shall prepare and keep current a “Capacity Benefit Margin Implementation Document” (CBMID) that includes, at a minimum, the following information: [Time Horizon: Operations Planning, Long-term Planning] | MEDIUM | Effective | 2011-04-01 |  | TSP
MOD-004-1 | Capacity Benefit Margin | R1.1. | The process through which a Load-Serving Entity within a Balancing Authority Area associated with the Transmission Service Provider, or the Resource Planner associated with that Balancing Authority Area, may ensure that its need for Transmission capacity to be set aside as CBM will be reviewed and accommodated by the Transmission Service Provider to the extent Transmission capacity is available. | No Individual VRF Assigned | Effective | 2011-04-01 |  | TSP
MOD-004-1 | Capacity Benefit Margin | R1.2. | The procedure and assumptions for establishing CBM for each Available Transfer Capability (ATC) Path or Flowgate. | No Individual VRF Assigned | Effective | 2011-04-01 |  | TSP
MOD-004-1 | Capacity Benefit Margin | R1.3. | The procedure for a Load-Serving Entity or Balancing Authority to use Transmission capacity set aside as CBM, including the manner in which the Transmission Service Provider will manage situations where the requested use of CBM exceeds the amount of CBM available. | No Individual VRF Assigned | Effective | 2011-04-01 |  | TSP
MOD-004-1 | Capacity Benefit Margin | R10. | The Load-Serving Entity or Balancing Authority shall request to import energy over firm Transfer Capability set aside as CBM only when experiencing a declared NERC Energy Emergency Alert (EEA) 2 or higher. [Time Horizon: Same-day Operations] | LOWER | Effective | 2011-04-01 |  | BA
MOD-004-1 | Capacity Benefit Margin | R11. | When reviewing an Arranged Interchange using CBM, all Balancing Authorities and Transmission Service Providers shall waive, within the bounds of reliable operation, any Real-time timing and ramping requirements. [Time Horizon: Same-day Operations] | MEDIUM | Effective | 2011-04-01 |  | TSP, BA
MOD-004-1 | Capacity Benefit Margin | R12. | The Transmission Service Provider that maintains CBM shall approve, within the bounds of reliable operation, any Arranged Interchange using CBM that is submitted by an “energy deficient entity ” under an EEA 2 if: [Time Horizon: Same-day Operations] | MEDIUM | Effective | 2011-04-01 |  | TSP
MOD-004-1 | Capacity Benefit Margin | R12.1. | The CBM is available | No Individual VRF Assigned | Effective | 2011-04-01 |  | TSP
MOD-004-1 | Capacity Benefit Margin | R12.2. | The EEA 2 is declared within the Balancing Authority Area of the “energy deficient entity,” and | No Individual VRF Assigned | Effective | 2011-04-01 |  | TSP
MOD-004-1 | Capacity Benefit Margin | R12.3. | The Load of the “energy deficient entity” is located within the Transmission Service Provider’s area. | No Individual VRF Assigned | Effective | 2011-04-01 |  | TSP
MOD-004-1 | Capacity Benefit Margin | R2. | The Transmission Service Provider that maintains CBM shall make available its current CBMID to the Transmission Operators, Transmission Service Providers, Reliability Coordinators, Transmission Planners, Resource Planners, and Planning Coordinators that are within or adjacent to the Transmission Service Provider’s area, and to the Load Serving Entities and Balancing Authorities within the Transmission Service Provider’s area, and notify those entities of any changes to the CBMID prior to the effective date of the change. [Time Horizon: Operations Planning] | MEDIUM | Effective | 2011-04-01 |  | TSP
MOD-004-1 | Capacity Benefit Margin | R3. | Each Load-Serving Entity determining the need for Transmission capacity to be set aside as CBM for imports into a Balancing Authority Area shall determine that need by: [Time Horizon: Operations Planning] | MEDIUM | Effective | 2011-04-01
MOD-004-1 | Capacity Benefit Margin | R3.1. | Using one or more of the following to determine the GCIR: Loss of Load Expectation (LOLE) studies Loss of Load Probability (LOLP) studies Deterministic risk-analysis studies Reserve margin or resource adequacy requirements established by other entities, such as municipalities, state commissions, regional transmission organizations, independent system operators, Regional Reliability Organizations, or regional entities | No Individual VRF Assigned | Effective | 2011-04-01
MOD-004-1 | Capacity Benefit Margin | R3.2. | Identifying expected import path(s) or source region(s). | No Individual VRF Assigned | Effective | 2011-04-01
MOD-004-1 | Capacity Benefit Margin | R4. | Each Resource Planner determining the need for Transmission capacity to be set aside as CBM for imports into a Balancing Authority Area shall determine that need by: [Time Horizon: Operations Planning] | MEDIUM | Effective | 2011-04-01 |  | RP
MOD-004-1 | Capacity Benefit Margin | R4.1. | Using one or more of the following to determine the GCIR: Loss of Load Expectation (LOLE) studies Loss of Load Probability (LOLP) studies Deterministic risk-analysis studies Reserve margin or resource adequacy requirements established by other entities, such as municipalities, state commissions, regional transmission organizations, independent system operators, Regional Reliability Organizations, or regional entities | No Individual VRF Assigned | Effective | 2011-04-01 |  | RP
MOD-004-1 | Capacity Benefit Margin | R4.2. | Identifying expected import path(s) or source region(s). | No Individual VRF Assigned | Effective | 2011-04-01 |  | RP
MOD-004-1 | Capacity Benefit Margin | R5. | At least every 13 months, the Transmission Service Provider that maintains CBM shall establish a CBM value for each ATC Path or Flowgate to be used for ATC or Available Flowgate Capability (AFC) calculations during the 13 full calendar months (months 2-14) following the current month (the month in which the Transmission Service Provider is establishing the CBM values). This value shall: [Time Horizon: Operations Planning] | MEDIUM | Effective | 2011-04-01 |  | TSP
MOD-004-1 | Capacity Benefit Margin | R5.1. | Reflect consideration of each of the following if available: Any studies (as described in R3.1) performed by Load-Serving Entities for loads within the Transmission Service Provider’s area Any studies (as described in R4.1) performed by Resource Planners for loads within the Transmission Service Provider’s area Any reserve margin or resource adequacy requirements for loads within the Transmission Service Provider’s area established by other entities, such as municipalities, state commissions, regional transmission organizations, independent system operators, Regional Reliability Organizations, or regional entities | No Individual VRF Assigned | Effective | 2011-04-01 |  | TSP
MOD-004-1 | Capacity Benefit Margin | R5.2. | Be allocated as follows: For ATC Paths, based on the expected import paths or source regions provided by Load-Serving Entities or Resource Planners For Flowgates, based on the expected import paths or source regions provided by Load-Serving Entities or Resource Planners and the distribution factors associated with those paths or regions, as determined by the Transmission Service Provider | No Individual VRF Assigned | Effective | 2011-04-01 |  | TSP
MOD-004-1 | Capacity Benefit Margin | R6. | At least every 13 months, the Transmission Planner shall establish a CBM value for each ATC Path or Flowgate to be used in planning during each of the full calendar years two through ten following the current year (the year in which the Transmission Planner is establishing the CBM values). This value shall: [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2011-04-01 |  | TP
MOD-004-1 | Capacity Benefit Margin | R6.1. | Reflect consideration of each of the following if available: Any studies (as described in R3.1) performed by Load-Serving Entities for loads within the Transmission Planner’s area Any studies (as described in R4.1) performed by Resource Planners for loads within the Transmission Planner’s area Any reserve margin or resource adequacy requirements for loads within the Transmission Planner’s area established by other entities, such as municipalities, state commissions, regional transmission organizations, independent system operators, Regional Reliability Organizations, or regional entities | No Individual VRF Assigned | Effective | 2011-04-01 |  | TP
MOD-004-1 | Capacity Benefit Margin | R6.2. | Be allocated as follows: For ATC Paths, based on the expected import paths or source regions provided by Load-Serving Entities or Resource Planners For Flowgates, based on the expected import paths or source regions provided by Load-Serving Entities or Resource Planners and the distribution factors associated with those paths or regions, as determined by the Transmission Planner. | No Individual VRF Assigned | Effective | 2011-04-01 |  | TP
MOD-004-1 | Capacity Benefit Margin | R7. | Less than 31 calendar days after the establishment of CBM, the Transmission Service Provider that maintains CBM shall notify all the Load-Serving Entities and Resource Planners that determined they had a need for CBM on the Transmission Service Provider’s system of the amount of CBM set aside. [Time Horizon: Operations Planning] | MEDIUM | Effective | 2011-04-01 |  | TSP
MOD-004-1 | Capacity Benefit Margin | R8. | Less than 31 calendar days after the establishment of CBM, the Transmission Planner shall notify all the Load-Serving Entities and Resource Planners that determined they had a need for CBM on the system being planned by the Transmission Planner of the amount of CBM set aside. [Time Horizon: Operations Planning] | MEDIUM | Effective | 2011-04-01 |  | TP
MOD-004-1 | Capacity Benefit Margin | R9. | The Transmission Service Provider that maintains CBM and the Transmission Planner shall each provide (subject to confidentiality and security requirements) copies of the applicable supporting data, including any models, used for determining CBM or allocating CBM over each ATC Path or Flowgate to the following: [Time Horizon: Operations Planning, Long-term Planning] | LOWER | Effective | 2011-04-01 |  | TSP, TP
MOD-004-1 | Capacity Benefit Margin | R9.1. | Each of its associated Transmission Operators within 30 calendar days of their making a request for the data. | No Individual VRF Assigned | Effective | 2011-04-01 |  | TSP, TP
MOD-004-1 | Capacity Benefit Margin | R9.2. | To any Transmission Service Provider, Reliability Coordinator, Transmission Planner, Resource Planner, or Planning Coordinator within 30 calendar days of their making a request for the data. | No Individual VRF Assigned | Effective | 2011-04-01 |  | TSP, TP
MOD-008-0 | TRM Calculation Methodology | R1. | Each Regional Reliability Organization, in conjunction with its members, shall develop and document a Regional TRM methodology. The Region’s TRM methodology shall specify or describe each of the following five items, and shall explain its use, if any, in determining TRM values. Other items that are Region-specific or that are considered in each respective Regional methodology shall also be explained along with their use in determining TRM values. | N/A | Never Came Into Effect in Ontario
MOD-008-0 | TRM Calculation Methodology | R1.1. | Specify the update frequency of TRM calculations. | N/A | Never Came Into Effect in Ontario
MOD-008-0 | TRM Calculation Methodology | R1.2. | Specify how TRM values are incorporated into Available Transfer Capability calculations. | N/A | Never Came Into Effect in Ontario
MOD-008-0 | TRM Calculation Methodology | R1.3. | Specify the uncertainties accounted for in TRM and the methods used to determine their impacts on the TRM values. Any component of uncertainty, other than those identified in MOD-008-0_R1.3.1 through MOD-008-0_R1.3.7, shall benefit the interconnected transmission systems as a whole before they shall be permitted to be included in TRM calculations. The components of uncertainty identified in MOD-008-0_R1.3.1 through MOD-008-0_R1.3.7, if applied, shall be accounted for solely in TRM and not CBM. | N/A | Never Came Into Effect in Ontario
MOD-008-0 | TRM Calculation Methodology | R1.3.1. | Aggregate Load forecast error (not included in determining generation reliability requirements). | N/A | Never Came Into Effect in Ontario
MOD-008-0 | TRM Calculation Methodology | R1.3.2. | Load distribution error. | N/A | Never Came Into Effect in Ontario
MOD-008-0 | TRM Calculation Methodology | R1.3.3. | Variations in facility Loadings due to balancing of generation within a Balancing Authority Area. | N/A | Never Came Into Effect in Ontario
MOD-008-0 | TRM Calculation Methodology | R1.3.4. | Forecast uncertainty in transmission system topology. | N/A | Never Came Into Effect in Ontario
MOD-008-0 | TRM Calculation Methodology | R1.3.5. | Allowances for parallel path (loop flow) impacts. | N/A | Never Came Into Effect in Ontario
MOD-008-0 | TRM Calculation Methodology | R1.3.6. | Allowances for simultaneous path interactions. | N/A | Never Came Into Effect in Ontario
MOD-008-0 | TRM Calculation Methodology | R1.3.7. | Variations in generation dispatch. | N/A | Never Came Into Effect in Ontario
MOD-008-0 | TRM Calculation Methodology | R1.3.8. | Short-term System Operator response (Operating Reserve actions not exceeding a 59-minute window). | N/A | Never Came Into Effect in Ontario
MOD-008-0 | TRM Calculation Methodology | R1.4. | Describe the conditions, if any, under which TRM may be available to the market as Non-Firm Transmission Service. | N/A | Never Came Into Effect in Ontario
MOD-008-0 | TRM Calculation Methodology | R1.5. | Describe the formal process for the Regional Reliability Organization to grant any variances to individual Transmission Service Providers from the Regional TRM methodology. | N/A | Never Came Into Effect in Ontario
MOD-008-0 | TRM Calculation Methodology | R2. | The Regional Reliability Organization shall make its most recent version of the documentation of its TRM methodology available on a web site accessible by NERC, the Regional Reliability Organizations, and transmission users. | N/A | Never Came Into Effect in Ontario
MOD-008-1 | Transmission Reliability Margin Calculation Methodology | R1. | Each Transmission Operator shall prepare and keep current a TRM Implementation Document (TRMID) that includes, as a minimum, the following information: [Time Horizon: Operations Planning] | MEDIUM | Effective | 2011-07-01 |  | TOP
MOD-008-1 | Transmission Reliability Margin Calculation Methodology | R1.1. | Identification of (on each of its respective ATC Paths or Flowgates) each of the following components of uncertainty if used in establishing TRM, and a description of how that component is used to establish a TRM value: - Aggregate Load forecast. - Load distribution uncertainty. - Forecast uncertainty in Transmission system topology (including, but not limited to, forced or unplanned outages and maintenance outages). - Allowances for parallel path (loop flow) impacts. - Allowances for simultaneous path interactions. - Variations in generation dispatch (including, but not limited to, forced or unplanned outages, maintenance outages and location of future generation). - Short-term System Operator response (Operating Reserve actions ). - Reserve sharing requirements. - Inertial response and frequency bias. | No Individual VRF Assigned | Effective | 2011-07-01 |  | TOP
MOD-008-1 | Transmission Reliability Margin Calculation Methodology | R1.2. | The description of the method used to allocate TRM across ATC Paths or Flowgates. | No Individual VRF Assigned | Effective | 2011-07-01 |  | TOP
MOD-008-1 | Transmission Reliability Margin Calculation Methodology | R1.3. | The identification of the TRM calculation used for the following time periods: | No Individual VRF Assigned | Effective | 2011-07-01 |  | TOP
MOD-008-1 | Transmission Reliability Margin Calculation Methodology | R1.3.1. | Same day and real-time. | No Individual VRF Assigned | Effective | 2011-07-01 |  | TOP
MOD-008-1 | Transmission Reliability Margin Calculation Methodology | R1.3.2. | Day-ahead and pre-schedule. | No Individual VRF Assigned | Effective | 2011-07-01 |  | TOP
MOD-008-1 | Transmission Reliability Margin Calculation Methodology | R1.3.3. | Beyond day-ahead and pre-schedule, up to thirteen months ahead. | No Individual VRF Assigned | Effective | 2011-07-01 |  | TOP
MOD-008-1 | Transmission Reliability Margin Calculation Methodology | R2. | Each Transmission Operator shall only use the components of uncertainty from R1.1 to establish TRM, and shall not include any of the components of Capacity Benefit Margin (CBM). Transmission capacity set aside for reserve sharing agreements can be included in TRM. [Time Horizon: Operations Planning] | MEDIUM | Effective | 2011-07-01 |  | TOP
MOD-008-1 | Transmission Reliability Margin Calculation Methodology | R2. | Each Transmission Operator shall only use the components of uncertainty from R1.1 to establish TRM, and shall not include any of the components of Capacity Benefit Margin (CBM). Transmission capacity set aside for reserve sharing agreements can be included in TRM. [Time Horizon: Operations Planning] | MEDIUM | Effective | 2011-07-01 |  | TOP
MOD-008-1 | Transmission Reliability Margin Calculation Methodology | R3. | Each Transmission Operator shall make available its TRMID, and if requested, underlying documentation (if any) used to determine TRM, in the format used by the Transmission Operator, to any of the following who make a written request no more than 30 calendar days after receiving the request. [Time Horizon: Operations Planning] • Transmission Service Providers • Reliability Coordinators • Planning Coordinators • Transmission Planner • Transmission Operators | LOWER | Effective | 2011-07-01 |  | TOP
MOD-008-1 | Transmission Reliability Margin Calculation Methodology | R4. | Each Transmission Operator that maintains TRM shall establish TRM values in accordance with the TRMID at least once every 13 months. [Time Horizon: Operations Planning] | MEDIUM | Effective | 2011-07-01 |  | TOP
MOD-008-1 | Transmission Reliability Margin Calculation Methodology | R5. | The Transmission Operator that maintains TRM shall provide the TRM values to its Transmission Service Provider(s) and Transmission Planner(s) no more than seven calendar days after a TRM value is initially established or subsequently changed. [Time Horizon: Operations Planning] | MEDIUM | Effective | 2011-07-01 |  | TOP
MOD-008-1 | Transmission Reliability Margin Calculation Methodology | R5. | The Transmission Operator that maintains TRM shall provide the TRM values to its Transmission Service Provider(s) and Transmission Planner(s) no more than seven calendar days after a TRM value is initially established or subsequently changed. [Time Horizon: Operations Planning] | MEDIUM | Effective | 2011-07-01 |  | TOP
MOD-010-0 | Steady-State Data for Modeling and Simulation of the Interconnected Transmission System | R1. | The Transmission Owners, Transmission Planners, Generator Owners, and Resource Planners (specified in the data requirements and reporting procedures of MOD-011-0_R1) shall provide appropriate equipment characteristics, system data, and existing and future Interchange Schedules in compliance with its respective Interconnection Regional steady-state Real-Time Applications and simulation data requirements and reporting procedures as defined in Reliability Standard MOD-011-0_R 1. | MEDIUM | Retired | 2005-02-08 | 2016-06-30 | TP, TO, RP, GO
MOD-010-0 | Steady-State Data for Modeling and Simulation of the Interconnected Transmission System | R2. | The Transmission Owners, Transmission Planners, Generator Owners, and Resource Planners (specified in the data requirements and reporting procedures of MOD-011-0_R1) shall provide this steady-state Real-Time Applications and simulation data to the Regional Reliability Organizations, NERC, and those entities specified within Reliability Standard MOD-011-0_R 1. If no schedule exists, then these entities shall provide the data on request (30 calendar days). | MEDIUM | Retired | 2005-02-08 | 2016-06-30 | TP, TO, RP, GO
MOD-012-0 | Dynamics Data for Modeling and Simulation of the Interconnected Transmission System | R1. | The Transmission Owners, Transmission Planners, Generator Owners, and Resource Planners (specified in the data requirements and reporting procedures of MOD-013-0_R1) shall provide appropriate equipment characteristics and system data in compliance with the respective Interconnection-wide Regional dynamics system Real-Time Applications and simulation data requirements and reporting procedures as defined in Reliability Standard MOD-013-0_R1. | MEDIUM | Retired | 2005-02-08 | 2016-06-30 | TP, TO, RP, GO
MOD-012-0 | Dynamics Data for Modeling and Simulation of the Interconnected Transmission System | R2. | The Transmission Owners, Transmission Planners, Generator Owners, and Resource Planners (specified in the data requirements and reporting procedures of MOD-013-0_R4) shall provide dynamics system Real-Time Applications and simulation data to its Regional Reliability Organization(s), NERC, and those entities specified within the applicable reporting procedures identified in Reliability Standard MOD-013-0_R 1. If no schedule exists, then these entities shall provide data on request (30 calendar days). | MEDIUM | Retired | 2005-02-08 | 2016-06-30 | TP, TO, RP, GO
MOD-015-0 | Development of Dynamics System Models | R1. | The Regional Reliability Organization(s) within each Interconnection shall coordinate and jointly develop and maintain a library of initialized (with no Faults or system Disturbances) Interconnection-specific dynamics system models linked to the steadystate system models, as appropriate, of Reliability Standard MOD-014-0_R1. | N/A | Never Came Into Effect in Ontario
MOD-015-0 | Development of Dynamics System Models | R1.1. | The Regional Reliability Organization(s) shall develop Interconnectionspecific dynamics system models for at least two timeframes (present or nearterm model and a future or longer-term model), and additional seasonal and demand level models, as necessary, to analyze the dynamic response of that Interconnection. | N/A | Never Came Into Effect in Ontario
MOD-015-0 | Development of Dynamics System Models | R2. | The Regional Reliability Organization(s) within each Interconnection shall develop Interconnection dynamics system models for their Interconnection annually for selected study years as determined by the Regional Reliability Organization(s) within each Interconnection and shall provide the most recent initialized (approximately 25 seconds, no-fault) models to NERC in accordance with each Interconnection’s schedule for submission. | N/A | Never Came Into Effect in Ontario
MOD-015-0.1 | Development of Dynamics System Models | R1. | The Regional Reliability Organization(s) within each Interconnection shall coordinate and jointly develop and maintain a library of initialized (with no Faults or system Disturbances) Interconnection-specific dynamics system models linked to the steadystate system models, as appropriate, of Reliability Standard MOD-014-0_R1. |  | Never Came Into Effect in Ontario
MOD-015-0.1 | Development of Dynamics System Models | R1.1. | R1.1. The Regional Reliability Organization(s) shall develop Interconnection specific dynamics system models for at least two timeframes (present or near-term model and a future or longer-term model), and additional seasonal and demand level models, as necessary, to analyze the dynamic response of that Interconnection. |  | Never Came Into Effect in Ontario
MOD-015-0.1 | Development of Dynamics System Models | R2. | The Regional Reliability Organization(s) within each Interconnection shall develop Interconnection dynamics system models for their Interconnection annually for selected study years as determined by the Regional Reliability Organization(s) within each Interconnection and shall provide the most recent initialized (approximately 25 seconds, no-fault) models to NERC in accordance with each Interconnection’s schedule for submission. |  | Never Came Into Effect in Ontario
MOD-016-1.1 | Documentation of Data Reporting Requirements for Actual and Forecast Demands, Net Energy for Load, and Controllable Demand-Side Management | R1. | The Planning Authority and Regional Reliability Organization shall have documentation identifying the scope and details of the actual and forecast (a) Demand data, (b) Net Energy for Load data, and (c) controllable DSM data to be reported for system modeling and reliability analyses. | LOWER | Retired | 2009-09-13 | 2016-06-30 | PA
MOD-016-1.1 | Documentation of Data Reporting Requirements for Actual and Forecast Demands, Net Energy for Load, and Controllable Demand-Side Management | R1.1. | The aggregated and dispersed data submittal requirements shall ensure that consistent data is supplied for Reliability Standards TPL-005, TPL-006, MOD-010, MOD-011, MOD-012, MOD-013, MOD-014, MOD-015, MOD-016, MOD-017, MOD-018, MOD-019, MOD-020, and MOD-021. The data submittal requirements shall stipulate that each Load-Serving Entity count its customer Demand once and only once, on an aggregated and dispersed basis, in developing its actual and forecast customer Demand values. | LOWER | Retired | 2009-09-13 | 2016-06-30 | PA
MOD-016-1.1 | Documentation of Data Reporting Requirements for Actual and Forecast Demands, Net Energy for Load, and Controllable Demand-Side Management | R2. | The Regional Reliability Organization shall distribute its documentation required in Requirement 1 and any changes to that documentation, to all Planning Authorities that work within its Region. | LOWER | Retired | 2009-09-13 | 2016-06-30
MOD-016-1.1 | Documentation of Data Reporting Requirements for Actual and Forecast Demands, Net Energy for Load, and Controllable Demand-Side Management | R2.1. | The Regional Reliability Organization shall make this distribution within 30 calendar days of approval. | LOWER | Retired | 2009-09-13 | 2016-06-30
MOD-016-1.1 | Documentation of Data Reporting Requirements for Actual and Forecast Demands, Net Energy for Load, and Controllable Demand-Side Management | R3. | The Planning Authority shall distribute its documentation required in R1 for reporting customer data and any changes to that documentation, to its Transmission Planners and Load-Serving Entities that work within its Planning Authority Area. | LOWER | Retired | 2009-09-13 | 2016-06-30 | PA
MOD-016-1.1 | Documentation of Data Reporting Requirements for Actual and Forecast Demands, Net Energy for Load, and Controllable Demand-Side Management | R3.1. | The Planning Authority shall make this distribution within 30 calendar days of approval. | LOWER | Retired | 2009-09-13 | 2016-06-30 | PA
MOD-017-0.1 | Aggregated Actual and Forecast Demands and Net Energy for Load | R1. | The Load-Serving Entity, Planning Authority and Resource Planner shall each provide the following information annually on an aggregated Regional, subregional, Power Pool, individual system, or Load-Serving Entity basis to NERC, the Regional Reliability Organizations, and any other entities specified by the documentation in Standard MOD-016-1_R1. | MEDIUM | Retired | 2009-09-13 | 2016-06-30 | RP, PA
MOD-017-0.1 | Aggregated Actual and Forecast Demands and Net Energy for Load | R1.1. | Integrated hourly demands in megawatts (MW) for the prior year. | MEDIUM | Retired | 2009-09-13 | 2016-06-30 | RP, PA
MOD-017-0.1 | Aggregated Actual and Forecast Demands and Net Energy for Load | R1.2. | Monthly and annual peak hour actual demands in MW and Net Energy for Load in gigawatthours (GWh) for the prior year. | MEDIUM | Retired | 2009-09-13 | 2016-06-30 | RP, PA
MOD-017-0.1 | Aggregated Actual and Forecast Demands and Net Energy for Load | R1.3. | Monthly peak hour forecast demands in MW and Net Energy for Load in GWh for the next two years. | MEDIUM | Retired | 2009-09-13 | 2016-06-30 | RP, PA
MOD-017-0.1 | Aggregated Actual and Forecast Demands and Net Energy for Load | R1.4. | Annual Peak hour forecast demands (summer and winter) in MW and annual Net Energy for load in GWh for at least five years and up to ten years into the future, as requested. | MEDIUM | Retired | 2009-09-13 | 2016-06-30 | RP, PA
MOD-018-0 | Treatment of Nonmember Demand Data and How Uncertainties are Addressed in the Forecasts of Demand and Net Energy for Load | R1. | The Load-Serving Entity, Planning Authority, Transmission Planner and Resource Planner’s report of actual and forecast demand data (reported on either an aggregated or dispersed basis) shall: | MEDIUM | Retired | 2005-02-08 | 2016-06-30 | TP, RP, PA
MOD-018-0 | Treatment of Nonmember Demand Data and How Uncertainties are Addressed in the Forecasts of Demand and Net Energy for Load | R1.1. | Indicate whether the demand data of nonmember entities within an area or Regional Reliability Organization are included, and | MEDIUM | Retired | 2005-02-08 | 2016-06-30 | TP, RP, PA
MOD-018-0 | Treatment of Nonmember Demand Data and How Uncertainties are Addressed in the Forecasts of Demand and Net Energy for Load | R1.2. | Address assumptions, methods, and the manner in which uncertainties are treated in the forecasts of aggregated peak demands and Net Energy for Load. | LOWER | Retired | 2005-02-08 | 2016-06-30 | TP, RP, PA
MOD-018-0 | Treatment of Nonmember Demand Data and How Uncertainties are Addressed in the Forecasts of Demand and Net Energy for Load | R1.3. | Items (MOD-018-0_R 1.1) and (MOD-018-0_R 1.2) shall be addressed as described in the reporting procedures developed for Standard MOD-016-1_R 1. | LOWER | Retired | 2005-02-08 | 2016-06-30 | TP, RP, PA
MOD-018-0 | Treatment of Nonmember Demand Data and How Uncertainties are Addressed in the Forecasts of Demand and Net Energy for Load | R2. | The Load-Serving Entity, Planning Authority, Transmission Planner, and Resource Planner shall each report data associated with Reliability Standard MOD-018-0_R1 to NERC, the Regional Reliability Organization, Load-Serving Entity, Planning Authority, and Resource Planner on request (within 30 calendar days). | LOWER | Retired | 2005-02-08 | 2016-06-30 | TP, RP, PA
MOD-019-0.1 | Reporting of Interruptible Demands and Direct Control Load Management | R1. | The Load-Serving Entity, Planning Authority, Transmission Planner, and Resource Planner shall each provide annually its forecasts of interruptible demands and Direct Control Load Management (DCLM) data for at least five years and up to ten years into the future, as requested, for summer and winter peak system conditions to NERC, the Regional Reliability Organizations, and other entities (Load-Serving Entities, Planning Authorities, and Resource Planners) as specified by the documentation in Reliability Standard MOD-016-1_R 1. | MEDIUM | Retired | 2009-09-13 | 2016-06-30 | TP, RP, PA
MOD-020-0 | Providing Interruptible Demands and Direct Control Load Management Data to System Operators and Reliability Coordinators | R1. | The Load-Serving Entity, Transmission Planner, and Resource Planner shall each make known its amount of interruptible demands and Direct Control Load Management (DCLM) to Transmission Operators, Balancing Authorities, and Reliability Coordinators on request within 30 calendar days. | LOWER | Retired | 2005-02-08 | 2020-12-31 | TP, RP
MOD-021-1 | Documentation of the Accounting Methodology for the Effects of Demand-Side Management in Demand and Energy Forecasts | R1. | The Load-Serving Entity, Transmission Planner and Resource Planner’s forecasts shall each clearly document how the Demand and energy effects of DSM programs (such as conservation, time-of-use rates, interruptible Demands, and Direct Control Load Management) are addressed. | LOWER | Retired | 2010-10-01 | 2016-06-30 | TP, RP
MOD-021-1 | Documentation of the Accounting Methodology for the Effects of Demand-Side Management in Demand and Energy Forecasts | R2. | The Load-Serving Entity, Transmission Planner and Resource Planner shall each include information detailing how Demand-Side Management measures are addressed in the forecasts of its Peak Demand and annual Net Energy for Load in the data reporting procedures of Standard MOD-016-0_R1. | LOWER | Retired | 2010-10-01 | 2016-06-30 | TP, RP
MOD-021-1 | Documentation of the Accounting Methodology for the Effects of Demand-Side Management in Demand and Energy Forecasts | R3. | The Load-Serving Entity, Transmission Planner and Resource Planner shall each make documentation on the treatment of its DSM programs available to NERC on request (within 30 calendar days). | LOWER | Retired | 2010-10-01 | 2016-06-30 | TP, RP
MOD-024-1 | Verification of Generator Gross and Net Real Power Capability | R1. | The Regional Reliability Organization shall establish and maintain procedures to address verification of generator gross and net Real Power capability. These procedures shall include the following: | MEDIUM | Never Came Into Effect in Ontario
MOD-024-1 | Verification of Generator Gross and Net Real Power Capability | R1.1. | Generating unit exemption criteria including documentation of those units that are exempt from a portion or all of these procedures. | MEDIUM | Never Came Into Effect in Ontario
MOD-024-1 | Verification of Generator Gross and Net Real Power Capability | R1.2. | Criteria for reporting generating unit auxiliary loads. | LOWER | Never Came Into Effect in Ontario
MOD-024-1 | Verification of Generator Gross and Net Real Power Capability | R1.3. | Acceptable methods for model and data verification, including any applicable conditions under which the data should be verified. Such methods can include use of manufacturer data, commissioning data, performance tracking, and testing, etc. | MEDIUM | Never Came Into Effect in Ontario
MOD-024-1 | Verification of Generator Gross and Net Real Power Capability | R1.4. | Periodicity and schedule of model and data verification and reporting. | MEDIUM | Never Came Into Effect in Ontario
MOD-024-1 | Verification of Generator Gross and Net Real Power Capability | R1.5. | Information to be verified and reported: | MEDIUM | Never Came Into Effect in Ontario
MOD-024-1 | Verification of Generator Gross and Net Real Power Capability | R1.5.1. | Seasonal gross and net Real Power generating capabilities. | MEDIUM | Never Came Into Effect in Ontario
MOD-024-1 | Verification of Generator Gross and Net Real Power Capability | R1.5.2. | Real power requirements of auxiliary loads. | LOWER | Never Came Into Effect in Ontario
MOD-024-1 | Verification of Generator Gross and Net Real Power Capability | R1.5.3. | Method of verification, including date and conditions. | MEDIUM | Never Came Into Effect in Ontario
MOD-024-1 | Verification of Generator Gross and Net Real Power Capability | R2. | The Regional Reliability Organization shall provide its generator gross and net Real Power capability verification and reporting procedures, and any changes to those procedures, to the Generator Owners, Generator Operators, Transmission Operators, Planning Authorities, and Transmission Planners affected by the procedure within 30 calendar days of the approval. | LOWER | Never Came Into Effect in Ontario |  |  | GOP, GO
MOD-024-1 | Verification of Generator Gross and Net Real Power Capability | R3. | The Generator Owner shall follow its Regional Reliability Organization’s procedures for verifying and reporting its gross and net Real Power generating capability per R1. | MEDIUM | Never Came Into Effect in Ontario |  |  | GO
MOD-025-1 | Verification of Generator Gross and Net Reactive Power Capability | R1. | The Regional Reliability Organization shall establish and maintain procedures to address verification of generator gross and net Reactive Power capability. These procedures shall include the following: | LOWER | Never Came Into Effect in Ontario
MOD-025-1 | Verification of Generator Gross and Net Reactive Power Capability | R1.1. | Generating unit exemption criteria including documentation of those units that are exempt from a portion or all of these procedures. | LOWER | Never Came Into Effect in Ontario
MOD-025-1 | Verification of Generator Gross and Net Reactive Power Capability | R1.2. | Criteria for reporting generating unit auxiliary loads. | LOWER | Never Came Into Effect in Ontario
MOD-025-1 | Verification of Generator Gross and Net Reactive Power Capability | R1.3. | Acceptable methods for model and data verification, including any applicable conditions under which the data should be verified. Such methods can include use of commissioning data, performance tracking, engineering analysis, testing, etc. | LOWER | Never Came Into Effect in Ontario
MOD-025-1 | Verification of Generator Gross and Net Reactive Power Capability | R1.4. | Periodicity and schedule of model and data verification and reporting. | LOWER | Never Came Into Effect in Ontario
MOD-025-1 | Verification of Generator Gross and Net Reactive Power Capability | R1.5. | Information to be reported: | LOWER | Never Came Into Effect in Ontario
MOD-025-1 | Verification of Generator Gross and Net Reactive Power Capability | R1.5.1. | Verified maximum gross and net Reactive Power capability (both lagging and leading) at Seasonal Real Power generating capabilities as reported in accordance with Reliability Standard MOD-024 Requirement 1.5.1. | LOWER | Never Came Into Effect in Ontario
MOD-025-1 | Verification of Generator Gross and Net Reactive Power Capability | R1.5.2. | Verified Reactive Power limitations, such as generator terminal voltage limitations, shorted rotor turns, etc. | LOWER | Never Came Into Effect in Ontario
MOD-025-1 | Verification of Generator Gross and Net Reactive Power Capability | R1.5.3. | Verified Reactive Power of auxiliary loads. | LOWER | Never Came Into Effect in Ontario
MOD-025-1 | Verification of Generator Gross and Net Reactive Power Capability | R1.5.4. | Method of verification, including date and conditions. | LOWER | Never Came Into Effect in Ontario
MOD-025-1 | Verification of Generator Gross and Net Reactive Power Capability | R2. | The Regional Reliability Organization shall provide its generator gross and net Reactive Power capability verification and reporting procedures, and any changes to those procedures, to the Generator Owners, Generator Operators, Transmission Operators, Planning Authorities, and Transmission Planners affected by the procedure within 30 calendar days of the approval. | LOWER | Never Came Into Effect in Ontario |  |  | GOP, GO
MOD-025-1 | Verification of Generator Gross and Net Reactive Power Capability | R3. | The Generator Owner shall follow its Regional Reliability Organization’s procedures for verifying and reporting its gross and net Reactive Power generating capability per R1. | LOWER | Never Came Into Effect in Ontario |  |  | GO
MOD-025-2 | Verification and Data Reporting of Generator Real and Reactive Power Capability and Synchronous Condenser Reactive Power Capability | R1. | Each Generator Owner shall provide its Transmission Planner with verification of the Real Power capability of its applicable Facilities as follows: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2016-07-01 |  | TO, GO
MOD-025-2 | Verification and Data Reporting of Generator Real and Reactive Power Capability and Synchronous Condenser Reactive Power Capability | R1.1. | Verify the Real Power capability of its generating units in accordance with Attachment 1. | MEDIUM | Effective | 2016-07-01 |  | TO, GO
MOD-025-2 | Verification and Data Reporting of Generator Real and Reactive Power Capability and Synchronous Condenser Reactive Power Capability | R1.2. | Submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner within 90 calendar days of either (i) the date the data is recorded for a staged test; or (ii) the date the data is selected for verification using historical operational data. | MEDIUM | Effective | 2016-07-01 |  | TO, GO
MOD-025-2 | Verification and Data Reporting of Generator Real and Reactive Power Capability and Synchronous Condenser Reactive Power Capability | R2. | Each Generator Owner shall provide its Transmission Planner with verification of the Reactive Power capability of its applicable Facilities as follows: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2016-07-01 |  | TO, GO
MOD-025-2 | Verification and Data Reporting of Generator Real and Reactive Power Capability and Synchronous Condenser Reactive Power Capability | R2.1. | Verify, in accordance with Attachment 1, (i) the Reactive Power capability of its generating units and (ii) the Reactive Power capability of its synchronous condenser units. | MEDIUM | Effective | 2016-07-01 |  | TO, GO
MOD-025-2 | Verification and Data Reporting of Generator Real and Reactive Power Capability and Synchronous Condenser Reactive Power Capability | R2.2. | Submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner within 90 calendar days of either (i) the date the data is recorded for a staged test; or (ii) the date the data is selected for verification using historical operational data. | MEDIUM | Effective | 2016-07-01 |  | TO, GO
MOD-025-2 | Verification and Data Reporting of Generator Real and Reactive Power Capability and Synchronous Condenser Reactive Power Capability | R3. | Each Transmission Owner shall provide its Transmission Planner with verification of the Reactive Power capability of its applicable Facilities as follows: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2016-07-01 |  | TO, GO
MOD-025-2 | Verification and Data Reporting of Generator Real and Reactive Power Capability and Synchronous Condenser Reactive Power Capability | R3.1. | Verify, in accordance with Attachment 1, the Reactive Power capability of its synchronous condenser units. | MEDIUM | Effective | 2016-07-01 |  | TO, GO
MOD-025-2 | Verification and Data Reporting of Generator Real and Reactive Power Capability and Synchronous Condenser Reactive Power Capability | R3.2. | Submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner within 90 calendar days of either (i) the date the data is recorded for a staged test; or (ii) the date the data is selected for verification using historical operational data. | MEDIUM | Effective | 2016-07-01 |  | TO, GO
MOD-026-1 | Verification of Models and Data for Generator Excitation Control System or Plant Volt/Var Control Functions | R1. | Each Transmission Planner shall provide the following requested information to the Generator Owner within 90 calendar days of receiving a written request : [Violation Risk Factor: Lower] [Time Horizon: Operations Planning]  Instructions on how to obtain the list of excitation control system or plant volt/var control function models that are acceptable to the Transmission Planner for use in dynamic simulation,  Instructions on how to obtain the dynamic excitation control system or plant volt/var control function model library block diagrams and/or data sheets for models that are acceptable to the Transmission Planner, or  Model data for any of the Generator Owner’s existing applicable unit specific excitation control system or plant volt/var control function contained in the Transmission Planner’s dynamic database from the current (in-use) models, including generator MVA base. | LOWER | Effective | 2014-07-01 |  | TP
MOD-026-1 | Verification of Models and Data for Generator Excitation Control System or Plant Volt/Var Control Functions | R2. | Each Generator Owner shall provide for each applicable unit, a verified generator excitation control system or plant volt/var control function model, including documentation and data (as specified in Part 2.1) to its Transmission Planner in accordance with the periodicity specified in MOD-026 Attachment 1. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2018-07-01 |  | GO
MOD-026-1 | Verification of Models and Data for Generator Excitation Control System or Plant Volt/Var Control Functions | R2.1. | Each applicable unit’s model shall be verified by the Generator Owner using one or more models acceptable to the Transmission Planner. Verification for individual units less than 20 MVA (gross nameplate rating) in a generating plant (per Section 4.2.1.2, 4.2.2.2, or 4.2.3.2) may be performed using either individual unit or aggregate unit model(s), or both. Each verification shall include the following | MEDIUM | Effective | 2018-07-01 |  | GO
MOD-026-1 | Verification of Models and Data for Generator Excitation Control System or Plant Volt/Var Control Functions | R2.1.1. | Documentation demonstrating the applicable unit’s model response matches the recorded response for a voltage excursion from either a staged test or a measured system disturbance, | MEDIUM | Effective | 2018-07-01 |  | GO
MOD-026-1 | Verification of Models and Data for Generator Excitation Control System or Plant Volt/Var Control Functions | R2.1.2. | Manufacturer, model number (if available), and type of the excitation control system including, but not limited to static, AC brushless, DC rotating, and/or the plant volt/var control function (if installed), | MEDIUM | Effective | 2018-07-01 |  | GO
MOD-026-1 | Verification of Models and Data for Generator Excitation Control System or Plant Volt/Var Control Functions | R2.1.3. | Model structure and data including, but not limited to reactance, time constants, saturation factors, total rotational inertia, or equivalent data for the generator, | MEDIUM | Effective | 2018-07-01 |  | GO
MOD-026-1 | Verification of Models and Data for Generator Excitation Control System or Plant Volt/Var Control Functions | R2.1.4. | Model structure and data for the excitation control system, including the closed loop voltage regulator if a closed loop voltage regulator is installed or the model structure and data for the plant volt/var control function system, | MEDIUM | Effective | 2018-07-01 |  | GO
MOD-026-1 | Verification of Models and Data for Generator Excitation Control System or Plant Volt/Var Control Functions | R2.1.5. | Compensation settings (such as droop, line drop, differential compensation), if used, and | MEDIUM | Effective | 2018-07-01 |  | GO
MOD-026-1 | Verification of Models and Data for Generator Excitation Control System or Plant Volt/Var Control Functions | R2.1.6. | Model structure and data for power system stabilizer, if so equipped. | MEDIUM | Effective | 2018-07-01 |  | GO
MOD-026-1 | Verification of Models and Data for Generator Excitation Control System or Plant Volt/Var Control Functions | R3. | Each Generator Owner shall provide a written response to its Transmission Planner within 90 calendar days of receiving one of the following items for an applicable unit:  Written notification from its Transmission Planner (in accordance with Requirement R6) that the excitation control system or plant volt/var control function model is not usable,  Written comments from its Transmission Planner identifying technical concerns with the verification documentation related to the excitation control system or plant volt/var control function model, or  Written comments and supporting evidence from its Transmission Planner indicating that the simulated excitation control system or plant volt/var control function model response did not match the recorded response to a transmission system event. The written response shall contain either the technical basis for maintaining the current model, the model changes, or a plan to perform model verification3 (in accordance with Requirement R2). [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Effective | 2014-07-01 |  | GO
MOD-026-1 | Verification of Models and Data for Generator Excitation Control System or Plant Volt/Var Control Functions | R4. | Each Generator Owner shall provide revised model data or plans to perform model verification4 (in accordance with Requirement R2) for an applicable unit to its Transmission Planner within 180 calendar days of making changes to the excitation control system or plant volt/var control function that alter the equipment response characteristic.5 [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Effective | 2014-07-01 |  | GO
MOD-026-1 | Verification of Models and Data for Generator Excitation Control System or Plant Volt/Var Control Functions | R5. | Each Generator Owner shall provide a written response to its Transmission Planner, within 90 calendar days following receipt of a technically justified6 unit request from the Transmission Planner to perform a model review of a unit or plant that includes one of the following: [Violation Risk Factor: Lower] [Time Horizon: Operations Planning]  Details of plans to verify the model (in accordance with Requirement R2), or  Corrected model data including the source of revised model data such as discovery of manufacturer test values to replace generic model data or updating of data parameters based on an on-site review of the equipment. | LOWER | Effective | 2014-07-01 |  | GO
MOD-026-1 | Verification of Models and Data for Generator Excitation Control System or Plant Volt/Var Control Functions | R6. | Each Transmission Planner shall provide a written response to the Generator Owner within 90 calendar days of receiving the verified excitation control system or plant volt/var control function model information in accordance with Requirement R2 that the model is usable (meets the criteria specified in Parts 6.1 through 6.3) or is not usable. | MEDIUM | Effective | 2014-07-01 |  | TP
MOD-026-1 | Verification of Models and Data for Generator Excitation Control System or Plant Volt/Var Control Functions | R6.1. | The excitation control system or plant volt/var control function model initializes to compute Real-Time Applications data without error, | MEDIUM | Effective | 2014-07-01 |  | TP
MOD-026-1 | Verification of Models and Data for Generator Excitation Control System or Plant Volt/Var Control Functions | R6.1. | The excitation control system or plant volt/var control function model initializes to compute Real-Time Applications data without error, | MEDIUM | Effective | 2014-07-01 |  | TP
MOD-026-1 | Verification of Models and Data for Generator Excitation Control System or Plant Volt/Var Control Functions | R6.2. | A no-disturbance simulation results in negligible transients, and | MEDIUM | Effective | 2014-07-01 |  | TP
MOD-026-1 | Verification of Models and Data for Generator Excitation Control System or Plant Volt/Var Control Functions | R6.2. | A no-disturbance simulation results in negligible transients, and | MEDIUM | Effective | 2014-07-01 |  | TP
MOD-026-1 | Verification of Models and Data for Generator Excitation Control System or Plant Volt/Var Control Functions | R6.3. | For an otherwise stable simulation, a disturbance simulation results in the excitation control and plant volt/var control function model exhibiting positive damping. If the model is not usable, the Transmission Planner shall provide a technical description of why the model is not usable. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Effective | 2014-07-01 |  | TP
MOD-026-1 | Verification of Models and Data for Generator Excitation Control System or Plant Volt/Var Control Functions | R6.3. | For an otherwise stable simulation, a disturbance simulation results in the excitation control and plant volt/var control function model exhibiting positive damping. If the model is not usable, the Transmission Planner shall provide a technical description of why the model is not usable. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Effective | 2014-07-01 |  | TP
MOD-027-1 | Verification of Models and Data for Turbine/Governor and Load Control or Active Power/Frequency Control Functions | R1. | Each Transmission Planner shall provide the following requested information to the Generator Owner within 90 calendar days of receiving a written request: [Violation Risk Factor: Lower] [Time Horizon: Operations Planning]  Instructions on how to obtain the list of turbine/governor and load control or active power/frequency control system models that are acceptable to the Transmission Planner for use in dynamic simulation,  Instructions on how to obtain the dynamic turbine/governor and load control or active power/frequency control function model library block diagrams and/or data sheets for models that are acceptable to the Transmission Planner, or  Model data for any of the Generator Owner’s existing applicable unit specific turbine/governor and load control or active power/frequency control system contained in the Transmission Planner’s dynamic database from the current (in-use) models. | LOWER | Effective | 2014-07-01 |  | TP
MOD-027-1 | Verification of Models and Data for Turbine/Governor and Load Control or Active Power/Frequency Control Functions | R2. | Each Generator Owner shall provide, for each applicable unit, a verified turbine/governor and load control or active power/frequency control model, including documentation and data (as specified in Part 2.1) to its Transmission Planner in accordance with the periodicity specified in MOD-027 Attachment 1. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2018-07-01 |  | GO
MOD-027-1 | Verification of Models and Data for Turbine/Governor and Load Control or Active Power/Frequency Control Functions | R2.1. | Each applicable unit’s model shall be verified by the Generator Owner using one or more models acceptable to the Transmission Planner. Verification for individual units rated less than 20 MVA (gross nameplate rating) in a generating plant (per Section 4.2.1.2, 4.2.2.2, or 4.2.3.2) may be performed using either individual unit or aggregate unit model(s) or both. Each verification shall include the following: | MEDIUM | Effective | 2018-07-01 |  | GO
MOD-027-1 | Verification of Models and Data for Turbine/Governor and Load Control or Active Power/Frequency Control Functions | R2.1.1. | Documentation comparing the applicable unit’s MW model response to the recorded MW response for either:  A frequency excursion from a system disturbance that meets MOD-027 Attachment 1 Note 1 with the applicable unit on-line,  A speed governor reference change with the applicable unit online, or  A partial load rejection test,2 | MEDIUM | Effective | 2018-07-01 |  | GO
MOD-027-1 | Verification of Models and Data for Turbine/Governor and Load Control or Active Power/Frequency Control Functions | R2.1.2. | Type of governor and load control or active power control/frequency control1 equipment, | MEDIUM | Effective | 2018-07-01 |  | GO
MOD-027-1 | Verification of Models and Data for Turbine/Governor and Load Control or Active Power/Frequency Control Functions | R2.1.3. | A description of the turbine (e.g. for hydro turbine - Kaplan, Francis, or Pelton; for steam turbine - boiler type, normal fuel type, and turbine type; for gas turbine - the type and manufacturer; for variable energy plant - type and manufacturer), | MEDIUM | Effective | 2018-07-01 |  | GO
MOD-027-1 | Verification of Models and Data for Turbine/Governor and Load Control or Active Power/Frequency Control Functions | R2.1.4. | Model structure and data for turbine/governor and load control or active power/frequency control, and | MEDIUM | Effective | 2018-07-01 |  | GO
MOD-027-1 | Verification of Models and Data for Turbine/Governor and Load Control or Active Power/Frequency Control Functions | R2.1.5. | Representation of the real power response effects of outer loop controls (such as operator set point controls, and load control but excluding AGC control) that would override the governor response (including blocked or nonfunctioning governors or modes of operation that limit Frequency Response), if applicable. | MEDIUM | Effective | 2018-07-01 |  | GO
MOD-027-1 | Verification of Models and Data for Turbine/Governor and Load Control or Active Power/Frequency Control Functions | R3. | Each Generator Owner shall provide a written response to its Transmission Planner within 90 calendar days of receiving one of the following items for an applicable unit.  Written notification, from its Transmission Planner (in accordance with Requirement R5) that the turbine/governor and load control or active power/frequency control model is not “usable,”  Written comments from its Transmission Planner identifying technical concerns with the verification documentation related to the turbine/governor and load control or active power/frequency control model, or  Written comments and supporting evidence from its Transmission Planner indicating that the simulated turbine/governor and load control or active power/frequency control response did not approximate the recorded response for three or more transmission system events. The written response shall contain either the technical basis for maintaining the current model, the model changes, or a plan to perform model verification3 (in accordance with Requirement R2). [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Effective | 2014-07-01 |  | GO
MOD-027-1 | Verification of Models and Data for Turbine/Governor and Load Control or Active Power/Frequency Control Functions | R4. | Each Generator Owner shall provide revised model data or plans to perform model verification4 (in accordance with Requirement R2) for an applicable unit to its Transmission Planner within 180 calendar days of making changes to the turbine/governor and load control or active power/frequency control system that alter the equipment response characteristic5. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Effective | 2014-07-01 |  | GO
MOD-027-1 | Verification of Models and Data for Turbine/Governor and Load Control or Active Power/Frequency Control Functions | R5. | Each Transmission Planner shall provide a written response to the Generator Owner within 90 calendar days of receiving the turbine/governor and load control or active power/frequency control system verified model information in accordance with Requirement R2 that the model is usable (meets the criteria specified in Parts 5.1 through 5.3) or is not usable. | MEDIUM | Effective | 2014-07-01 |  | TP
MOD-027-1 | Verification of Models and Data for Turbine/Governor and Load Control or Active Power/Frequency Control Functions | R5.1. | The turbine/governor and load control or active power/frequency control function model initializes to compute Real-Time Applications data without error, | MEDIUM | Effective | 2014-07-01 |  | TP
MOD-027-1 | Verification of Models and Data for Turbine/Governor and Load Control or Active Power/Frequency Control Functions | R5.2. | A no-disturbance simulation results in negligible transients, and | MEDIUM | Effective | 2014-07-01 |  | TP
MOD-027-1 | Verification of Models and Data for Turbine/Governor and Load Control or Active Power/Frequency Control Functions | R5.3. | For an otherwise stable simulation, a disturbance simulation results in the turbine/governor and load control or active power/frequency control model exhibiting positive damping. If the model is not usable, the Transmission Planner shall provide a technical description of why the model is not usable. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Effective | 2014-07-01 |  | TP
MOD-028-2 | Area Interchange Methodology | R1. | Each Transmission Service Provider shall include in its Available Transfer Capability Implementation Document (ATCID), at a minimum, the following information relative to its methodology for determining Total Transfer Capability (TTC): [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Effective | 2013-10-01 |  | TSP
MOD-028-2 | Area Interchange Methodology | R1.1. | Information describing how the selected methodology has been implemented, in such detail that, given the same information used by the Transmission Operator, the results of the TTC calculations can be validated. | No Individual VRF Assigned | Effective | 2013-10-01 |  | TSP
MOD-028-2 | Area Interchange Methodology | R1.2. | A description of the manner in which the Transmission Operator will account for Interchange Schedules in the calculation of TTC. | No Individual VRF Assigned | Effective | 2013-10-01 |  | TSP
MOD-028-2 | Area Interchange Methodology | R1.3. | Any contractual obligations for allocation of TTC. | No Individual VRF Assigned | Effective | 2013-10-01 |  | TSP
MOD-028-2 | Area Interchange Methodology | R1.4. | A description of the manner in which Contingencies are identified for use in the TTC process. | No Individual VRF Assigned | Effective | 2013-10-01 |  | TSP
MOD-028-2 | Area Interchange Methodology | R1.5. | The following information on how source and sink for transmission service is accounted for in ATC calculations including: | No Individual VRF Assigned | Effective | 2013-10-01 |  | TSP
MOD-028-2 | Area Interchange Methodology | R1.5.1. | Define if the source used for Available Transfer Capability (ATC) calculations is obtained from the source field or the Point of Receipt (POR) field of the transmission reservation | No Individual VRF Assigned | Effective | 2013-10-01 |  | TSP
MOD-028-2 | Area Interchange Methodology | R1.5.2. | Define if the sink used for ATC calculations is obtained from the sink field or the Point of Delivery (POD) field of the transmission reservation | No Individual VRF Assigned | Effective | 2013-10-01 |  | TSP
MOD-028-2 | Area Interchange Methodology | R1.5.3. | The source/sink or POR/POD identification and mapping to the model. | No Individual VRF Assigned | Effective | 2013-10-01 |  | TSP
MOD-028-2 | Area Interchange Methodology | R1.5.4. | If the Transmission Service Provider’s ATC calculation process involves a grouping of generation, the ATCID must identify how these generators participate in the group. | No Individual VRF Assigned | Effective | 2013-10-01 |  | TSP
MOD-028-2 | Area Interchange Methodology | R10. | When calculating firm ATC for an ATC Path for a specified period, the Transmission Service Provider shall utilize the following algorithm: [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] See Standard for Formula | LOWER | Effective | 2013-10-01 |  | TSP
MOD-028-2 | Area Interchange Methodology | R11. | When calculating non-firm ATC for a ATC Path for a specified period, the Transmission Service Provider shall use the following algorithm: [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] See Standard for Formula | LOWER | Effective | 2013-10-01 |  | TSP
MOD-028-2 | Area Interchange Methodology | R2. | When calculating TTC for ATC Paths, the Transmission Operator shall use a Transmission model that contains all of the following: [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Effective | 2013-10-01 |  | TOP
MOD-028-2 | Area Interchange Methodology | R2.1. | Modeling data and topology of its Reliability Coordinator’s area of responsibility. Equivalent representation of radial lines and facilities 161 kV or below is allowed. | No Individual VRF Assigned | Effective | 2013-10-01 |  | TOP
MOD-028-2 | Area Interchange Methodology | R2.2. | Modeling data and topology (or equivalent representation) for immediately adjacent and beyond Reliability Coordination areas. | No Individual VRF Assigned | Effective | 2013-10-01 |  | TOP
MOD-028-2 | Area Interchange Methodology | R2.3. | Facility Ratings specified by the Generator Owners and Transmission Owners. | No Individual VRF Assigned | Effective | 2013-10-01 |  | TOP
MOD-028-2 | Area Interchange Methodology | R3. | When calculating TTCs for ATC Paths, the Transmission Operator shall include the following data for the Transmission Service Provider’s area. The Transmission Operator shall also include the following data associated with Facilities that are explicitly represented in the Transmission model, as provided by adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed: [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Effective | 2013-10-01 |  | TOP
MOD-028-2 | Area Interchange Methodology | R3.1. | For TTCs, use the following (as well as any other values and additional parameters as specified in the ATCID): | No Individual VRF Assigned | Effective | 2013-10-01 |  | TOP
MOD-028-2 | Area Interchange Methodology | R3.1.1. | Expected generation and Transmission outages, additions, and retirements, included as specified in the ATCID. | No Individual VRF Assigned | Effective | 2013-10-01 |  | TOP
MOD-028-2 | Area Interchange Methodology | R3.1.2. | A daily or hourly load forecast for TTCs used in current-day and next-day ATC calculations. | No Individual VRF Assigned | Effective | 2013-10-01 |  | TOP
MOD-028-2 | Area Interchange Methodology | R3.1.3. | A daily load forecast for TTCs used in ATC calculations for days two through 31. | No Individual VRF Assigned | Effective | 2013-10-01 |  | TOP
MOD-028-2 | Area Interchange Methodology | R3.1.4. | A monthly load forecast for TTCs used in ATC calculations for months two through 13 months TTCs. | No Individual VRF Assigned | Effective | 2013-10-01 |  | TOP
MOD-028-2 | Area Interchange Methodology | R3.1.5. | Unit commitment and dispatch order, to include all designated network resources and other resources that are committed or have the legal obligation to run, (within or out of economic dispatch) as they are expected to run. | No Individual VRF Assigned | Effective | 2013-10-01 |  | TOP
MOD-028-2 | Area Interchange Methodology | R4. | When calculating TTCs for ATC Paths, the Transmission Operator shall meet all of the following conditions: [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Effective | 2013-10-01 |  | TOP
MOD-028-2 | Area Interchange Methodology | R4.1. | Use all Contingencies meeting the criteria described in the ATCID. | No Individual VRF Assigned | Effective | 2013-10-01 |  | TOP
MOD-028-2 | Area Interchange Methodology | R4.2. | Respect any contractual allocations of TTC. | No Individual VRF Assigned | Effective | 2013-10-01 |  | TOP
MOD-028-2 | Area Interchange Methodology | R4.3. | Include, for each time period, the Firm Transmission Service expected to be scheduled as specified in the ATCID (filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers) for the Transmission Service Provider, all adjacent Transmission Service Providers, and any Transmission Service Providers with which coordination agreements have been executed modeling the source and sink as follows: - If the source, as specified in the ATCID, has been identified in the reservation and it is discretely modeled in the Transmission Service Provider’s Transmission model, use the discretely modeled point as the source. - If the source, as specified in the ATCID, has been identified in the reservation and the point can be mapped to an “equivalence” or “aggregate representation” in the Transmission Service Provider’s Transmission model, use the modeled equivalence or aggregate as the source. - If the source, as specified in the ATCID, has been identified in the reservation and the point cannot be mapped to a discretely modeled point, an “equivalence,” or an “aggregate representation” in the Transmission Service Provider’s Transmission model, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider from which the power is to be received as the source. - If the source, as specified in the ATCID, has not been identified in the reservation, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider from which the power is to be received as the source. - If the sink, as specified in the ATCID, has been identified in the reservation and it is discretely modeled in the Transmission Service Provider’s Transmission model, use the discretely modeled point shall as the sink. - If the sink, as specified in the ATCID, has been identified in the reservation and the point can be mapped to an “equivalence” or “aggregate representation” in the Transmission Service Provider’s Transmission model, use the modeled equivalence or aggregate as the sink. - If the sink, as specified in the ATCID, has been identified in the reservation and the point can not be mapped to a discretely modeled point, an “equivalence,” or an “aggregate representation” in the Transmission Service Provider’s Transmission model, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider to which the power is to be delivered as the sink. - If the sink, as specified in the ATCID, has not been identified in the reservation, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider to which the power is being delivered as the sink. | No Individual VRF Assigned | Effective | 2013-10-01 |  | TOP
MOD-028-2 | Area Interchange Methodology | R5. | Each Transmission Operator shall establish TTC for each ATC Path as defined below: [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Effective | 2013-10-01 |  | TOP
MOD-028-2 | Area Interchange Methodology | R5.1. | At least once within the seven calendar days prior to the specified period for TTCs used in hourly and daily ATC calculations. | No Individual VRF Assigned | Effective | 2013-10-01 |  | TOP
MOD-028-2 | Area Interchange Methodology | R5.2. | At least once per calendar month for TTCs used in monthly ATC calculations. | No Individual VRF Assigned | Effective | 2013-10-01 |  | TOP
MOD-028-2 | Area Interchange Methodology | R5.3. | Within 24 hours of the unexpected outage of a 500 kV or higher transmission Facility or a transformer with a low-side voltage of 200 kV or higher for TTCs in effect during the anticipated duration of the outage, provided such outage is expected to last 24 hours or longer. | No Individual VRF Assigned | Effective | 2013-10-01 |  | TOP
MOD-028-2 | Area Interchange Methodology | R6. | Each Transmission Operator shall establish TTC for each ATC Path using the following process: [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Effective | 2013-10-01 |  | TOP
MOD-028-2 | Area Interchange Methodology | R6.1. | Determine the incremental Transfer Capability for each ATC Path by increasing generation and/or decreasing load within the source Balancing Authority area and decreasing generation and/or increasing load within the sink Balancing Authority area until either: - A System Operating Limit is reached on the Transmission Service Provider’s system, or - A SOL is reached on any other adjacent system in the Transmission model that is not on the study path and the distribution factor is 5% or greater1. | No Individual VRF Assigned | Effective | 2013-10-01 |  | TOP
MOD-028-2 | Area Interchange Methodology | R6.2. | If the limit in step R6.1 can not be reached by adjusting any combination of load or generation, then set the incremental Transfer Capability by the results of the case where the maximum adjustments were applied. | No Individual VRF Assigned | Effective | 2013-10-01 |  | TOP
MOD-028-2 | Area Interchange Methodology | R6.3. | Use (as the TTC) the lesser of: − The sum of the incremental Transfer Capability and the impacts of Firm Transmission Services, as specified in the Transmission Service Provider’s ATCID, that were included in the study model, or − The sum of Facility Ratings of all ties comprising the ATC Path. | No Individual VRF Assigned | Effective | 2013-10-01 |  | TOP
MOD-028-2 | Area Interchange Methodology | R6.4. | For ATC Paths whose capacity uses jointly-owned or allocated Facilities, limit TTC for each Transmission Service Provider so the TTC does not exceed each Transmission Service Provider’s contractual rights. | No Individual VRF Assigned | Effective | 2013-10-01 |  | TOP
MOD-028-2 | Area Interchange Methodology | R7. | The Transmission Operator shall provide the Transmission Service Provider of that ATC Path with the most current value for TTC for that ATC Path no more than: [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Effective | 2013-10-01 |  | TOP
MOD-028-2 | Area Interchange Methodology | R7.1. | One calendar day after its determination for TTCs used in hourly and daily ATC calculations. | No Individual VRF Assigned | Effective | 2013-10-01 |  | TOP
MOD-028-2 | Area Interchange Methodology | R7.2. | Seven calendar days after its determination for TTCs used in monthly ATC calculations. | No Individual VRF Assigned | Effective | 2013-10-01 |  | TOP
MOD-028-2 | Area Interchange Methodology | R8. | When calculating Existing Transmission Commitments (ETCs) for firm commitments (ETCF) for all time periods for an ATC Path the Transmission Service Provider shall use the following algorithm: [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] See Standard for Formula | LOWER | Effective | 2013-10-01 |  | TSP
MOD-028-2 | Area Interchange Methodology | R9. | When calculating ETC for non-firm commitments (ETCNF) for all time periods for an ATC Path the Transmission Service Provider shall use the following algorithm: [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] See Standard for Formula | LOWER | Effective | 2013-10-01 |  | TSP
MOD-029-1a | Rated System Path Methodology | R1. | When calculating TTCs for ATC Paths, the Transmission Operator shall use a Transmission model which satisfies the following requirements: [Time Horizon: Operations Planning] | MEDIUM | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R1. | When calculating TTCs for ATC Paths, the Transmission Operator shall use a Transmission model which satisfies the following requirements: [Time Horizon: Operations Planning] | MEDIUM | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R1.1. | The model utilizes data and assumptions consistent with the time period being studied and that meets the following criteria: | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R1.1. | The model utilizes data and assumptions consistent with the time period being studied and that meets the following criteria: | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R1.1.1. | Includes at least: | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R1.1.1. | Includes at least: | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R1.1.1.1. | The Transmission Operator area. Equivalent representation of radial lines and facilities 161kV or below is allowed. | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R1.1.1.1. | The Transmission Operator area. Equivalent representation of radial lines and facilities 161kV or below is allowed. | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R1.1.1.2. | All Transmission Operator areas contiguous with its own Transmission Operator area. (Equivalent representation is allowed.) | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R1.1.1.2. | All Transmission Operator areas contiguous with its own Transmission Operator area. (Equivalent representation is allowed.) | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R1.1.1.3. | Any other Transmission Operator area linked to the Transmission Operator’s area by joint operating agreement. (Equivalent representation is allowed.) | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R1.1.1.3. | Any other Transmission Operator area linked to the Transmission Operator’s area by joint operating agreement. (Equivalent representation is allowed.) | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R1.1.10. | Includes any other modeling requirements or criteria specified in the ATCID. | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R1.1.10. | Includes any other modeling requirements or criteria specified in the ATCID. | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R1.1.2. | Models all system Elements as in-service for the assumed initial conditions. | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R1.1.2. | Models all system Elements as in-service for the assumed initial conditions. | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R1.1.3. | Models all generation (may be either a single generator or multiple generators) that is greater than 20 MVA at the point of interconnection in the studied area. | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R1.1.3. | Models all generation (may be either a single generator or multiple generators) that is greater than 20 MVA at the point of interconnection in the studied area. | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R1.1.4. | Models phase shifters in non-regulating mode, unless otherwise specified in the Available Transfer Capability Implementation Document (ATCID). | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R1.1.4. | Models phase shifters in non-regulating mode, unless otherwise specified in the Available Transfer Capability Implementation Document (ATCID). | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R1.1.5. | Uses Load forecast by Balancing Authority. | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R1.1.5. | Uses Load forecast by Balancing Authority. | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R1.1.6. | Uses Transmission Facility additions and retirements. | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R1.1.6. | Uses Transmission Facility additions and retirements. | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R1.1.7. | Uses Generation Facility additions and retirements. | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R1.1.7. | Uses Generation Facility additions and retirements. | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R1.1.8. | Uses Special Protection System (SPS) models where currently existing or projected for implementation within the studied time horizon. | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R1.1.8. | Uses Special Protection System (SPS) models where currently existing or projected for implementation within the studied time horizon. | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R1.1.9. | Models series compensation for each line at the expected operating level unless specified otherwise in the ATCID. | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R1.1.9. | Models series compensation for each line at the expected operating level unless specified otherwise in the ATCID. | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R1.2. | Uses Facility Ratings as provided by the Transmission Owner and Generator Owner | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R1.2. | Uses Facility Ratings as provided by the Transmission Owner and Generator Owner | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R2. | The Transmission Operator shall use the following process to determine TTC: [Time Horizon: Operations Planning] | MEDIUM | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R2. | The Transmission Operator shall use the following process to determine TTC: [Time Horizon: Operations Planning] | MEDIUM | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R2.1. | Except where otherwise specified within MOD-029-1, adjust base case generation and Load levels within the updated power flow model to determine the TTC (maximum flow or reliability limit) that can be simulated on the ATC Path while at the same time satisfying all planning criteria contingencies as follows: | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R2.1. | Except where otherwise specified within MOD-029-1, adjust base case generation and Load levels within the updated power flow model to determine the TTC (maximum flow or reliability limit) that can be simulated on the ATC Path while at the same time satisfying all planning criteria contingencies as follows: | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R2.1.1. | When modeling normal conditions, all Transmission Elements will be modeled at or below 100% of their continuous rating. | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R2.1.1. | When modeling normal conditions, all Transmission Elements will be modeled at or below 100% of their continuous rating. | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R2.1.2. | When modeling contingencies the system shall demonstrate transient, dynamic and voltage stability, with no Transmission Element modeled above its Emergency Rating. | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R2.1.2. | When modeling contingencies the system shall demonstrate transient, dynamic and voltage stability, with no Transmission Element modeled above its Emergency Rating. | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R2.1.3. | Uncontrolled separation shall not occur. | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R2.1.3. | Uncontrolled separation shall not occur. | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R2.2. | Where it is impossible to actually simulate a reliability-limited flow in a direction counter to prevailing flows (on an alternating current Transmission line), set the TTC for the non-prevailing direction equal to the TTC in the prevailing direction. If the TTC in the prevailing flow direction is dependant on a Special Protection System (SPS), set the TTC for the non-prevailing flow direction equal to the greater of the maximum flow that can be simulated in the non-prevailing flow direction or the maximum TTC that can be achieved in the prevailing flow direction without use of a SPS. | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R2.2. | Where it is impossible to actually simulate a reliability-limited flow in a direction counter to prevailing flows (on an alternating current Transmission line), set the TTC for the non-prevailing direction equal to the TTC in the prevailing direction. If the TTC in the prevailing flow direction is dependant on a Special Protection System (SPS), set the TTC for the non-prevailing flow direction equal to the greater of the maximum flow that can be simulated in the non-prevailing flow direction or the maximum TTC that can be achieved in the prevailing flow direction without use of a SPS. | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R2.3. | For an ATC Path whose capacity is limited by contract, set TTC on the ATC Path at the lesser of the maximum allowable contract capacity or the reliability limit as determined by R2.1. | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R2.3. | For an ATC Path whose capacity is limited by contract, set TTC on the ATC Path at the lesser of the maximum allowable contract capacity or the reliability limit as determined by R2.1. | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R2.4. | For an ATC Path whose TTC varies due to simultaneous interaction with one or more other paths, develop a nomogram describing the interaction of the paths and the resulting TTC under specified conditions. | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R2.4. | For an ATC Path whose TTC varies due to simultaneous interaction with one or more other paths, develop a nomogram describing the interaction of the paths and the resulting TTC under specified conditions. | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R2.5. | The Transmission Operator shall identify when the TTC for the ATC Path being studied has an adverse impact on the TTC value of any existing path. Do this by modeling the flow on the path being studied at its proposed new TTC level simultaneous with the flow on the existing path at its TTC level while at the same time honoring the reliability criteria outlined in R2.1. The Transmission Operator shall include the resolution of this adverse impact in its study report for the ATC Path. | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R2.5. | The Transmission Operator shall identify when the TTC for the ATC Path being studied has an adverse impact on the TTC value of any existing path. Do this by modeling the flow on the path being studied at its proposed new TTC level simultaneous with the flow on the existing path at its TTC level while at the same time honoring the reliability criteria outlined in R2.1. The Transmission Operator shall include the resolution of this adverse impact in its study report for the ATC Path. | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R2.6. | Where multiple ownership of Transmission rights exists on an ATC Path, allocate TTC of that ATC Path in accordance with the contractual agreement made by the multiple owners of that ATC Path. | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R2.6. | Where multiple ownership of Transmission rights exists on an ATC Path, allocate TTC of that ATC Path in accordance with the contractual agreement made by the multiple owners of that ATC Path. | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R2.7. | For ATC Paths whose path rating, adjusted for seasonal variance, was established, known and used in operation since January 1, 1994, and no action has been taken to have the path rated using a different method, set the TTC at that previously established amount. | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R2.7. | For ATC Paths whose path rating, adjusted for seasonal variance, was established, known and used in operation since January 1, 1994, and no action has been taken to have the path rated using a different method, set the TTC at that previously established amount. | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R2.8. | Create a study report that describes the steps above that were undertaken (R2.1 - R2.7), including the contingencies and assumptions used, when determining the TTC and the results of the study. Where three phase fault damping is used to determine stability limits, that report shall also identify the percent used and include justification for use unless specified otherwise in the ATCID. | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R2.8. | Create a study report that describes the steps above that were undertaken (R2.1 - R2.7), including the contingencies and assumptions used, when determining the TTC and the results of the study. Where three phase fault damping is used to determine stability limits, that report shall also identify the percent used and include justification for use unless specified otherwise in the ATCID. | No Individual VRF Assigned | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R3. | Each Transmission Operator shall establish the TTC at the lesser of the value calculated in R2 or any System Operating Limit (SOL) for that ATC Path. [Time Horizon: Operations Planning] | MEDIUM | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R3. | Each Transmission Operator shall establish the TTC at the lesser of the value calculated in R2 or any System Operating Limit (SOL) for that ATC Path. [Time Horizon: Operations Planning] | MEDIUM | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R4. | Within seven calendar days of the finalization of the study report, the Transmission Operator shall make available to the Transmission Service Provider of the ATC Path, the most current value for TTC and the TTC study report documenting the assumptions used and steps taken in determining the current value for TTC for that ATC Path. [Time Horizon: Operations Planning] | MEDIUM | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R4. | Within seven calendar days of the finalization of the study report, the Transmission Operator shall make available to the Transmission Service Provider of the ATC Path, the most current value for TTC and the TTC study report documenting the assumptions used and steps taken in determining the current value for TTC for that ATC Path. [Time Horizon: Operations Planning] | MEDIUM | Retired | 2010-04-18 | 2017-03-31 | TOP
MOD-029-1a | Rated System Path Methodology | R5. | When calculating ETC for firm Existing Transmission Commitments (ETCF) for a specified period for an ATC Path, the Transmission Service Provider shall use the algorithm below: [Time Horizon: Operations Planning] See Standard for Formula | MEDIUM | Retired | 2010-04-18 | 2017-03-31 | TSP
MOD-029-1a | Rated System Path Methodology | R6. | When calculating ETC for non-firm Existing Transmission Commitments (ETCNF) for all time horizons for an ATC Path the Transmission Service Provider shall use the following algorithm: [Time Horizon: Operations Planning] See Standard for Formula | LOWER | Retired | 2010-04-18 | 2017-03-31 | TSP
MOD-029-1a | Rated System Path Methodology | R7. | When calculating firm ATC for an ATC Path for a specified period, the Transmission Service Provider shall use the following algorithm: [Time Horizon: Operations Planning] See Standard for Formula | MEDIUM | Retired | 2010-04-18 | 2017-03-31 | TSP
MOD-029-1a | Rated System Path Methodology | R8. | When calculating non-firm ATC for an ATC Path for a specified period, the Transmission Service Provider shall use the following algorithm:[Time Horizon: Operations Planning] See Standard for Formula | LOWER | Retired | 2010-04-18 | 2017-03-31 | TSP
MOD-029-2a | Rated System Path Methodology | R1. | When calculating TTCs for ATC Paths, the Transmission Operator shall use a Transmission model which satisfies the following requirements: [Time Horizon: Operations Planning] | MEDIUM | Effective | 2017-04-01 |  | TOP
MOD-029-2a | Rated System Path Methodology | R1. | When calculating TTCs for ATC Paths, the Transmission Operator shall use a Transmission model which satisfies the following requirements: [Time Horizon: Operations Planning] | MEDIUM | Effective | 2017-04-01 |  | TOP
MOD-029-2a | Rated System Path Methodology | R1.1. | The model utilizes data and assumptions consistent with the time period being studied and that meets the following criteria: | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-029-2a | Rated System Path Methodology | R1.1. | The model utilizes data and assumptions consistent with the time period being studied and that meets the following criteria: | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-029-2a | Rated System Path Methodology | R1.1.1. | Includes at least: | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-029-2a | Rated System Path Methodology | R1.1.1. | Includes at least: | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-029-2a | Rated System Path Methodology | R1.1.1.1. | The Transmission Operator area. Equivalent representation of radial lines and facilities 161kV or below is allowed. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-029-2a | Rated System Path Methodology | R1.1.1.1. | The Transmission Operator area. Equivalent representation of radial lines and facilities 161kV or below is allowed. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-029-2a | Rated System Path Methodology | R1.1.1.2. | All Transmission Operator areas contiguous with its own Transmission Operator area. (Equivalent representation is allowed.) | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-029-2a | Rated System Path Methodology | R1.1.1.2. | All Transmission Operator areas contiguous with its own Transmission Operator area. (Equivalent representation is allowed.) | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-029-2a | Rated System Path Methodology | R1.1.1.3. | Any other Transmission Operator area linked to the Transmission Operator’s area by joint operating agreement. (Equivalent representation is allowed.) | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-029-2a | Rated System Path Methodology | R1.1.1.3. | Any other Transmission Operator area linked to the Transmission Operator’s area by joint operating agreement. (Equivalent representation is allowed.) | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-029-2a | Rated System Path Methodology | R1.1.10. | Includes any other modeling requirements or criteria specified in the ATCID. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-029-2a | Rated System Path Methodology | R1.1.10. | Includes any other modeling requirements or criteria specified in the ATCID. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-029-2a | Rated System Path Methodology | R1.1.2. | Models all system Elements as in-service for the assumed initial conditions. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-029-2a | Rated System Path Methodology | R1.1.2. | Models all system Elements as in-service for the assumed initial conditions. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-029-2a | Rated System Path Methodology | R1.1.3. | Models all generation (may be either a single generator or multiple generators) that is greater than 20 MVA at the point of interconnection in the studied area. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-029-2a | Rated System Path Methodology | R1.1.3. | Models all generation (may be either a single generator or multiple generators) that is greater than 20 MVA at the point of interconnection in the studied area. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-029-2a | Rated System Path Methodology | R1.1.4. | Models phase shifters in non-regulating mode, unless otherwise specified in the Available Transfer Capability Implementation Document (ATCID). | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-029-2a | Rated System Path Methodology | R1.1.4. | Models phase shifters in non-regulating mode, unless otherwise specified in the Available Transfer Capability Implementation Document (ATCID). | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-029-2a | Rated System Path Methodology | R1.1.5. | Uses Load forecast by Balancing Authority. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-029-2a | Rated System Path Methodology | R1.1.5. | Uses Load forecast by Balancing Authority. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-029-2a | Rated System Path Methodology | R1.1.6. | Uses Transmission Facility additions and retirements. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-029-2a | Rated System Path Methodology | R1.1.6. | Uses Transmission Facility additions and retirements. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-029-2a | Rated System Path Methodology | R1.1.7. | Uses Generation Facility additions and retirements. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-029-2a | Rated System Path Methodology | R1.1.7. | Uses Generation Facility additions and retirements. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-029-2a | Rated System Path Methodology | R1.1.8. | Uses Remedial Action Scheme (RAS) models where currently existing or projected for implementation within the studied time horizon. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-029-2a | Rated System Path Methodology | R1.1.8. | Uses Remedial Action Scheme (RAS) models where currently existing or projected for implementation within the studied time horizon. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-029-2a | Rated System Path Methodology | R1.1.9. | Models series compensation for each line at the expected operating level unless specified otherwise in the ATCID. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-029-2a | Rated System Path Methodology | R1.1.9. | Models series compensation for each line at the expected operating level unless specified otherwise in the ATCID. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-029-2a | Rated System Path Methodology | R1.2. | Uses Facility Ratings as provided by the Transmission Owner and Generator Owner | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-029-2a | Rated System Path Methodology | R1.2. | Uses Facility Ratings as provided by the Transmission Owner and Generator Owner | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-029-2a | Rated System Path Methodology | R2. | The Transmission Operator shall use the following process to determine TTC: [Time Horizon: Operations Planning] | MEDIUM | Effective | 2017-04-01 |  | TOP
MOD-029-2a | Rated System Path Methodology | R2.1. | Except where otherwise specified within MOD-029-2a, adjust base case generation and Load levels within the updated power flow model to determine the TTC (maximum flow or reliability limit) that can be simulated on the ATC Path while at the same time satisfying all planning criteria contingencies as follows: | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-029-2a | Rated System Path Methodology | R2.1.1. | When modeling normal conditions, all Transmission Elements will be modeled at or below 100% of their continuous rating. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-029-2a | Rated System Path Methodology | R2.1.2. | When modeling contingencies the system shall demonstrate transient, dynamic and voltage stability, with no Transmission Element modeled above its Emergency Rating. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-029-2a | Rated System Path Methodology | R2.1.3. | Uncontrolled separation shall not occur. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-029-2a | Rated System Path Methodology | R2.2. | Where it is impossible to actually simulate a reliability-limited flow in a direction counter to prevailing flows (on an alternating current Transmission line), set the TTC for the non-prevailing direction equal to the TTC in the prevailing direction. If the TTC in the prevailing flow direction is dependent on a Remedial Action Scheme (RAS), set the TTC for the non-prevailing flow direction equal to the greater of the maximum flow that can be simulated in the non-prevailing flow direction or the maximum TTC that can be achieved in the prevailing flow direction without use of a RAS. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-029-2a | Rated System Path Methodology | R2.3. | For an ATC Path whose capacity is limited by contract, set TTC on the ATC Path at the lesser of the maximum allowable contract capacity or the reliability limit as determined by R2.1. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-029-2a | Rated System Path Methodology | R2.4. | For an ATC Path whose TTC varies due to simultaneous interaction with one or more other paths, develop a nomogram describing the interaction of the paths and the resulting TTC under specified conditions. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-029-2a | Rated System Path Methodology | R2.5. | The Transmission Operator shall identify when the TTC for the ATC Path being studied has an adverse impact on the TTC value of any existing path. Do this by modeling the flow on the path being studied at its proposed new TTC level simultaneous with the flow on the existing path at its TTC level while at the same time honoring the reliability criteria outlined in R2.1. The Transmission Operator shall include the resolution of this adverse impact in its study report for the ATC Path. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-029-2a | Rated System Path Methodology | R2.6. | Where multiple ownership of Transmission rights exists on an ATC Path, allocate TTC of that ATC Path in accordance with the contractual agreement made by the multiple owners of that ATC Path. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-029-2a | Rated System Path Methodology | R2.7. | For ATC Paths whose path rating, adjusted for seasonal variance, was established, known and used in operation since January 1, 1994, and no action has been taken to have the path rated using a different method, set the TTC at that previously established amount. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-029-2a | Rated System Path Methodology | R2.8. | Create a study report that describes the steps above that were undertaken (R2.1 - R2.7), including the contingencies and assumptions used, when determining the TTC and the results of the study. Where three phase fault damping is used to determine stability limits, that report shall also identify the percent used and include justification for use unless specified otherwise in the ATCID. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-029-2a | Rated System Path Methodology | R3. | Each Transmission Operator shall establish the TTC at the lesser of the value calculated in R2 or any System Operating Limit (SOL) for that ATC Path. [Time Horizon: Operations Planning] | MEDIUM | Effective | 2017-04-01 |  | TOP
MOD-029-2a | Rated System Path Methodology | R4. | Within seven calendar days of the finalization of the study report, the Transmission Operator shall make available to the Transmission Service Provider of the ATC Path, the most current value for TTC and the TTC study report documenting the assumptions used and steps taken in determining the current value for TTC for that ATC Path. [Time Horizon: Operations Planning] | MEDIUM | Effective | 2017-04-01 |  | TOP
MOD-029-2a | Rated System Path Methodology | R5. | When calculating ETC for firm Existing Transmission Commitments (ETCF) for a specified period for an ATC Path, the Transmission Service Provider shall use the algorithm below: [Time Horizon: Operations Planning] ETCF = NLF + NITSF + GFF + PTPF + RORF + OSF Where: NLF is the firm capacity set aside to serve peak Native Load forecast commitments for the time period being calculated, to include losses, and Native Load growth, not otherwise included in Transmission Reliability Margin or Capacity Benefit Margin. NITSF is the firm capacity reserved for Network Integration Transmission Service serving Load, to include losses, and Load growth, not otherwise included in Transmission Reliability Margin or Capacity Benefit Margin. GFF is the firm capacity set aside for grandfathered Transmission Service and contracts for energy and/or Transmission Service, where executed prior to theeffective date of a Transmission Service Provider’s Open Access Transmission Tariff or “safe harbor tariff.” PTPF is the firm capacity reserved for confirmed Point-to-Point Transmission Service. RORF is the firm capacity reserved for Roll-over rights for contracts granting Transmission Customers the right of first refusal to take or continue to take Transmission Service when the Transmission Customer’s Transmission Service contract expires or is eligible for renewal. OSF is the firm capacity reserved for any other service(s), contract(s), or agreement(s) not specified above using Firm Transmission Service as specified in the ATCID. | MEDIUM | Effective | 2017-04-01 |  | TSP
MOD-029-2a | Rated System Path Methodology | R6. | When calculating ETC for non-firm Existing Transmission Commitments (ETCNF) for all time horizons for an ATC Path the Transmission Service Provider shall use the following algorithm: [Time Horizon: Operations Planning] ETCNF = NITSNF + GFNF + PTPNF + OSNF Where: NITSNF is the non-firm capacity set aside for Network Integration Transmission Service serving Load (i.e., secondary service), to include losses, and load growth not otherwise included in Transmission Reliability Margin or Capacity Benefit Margin. GFNF is the non-firm capacity set aside for grandfathered Transmission Service and contracts for energy and/or Transmission Service, where executed prior to the effective date of a Transmission Service Provider’s Open Access Transmission Tariff or “safe harbor tariff.” PTPNF is non-firm capacity reserved for confirmed Point-to-Point Transmission Service. OSNF is the non-firm capacity reserved for any other service(s), contract(s), or agreement(s) not specified above using non-firm transmission service as specified in the ATCID. | LOWER | Effective | 2017-04-01 |  | TSP
MOD-029-2a | Rated System Path Methodology | R7. | When calculating firm ATC for an ATC Path for a specified period, the Transmission Service Provider shall use the following algorithm: [Time Horizon: Operations Planning] ATCF = TTC – ETCF – CBM – TRM + PostbacksF + counterflowsF Where ATCF is the firm Available Transfer Capability for the ATC Path for that period. TTC is the Total Transfer Capability of the ATC Path for that period. ETCF is the sum of existing firm commitments for the ATC Path during that period. CBM is the Capacity Benefit Margin for the ATC Path during that period. TRM is the Transmission Reliability Margin for the ATC Path during that period. PostbacksF are changes to firm Available Transfer Capability due to a change in the use of Transmission Service for that period, as defined in Business Practices. counterflowsF are adjustments to firm Available Transfer Capability as determined by the Transmission Service Provider and specified in their ATCID. | MEDIUM | Effective | 2017-04-01 |  | TSP
MOD-029-2a | Rated System Path Methodology | R8. | When calculating non-firm ATC for an ATC Path for a specified period, the Transmission Service Provider shall use the following algorithm:[Time Horizon: Operations Planning] See Standard for Formula ATCNF = TTC – ETCF – ETCNF – CBMS – TRMU + PostbacksNF + counterflowsNF Where: ATCNF is the non-firm Available Transfer Capability for the ATC Path for that period. TTC is the Total Transfer Capability of the ATC Path for that period. ETCF is the sum of existing firm commitments for the ATC Path during that period. ETCNF is the sum of existing non-firm commitments for the ATC Path during that period. CBMS is the Capacity Benefit Margin for the ATC Path that has been scheduled during that period. TRMU is the Transmission Reliability Margin for the ATC Path that has not been released for sale (unreleased) as non-firm capacity by the Transmission Service Provider during that period. PostbacksNF are changes to non-firm Available Transfer Capability due to a change in the use of Transmission Service for that period, as defined in Business Practices. counterflowsNF are adjustments to non-firm Available Transfer Capability as determined by the Transmission Service Provider and specified in its ATCID. | LOWER | Effective | 2017-04-01 |  | TSP
MOD-030-2 | Flowgate Methodology | R1. | The Transmission Service Provider shall include in its “Available Transfer Capability Implementation Document” (ATCID): [Time Horizon: Operations Planning] | MEDIUM | Retired | 2011-07-01 | 2017-03-31 | TSP
MOD-030-2 | Flowgate Methodology | R1.1. | The criteria used by the Transmission Operator to identify sets of Transmission Facilities as Flowgates that are to be considered in Available Flowgate Capability (AFC) calculations. | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TSP
MOD-030-2 | Flowgate Methodology | R1.2. | The following information on how source and sink for transmission service is accounted for in AFC calculations including: | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TSP
MOD-030-2 | Flowgate Methodology | R1.2.1. | Define if the source used for AFC calculations is obtained from the source field or the Point of Receipt (POR) field of the transmission reservation. | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TSP
MOD-030-2 | Flowgate Methodology | R1.2.2. | Define if the sink used for AFC calculations is obtained from the sink field or the Point of Delivery (POD) field of the transmission reservation. | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TSP
MOD-030-2 | Flowgate Methodology | R1.2.3. | The source/sink or POR/POD identification and mapping to the model. | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TSP
MOD-030-2 | Flowgate Methodology | R1.2.4. | If the Transmission Service Provider’s AFC calculation process involves a grouping of generators, the ATCID must identify how these generators participate in the group. | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TSP
MOD-030-2 | Flowgate Methodology | R10. | Each Transmission Service Provider shall recalculate AFC, utilizing the updated models described in R3.2, R3.3, and R5, at a minimum on the following frequency, unless none of the calculated values identified in the AFC equation have changed: [Time Horizon: Operations Planning] | MEDIUM | Retired | 2011-07-01 | 2017-03-31 | TSP
MOD-030-2 | Flowgate Methodology | R10.1. | For hourly AFC, once per hour. Transmission Service Providers are allowed up to 175 hours per calendar year during which calculations are not required to be performed, despite a change in a calculated value identified in the AFC equation. | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TSP
MOD-030-2 | Flowgate Methodology | R10.2. | For daily AFC, once per day. | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TSP
MOD-030-2 | Flowgate Methodology | R10.3. | For monthly AFC, once per week. | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TSP
MOD-030-2 | Flowgate Methodology | R11. | When converting Flowgate AFCs to ATCs for ATC Paths, the Transmission Service Provider shall convert those values based on the following algorithm: [Time Horizon: Operations Planning] See Standard for Formula | LOWER | Retired | 2011-07-01 | 2017-03-31 | TSP
MOD-030-2 | Flowgate Methodology | R2. | The Transmission Operator shall perform the following: [Time Horizon: Operations Planning] | MEDIUM | Retired | 2011-07-01 | 2017-03-31 | TOP
MOD-030-2 | Flowgate Methodology | R2.1. | Include Flowgates used in the AFC process based, at a minimum, on the following criteria: | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TOP
MOD-030-2 | Flowgate Methodology | R2.1.1. | Results of a first Contingency transfer analysis for ATC Paths internal to a Transmission Operator’s system up to the path capability such that at a minimum the first three limiting Elements and their worst associated Contingency combinations with an OTDF of at least 5% and within the Transmission Operator’s system are included as Flowgates. | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TOP
MOD-030-2 | Flowgate Methodology | R2.1.1.1. | Use first Contingency criteria consistent with those first Contingency criteria used in planning of operations for the applicable time periods, including use of Special Protection Systems. | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TOP
MOD-030-2 | Flowgate Methodology | R2.1.1.2. | Only the most limiting element in a series configuration needs to be included as a Flowgate. | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TOP
MOD-030-2 | Flowgate Methodology | R2.1.1.3. | If any limiting element is kept within its limit for its associated worst Contingency by operating within the limits of another Flowgate, then no new Flowgate needs to be established for such limiting elements or Contingencies. | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TOP
MOD-030-2 | Flowgate Methodology | R2.1.2. | Results of a first Contingency transfer analysis from all adjacent Balancing Authority source and sink (as defined in the ATCID) combinations up to the path capability such that at a minimum the first three limiting Elements and their worst associated Contingency combinations with an Outage Transfer Distribution Factor (OTDF) of at least 5% and within the Transmission Operator’s system are included as Flowgates unless the interface between such adjacent Balancing Authorities is accounted for using another ATC methodology. | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TOP
MOD-030-2 | Flowgate Methodology | R2.1.2.1. | Use first Contingency criteria consistent with those first Contingency criteria used in planning of operations for the applicable time periods, including use of Special Protection Systems. | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TOP
MOD-030-2 | Flowgate Methodology | R2.1.2.2. | Only the most limiting element in a series configuration needs to be included as a Flowgate. | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TOP
MOD-030-2 | Flowgate Methodology | R2.1.2.3. | If any limiting element is kept within its limit for its associated worst Contingency by operating within the limits of another Flowgate, then no new Flowgate needs to be established for such limiting elements or Contingencies. | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TOP
MOD-030-2 | Flowgate Methodology | R2.1.3. | Any limiting Element/Contingency combination at least within its Reliability Coordinator’s Area that has been subjected to an Interconnection-wide congestion management procedure within the last 12 months, unless the limiting Element/Contingency combination is accounted for using another ATC methodology or was created to address temporary operating conditions. | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TOP
MOD-030-2 | Flowgate Methodology | R2.1.4. | Any limiting Element/Contingency combination within the Transmission model that has been requested to be included by any other Transmission Service Provider using the Flowgate Methodology or Area Interchange Methodology, where: | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TOP
MOD-030-2 | Flowgate Methodology | R2.1.4.1. | The coordination of the limiting Element/Contingency combination is not already addressed through a different methodology, and - Any generator within the Transmission Service Provider’s area has at least a 5% Power Transfer Distribution Factor (PTDF) or Outage Transfer Distribution Factor (OTDF) impact on the Flowgate when delivered to the aggregate load of its own area, or - A transfer from any Balancing Area within the Transmission Service Provider’s area to a Balancing Area adjacent has at least a 5% PTDF or OTDF impact on the Flowgate. - The Transmission Operator may utilize distribution factors less than 5% if desired. | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TOP
MOD-030-2 | Flowgate Methodology | R2.1.4.2. | The limiting Element/Contingency combination is included in the requesting Transmission Service Provider’s methodology. | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TOP
MOD-030-2 | Flowgate Methodology | R2.2. | At a minimum, establish a list of Flowgates by creating, modifying, or deleting Flowgate definitions at least once per calendar year. | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TOP
MOD-030-2 | Flowgate Methodology | R2.3. | At a minimum, establish a list of Flowgates by creating, modifying, or deleting Flowgates that have been requested as part of R2.1.4 within thirty calendar days from the request. | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TOP
MOD-030-2 | Flowgate Methodology | R2.4. | Establish the TFC of each of the defined Flowgates as equal to: - For thermal limits, the System Operating Limit (SOL) of the Flowgate. - For voltage or stability limits, the flow that will respect the SOL of the Flowgate. | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TOP
MOD-030-2 | Flowgate Methodology | R2.5. | At a minimum, establish the TFC once per calendar year. | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TOP
MOD-030-2 | Flowgate Methodology | R2.5.1. | If notified of a change in the Rating by the Transmission Owner that would affect the TFC of a flowgate used in the AFC process, the TFC should be updated within seven calendar days of the notification. | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TOP
MOD-030-2 | Flowgate Methodology | R2.6. | Provide the Transmission Service Provider with the TFCs within seven calendar days of their establishment. | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TOP
MOD-030-2 | Flowgate Methodology | R3. | The Transmission Operator shall make available to the Transmission Service Provider a Transmission model to determine Available Flowgate Capability (AFC) that meets the following criteria: [Time Horizon: Operations Planning] | MEDIUM | Retired | 2011-07-01 | 2017-03-31 | TOP
MOD-030-2 | Flowgate Methodology | R3.1. | Contains generation Facility Ratings, such as generation maximum and minimum output levels, specified by the Generator Owners of the Facilities within the model. | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TOP
MOD-030-2 | Flowgate Methodology | R3.2. | Updated at least once per day for AFC calculations for intra-day, next day, and days two through 30. | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TOP
MOD-030-2 | Flowgate Methodology | R3.3. | Updated at least once per month for AFC calculations for months two through 13. | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TOP
MOD-030-2 | Flowgate Methodology | R3.4. | Contains modeling data and system topology for the Facilities within its Reliability Coordinator’s Area. Equivalent representation of radial lines and Facilities161kV or below is allowed. | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TOP
MOD-030-2 | Flowgate Methodology | R3.5. | Contains modeling data and system topology (or equivalent representation) for immediately adjacent and beyond Reliability Coordination Areas. | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TOP
MOD-030-2 | Flowgate Methodology | R4. | When calculating AFCs, the Transmission Service Provider shall represent the impact of Transmission Service as follows: [Time Horizon: Operations Planning] - If the source, as specified in the ATCID, has been identified in the reservation and it is discretely modeled in the Transmission Service Provider’s Transmission model, use the discretely modeled point as the source. - If the source, as specified in the ATCID, has been identified in the reservation and the point can be mapped to an “equivalence” or “aggregate” representation in the Transmission Service Provider’s Transmission model, use the modeled equivalence or aggregate as the source. - If the source, as specified in the ATCID, has been identified in the reservation and the point cannot be mapped to a discretely modeled point or an “equivalence” representation in the Transmission Service Provider’s Transmission model, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider from which the power is to be received as the source. - If the source, as specified in the ATCID, has not been identified in the reservation use the immediately adjacent Balancing Authority associated with the Transmission Service Provider from which the power is to be received as the source. - If the sink, as specified in the ATCID, has been identified in the reservation and it is discretely modeled in the Transmission Service Provider’s Transmission model, use the discretely modeled point as the sink. - If the sink, as specified in the ATCID, has been identified in the reservation and the point can be mapped to an “equivalence” or “aggregate” representation in the Transmission Service Provider’s Transmission model, use the modeled equivalence or aggregate as the sink. - If the sink, as specified in the ATCID, has been identified in the reservation and the point cannot be mapped to a discretely modeled point or an “equivalence” representation in the Transmission Service Provider’s Transmission model, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider receiving the power as the sink. - If the sink, as specified in the ATCID, has not been identified in the reservation use the immediately adjacent Balancing Authority associated with the Transmission Service Provider receiving the power as the sink. | MEDIUM | Retired | 2011-07-01 | 2017-03-31 | TSP
MOD-030-2 | Flowgate Methodology | R5. | When calculating AFCs, the Transmission Service Provider shall: [Time Horizon: Operations Planning] | MEDIUM | Retired | 2011-07-01 | 2017-03-31 | TSP
MOD-030-2 | Flowgate Methodology | R5.1. | Use the models provided by the Transmission Operator. | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TSP
MOD-030-2 | Flowgate Methodology | R5.2. | Include in the transmission model expected generation and Transmission outages, additions, and retirements within the scope of the model as specified in the ATCID and in effect during the applicable period of the AFC calculation for the Transmission Service Provider’s area, all adjacent Transmission Service Providers, and any Transmission Service Providers with which coordination agreements have been executed. | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TSP
MOD-030-2 | Flowgate Methodology | R5.3. | For external Flowgates, identified in R2.1.4, use the AFC provided by the Transmission Service Provider that calculates AFC for that Flowgate. | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TSP
MOD-030-2 | Flowgate Methodology | R6. | When calculating the impact of ETC for firm commitments (ETCFi) for all time periods for a Flowgate, the Transmission Service Provider shall sum the following: [Time Horizon: Operations Planning] | MEDIUM | Retired | 2011-07-01 | 2017-03-31 | TSP
MOD-030-2 | Flowgate Methodology | R6.1. | The impact of firm Network Integration Transmission Service, including the impacts of generation to load, in the model referenced in R5.2 for the Transmission Service Provider’s area, based on: | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TSP
MOD-030-2 | Flowgate Methodology | R6.1.1. | Load forecast for the time period being calculated, including Native Load and Network Service load | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TSP
MOD-030-2 | Flowgate Methodology | R6.1.2. | Unit commitment and Dispatch Order, to include all designated network resources and other resources that are committed or have the legal obligation to run as specified in the Transmission Service Provider's ATCID. | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TSP
MOD-030-2 | Flowgate Methodology | R6.2. | The impact of any firm Network Integration Transmission Service, including the impacts of generation to load in the model referenced in R5.2 and has a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed based on: | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TSP
MOD-030-2 | Flowgate Methodology | R6.2.1. | Load forecast for the time period being calculated, including Native Load and Network Service load | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TSP
MOD-030-2 | Flowgate Methodology | R6.2.2. | Unit commitment and Dispatch Order, to include all designated network resources and other resources that are committed or have the legal obligation to run as specified in the Transmission Service Provider's ATCID. | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TSP
MOD-030-2 | Flowgate Methodology | R6.3. | The impact of all confirmed firm Point-to-Point Transmission Service expected to be scheduled, including roll-over rights for Firm Transmission Service contracts, for the Transmission Service Provider’s area. | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TSP
MOD-030-2 | Flowgate Methodology | R6.4. | The impact of any confirmed firm Point-to-Point Transmission Service expected to be scheduled, filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers, including roll-over rights for Firm Transmission Service contracts having a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TSP
MOD-030-2 | Flowgate Methodology | R6.5. | The impact of any Grandfathered firm obligations expected to be scheduled or expected to flow for the Transmission Service Provider’s area. | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TSP
MOD-030-2 | Flowgate Methodology | R6.6. | The impact of any Grandfathered firm obligations expected to be scheduled or expected to flow that have a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TSP
MOD-030-2 | Flowgate Methodology | R6.7. | The impact of other firm services determined by the Transmission Service Provider. | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TSP
MOD-030-2 | Flowgate Methodology | R7. | When calculating the impact of ETC for non-firm commitments (ETCNFi) for all time periods for a Flowgate the Transmission Service Provider shall sum: [Time Horizon: Operations Planning] | LOWER | Retired | 2011-07-01 | 2017-03-31 | TSP
MOD-030-2 | Flowgate Methodology | R7.1. | The impact of all confirmed non-firm Point-to-Point Transmission Service expected to be scheduled for the Transmission Service Provider’s area. | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TSP
MOD-030-2 | Flowgate Methodology | R7.2. | The impact of any confirmed non-firm Point-to-Point Transmission Service expected to be scheduled, filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers, that have a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TSP
MOD-030-2 | Flowgate Methodology | R7.3. | The impact of any Grandfathered non-firm obligations expected to be scheduled or expected to flow for the Transmission Service Provider’s area. | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TSP
MOD-030-2 | Flowgate Methodology | R7.4. | The impact of any Grandfathered non-firm obligations expected to be scheduled or expected to flow that have a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TSP
MOD-030-2 | Flowgate Methodology | R7.5. | The impact of non-firm Network Integration Transmission Service serving Load within the Transmission Service Provider’s area (i.e., secondary service), to include load growth, and losses not otherwise included in Transmission Reliability Margin or Capacity Benefit Margin. | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TSP
MOD-030-2 | Flowgate Methodology | R7.6. | The impact of any non-firm Network Integration Transmission Service (secondary service) with a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TSP
MOD-030-2 | Flowgate Methodology | R7.7. | The impact of other non-firm services determined by the Transmission Service Provider. | No Individual VRF Assigned | Retired | 2011-07-01 | 2017-03-31 | TSP
MOD-030-2 | Flowgate Methodology | R8. | When calculating firm AFC for a Flowgate for a specified period, the Transmission Service Provider shall use the following algorithm (subject to allocation processes described in the ATCID): [Time Horizon: Operations Planning] See Standard for Formula | MEDIUM | Retired | 2011-07-01 | 2017-03-31 | TSP
MOD-030-2 | Flowgate Methodology | R9. | When calculating non-firm AFC for a Flowgate for a specified period, the Transmission Service Provider shall use the following algorithm (subject to allocation processes described in the ATCID): [Time Horizon: Operations Planning] See Standard for Formula | LOWER | Retired | 2011-07-01 | 2017-03-31 | TSP
MOD-030-3 | Flowgate Methodology | R1. | The Transmission Service Provider shall include in its “Available Transfer Capability Implementation Document” (ATCID): [Time Horizon: Operations Planning] | N/A | Effective | 2017-04-01 |  | TSP
MOD-030-3 | Flowgate Methodology | R1.1. | The criteria used by the Transmission Operator to identify sets of Transmission Facilities as Flowgates that are to be considered in Available Flowgate Capability (AFC) calculations. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TSP
MOD-030-3 | Flowgate Methodology | R1.2. | The following information on how source and sink for transmission service is accounted for in AFC calculations including: | No Individual VRF Assigned | Effective | 2017-04-01 |  | TSP
MOD-030-3 | Flowgate Methodology | R1.2.1. | Define if the source used for AFC calculations is obtained from the source field or the Point of Receipt (POR) field of the transmission reservation. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TSP
MOD-030-3 | Flowgate Methodology | R1.2.2. | Define if the sink used for AFC calculations is obtained from the sink field or the Point of Delivery (POD) field of the transmission reservation. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TSP
MOD-030-3 | Flowgate Methodology | R1.2.3. | The source/sink or POR/POD identification and mapping to the model. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TSP
MOD-030-3 | Flowgate Methodology | R1.2.4. | If the Transmission Service Provider’s AFC calculation process involves a grouping of generators, the ATCID must identify how these generators participate in the group. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TSP
MOD-030-3 | Flowgate Methodology | R10. | Each Transmission Service Provider shall recalculate AFC, utilizing the updated models described in R3.2, R3.3, and R5, at a minimum on the following frequency, unless none of the calculated values identified in the AFC equation have changed: [Violation Risk Factor: To Be Determined] [Time Horizon: Operations Planning] | N/A | Effective | 2017-04-01 |  | TSP
MOD-030-3 | Flowgate Methodology | R10.1. | For hourly AFC, once per hour. Transmission Service Providers are allowed up to 175 hours per calendar year during which calculations are not required to be performed, despite a change in a calculated value identified in the AFC equation. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TSP
MOD-030-3 | Flowgate Methodology | R10.2. | For daily AFC, once per day. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TSP
MOD-030-3 | Flowgate Methodology | R10.3. | For monthly AFC, once per week. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TSP
MOD-030-3 | Flowgate Methodology | R11. | When converting Flowgate AFCs to ATCs for ATC Paths, the Transmission Service Provider shall convert those values based on the following algorithm: [Time Horizon: Operations Planning] See Standard for Formula | N/A | Effective | 2017-04-01 |  | TSP
MOD-030-3 | Flowgate Methodology | R2. | The Transmission Operator shall perform the following: [Violation Risk Factor: To Be Determined] [Time Horizon: Operations Planning] | N/A | Effective | 2017-04-01 |  | TOP
MOD-030-3 | Flowgate Methodology | R2.1. | Include Flowgates used in the AFC process based, at a minimum, on the following criteria: | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-030-3 | Flowgate Methodology | R2.1.1. | Results of a first Contingency transfer analysis for ATC Paths internal to a Transmission Operator’s system up to the path capability such that at a minimum the first three limiting Elements and their worst associated Contingency combinations with an OTDF of at least 5% and within the Transmission Operator’s system are included as Flowgates. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-030-3 | Flowgate Methodology | R2.1.1.1. | Use first Contingency criteria consistent with those first Contingency criteria used in planning of operations for the applicable time periods, including use of Remedial Action Schemes. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-030-3 | Flowgate Methodology | R2.1.1.2. | Only the most limiting element in a series configuration needs to be included as a Flowgate. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-030-3 | Flowgate Methodology | R2.1.1.3. | If any limiting element is kept within its limit for its associated worst Contingency by operating within the limits of another Flowgate, then no new Flowgate needs to be established for such limiting elements or Contingencies. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-030-3 | Flowgate Methodology | R2.1.2. | Results of a first Contingency transfer analysis from all adjacent Balancing Authority source and sink (as defined in the ATCID) combinations up to the path capability such that at a minimum the first three limiting Elements and their worst associated Contingency combinations with an Outage Transfer Distribution Factor (OTDF) of at least 5% and within the Transmission Operator’s system are included as Flowgates unless the interface between such adjacent Balancing Authorities is accounted for using another ATC methodology. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-030-3 | Flowgate Methodology | R2.1.2.1. | Use first Contingency criteria consistent with those first Contingency criteria used in planning of operations for the applicable time periods, including use of Remedial Action Schemes. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-030-3 | Flowgate Methodology | R2.1.2.2. | Only the most limiting element in a series configuration needs to be included as a Flowgate. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-030-3 | Flowgate Methodology | R2.1.2.3. | If any limiting element is kept within its limit for its associated worst Contingency by operating within the limits of another Flowgate, then no new Flowgate needs to be established for such limiting elements or Contingencies. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-030-3 | Flowgate Methodology | R2.1.3. | Any limiting Element/Contingency combination at least within its Reliability Coordinator’s Area that has been subjected to an Interconnection-wide congestion management procedure within the last 12 months, unless the limiting Element/Contingency combination is accounted for using another ATC methodology or was created to address temporary operating conditions. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-030-3 | Flowgate Methodology | R2.1.4. | Any limiting Element/Contingency combination within the Transmission model that has been requested to be included by any other Transmission Service Provider using the Flowgate Methodology or Area Interchange Methodology, where: | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-030-3 | Flowgate Methodology | R2.1.4.1. | The coordination of the limiting Element/Contingency combination is not already addressed through a different methodology, and - Any generator within the Transmission Service Provider’s area has at least a 5% Power Transfer Distribution Factor (PTDF) or Outage Transfer Distribution Factor (OTDF) impact on the Flowgate when delivered to the aggregate load of its own area, or - A transfer from any Balancing Area within the Transmission Service Provider’s area to a Balancing Area adjacent has at least a 5% PTDF or OTDF impact on the Flowgate. - The Transmission Operator may utilize distribution factors less than 5% if desired. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-030-3 | Flowgate Methodology | R2.1.4.2. | The limiting Element/Contingency combination is included in the requesting Transmission Service Provider’s methodology. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-030-3 | Flowgate Methodology | R2.2. | At a minimum, establish a list of Flowgates by creating, modifying, or deleting Flowgate definitions at least once per calendar year. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-030-3 | Flowgate Methodology | R2.3. | At a minimum, establish a list of Flowgates by creating, modifying, or deleting Flowgates that have been requested as part of R2.1.4 within thirty calendar days from the request. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-030-3 | Flowgate Methodology | R2.4. | Establish the TFC of each of the defined Flowgates as equal to: - For thermal limits, the System Operating Limit (SOL) of the Flowgate. - For voltage or stability limits, the flow that will respect the SOL of the Flowgate. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-030-3 | Flowgate Methodology | R2.5. | At a minimum, establish the TFC once per calendar year. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-030-3 | Flowgate Methodology | R2.5.1. | If notified of a change in the Rating by the Transmission Owner that would affect the TFC of a flowgate used in the AFC process, the TFC should be updated within seven calendar days of the notification. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-030-3 | Flowgate Methodology | R2.6. | Provide the Transmission Service Provider with the TFCs within seven calendar days of their establishment. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-030-3 | Flowgate Methodology | R3. | The Transmission Operator shall make available to the Transmission Service Provider a Transmission model to determine Available Flowgate Capability (AFC) that meets the following criteria: [Violation Risk Factor: To Be Determined] [Time Horizon: Operations Planning] | N/A | Effective | 2017-04-01 |  | TOP
MOD-030-3 | Flowgate Methodology | R3.1. | Contains generation Facility Ratings, such as generation maximum and minimum output levels, specified by the Generator Owners of the Facilities within the model. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-030-3 | Flowgate Methodology | R3.2. | Updated at least once per day for AFC calculations for intra-day, next day, and days two through 30. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-030-3 | Flowgate Methodology | R3.3. | Updated at least once per month for AFC calculations for months two through 13. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-030-3 | Flowgate Methodology | R3.4. | Contains modeling data and system topology for the Facilities within its Reliability Coordinator’s Area. Equivalent representation of radial lines and Facilities161kV or below is allowed. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-030-3 | Flowgate Methodology | R3.5. | Contains modeling data and system topology (or equivalent representation) for immediately adjacent and beyond Reliability Coordination Areas. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TOP
MOD-030-3 | Flowgate Methodology | R4. | When calculating AFCs, the Transmission Service Provider shall represent the impact of Transmission Service as follows: [Time Horizon: Operations Planning] - If the source, as specified in the ATCID, has been identified in the reservation and it is discretely modeled in the Transmission Service Provider’s Transmission model, use the discretely modeled point as the source. - If the source, as specified in the ATCID, has been identified in the reservation and the point can be mapped to an “equivalence” or “aggregate” representation in the Transmission Service Provider’s Transmission model, use the modeled equivalence or aggregate as the source. - If the source, as specified in the ATCID, has been identified in the reservation and the point cannot be mapped to a discretely modeled point or an “equivalence” representation in the Transmission Service Provider’s Transmission model, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider from which the power is to be received as the source. - If the source, as specified in the ATCID, has not been identified in the reservation use the immediately adjacent Balancing Authority associated with the Transmission Service Provider from which the power is to be received as the source. - If the sink, as specified in the ATCID, has been identified in the reservation and it is discretely modeled in the Transmission Service Provider’s Transmission model, use the discretely modeled point as the sink. - If the sink, as specified in the ATCID, has been identified in the reservation and the point can be mapped to an “equivalence” or “aggregate” representation in the Transmission Service Provider’s Transmission model, use the modeled equivalence or aggregate as the sink. - If the sink, as specified in the ATCID, has been identified in the reservation and the point cannot be mapped to a discretely modeled point or an “equivalence” representation in the Transmission Service Provider’s Transmission model, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider receiving the power as the sink. - If the sink, as specified in the ATCID, has not been identified in the reservation use the immediately adjacent Balancing Authority associated with the Transmission Service Provider receiving the power as the sink. | N/A | Effective | 2017-04-01 |  | TSP
MOD-030-3 | Flowgate Methodology | R5. | When calculating AFCs, the Transmission Service Provider shall: [Violation Risk Factor: To Be Determined] [Time Horizon: Operations Planning] | N/A | Effective | 2017-04-01 |  | TSP
MOD-030-3 | Flowgate Methodology | R5.1. | Use the models provided by the Transmission Operator. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TSP
MOD-030-3 | Flowgate Methodology | R5.2. | Include in the transmission model expected generation and Transmission outages, additions, and retirements within the scope of the model as specified in the ATCID and in effect during the applicable period of the AFC calculation for the Transmission Service Provider’s area, all adjacent Transmission Service Providers, and any Transmission Service Providers with which coordination agreements have been executed. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TSP
MOD-030-3 | Flowgate Methodology | R5.3. | For external Flowgates, identified in R2.1.4, use the AFC provided by the Transmission Service Provider that calculates AFC for that Flowgate. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TSP
MOD-030-3 | Flowgate Methodology | R6. | When calculating the impact of ETC for firm commitments (ETCFi) for all time periods for a Flowgate, the Transmission Service Provider shall sum the following: [Violation Risk Factor: To Be Determined] [Time Horizon: Operations Planning] | N/A | Effective | 2017-04-01 |  | TSP
MOD-030-3 | Flowgate Methodology | R6.1. | The impact of firm Network Integration Transmission Service, including the impacts of generation to load, in the model referenced in R5.2 for the Transmission Service Provider’s area, based on: | No Individual VRF Assigned | Effective | 2017-04-01 |  | TSP
MOD-030-3 | Flowgate Methodology | R6.1.1. | Load forecast for the time period being calculated, including Native Load and Network Service load | No Individual VRF Assigned | Effective | 2017-04-01 |  | TSP
MOD-030-3 | Flowgate Methodology | R6.1.2. | Unit commitment and Dispatch Order, to include all designated network resources and other resources that are committed or have the legal obligation to run as specified in the Transmission Service Provider's ATCID. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TSP
MOD-030-3 | Flowgate Methodology | R6.2. | The impact of any firm Network Integration Transmission Service, including the impacts of generation to load in the model referenced in R5.2 and has a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed based on: | No Individual VRF Assigned | Effective | 2017-04-01 |  | TSP
MOD-030-3 | Flowgate Methodology | R6.2.1. | Load forecast for the time period being calculated, including Native Load and Network Service load | No Individual VRF Assigned | Effective | 2017-04-01 |  | TSP
MOD-030-3 | Flowgate Methodology | R6.2.2. | Unit commitment and Dispatch Order, to include all designated network resources and other resources that are committed or have the legal obligation to run as specified in the Transmission Service Provider's ATCID. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TSP
MOD-030-3 | Flowgate Methodology | R6.3. | The impact of all confirmed firm Point-to-Point Transmission Service expected to be scheduled, including roll-over rights for Firm Transmission Service contracts, for the Transmission Service Provider’s area. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TSP
MOD-030-3 | Flowgate Methodology | R6.4. | The impact of any confirmed firm Point-to-Point Transmission Service expected to be scheduled, filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers, including roll-over rights for Firm Transmission Service contracts having a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TSP
MOD-030-3 | Flowgate Methodology | R6.5. | The impact of any Grandfathered firm obligations expected to be scheduled or expected to flow for the Transmission Service Provider’s area. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TSP
MOD-030-3 | Flowgate Methodology | R6.6. | The impact of any Grandfathered firm obligations expected to be scheduled or expected to flow that have a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TSP
MOD-030-3 | Flowgate Methodology | R6.7. | The impact of other firm services determined by the Transmission Service Provider. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TSP
MOD-030-3 | Flowgate Methodology | R7. | When calculating the impact of ETC for non-firm commitments (ETCNFi) for all time periods for a Flowgate the Transmission Service Provider shall sum: [Violation Risk Factor: To Be Determined] [Time Horizon: Operations Planning] | N/A | Effective | 2017-04-01 |  | TSP
MOD-030-3 | Flowgate Methodology | R7.1. | The impact of all confirmed non-firm Point-to-Point Transmission Service expected to be scheduled for the Transmission Service Provider’s area. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TSP
MOD-030-3 | Flowgate Methodology | R7.2. | The impact of any confirmed non-firm Point-to-Point Transmission Service expected to be scheduled, filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers, that have a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TSP
MOD-030-3 | Flowgate Methodology | R7.3. | The impact of any Grandfathered non-firm obligations expected to be scheduled or expected to flow for the Transmission Service Provider’s area. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TSP
MOD-030-3 | Flowgate Methodology | R7.4. | The impact of any Grandfathered non-firm obligations expected to be scheduled or expected to flow that have a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TSP
MOD-030-3 | Flowgate Methodology | R7.5. | The impact of non-firm Network Integration Transmission Service serving Load within the Transmission Service Provider’s area (i.e., secondary service), to include load growth, and losses not otherwise included in Transmission Reliability Margin or Capacity Benefit Margin. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TSP
MOD-030-3 | Flowgate Methodology | R7.6. | The impact of any non-firm Network Integration Transmission Service (secondary service) with a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TSP
MOD-030-3 | Flowgate Methodology | R7.7. | The impact of other non-firm services determined by the Transmission Service Provider. | No Individual VRF Assigned | Effective | 2017-04-01 |  | TSP
MOD-030-3 | Flowgate Methodology | R8. | When calculating firm AFC for a Flowgate for a specified period, the Transmission Service Provider shall use the following algorithm (subject to allocation processes described in the ATCID): [Time Horizon: Operations Planning] See Standard for Formula | N/A | Effective | 2017-04-01 |  | TSP
MOD-030-3 | Flowgate Methodology | R9. | When calculating non-firm AFC for a Flowgate for a specified period, the Transmission Service Provider shall use the following algorithm (subject to allocation processes described in the ATCID): [Time Horizon: Operations Planning] See Standard for Formula | N/A | Effective | 2017-04-01 |  | TSP
MOD-031-1 | Demand and Energy Data | R1. | Each Planning Coordinator or Balancing Authority that identifies a need for the collection of Total Internal Demand, Net Energy for Load, and Demand Side Management data shall develop and issue a data request to the applicable entities in its area. The data request shall include: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Retired | 2016-07-01 | 2016-09-30 | PC, BA
MOD-031-1 | Demand and Energy Data | R1.1. | A list of Transmission Planners, Balancing Authorities, Load Serving Entities, and Distribution Providers that are required to provide the data (“Applicable Entities”). | MEDIUM | Retired | 2016-07-01 | 2016-09-30 | PC, BA
MOD-031-1 | Demand and Energy Data | R1.2. | A timetable for providing the data. (A minimum of 30 calendar days must be allowed for responding to the request). | MEDIUM | Retired | 2016-07-01 | 2016-09-30 | PC, BA
MOD-031-1 | Demand and Energy Data | R1.3. | A request to provide any or all of the following actual data, as necessary: | MEDIUM | Retired | 2016-07-01 | 2016-09-30 | PC, BA
MOD-031-1 | Demand and Energy Data | R1.3.1. | Integrated hourly Demands in megawatts for the prior calendar year. | MEDIUM | Retired | 2016-07-01 | 2016-09-30 | PC, BA
MOD-031-1 | Demand and Energy Data | R1.3.2. | Monthly and annual integrated peak hour Demands in megawatts for the prior calendar year. | MEDIUM | Retired | 2016-07-01 | 2016-09-30 | PC, BA
MOD-031-1 | Demand and Energy Data | R1.3.2.1. | If the annual peak hour actual Demand varies due to weather-related conditions (e.g., temperature, humidity or wind speed), the Applicable Entity shall also provide the weather normalized annual peak hour actual Demand for the prior calendar year. | MEDIUM | Retired | 2016-07-01 | 2016-09-30 | PC, BA
MOD-031-1 | Demand and Energy Data | R1.3.3. | Monthly and annual Net Energy for Load in gigawatthours for the prior calendar year. | MEDIUM | Retired | 2016-07-01 | 2016-09-30 | PC, BA
MOD-031-1 | Demand and Energy Data | R1.3.4. | Monthly and annual peak hour controllable and dispatchable Demand Side Management under the control or supervision of the System Operator in megawatts for the prior calendar year. Three values shall be reported for each hour: 1) the committed megawatts (the amount under control or supervision), 2) the dispatched megawatts (the amount, if any, activated for use by the System Operator), and 3) the realized megawatts (the amount of actual demand reduction). | MEDIUM | Retired | 2016-07-01 | 2016-09-30 | PC, BA
MOD-031-1 | Demand and Energy Data | R1.4. | A request to provide any or all of the following forecast data, as necessary: | MEDIUM | Retired | 2016-07-01 | 2016-09-30 | PC, BA
MOD-031-1 | Demand and Energy Data | R1.4.1. | Monthly peak hour forecast Total Internal Demands in megawatts for the next two calendar years. | MEDIUM | Retired | 2016-07-01 | 2016-09-30 | PC, BA
MOD-031-1 | Demand and Energy Data | R1.4.2. | Monthly forecast Net Energy for Load in gigawatthours for the next two calendar years. | MEDIUM | Retired | 2016-07-01 | 2016-09-30 | PC, BA
MOD-031-1 | Demand and Energy Data | R1.4.3. | Peak hour forecast Total Internal Demands (summer and winter) in megawatts for ten calendar years into the future. | MEDIUM | Retired | 2016-07-01 | 2016-09-30 | PC, BA
MOD-031-1 | Demand and Energy Data | R1.4.4. | Annual forecast Net Energy for Load in gigawatthours for ten calendar years into the future. | MEDIUM | Retired | 2016-07-01 | 2016-09-30 | PC, BA
MOD-031-1 | Demand and Energy Data | R1.4.5. | Total and available peak hour forecast of controllable and dispatchable Demand Side Management (summer and winter), in megawatts, under the control or supervision of the System Operator for ten calendar years into the future. | MEDIUM | Retired | 2016-07-01 | 2016-09-30 | PC, BA
MOD-031-1 | Demand and Energy Data | R1.5. | A request to provide any or all of the following summary explanations, as necessary,: | MEDIUM | Retired | 2016-07-01 | 2016-09-30 | PC, BA
MOD-031-1 | Demand and Energy Data | R1.5.1. | The assumptions and methods used in the development of aggregated Peak Demand and Net Energy for Load forecasts. | MEDIUM | Retired | 2016-07-01 | 2016-09-30 | PC, BA
MOD-031-1 | Demand and Energy Data | R1.5.2. | The Demand and energy effects of controllable and dispatchable Demand Side Management under the control or supervision of the System Operator. | MEDIUM | Retired | 2016-07-01 | 2016-09-30 | PC, BA
MOD-031-1 | Demand and Energy Data | R1.5.3. | How Demand Side Management is addressed in the forecasts of its Peak Demand and annual Net Energy for Load. | MEDIUM | Retired | 2016-07-01 | 2016-09-30 | PC, BA
MOD-031-1 | Demand and Energy Data | R1.5.4. | How the controllable and dispatchable Demand Side Management forecast compares to actual controllable and dispatchable Demand Side Management for the prior calendar year and, if applicable, how the assumptions and methods for future forecasts were adjusted. | MEDIUM | Retired | 2016-07-01 | 2016-09-30 | PC, BA
MOD-031-1 | Demand and Energy Data | R1.5.5. | How the peak Demand forecast compares to actual Demand for the prior calendar year with due regard to any relevant weather-related variations (e.g., temperature, humidity, or wind speed) and, if applicable, how the assumptions and methods for future forecasts were adjusted. | MEDIUM | Retired | 2016-07-01 | 2016-09-30 | PC, BA
MOD-031-1 | Demand and Energy Data | R2. | Each Applicable Entity identified in a data request shall provide the data requested by its Planning Coordinator or Balancing Authority in accordance with the data request issued pursuant to Requirement R1. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Retired | 2016-07-01 | 2016-09-30 | TP, RP, DP
MOD-031-1 | Demand and Energy Data | R3. | The Planning Coordinator or the Balancing Authority shall provide the data collected under Requirement R2 to the applicable Regional Entity within 75 calendar days of receiving a request for such data, unless otherwise agreed upon by the parties. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Retired | 2016-07-01 | 2016-09-30 | PC, BA
MOD-031-1 | Demand and Energy Data | R4. | Any Applicable Entity shall, in response to a written request for the data included in parts 1.3-1.5 of Requirement R1 from a Planning Coordinator, Balancing Authority, Transmission Planner or Resource Planner with a demonstrated need for such data in order to conduct reliability assessments of the Bulk Electric System, provide or otherwise make available that data to the requesting entity. This requirement does not modify an entity’s obligation pursuant to Requirement R2 to respond to data requests issued by its Planning Coordinator or Balancing Authority pursuant to Requirement R1. Unless otherwise agreed upon, the Applicable Entity: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning]  shall provide the requested data within 45 calendar days of the written request, subject to part 4.1 of this requirement; and  shall not be required to alter the format in which it maintains or uses the data. | MEDIUM | Retired | 2016-07-01 | 2016-09-30 | TP, RP, DP
MOD-031-1 | Demand and Energy Data | R4.1. | If the Applicable Entity does not provide data requested under this requirement because (1) the requesting entity did not demonstrate a reliability need for the data; or (2) providing the data would conflict with the Applicable Entity’s confidentiality, regulatory, or security requirements, the Applicable Entity shall, within 30 calendar days of the written request, provide a written response to the requesting entity specifying the data that is not being provided and on what basis. | MEDIUM | Retired | 2016-07-01 | 2016-09-30 | TP, RP, DP
MOD-031-2 | Demand and Energy Data | R1. | Each Planning Coordinator or Balancing Authority that identifies a need for the collection of Total Internal Demand, Net Energy for Load, and Demand Side Management data shall develop and issue a data request to the applicable entities in its area. The data request shall include: [Violation Risk Factor: Medium] [Time Horizon: Long‐term Planning] | MEDIUM | Retired | 2016-10-01 | 2021-03-31 | PC, PA, BA
MOD-031-2 | Demand and Energy Data | R1.1. | A list of Transmission Planners, Balancing Authorities, Load Serving Entities, and Distribution Providers that are required to provide the data (“Applicable Entities”). | MEDIUM | Retired | 2016-10-01 | 2021-03-31 | PC, PA, BA
MOD-031-2 | Demand and Energy Data | R1.2. | A timetable for providing the data. (A minimum of 30 calendar days must be allowed for responding to the request). | MEDIUM | Retired | 2016-10-01 | 2021-03-31 | PC, PA, BA
MOD-031-2 | Demand and Energy Data | R1.3. | A request to provide any or all of the following actual data, as necessary: | MEDIUM | Retired | 2016-10-01 | 2021-03-31 | PC, PA, BA
MOD-031-2 | Demand and Energy Data | R1.3.1. | Integrated hourly Demands in megawatts for the prior calendar year. | MEDIUM | Retired | 2016-10-01 | 2021-03-31 | PC, PA, BA
MOD-031-2 | Demand and Energy Data | R1.3.2. | Monthly and annual integrated peak hour Demands in megawatts for the prior calendar year. | MEDIUM | Retired | 2016-10-01 | 2021-03-31 | PC, PA, BA
MOD-031-2 | Demand and Energy Data | R1.3.2.1. | If the annual peak hour actual Demand varies due to weatherrelated conditions (e.g., temperature, humidity or wind speed), the Applicable Entity shall also provide the weather normalized annual peak hour actual Demand for the prior calendar year. | MEDIUM | Retired | 2016-10-01 | 2021-03-31 | PC, PA, BA
MOD-031-2 | Demand and Energy Data | R1.3.3. | Monthly and annual Net Energy for Load in gigawatthours for the prior calendar year. | MEDIUM | Retired | 2016-10-01 | 2021-03-31 | PC, PA, BA
MOD-031-2 | Demand and Energy Data | R1.3.4. | Monthly and annual peak hour controllable and dispatchable Demand Side Management under the control or supervision of the System Operator in megawatts for the prior calendar year. Three values shall be reported for each hour: 1) the committed megawatts (the amount under control or supervision), 2) the dispatched megawatts (the amount, if any, activated for use by the System Operator), and 3) the realized megawatts (the amount of actual demand reduction). | MEDIUM | Retired | 2016-10-01 | 2021-03-31 | PC, PA, BA
MOD-031-2 | Demand and Energy Data | R1.4. | A request to provide any or all of the following forecast data, as necessary: | MEDIUM | Retired | 2016-10-01 | 2021-03-31 | PC, PA, BA
MOD-031-2 | Demand and Energy Data | R1.4.1. | Monthly peak hour forecast Total Internal Demands in megawatts for the next two calendar years. | MEDIUM | Retired | 2016-10-01 | 2021-03-31 | PC, PA, BA
MOD-031-2 | Demand and Energy Data | R1.4.2. | Monthly forecast Net Energy for Load in gigawatthours for the next two calendar years. | MEDIUM | Retired | 2016-10-01 | 2021-03-31 | PC, PA, BA
MOD-031-2 | Demand and Energy Data | R1.4.3. | Peak hour forecast Total Internal Demands (summer and winter) in megawatts for ten calendar years into the future. | MEDIUM | Retired | 2016-10-01 | 2021-03-31 | PC, PA, BA
MOD-031-2 | Demand and Energy Data | R1.4.4. | Annual forecast Net Energy for Load in gigawatthours for ten calendar years into the future. | MEDIUM | Retired | 2016-10-01 | 2021-03-31 | PC, PA, BA
MOD-031-2 | Demand and Energy Data | R1.4.5. | Total and available peak hour forecast of controllable and dispatchable Demand Side Management (summer and winter), in megawatts, under the control or supervision of the System Operator for ten calendar years into the future. | MEDIUM | Retired | 2016-10-01 | 2021-03-31 | PC, PA, BA
MOD-031-2 | Demand and Energy Data | R1.5. | A request to provide any or all of the following summary explanations, as necessary,: | MEDIUM | Retired | 2016-10-01 | 2021-03-31 | PC, PA, BA
MOD-031-2 | Demand and Energy Data | R1.5.1. | The assumptions and methods used in the development of aggregated Peak Demand and Net Energy for Load forecasts. | MEDIUM | Retired | 2016-10-01 | 2021-03-31 | PC, PA, BA
MOD-031-2 | Demand and Energy Data | R1.5.2. | The Demand and energy effects of controllable and dispatchable Demand Side Management under the control or supervision of the System Operator. | MEDIUM | Retired | 2016-10-01 | 2021-03-31 | PC, PA, BA
MOD-031-2 | Demand and Energy Data | R1.5.3. | How Demand Side Management is addressed in the forecasts of its Peak Demand and annual Net Energy for Load. | MEDIUM | Retired | 2016-10-01 | 2021-03-31 | PC, PA, BA
MOD-031-2 | Demand and Energy Data | R1.5.4. | How the controllable and dispatchable Demand Side Management forecast compares to actual controllable and dispatchable Demand Side Management for the prior calendar year and, if applicable, how the assumptions and methods for future forecasts were adjusted. | MEDIUM | Retired | 2016-10-01 | 2021-03-31 | PC, PA, BA
MOD-031-2 | Demand and Energy Data | R1.5.5. | How the peak Demand forecast compares to actual Demand for the prior calendar year with due regard to any relevant weather‐related variations (e.g., temperature, humidity, or wind speed) and, if applicable, how the assumptions and methods for future forecasts were adjusted. | MEDIUM | Retired | 2016-10-01 | 2021-03-31 | PC, PA, BA
MOD-031-2 | Demand and Energy Data | R2. | Each Applicable Entity identified in a data request shall provide the data requested by its Planning Coordinator or Balancing Authority in accordance with the data request issued pursuant to Requirement R1. [Violation Risk Factor: Medium] [Time Horizon: Long‐term Planning] | MEDIUM | Retired | 2016-10-01 | 2021-03-31 | RP, PC, PA, DP, BA
MOD-031-2 | Demand and Energy Data | R3. | The Planning Coordinator or the Balancing Authority shall provide the data listed under Requirement R1 Parts 1.3 through 1.5 for their area to the applicable Regional Entity within 75 calendar days of receiving a request for such data, unless otherwise agreed upon by the parties. [Violation Risk Factor: Medium] [Time Horizon: Long‐term Planning] | MEDIUM | Retired | 2016-10-01 | 2021-03-31 | PC, PA, BA
MOD-031-2 | Demand and Energy Data | R4. | Any Applicable Entity shall, in response to a written request for the data included in parts 1.3‐1.5 of Requirement R1 from a Planning Coordinator, Balancing Authority, Transmission Planner or Resource Planner with a demonstrated need for such data in order to conduct reliability assessments of the Bulk Electric System, provide or otherwise make available that data to the requesting entity. This requirement does not modify an entity’s obligation pursuant to Requirement R2 to respond to data requests issued by its Planning Coordinator or Balancing Authority pursuant to Requirement R1. Unless otherwise agreed upon, the Applicable Entity: [Violation Risk Factor: Medium] [Time Horizon: Long‐term Planning] ● shall not be required to alter the format in which it maintains or uses the data; ● shall provide the requested data within 45 calendar days of the written request, subject to part 4.1 of this requirement; unless providing the requested data would conflict with the Applicable Entity’s confidentialit , regulatory, or security requirements | MEDIUM | Retired | 2016-10-01 | 2021-03-31 | RP, PC, PA, DP, BA
MOD-031-2 | Demand and Energy Data | R4.1. | If the Applicable Entity does not provide data requested because (1) the requesting entity did not demonstrate a reliability need for the data; or (2) providing the data would conflict with the Applicable Entity’s confidentiality, regulatory, or security requirements, the Applicable Entity shall, within 30 calendar days of the written request, provide a written response to the requesting entity specifying the data that is not being provided and on what basis. | MEDIUM | Retired | 2016-10-01 | 2021-03-31 | RP, PC, PA, DP, BA
MOD-031-3 | Demand and Energy Data | R1. | Each Planning Coordinator or Balancing Authority that identifies a need for the collection of Total Internal Demand, Net Energy for Load, and Demand Side Management data shall develop and issue a data request to the applicable entities in its area. The data request shall include: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2021-04-01 |  | DP, RP, BA, TP, PC
MOD-031-3 | Demand and Energy Data | R1.1. | A list of Transmission Planners, Balancing Authorities, and Distribution Providers that are required to provide the data (“Applicable Entities”). | MEDIUM | Effective | 2021-04-01 |  | DP, RP, BA, TP, PA
MOD-031-3 | Demand and Energy Data | R1.2. | A timetable for providing the data. (A minimum of 30 calendar days must be allowed for responding to the request). | MEDIUM | Effective | 2021-04-01 |  | DP, RP, BA, TP, PC
MOD-031-3 | Demand and Energy Data | R1.3. | A request to provide any or all of the following actual data, as necessary: | MEDIUM | Effective | 2021-04-01 |  | DP, RP, BA, TP, PC
MOD-031-3 | Demand and Energy Data | R1.3.1. | Integrated hourly Demands in megawatts for the prior calendar year. | MEDIUM | Effective | 2021-04-01 |  | DP, RP, BA, TP, PC
MOD-031-3 | Demand and Energy Data | R1.3.2. | Monthly and annual integrated peak hour Demands in megawatts for the prior calendar year. | MEDIUM | Effective | 2021-04-01 |  | BA, TP, PC, DP, RP
MOD-031-3 | Demand and Energy Data | R1.3.2.1. | If the annual peak hour actual Demand varies due to weather-related conditions (e.g., temperature, humidity or wind speed), the Applicable Entity shall also provide the weather normalized annual peak hour actual Demand for the prior calendar year. | MEDIUM | Effective | 2021-04-01 |  | DP, RP, BA, TP, PC
MOD-031-3 | Demand and Energy Data | R1.3.3. | Monthly and annual Net Energy for Load in gigawatt hours for the prior calendar year. | MEDIUM | Effective | 2021-04-01 |  | DP, RP, BA, TP, PC
MOD-031-3 | Demand and Energy Data | R1.3.4. | Monthly and annual peak hour controllable and dispatchable Demand Side Management under the control or supervision of the System Operator in megawatts for the prior calendar year. Three values shall be reported for each hour: 1) the committed megawatts (the amount under control or supervision), 2) the dispatched megawatts (the amount, if any, activated for use by the System Operator), | MEDIUM | Effective | 2021-04-01 |  | DP, RP, BA, TP, PC
MOD-031-3 | Demand and Energy Data | R1.4. | A request to provide any or all of the following forecast data, as necessary: | MEDIUM | Effective | 2021-04-01 |  | DP, RP, BA, TP, PC
MOD-031-3 | Demand and Energy Data | R1.4.1. | Monthly peak hour forecast Total Internal Demands in megawatts for the next two calendar years. | MEDIUM | Effective | 2021-04-01 |  | DP, RP, BA, TP, PC
MOD-031-3 | Demand and Energy Data | R1.4.2. | Monthly forecast Net Energy for Load in gigawatthours for the next two calendar years. | MEDIUM | Effective | 2021-04-01 |  | DP, RP, BA, TP, PC
MOD-031-3 | Demand and Energy Data | R1.4.3. | Peak hour forecast Total Internal Demands (summer and winter) in megawatts for ten calendar years into the future. | MEDIUM | Effective | 2021-04-01 |  | DP, RP, BA, TP, PC
MOD-031-3 | Demand and Energy Data | R1.4.4. | Annual forecast Net Energy for Load in gigawatthours for ten calendar years into the future. | MEDIUM | Effective | 2021-04-01 |  | DP, RP, BA, TP, PC
MOD-031-3 | Demand and Energy Data | R1.4.5. | Total and available peak hour forecast of controllable and dispatchable Demand Side Management (summer and winter), in megawatts, under the control or supervision of the System Operator for ten calendar years into the future. | MEDIUM | Effective | 2021-04-01 |  | DP, RP, BA, TP, PC
MOD-031-3 | Demand and Energy Data | R1.5. | A request to provide any or all of the following summary explanations, as necessary,: | MEDIUM | Effective | 2021-04-01 |  | DP, RP, BA, TP, PC
MOD-031-3 | Demand and Energy Data | R1.5.1. | The assumptions and methods used in the development of aggregated Peak Demand and Net Energy for Load forecasts. | MEDIUM | Effective | 2021-04-01 |  | DP, RP, BA, TP, PC
MOD-031-3 | Demand and Energy Data | R1.5.2. | The Demand and energy effects of controllable and dispatchable Demand Side Management under the control or supervision of the System Operator. | MEDIUM | Effective | 2021-04-01 |  | DP, RP, BA, TP, PC
MOD-031-3 | Demand and Energy Data | R1.5.3. | How Demand Side Management is addressed in the forecasts of its Peak Demand and annual Net Energy for Load. | MEDIUM | Effective | 2021-04-01 |  | DP, RP, BA, TP, PC
MOD-031-3 | Demand and Energy Data | R1.5.4. | How the controllable and dispatchable Demand Side Management forecast compares to actual controllable and dispatchable Demand Side Management for the prior calendar year and, if applicable, how the assumptions and methods for future forecasts were adjusted. | MEDIUM | Effective | 2021-04-01 |  | DP, RP, BA, TP, PC
MOD-031-3 | Demand and Energy Data | R1.5.5. | How the peak Demand forecast compares to actual Demand for the prior calendar year with due regard to any relevant weather-related variations (e.g., temperature, humidity, or wind speed) and, if applicable, how the assumptions and methods for future forecasts were adjusted. | MEDIUM | Effective | 2021-04-01 |  | DP, RP, BA, TP, PC
MOD-031-3 | Demand and Energy Data | R2. | Each Applicable Entity identified in a data request shall provide the data requested by its Planning Coordinator or Balancing Authority in accordance with the data request issued pursuant to Requirement R1. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2021-04-01 |  | DP, RP, BA, TP, PC
MOD-031-3 | Demand and Energy Data | R3. | The Planning Coordinator or the Balancing Authority shall provide the data listed under Requirement R1 Parts 1.3 through 1.5 for their area to the applicable Regional Entity within 75 calendar days of receiving a request for such data, unless otherwise agreed upon by the parties. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2021-04-01 |  | DP, RP, BA, TP, PC
MOD-031-3 | Demand and Energy Data | R4. | Any Applicable Entity shall, in response to a written request for the data included in parts 1.3-1.5 of Requirement R1 from a Planning Coordinator, Balancing Authority, Transmission Planner or Resource Planner with a demonstrated need for such data in order to conduct reliability assessments of the Bulk Electric System, provide or otherwise make available that data to the requesting entity. This requirement does not modify an entity’s obligation pursuant to Requirement R2 to respond to data requests issued by its Planning Coordinator or Balancing Authority pursuant to Requirement R1. Unless otherwise agreed upon, the Applicable Entity: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] • shall not be required to alter the format in which it maintains or uses the data; • shall provide the requested data within 45 calendar days of the written request, subject to part 4.1 of this requirement; unless providing the requested data would conflict with the Applicable Entity’s confidentiality, regulatory, or security requirements | MEDIUM | Effective | 2021-04-01 |  | DP, RP, BA, TP, PC
MOD-031-3 | Demand and Energy Data | R4.1. | If the Applicable Entity does not provide data requested because (1) the requesting entity did not demonstrate a reliability need for the data; or (2) providing the data would conflict with the Applicable Entity’s confidentiality, regulatory, or security requirements, the Applicable Entity shall, within 30 calendar days of the written request, provide a written response to the requesting entity specifying the data that is not being provided and on what basis. | MEDIUM | Effective | 2021-04-01 |  | DP, RP, BA, TP, PC
MOD-032-1 | Data for Power System Modeling and Analysis | R1. | Each Planning Coordinator and each of its Transmission Planners shall jointly develop steady‐state, dynamics, and short circuit Real-Time Applications data requirements and reporting procedures for the Planning Coordinator’s planning area that include: [Violation Risk Factor: Lower] [Time Horizon: Long‐term Planning] | LOWER | Effective | 2015-07-01 |  | TP, PC
MOD-032-1 | Data for Power System Modeling and Analysis | R1.1. | The data listed in Attachment 1. | LOWER | Effective | 2015-07-01 |  | TP, PC
MOD-032-1 | Data for Power System Modeling and Analysis | R1.2. | Specifications of the following items consistent with procedures for building the Interconnection‐wide case(s): | LOWER | Effective | 2015-07-01 |  | TP, PC
MOD-032-1 | Data for Power System Modeling and Analysis | R1.2.1. | Data format; | LOWER | Effective | 2015-07-01 |  | TP, PC
MOD-032-1 | Data for Power System Modeling and Analysis | R1.2.2. | Level of detail to which equipment shall be modeled; | LOWER | Effective | 2015-07-01 |  | TP, PC
MOD-032-1 | Data for Power System Modeling and Analysis | R1.2.3. | Case types or scenarios to be modeled; and | LOWER | Effective | 2015-07-01 |  | TP, PC
MOD-032-1 | Data for Power System Modeling and Analysis | R1.2.4. | A schedule for submission of data at least once every 13 calendar months. | LOWER | Effective | 2015-07-01 |  | TP, PC
MOD-032-1 | Data for Power System Modeling and Analysis | R1.3. | Specifications for distribution or posting of the data requirements and reporting procedures so that they are available to those entities responsible for providing the data. | LOWER | Effective | 2015-07-01 |  | TP, PC
MOD-032-1 | Data for Power System Modeling and Analysis | R2. | Each Balancing Authority, Generator Owner, Load Serving Entity, Resource Planner, Transmission Owner, and Transmission Service Provider shall provide steady‐state, dynamics, and short circuit Real-Time Applications data to its Transmission Planner(s) and Planning Coordinator(s) according to the data requirements and reporting procedures developed by its Planning Coordinator and Transmission Planner in Requirement R1. For data that has not changed since the last submission, a written confirmation that the data has not changed is sufficient. [Violation Risk Factor: Medium] [Time Horizon: Long‐term Planning] | LOWER | Effective | 2015-07-01 |  | TSP, TO, RP, GO, BA
MOD-032-1 | Data for Power System Modeling and Analysis | R3. | Upon receipt of written notification from its Planning Coordinator or Transmission Planner regarding technical concerns with the data submitted under Requirement R2, including the technical basis or reason for the technical concerns, each notified Balancing Authority, Generator Owner, Load Serving Entity, Resource Planner, Transmission Owner, or Transmission Service Provider shall respond to the notifying Planning Coordinator or Transmission Planner as follows: [Violation Risk Factor: Lower] [Time Horizon: Long‐term Planning] | LOWER | Effective | 2015-07-01 |  | TSP, TO, RP, GO, BA
MOD-032-1 | Data for Power System Modeling and Analysis | R3.1. | Provide either updated data or an explanation with a technical basis for maintaining the current data; | LOWER | Effective | 2015-07-01 |  | TSP, TO, RP, GO, BA
MOD-032-1 | Data for Power System Modeling and Analysis | R3.2. | Provide the response within 90 calendar days of receipt, unless a longer time period is agreed upon by the notifying Planning Coordinator or Transmission Planner. | LOWER | Effective | 2015-07-01 |  | TSP, TO, RP, GO, BA
MOD-032-1 | Data for Power System Modeling and Analysis | R4. | Each Planning Coordinator shall make available models for its planning area reflecting data provided to it under Requirement R2 to the Electric Reliability Organization (ERO) or its designee to support creation of the Interconnection‐wide case(s) that includes the Planning Coordinator’s planning area. [Violation Risk Factor: Medium] [Time Horizon: Long‐term Planning] | LOWER | Effective | 2015-07-01 |  | PC
MOD-033-1 | Steady‐State and Dynamic System Model Validation | R1. | Each Planning Coordinator shall implement a documented data validation process that includes the following attributes: [Violation Risk Factor: Medium] [Time Horizon: Long‐term Planning] | MEDIUM | Retired | 2017-07-01 | 2021-03-31 | PC
MOD-033-1 | Steady‐State and Dynamic System Model Validation | R1.1. | Comparison of the performance of the Planning Coordinator’s portion of the existing system in a planning power flow model to actual system behavior, represented by a state estimator case or other Real‐time data sources, at least once every 24 calendar months through simulation; | MEDIUM | Retired | 2017-07-01 | 2021-03-31 | PC
MOD-033-1 | Steady‐State and Dynamic System Model Validation | R1.2. | Comparison of the performance of the Planning Coordinator’s portion of the existing system in a planning dynamic model to actual system response, through simulation of a dynamic local event, at least once every 24 calendar months (use a dynamic local event that occurs within 24 calendar months of the last dynamic local event used in comparison, and complete each comparison within 24 calendar months of the dynamic local event). If no dynamic local event occurs within the 24 calendar months, use the next dynamic local event that occurs; | MEDIUM | Retired | 2017-07-01 | 2021-03-31 | PC
MOD-033-1 | Steady‐State and Dynamic System Model Validation | R1.3. | Guidelines the Planning Coordinator will use to determine unacceptable differences in performance under Part 1.1 or 1.2; and | MEDIUM | Retired | 2017-07-01 | 2021-03-31 | PC
MOD-033-1 | Steady‐State and Dynamic System Model Validation | R1.4. | Guidelines to resolve the unacceptable differences in performance identified under Part 1.3. | MEDIUM | Retired | 2017-07-01 | 2021-03-31 | PC
MOD-033-1 | Steady‐State and Dynamic System Model Validation | R2. | Each Reliability Coordinator and Transmission Operator shall provide actual system behavior data (or a written response that it does not have the requested data) to any Planning Coordinator performing validation under Requirement R1 within 30 calendar days of a written request, such as, but not limited to, state estimator case or other Real‐time data (including disturbance data recordings) necessary for actual system response validation. [Violation Risk Factor: Lower] [Time Horizon: Long‐term Planning] | MEDIUM | Retired | 2017-07-01 | 2021-03-31 | TOP, RC
MOD-033-2 | Steady-State and Dynamic System Model Validation | R1. | Each Planning Coordinator shall implement a documented data validation process that includes the following attributes: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2021-04-01 |  | TOP, RC, PC
MOD-033-2 | Steady-State and Dynamic System Model Validation | R1.1. | Comparison of the performance of the Planning Coordinator’s portion of the existing system in a planning power flow model to actual system behavior, represented by a state estimator case or other Real-time data sources, at least once every 24 calendar months through simulation; | MEDIUM | Effective | 2021-04-01 |  | TOP, RC, PC
MOD-033-2 | Steady-State and Dynamic System Model Validation | R1.2. | Comparison of the performance of the Planning Coordinator’s portion of the existing system in a planning dynamic model to actual system response, through simulation of a dynamic local event, at least once every 24 calendar months (use a dynamic local event that occurs within 24 calendar months of the last dynamic local event used in comparison, and complete each comparison within 24 calendar months of the dynamic local event). If no dynamic local event occurs within the 24 calendar months, use the next dynamic local event that occurs; | MEDIUM | Effective | 2021-04-01 |  | TOP, RC, PC
MOD-033-2 | Steady-State and Dynamic System Model Validation | R1.3. | Guidelines the Planning Coordinator will use to determine unacceptable differences in performance under Part 1.1 or 1.2; and | MEDIUM | Effective | 2021-04-01 |  | TOP, RC, PC
MOD-033-2 | Steady-State and Dynamic System Model Validation | R1.4. | Guidelines to resolve the unacceptable differences in performance identified under Part 1.3. | MEDIUM | Effective | 2021-04-01 |  | TOP, RC, PC
MOD-033-2 | Steady-State and Dynamic System Model Validation | R2. | Each Reliability Coordinator and Transmission Operator shall provide actual system behavior data (or a written response that it does not have the requested data) to any Planning Coordinator performing validation under Requirement R1 within 30 calendar days of a written request, such as, but not limited to, state estimator case or other Real-time data (including disturbance data recordings) necessary for actual system response validation. [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2021-04-01 |  | TOP, RC, PC
NUC-001-2.1 | Nuclear Plant Interface Coordination | R1. | The Nuclear Plant Generator Operator shall provide the proposed NPIRs in writing to the applicable Transmission Entities and shall verify receipt [Risk Factor: Lower] | LOWER | Retired | 2013-04-01 | 2016-03-31 | GOP
NUC-001-2.1 | Nuclear Plant Interface Coordination | R2. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall have in effect one or more Agreements1 that include mutually agreed to NPIRs and document how the Nuclear Plant Generator Operator and the applicable Transmission Entities shall address and implement these NPIRs. [Risk Factor: Medium] | MEDIUM | Retired | 2013-04-01 | 2016-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1 | Nuclear Plant Interface Coordination | R3. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall incorporate the NPIRs into their planning analyses of the electric system and shall communicate the results of these analyses to the Nuclear Plant Generator Operator. [Risk Factor: Medium] | MEDIUM | Retired | 2013-04-01 | 2016-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1 | Nuclear Plant Interface Coordination | R3. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall incorporate the NPIRs into their planning analyses of the electric system and shall communicate the results of these analyses to the Nuclear Plant Generator Operator. [Risk Factor: Medium] | MEDIUM | Retired | 2013-04-01 | 2016-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1 | Nuclear Plant Interface Coordination | R4. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall: [Risk Factor: High] | HIGH | Retired | 2013-04-01 | 2016-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1 | Nuclear Plant Interface Coordination | R4. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall: [Risk Factor: High] | HIGH | Retired | 2013-04-01 | 2016-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1 | Nuclear Plant Interface Coordination | R4. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall: [Risk Factor: High] | HIGH | Retired | 2013-04-01 | 2016-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1 | Nuclear Plant Interface Coordination | R4.1. | Incorporate the NPIRs into their operating analyses of the electric system. | No Individual VRF Assigned | Retired | 2013-04-01 | 2016-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1 | Nuclear Plant Interface Coordination | R4.1. | Incorporate the NPIRs into their operating analyses of the electric system. | No Individual VRF Assigned | Retired | 2013-04-01 | 2016-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1 | Nuclear Plant Interface Coordination | R4.1. | Incorporate the NPIRs into their operating analyses of the electric system. | No Individual VRF Assigned | Retired | 2013-04-01 | 2016-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1 | Nuclear Plant Interface Coordination | R4.2. | Operate the electric system to meet the NPIRs. | No Individual VRF Assigned | Retired | 2013-04-01 | 2016-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1 | Nuclear Plant Interface Coordination | R4.3. | Inform the Nuclear Plant Generator Operator when the ability to assess the operation of the electric system affecting NPIRs is lost. | No Individual VRF Assigned | Retired | 2013-04-01 | 2016-03-31 | TSP, TP, TOP, TO, RC, PC, PA, GOP, GO, DP, BA
NUC-001-2.1 | Nuclear Plant Interface Coordination | R5. | The Nuclear Plant Generator Operator shall operate per the Agreements developed in accordance with this standard. [Risk Factor: High] | HIGH | Retired | 2013-04-01 | 2016-03-31 | GOP
NUC-001-2.1 | Nuclear Plant Interface Coordination | R6. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities and the Nuclear Plant Generator Operator shall coordinate outages and maintenance activities which affect the NPIRs. [Risk Factor: Medium] | MEDIUM | Retired | 2013-04-01 | 2016-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1 | Nuclear Plant Interface Coordination | R7. | Per the Agreements developed in accordance with this standard, the Nuclear Plant Generator Operator shall inform the applicable Transmission Entities of actual or proposed changes to nuclear plant design, configuration, operations, limits, Protection Systems, or capabilities that may impact the ability of the electric system to meet the NPIRs. [Risk Factor: High] | HIGH | Retired | 2013-04-01 | 2016-03-31 | GOP
NUC-001-2.1 | Nuclear Plant Interface Coordination | R8. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall inform the Nuclear Plant Generator Operator of actual or proposed changes to electric system design, configuration, operations, limits, Protection Systems, or capabilities that may impact the ability of the electric system to meet the NPIRs. [Risk Factor: High] | HIGH | Retired | 2013-04-01 | 2016-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1 | Nuclear Plant Interface Coordination | R8. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall inform the Nuclear Plant Generator Operator of actual or proposed changes to electric system design, configuration, operations, limits, Protection Systems, or capabilities that may impact the ability of the electric system to meet the NPIRs. [Risk Factor: High] | HIGH | Retired | 2013-04-01 | 2016-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1 | Nuclear Plant Interface Coordination | R8. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall inform the Nuclear Plant Generator Operator of actual or proposed changes to electric system design, configuration, operations, limits, Protection Systems, or capabilities that may impact the ability of the electric system to meet the NPIRs. [Risk Factor: High] | HIGH | Retired | 2013-04-01 | 2016-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1 | Nuclear Plant Interface Coordination | R8. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall inform the Nuclear Plant Generator Operator of actual or proposed changes to electric system design, configuration, operations, limits, Protection Systems, or capabilities that may impact the ability of the electric system to meet the NPIRs. [Risk Factor: High] | HIGH | Retired | 2013-04-01 | 2016-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1 | Nuclear Plant Interface Coordination | R9. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall include, as a minimum, the following elements within the agreement(s) identified in R2: [Risk Factor: Medium] | MEDIUM | Retired | 2013-04-01 | 2016-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1 | Nuclear Plant Interface Coordination | R9. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall include, as a minimum, the following elements within the agreement(s) identified in R2: [Risk Factor: Medium] | MEDIUM | Retired | 2013-04-01 | 2016-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1 | Nuclear Plant Interface Coordination | R9. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall include, as a minimum, the following elements within the agreement(s) identified in R2: [Risk Factor: Medium] | MEDIUM | Retired | 2013-04-01 | 2016-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1 | Nuclear Plant Interface Coordination | R9.2. | Technical requirements and analysis: | No Individual VRF Assigned | Retired | 2013-04-01 | 2016-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1 | Nuclear Plant Interface Coordination | R9.2.1. | Identification of parameters, limits, configurations, and operating scenarios included in the NPIRs and, as applicable, procedures for providing any specific data not provided within the agreement. | No Individual VRF Assigned | Retired | 2013-04-01 | 2016-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1 | Nuclear Plant Interface Coordination | R9.2.2. | Identification of facilities, components, and configuration restrictions that are essential for meeting the NPIRs. | No Individual VRF Assigned | Retired | 2013-04-01 | 2016-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1 | Nuclear Plant Interface Coordination | R9.2.3. | Types of planning and operational analyses performed specifically to support the NPIRs, including the frequency of studies and types of Contingencies and scenarios required. | No Individual VRF Assigned | Retired | 2013-04-01 | 2016-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1 | Nuclear Plant Interface Coordination | R9.3. | Operations and maintenance coordination: | No Individual VRF Assigned | Retired | 2013-04-01 | 2016-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1 | Nuclear Plant Interface Coordination | R9.3. | Operations and maintenance coordination: | No Individual VRF Assigned | Retired | 2013-04-01 | 2016-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1 | Nuclear Plant Interface Coordination | R9.3. | Operations and maintenance coordination: | No Individual VRF Assigned | Retired | 2013-04-01 | 2016-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1 | Nuclear Plant Interface Coordination | R9.3.1. | Designation of ownership of electrical facilities at the interface between the electric system and the nuclear plant and responsibilities for operational control coordination and maintenance of these facilities. | No Individual VRF Assigned | Retired | 2013-04-01 | 2016-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1 | Nuclear Plant Interface Coordination | R9.3.2. | Identification of any maintenance requirements for equipment not owned or controlled by the Nuclear Plant Generator Operator that are necessary to meet the NPIRs. | No Individual VRF Assigned | Retired | 2013-04-01 | 2016-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1 | Nuclear Plant Interface Coordination | R9.3.3. | Coordination of testing, calibration and maintenance of on-site and off-site power supply systems and related components. | No Individual VRF Assigned | Retired | 2013-04-01 | 2016-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1 | Nuclear Plant Interface Coordination | R9.3.4. | Provisions to address mitigating actions needed to avoid violating NPIRs and to address periods when responsible Transmission Entity loses the ability to assess the capability of the electric system to meet the NPIRs. These provisions shall include responsibility to notify the Nuclear Plant Generator Operator within a specified time frame. | No Individual VRF Assigned | Retired | 2013-04-01 | 2016-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1 | Nuclear Plant Interface Coordination | R9.3.5. | Provision for considering, within the restoration process, the requirements and urgency of a nuclear plant that has lost all off-site and on-site AC power. | No Individual VRF Assigned | Retired | 2013-04-01 | 2016-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1 | Nuclear Plant Interface Coordination | R9.3.6. | Coordination of physical and cyber security protection of the Bulk Electric System at the nuclear plant interface to ensure each asset is covered under at least one entity’s plan. | No Individual VRF Assigned | Retired | 2013-04-01 | 2016-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1 | Nuclear Plant Interface Coordination | R9.3.7. | Coordination of the NPIRs with transmission system Special Protection Systems and underfrequency and undervoltage load shedding programs. | No Individual VRF Assigned | Retired | 2013-04-01 | 2016-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1 | Nuclear Plant Interface Coordination | R9.4. | Communications and training: | No Individual VRF Assigned | Retired | 2013-04-01 | 2016-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1 | Nuclear Plant Interface Coordination | R9.4. | Communications and training: | No Individual VRF Assigned | Retired | 2013-04-01 | 2016-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1 | Nuclear Plant Interface Coordination | R9.4.1. | Provisions for communications between the Nuclear Plant Generator Operator and Transmission Entities, including communications protocols, notification time requirements, and definitions of terms. | No Individual VRF Assigned | Retired | 2013-04-01 | 2016-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1 | Nuclear Plant Interface Coordination | R9.4.2. | Provisions for coordination during an off-normal or emergency event affecting the NPIRs, including the need to provide timely information explaining the event, an estimate of when the system will be returned to a normal state, and the actual time the system is returned to normal. | No Individual VRF Assigned | Retired | 2013-04-01 | 2016-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1 | Nuclear Plant Interface Coordination | R9.4.3. | Provisions for coordinating investigations of causes of unplanned events affecting the NPIRs and developing solutions to minimize future risk of such events. | No Individual VRF Assigned | Retired | 2013-04-01 | 2016-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1 | Nuclear Plant Interface Coordination | R9.4.4. | Provisions for supplying information necessary to report to government agencies, as related to NPIRs. | No Individual VRF Assigned | Retired | 2013-04-01 | 2016-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1 | Nuclear Plant Interface Coordination | R9.4.5. | Provisions for personnel training, as related to NPIRs. | No Individual VRF Assigned | Retired | 2013-04-01 | 2016-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R1. | The Nuclear Plant Generator Operator shall provide the proposed NPIRs in writing to the applicable Transmission Entities and shall verify receipt [Risk Factor: Lower] | LOWER | Never Came Into Effect in Ontario |  |  | GOP
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R2. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall have in effect one or more Agreements1 that include mutually agreed to NPIRs and document how the Nuclear Plant Generator Operator and the applicable Transmission Entities shall address and implement these NPIRs. [Risk Factor: Medium] | MEDIUM | Never Came Into Effect in Ontario |  |  | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R3. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall incorporate the NPIRs into their planning analyses of the electric system and shall communicate the results of these analyses to the Nuclear Plant Generator Operator. [Risk Factor: Medium] | MEDIUM | Never Came Into Effect in Ontario |  |  | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R3. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall incorporate the NPIRs into their planning analyses of the electric system and shall communicate the results of these analyses to the Nuclear Plant Generator Operator. [Risk Factor: Medium] | MEDIUM | Never Came Into Effect in Ontario |  |  | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R4. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall: [Risk Factor: High] | HIGH | Never Came Into Effect in Ontario |  |  | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R4. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall: [Risk Factor: High] | HIGH | Never Came Into Effect in Ontario |  |  | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R4. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall: [Risk Factor: High] | HIGH | Never Came Into Effect in Ontario |  |  | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R4.1. | Incorporate the NPIRs into their operating analyses of the electric system. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R4.1. | Incorporate the NPIRs into their operating analyses of the electric system. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R4.1. | Incorporate the NPIRs into their operating analyses of the electric system. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R4.2. | Operate the electric system to meet the NPIRs. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R4.3. | Inform the Nuclear Plant Generator Operator when the ability to assess the operation of the electric system affecting NPIRs is lost. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TSP, TP, TOP, TO, RC, PC, PA, GOP, GO, DP, BA
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R5. | The Nuclear Plant Generator Operator shall operate per the Agreements developed in accordance with this standard. [Risk Factor: High] | HIGH | Never Came Into Effect in Ontario |  |  | GOP
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R6. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities and the Nuclear Plant Generator Operator shall coordinate outages and maintenance activities which affect the NPIRs. [Risk Factor: Medium] | MEDIUM | Never Came Into Effect in Ontario |  |  | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R7. | Per the Agreements developed in accordance with this standard, the Nuclear Plant Generator Operator shall inform the applicable Transmission Entities of actual or proposed changes to nuclear plant design, configuration, operations, limits, Protection Systems, or capabilities that may impact the ability of the electric system to meet the NPIRs. [Risk Factor: High] | HIGH | Never Came Into Effect in Ontario |  |  | GOP
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R8. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall inform the Nuclear Plant Generator Operator of actual or proposed changes to electric system design, configuration, operations, limits, Protection Systems, or capabilities that may impact the ability of the electric system to meet the NPIRs. [Risk Factor: High] | HIGH | Never Came Into Effect in Ontario |  |  | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R8. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall inform the Nuclear Plant Generator Operator of actual or proposed changes to electric system design, configuration, operations, limits, Protection Systems, or capabilities that may impact the ability of the electric system to meet the NPIRs. [Risk Factor: High] | HIGH | Never Came Into Effect in Ontario |  |  | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R8. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall inform the Nuclear Plant Generator Operator of actual or proposed changes to electric system design, configuration, operations, limits, Protection Systems, or capabilities that may impact the ability of the electric system to meet the NPIRs. [Risk Factor: High] | HIGH | Never Came Into Effect in Ontario |  |  | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R8. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall inform the Nuclear Plant Generator Operator of actual or proposed changes to electric system design, configuration, operations, limits, Protection Systems, or capabilities that may impact the ability of the electric system to meet the NPIRs. [Risk Factor: High] | HIGH | Never Came Into Effect in Ontario |  |  | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall include, as a minimum, the following elements within the agreement(s) identified in R2: [Risk Factor: Medium] | MEDIUM | Never Came Into Effect in Ontario |  |  | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall include, as a minimum, the following elements within the agreement(s) identified in R2: [Risk Factor: Medium] | MEDIUM | Never Came Into Effect in Ontario |  |  | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall include, as a minimum, the following elements within the agreement(s) identified in R2: [Risk Factor: Medium] | MEDIUM | Never Came Into Effect in Ontario |  |  | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.1. | Administrative elements: | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.1. | Administrative elements: | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.1.1. | Definitions of key terms used in the agreement. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.1.2. | Names of the responsible entities, organizational relationships, and responsibilities related to the NPIRs. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.1.3. | A requirement to review the agreement(s) at least every three years. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.1.4. | A dispute resolution mechanism. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.2. | Technical requirements and analysis: | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.2.1. | Identification of parameters, limits, configurations, and operating scenarios included in the NPIRs and, as applicable, procedures for providing any specific data not provided within the agreement. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.2.2. | Identification of facilities, components, and configuration restrictions that are essential for meeting the NPIRs. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.2.3. | Types of planning and operational analyses performed specifically to support the NPIRs, including the frequency of studies and types of Contingencies and scenarios required. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.3. | Operations and maintenance coordination: | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.3. | Operations and maintenance coordination: | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.3. | Operations and maintenance coordination: | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.3.1. | Designation of ownership of electrical facilities at the interface between the electric system and the nuclear plant and responsibilities for operational control coordination and maintenance of these facilities. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.3.2. | Identification of any maintenance requirements for equipment not owned or controlled by the Nuclear Plant Generator Operator that are necessary to meet the NPIRs. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.3.3. | Coordination of testing, calibration and maintenance of on-site and off-site power supply systems and related components. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.3.4. | Provisions to address mitigating actions needed to avoid violating NPIRs and to address periods when responsible Transmission Entity loses the ability to assess the capability of the electric system to meet the NPIRs. These provisions shall include responsibility to notify the Nuclear Plant Generator Operator within a specified time frame. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.3.5. | Provision for considering, within the restoration process, the requirements and urgency of a nuclear plant that has lost all off-site and on-site AC power. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.3.6. | Coordination of physical and cyber security protection of the Bulk Electric System at the nuclear plant interface to ensure each asset is covered under at least one entity’s plan. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.3.7. | Coordination of the NPIRs with transmission system Remedial Action Schemes and underfrequency and undervoltage load shedding programs. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.4. | Communications and training: | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.4. | Communications and training: | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.4.1. | Provisions for communications between the Nuclear Plant Generator Operator and Transmission Entities, including communications protocols, notification time requirements, and definitions of terms. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.4.2. | Provisions for coordination during an off-normal or emergency event affecting the NPIRs, including the need to provide timely information explaining the event, an estimate of when the system will be returned to a normal state, and the actual time the system is returned to normal. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.4.3. | Provisions for coordinating investigations of causes of unplanned events affecting the NPIRs and developing solutions to minimize future risk of such events. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.4.4. | Provisions for supplying information necessary to report to government agencies, as related to NPIRs. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.4.5. | Provisions for personnel training, as related to NPIRs. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-3 | Nuclear Plant Interface Coordination | R1. | The Nuclear Plant Generator Operator shall provide the proposed NPIRs in writing to the applicable Transmission Entities and shall verify receipt. | MEDIUM | Retired | 2016-04-01 | 2021-03-31 | GOP
NUC-001-3 | Nuclear Plant Interface Coordination | R2. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall have in effect one or more Agreements that include mutually agreed to NPIRs and document how the Nuclear Plant Generator Operator and the applicable Transmission Entities shall address and implement these NPIRs. | MEDIUM | Retired | 2016-04-01 | 2021-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-3 | Nuclear Plant Interface Coordination | R3. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall incorporate the NPIRs into their planning analyses of the electric system and shall communicate the results of these analyses to the Nuclear Plant Generator Operator.: | MEDIUM | Retired | 2016-04-01 | 2021-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-3 | Nuclear Plant Interface Coordination | R3. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall incorporate the NPIRs into their planning analyses of the electric system and shall communicate the results of these analyses to the Nuclear Plant Generator Operator.: | MEDIUM | Retired | 2016-04-01 | 2021-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-3 | Nuclear Plant Interface Coordination | R4. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall | HIGH | Retired | 2016-04-01 | 2021-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-3 | Nuclear Plant Interface Coordination | R4. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall | HIGH | Retired | 2016-04-01 | 2021-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-3 | Nuclear Plant Interface Coordination | R4. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall | HIGH | Retired | 2016-04-01 | 2021-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-3 | Nuclear Plant Interface Coordination | R4.1. | Incorporate the NPIRs into their operating analyses of the electric system. | HIGH | Retired | 2016-04-01 | 2021-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-3 | Nuclear Plant Interface Coordination | R4.1. | Incorporate the NPIRs into their operating analyses of the electric system. | HIGH | Retired | 2016-04-01 | 2021-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-3 | Nuclear Plant Interface Coordination | R4.1. | Incorporate the NPIRs into their operating analyses of the electric system. | HIGH | Retired | 2016-04-01 | 2021-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-3 | Nuclear Plant Interface Coordination | R4.2. | Operate the electric system to meet the NPIRs. | HIGH | Retired | 2016-04-01 | 2021-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-3 | Nuclear Plant Interface Coordination | R4.3. | Inform the Nuclear Plant Generator Operator when the ability to assess the operation of the electric system affecting NPIRs is lost. | HIGH | Retired | 2016-04-01 | 2021-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-3 | Nuclear Plant Interface Coordination | R5. | Per the Agreements developed in accordance with this standard, the Nuclear Plant Generator Operator shall operate the nuclear plant to meet the NPIRs. | HIGH | Retired | 2016-04-01 | 2021-03-31 | GOP
NUC-001-3 | Nuclear Plant Interface Coordination | R6. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities and the Nuclear Plant Generator Operator shall coordinate outages and maintenance activities which affect the NPIRs. | MEDIUM | Retired | 2016-04-01 | 2021-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-3 | Nuclear Plant Interface Coordination | R7. | Per the Agreements developed in accordance with this standard, the Nuclear Plant Generator Operator shall inform the applicable Transmission Entities of actual or proposed changes to nuclear plant design (e.g., protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the electric system to meet the NPIRs. | HIGH | Retired | 2016-04-01 | 2021-03-31 | GOP
NUC-001-3 | Nuclear Plant Interface Coordination | R8. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall inform the Nuclear Plant Generator Operator of actual or proposed changes to electric system design (e.g., protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the electric system to meet the NPIRs. | HIGH | Retired | 2016-04-01 | 2021-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-3 | Nuclear Plant Interface Coordination | R8. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall inform the Nuclear Plant Generator Operator of actual or proposed changes to electric system design (e.g., protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the electric system to meet the NPIRs. | HIGH | Retired | 2016-04-01 | 2021-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-3 | Nuclear Plant Interface Coordination | R8. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall inform the Nuclear Plant Generator Operator of actual or proposed changes to electric system design (e.g., protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the electric system to meet the NPIRs. | HIGH | Retired | 2016-04-01 | 2021-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-3 | Nuclear Plant Interface Coordination | R8. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall inform the Nuclear Plant Generator Operator of actual or proposed changes to electric system design (e.g., protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the electric system to meet the NPIRs. | HIGH | Retired | 2016-04-01 | 2021-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-3 | Nuclear Plant Interface Coordination | R9. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall include the following elements in aggregate within the Agreement(s) identified in R2. --Where multiple Agreements with a single Transmission Entity are put into effect, the R9 elements must be addressed in aggregate within the Agreements; however, each Agreement does not have to contain each element. The Nuclear Plant Generator Operator and the Transmission Entity are responsible for ensuring all the R9 elements are addressed in aggregate within the Agreements. -- Where Agreements with multiple Transmission Entities are required, the Nuclear Plant Generator Operator is responsible for ensuring all the R9 elements are addressed in aggregate within the Agreements with the Transmission Entities. The Agreements with each Transmission Entity do not have to contain each element; however, the Agreements with the multiple Transmission Entities, in the aggregate, must address all R9 elements. For each Agreement(s), the Nuclear Plant Generator Operator and the Transmission Entity are responsible to ensure the Agreement(s) contain(s) the elements of R9 applicable to that Transmission Entity. | MEDIUM | Retired | 2016-04-01 | 2021-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-3 | Nuclear Plant Interface Coordination | R9. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall include the following elements in aggregate within the Agreement(s) identified in R2. --Where multiple Agreements with a single Transmission Entity are put into effect, the R9 elements must be addressed in aggregate within the Agreements; however, each Agreement does not have to contain each element. The Nuclear Plant Generator Operator and the Transmission Entity are responsible for ensuring all the R9 elements are addressed in aggregate within the Agreements. -- Where Agreements with multiple Transmission Entities are required, the Nuclear Plant Generator Operator is responsible for ensuring all the R9 elements are addressed in aggregate within the Agreements with the Transmission Entities. The Agreements with each Transmission Entity do not have to contain each element; however, the Agreements with the multiple Transmission Entities, in the aggregate, must address all R9 elements. For each Agreement(s), the Nuclear Plant Generator Operator and the Transmission Entity are responsible to ensure the Agreement(s) contain(s) the elements of R9 applicable to that Transmission Entity. | MEDIUM | Retired | 2016-04-01 | 2021-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-3 | Nuclear Plant Interface Coordination | R9. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall include the following elements in aggregate within the Agreement(s) identified in R2. --Where multiple Agreements with a single Transmission Entity are put into effect, the R9 elements must be addressed in aggregate within the Agreements; however, each Agreement does not have to contain each element. The Nuclear Plant Generator Operator and the Transmission Entity are responsible for ensuring all the R9 elements are addressed in aggregate within the Agreements. -- Where Agreements with multiple Transmission Entities are required, the Nuclear Plant Generator Operator is responsible for ensuring all the R9 elements are addressed in aggregate within the Agreements with the Transmission Entities. The Agreements with each Transmission Entity do not have to contain each element; however, the Agreements with the multiple Transmission Entities, in the aggregate, must address all R9 elements. For each Agreement(s), the Nuclear Plant Generator Operator and the Transmission Entity are responsible to ensure the Agreement(s) contain(s) the elements of R9 applicable to that Transmission Entity. | MEDIUM | Retired | 2016-04-01 | 2021-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-3 | Nuclear Plant Interface Coordination | R9.2. | Technical requirements and analysis: | MEDIUM | Retired | 2016-04-01 | 2021-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-3 | Nuclear Plant Interface Coordination | R9.2.1. | Identification of parameters, limits, configurations, and operating scenarios included in the NPIRs and, as applicable, procedures for providing any specific data not provided within the Agreement. | MEDIUM | Retired | 2016-04-01 | 2021-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-3 | Nuclear Plant Interface Coordination | R9.2.2. | Identification of facilities, components, and configuration restrictions that are essential for meeting the NPIRs. | MEDIUM | Retired | 2016-04-01 | 2021-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-3 | Nuclear Plant Interface Coordination | R9.2.3. | Types of planning and operational analyses performed specifically to support the NPIRs, including the frequency of studies and types of Contingencies and scenarios required. | MEDIUM | Retired | 2016-04-01 | 2021-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-3 | Nuclear Plant Interface Coordination | R9.3. | Operations and maintenance coordination | MEDIUM | Retired | 2016-04-01 | 2021-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-3 | Nuclear Plant Interface Coordination | R9.3. | Operations and maintenance coordination | MEDIUM | Retired | 2016-04-01 | 2021-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-3 | Nuclear Plant Interface Coordination | R9.3. | Operations and maintenance coordination | MEDIUM | Retired | 2016-04-01 | 2021-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-3 | Nuclear Plant Interface Coordination | R9.3.1. | Designation of ownership of electrical facilities at the interface between the electric system and the nuclear plant and responsibilities for operational control coordination and maintenance of these facilities. | MEDIUM | Retired | 2016-04-01 | 2021-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-3 | Nuclear Plant Interface Coordination | R9.3.2. | Identification of any maintenance requirements for equipment not owned or controlled by the Nuclear Plant Generator Operator that are necessary to meet the NPIRs. | MEDIUM | Retired | 2016-04-01 | 2021-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-3 | Nuclear Plant Interface Coordination | R9.3.3. | Coordination of testing, calibration and maintenance of on-site and off-site power supply systems and related components. | MEDIUM | Retired | 2016-04-01 | 2021-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-3 | Nuclear Plant Interface Coordination | R9.3.4. | Provisions to address mitigating actions needed to avoid violating NPIRs and to address periods when responsible Transmission Entity loses the ability to assess the capability of the electric system to meet the NPIRs. These provisions shall include responsibility to notify the Nuclear Plant Generator Operator within a specified time frame. | MEDIUM | Retired | 2016-04-01 | 2021-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-3 | Nuclear Plant Interface Coordination | R9.3.5. | Provision for considering, within the restoration process, the requirements and urgency of a nuclear plant that has lost all off-site and on-site AC power. | MEDIUM | Retired | 2016-04-01 | 2021-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-3 | Nuclear Plant Interface Coordination | R9.3.6. | Coordination of physical and cyber security protection at the nuclear plant interface to ensure each asset is covered under at least one entity’s plan. | MEDIUM | Retired | 2016-04-01 | 2021-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-3 | Nuclear Plant Interface Coordination | R9.3.7. | Coordination of the NPIRs with transmission system Remedial Action Schemes and any programs that reduce or shed load based on underfrequency or undervoltage. | MEDIUM | Retired | 2016-04-01 | 2021-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-3 | Nuclear Plant Interface Coordination | R9.4. | Communications and training Administrative elements: | MEDIUM | Retired | 2016-04-01 | 2021-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-3 | Nuclear Plant Interface Coordination | R9.4. | Communications and training Administrative elements: | MEDIUM | Retired | 2016-04-01 | 2021-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-3 | Nuclear Plant Interface Coordination | R9.4.1. | Provisions for communications affecting the NPIRs between the Nuclear Plant Generator Operator and Transmission Entities, including communications protocols, notification time requirements, and definitions of applicable unique terms. | MEDIUM | Retired | 2016-04-01 | 2021-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-3 | Nuclear Plant Interface Coordination | R9.4.2. | Provisions for coordination during an off-normal or emergency event affecting the NPIRs, including the need to provide timely information explaining the event, an estimate of when the system will be returned to a normal state, and the actual time the system is returned to normal. | MEDIUM | Retired | 2016-04-01 | 2021-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-3 | Nuclear Plant Interface Coordination | R9.4.3. | Provisions for coordinating investigations of causes of unplanned events affecting the NPIRs and developing solutions to minimize future risk of such events. | MEDIUM | Retired | 2016-04-01 | 2021-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-3 | Nuclear Plant Interface Coordination | R9.4.4. | Provisions for supplying information necessary to report to government agencies, as related to NPIRs. | MEDIUM | Retired | 2016-04-01 | 2021-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-3 | Nuclear Plant Interface Coordination | R9.4.5. | Provisions for personnel training, as related to NPIRs. | MEDIUM | Retired | 2016-04-01 | 2021-03-31 | TSP, TP, TOP, TO, RC, PC, GOP, GO, DP, BA
NUC-001-4 | Nuclear Plant Interface Coordination | R1. | The Nuclear Plant Generator Operator shall provide the proposed NPIRs in writing to the applicable Transmission Entities and shall verify receipt. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning ] | MEDIUM | Effective | 2021-04-01 |  | GOP, GO, DP, PC, RC, BA, TSP, TP, TO, TOP
NUC-001-4 | Nuclear Plant Interface Coordination | R2. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall have in effect one or more Agreements1 that include mutually agreed to NPIRs and document how the Nuclear Plant Generator Operator and the applicable Transmission Entities shall address and implement these NPIRs. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning ] | MEDIUM | Effective | 2021-04-01 |  | GOP, GO, DP, PC, RC, BA, TSP, TP, TO, TOP
NUC-001-4 | Nuclear Plant Interface Coordination | R3. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall incorporate the NPIRs into their planning analyses of the electric system and shall communicate the results of these analyses to the Nuclear Plant Generator Operator.: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning ] | MEDIUM | Effective | 2021-04-01 |  | GOP, GO, DP, PC, RC, BA, TSP, TP, TO, TOP
NUC-001-4 | Nuclear Plant Interface Coordination | R3. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall incorporate the NPIRs into their planning analyses of the electric system and shall communicate the results of these analyses to the Nuclear Plant Generator Operator.: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning ] | MEDIUM | Effective | 2021-04-01 |  | GOP, GO, DP, PC, RC, BA, TSP, TP, TO, TOP
NUC-001-4 | Nuclear Plant Interface Coordination | R4. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall [Violation Risk Factor: High] [Time Horizon: Operations Planning and Real-time Operations] | MEDIUM | Effective | 2021-04-01 |  | GOP, GO, DP, PC, RC, BA, TSP, TP, TO, TOP
NUC-001-4 | Nuclear Plant Interface Coordination | R4. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall [Violation Risk Factor: High] [Time Horizon: Operations Planning and Real-time Operations] | MEDIUM | Effective | 2021-04-01 |  | GOP, GO, DP, PC, RC, BA, TSP, TP, TO, TOP
NUC-001-4 | Nuclear Plant Interface Coordination | R4. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall [Violation Risk Factor: High] [Time Horizon: Operations Planning and Real-time Operations] | MEDIUM | Effective | 2021-04-01 |  | GOP, GO, DP, PC, RC, BA, TSP, TP, TO, TOP
NUC-001-4 | Nuclear Plant Interface Coordination | R4.1. | Incorporate the NPIRs into their operating analyses of the electric system. | MEDIUM | Effective | 2021-04-01 |  | GOP, GO, DP, PC, RC, BA, TSP, TP, TO, TOP
NUC-001-4 | Nuclear Plant Interface Coordination | R4.1. | Incorporate the NPIRs into their operating analyses of the electric system. | MEDIUM | Effective | 2021-04-01 |  | GOP, GO, DP, PC, RC, BA, TSP, TP, TO, TOP
NUC-001-4 | Nuclear Plant Interface Coordination | R4.1. | Incorporate the NPIRs into their operating analyses of the electric system. | MEDIUM | Effective | 2021-04-01 |  | GOP, GO, DP, PC, RC, BA, TSP, TP, TO, TOP
NUC-001-4 | Nuclear Plant Interface Coordination | R4.2. | Operate the electric system to meet the NPIRs. | HIGH | Effective | 2021-04-01 |  | GOP, GO, DP, PC, RC, BA, TSP, TP, TO, TOP
NUC-001-4 | Nuclear Plant Interface Coordination | R4.3. | Inform the Nuclear Plant Generator Operator when the ability to assess the operation of the electric system affecting NPIRs is lost. | HIGH | Effective | 2021-04-01 |  | GOP, GO, DP, PC, RC, BA, TSP, TP, TO, TOP
NUC-001-4 | Nuclear Plant Interface Coordination | R5. | Per the Agreements developed in accordance with this standard, the Nuclear Plant Generator Operator shall operate the nuclear plant to meet the NPIRs. [Violation Risk Factor: High] [Time Horizon: Operations Planning and Real-time Operations ] | HIGH | Effective | 2021-04-01 |  | GOP, GO, DP, PC, RC, BA, TSP, TP, TO, TOP
NUC-001-4 | Nuclear Plant Interface Coordination | R6. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities and the Nuclear Plant Generator Operator shall coordinate outages and maintenance activities which affect the NPIRs. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Effective | 2021-04-01 |  | GOP, GO, DP, PC, RC, BA, TSP, TP, TO, TOP
NUC-001-4 | Nuclear Plant Interface Coordination | R7. | Per the Agreements developed in accordance with this standard, the Nuclear Plant Generator Operator shall inform the applicable Transmission Entities of actual or proposed changes to nuclear plant design (e.g., protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the electric system to meet the NPIRs. [Violation Risk Factor: High] [Time Horizon: Long-term Planning] | HIGH | Effective | 2021-04-01 |  | GOP, GO, DP, PC, RC, BA, TSP, TP, TO, TOP
NUC-001-4 | Nuclear Plant Interface Coordination | R8. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall inform the Nuclear Plant Generator Operator of actual or proposed changes to electric system design (e.g., protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the electric system to meet the NPIRs. [Violation Risk Factor: High] [Time Horizon: Long-term Planning] | HIGH | Effective | 2021-04-01 |  | GOP, GO, DP, PC, RC, BA, TSP, TP, TO, TOP
NUC-001-4 | Nuclear Plant Interface Coordination | R8. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall inform the Nuclear Plant Generator Operator of actual or proposed changes to electric system design (e.g., protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the electric system to meet the NPIRs. [Violation Risk Factor: High] [Time Horizon: Long-term Planning] | HIGH | Effective | 2021-04-01 |  | GOP, GO, DP, PC, RC, BA, TSP, TP, TO, TOP
NUC-001-4 | Nuclear Plant Interface Coordination | R8. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall inform the Nuclear Plant Generator Operator of actual or proposed changes to electric system design (e.g., protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the electric system to meet the NPIRs. [Violation Risk Factor: High] [Time Horizon: Long-term Planning] | HIGH | Effective | 2021-04-01 |  | GOP, GO, DP, PC, RC, BA, TSP, TP, TO, TOP
NUC-001-4 | Nuclear Plant Interface Coordination | R8. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall inform the Nuclear Plant Generator Operator of actual or proposed changes to electric system design (e.g., protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the electric system to meet the NPIRs. [Violation Risk Factor: High] [Time Horizon: Long-term Planning] | HIGH | Effective | 2021-04-01 |  | GOP, GO, DP, PC, RC, BA, TSP, TP, TO, TOP
NUC-001-4 | Nuclear Plant Interface Coordination | R9. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall include the following elements in aggregate within the Agreement(s) identified in R2. • Where multiple Agreements with a single Transmission Entity are put into effect, the R9 elements must be addressed in aggregate within the Agreements; however, each Agreement does not have to contain each element. The Nuclear Plant Generator Operator and the Transmission Entity are responsible for ensuring all the R9 elements are addressed in aggregate within the Agreements. • Where Agreements with multiple Transmission Entities are required, the Nuclear Plant Generator Operator is responsible for ensuring all the R9 elements are addressed in aggregate within the Agreements with the Transmission Entities. The Agreements with each Transmission Entity do not have to contain each element; however, the Agreements with the multiple Transmission Entities, in the aggregate, must address all R9 elements. For each Agreement(s), the Nuclear Plant Generator Operator and the Transmission Entity are responsible to ensure the Agreement(s) contain(s) the elements of R9 applicable to that Transmission Entity. : [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2021-04-01 |  | GOP, GO, DP, PC, RC, BA, TSP, TP, TO, TOP
NUC-001-4 | Nuclear Plant Interface Coordination | R9. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall include the following elements in aggregate within the Agreement(s) identified in R2. • Where multiple Agreements with a single Transmission Entity are put into effect, the R9 elements must be addressed in aggregate within the Agreements; however, each Agreement does not have to contain each element. The Nuclear Plant Generator Operator and the Transmission Entity are responsible for ensuring all the R9 elements are addressed in aggregate within the Agreements. • Where Agreements with multiple Transmission Entities are required, the Nuclear Plant Generator Operator is responsible for ensuring all the R9 elements are addressed in aggregate within the Agreements with the Transmission Entities. The Agreements with each Transmission Entity do not have to contain each element; however, the Agreements with the multiple Transmission Entities, in the aggregate, must address all R9 elements. For each Agreement(s), the Nuclear Plant Generator Operator and the Transmission Entity are responsible to ensure the Agreement(s) contain(s) the elements of R9 applicable to that Transmission Entity. : [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2021-04-01 |  | GOP, GO, DP, PC, RC, BA, TSP, TP, TO, TOP
NUC-001-4 | Nuclear Plant Interface Coordination | R9. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall include the following elements in aggregate within the Agreement(s) identified in R2. • Where multiple Agreements with a single Transmission Entity are put into effect, the R9 elements must be addressed in aggregate within the Agreements; however, each Agreement does not have to contain each element. The Nuclear Plant Generator Operator and the Transmission Entity are responsible for ensuring all the R9 elements are addressed in aggregate within the Agreements. • Where Agreements with multiple Transmission Entities are required, the Nuclear Plant Generator Operator is responsible for ensuring all the R9 elements are addressed in aggregate within the Agreements with the Transmission Entities. The Agreements with each Transmission Entity do not have to contain each element; however, the Agreements with the multiple Transmission Entities, in the aggregate, must address all R9 elements. For each Agreement(s), the Nuclear Plant Generator Operator and the Transmission Entity are responsible to ensure the Agreement(s) contain(s) the elements of R9 applicable to that Transmission Entity. : [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2021-04-01 |  | GOP, GO, DP, PC, RC, BA, TSP, TP, TO, TOP
NUC-001-4 | Nuclear Plant Interface Coordination | R9.1. | Retired. [Note: Part 9.1 was retired under the Paragraph 81 project. The NUC SDT proposes to leave this Part blank to avoid renumbering Requirement parts that would impact existing agreements throughout the industry.] | MEDIUM | Effective | 2021-04-01
NUC-001-4 | Nuclear Plant Interface Coordination | R9.2. | Technical requirements and analysis: | MEDIUM | Effective | 2021-04-01 |  | GOP, GO, DP, PC, RC, BA, TSP, TP, TO, TOP
NUC-001-4 | Nuclear Plant Interface Coordination | R9.2.1. | Identification of parameters, limits, configurations, and operating scenarios included in the NPIRs and, as applicable, procedures for providing any specific data not provided within the Agreement. | MEDIUM | Effective | 2021-04-01 |  | GOP, GO, DP, PC, RC, BA, TSP, TP, TO, TOP
NUC-001-4 | Nuclear Plant Interface Coordination | R9.2.2. | Identification of facilities, components, and configuration restrictions that are essential for meeting the NPIRs. | MEDIUM | Effective | 2021-04-01 |  | GOP, GO, DP, PC, RC, BA, TSP, TP, TO, TOP
NUC-001-4 | Nuclear Plant Interface Coordination | R9.2.3. | Types of planning and operational analyses performed specifically to support the NPIRs, including the frequency of studies and types of Contingencies and scenarios required. | MEDIUM | Effective | 2021-04-01 |  | GOP, GO, DP, PC, RC, BA, TSP, TP, TO, TOP
NUC-001-4 | Nuclear Plant Interface Coordination | R9.3. | Operations and maintenance coordination | MEDIUM | Effective | 2021-04-01 |  | GOP, GO, DP, PC, RC, BA, TSP, TP, TO, TOP
NUC-001-4 | Nuclear Plant Interface Coordination | R9.3. | Operations and maintenance coordination | MEDIUM | Effective | 2021-04-01 |  | GOP, GO, DP, PC, RC, BA, TSP, TP, TO, TOP
NUC-001-4 | Nuclear Plant Interface Coordination | R9.3. | Operations and maintenance coordination | MEDIUM | Effective | 2021-04-01 |  | GOP, GO, DP, PC, RC, BA, TSP, TP, TO, TOP
NUC-001-4 | Nuclear Plant Interface Coordination | R9.3.1. | Designation of ownership of electrical facilities at the interface between the electric system and the nuclear plant and responsibilities for operational control coordination and maintenance of these facilities. | MEDIUM | Effective | 2021-04-01 |  | GOP, GO, DP, PC, RC, BA, TSP, TP, TO, TOP
NUC-001-4 | Nuclear Plant Interface Coordination | R9.3.2. | Identification of any maintenance requirements for equipment not owned or controlled by the Nuclear Plant Generator Operator that are necessary to meet the NPIRs. | MEDIUM | Effective | 2021-04-01 |  | GOP, GO, DP, PC, RC, BA, TSP, TP, TO, TOP
NUC-001-4 | Nuclear Plant Interface Coordination | R9.3.3. | Coordination of testing, calibration and maintenance of on-site and off-site power supply systems and related components. | MEDIUM | Effective | 2021-04-01 |  | GOP, GO, DP, PC, RC, BA, TSP, TP, TO, TOP
NUC-001-4 | Nuclear Plant Interface Coordination | R9.3.4. | Provisions to address mitigating actions needed to avoid violating NPIRs and to address periods when responsible Transmission Entity loses the ability to assess the capability of the electric system to meet the NPIRs. These provisions shall include responsibility to notify the Nuclear Plant Generator Operator within a specified time frame. | MEDIUM | Effective | 2021-04-01 |  | GOP, GO, DP, PC, RC, BA, TSP, TP, TO, TOP
NUC-001-4 | Nuclear Plant Interface Coordination | R9.3.5. | Provision for considering, within the restoration process, the requirements and urgency of a nuclear plant that has lost all off-site and on-site AC power. | MEDIUM | Effective | 2021-04-01 |  | GOP, GO, DP, PC, RC, BA, TSP, TP, TO, TOP
NUC-001-4 | Nuclear Plant Interface Coordination | R9.3.6. | Coordination of physical and cyber security protection at the nuclear plant interface to ensure each asset is covered under at least one entity’s plan. | MEDIUM | Effective | 2021-04-01 |  | GOP, GO, DP, PC, RC, BA, TSP, TP, TO, TOP
NUC-001-4 | Nuclear Plant Interface Coordination | R9.3.7. | Coordination of the NPIRs with transmission system Remedial Action Schemes and any programs that reduce or shed load based on underfrequency or undervoltage. | MEDIUM | Effective | 2021-04-01 |  | GOP, GO, DP, PC, RC, BA, TSP, TP, TO, TOP
NUC-001-4 | Nuclear Plant Interface Coordination | R9.4. | Communications and training Administrative elements: | MEDIUM | Effective | 2021-04-01 |  | GOP, GO, DP, PC, RC, BA, TSP, TP, TO, TOP
NUC-001-4 | Nuclear Plant Interface Coordination | R9.4. | Communications and training Administrative elements: | MEDIUM | Effective | 2021-04-01 |  | GOP, GO, DP, PC, RC, BA, TSP, TP, TO, TOP
NUC-001-4 | Nuclear Plant Interface Coordination | R9.4.1. | Provisions for communications affecting the NPIRs between the Nuclear Plant Generator Operator and Transmission Entities, including communications protocols, notification time requirements, and definitions of applicable unique terms. | MEDIUM | Effective | 2021-04-01 |  | GOP, GO, DP, PC, RC, BA, TSP, TP, TO, TOP
NUC-001-4 | Nuclear Plant Interface Coordination | R9.4.2. | Provisions for coordination during an off-normal or emergency event affecting the NPIRs, including the need to provide timely information explaining the event, an estimate of when the system will be returned to a normal state, and the actual time the system is returned to normal. | MEDIUM | Effective | 2021-04-01 |  | GOP, GO, DP, PC, RC, BA, TSP, TP, TO, TOP
NUC-001-4 | Nuclear Plant Interface Coordination | R9.4.3. | Provisions for coordinating investigations of causes of unplanned events affecting the NPIRs and developing solutions to minimize future risk of such events. | MEDIUM | Effective | 2021-04-01 |  | GOP, GO, DP, PC, RC, BA, TSP, TP, TO, TOP
NUC-001-4 | Nuclear Plant Interface Coordination | R9.4.4. | Provisions for supplying information necessary to report to government agencies, as related to NPIRs. | MEDIUM | Effective | 2021-04-01 |  | TP, TO, TOP, GOP, GO, DP, PC, RC, BA, TSP
NUC-001-4 | Nuclear Plant Interface Coordination | R9.4.5. | Provisions for personnel training, as related to NPIRs. | MEDIUM | Effective | 2021-04-01 |  | GOP, GO, DP, PC, RC, BA, TSP, TP, TO, TOP
PER-001-0.2 | Operating Personnel Responsibility and Authority | R1. | Each Transmission Operator and Balancing Authority shall provide operating personnel with the responsibility and authority to implement real-time actions to ensure the stable and reliable operation of the Bulk Electric System. | HIGH | Retired | 2012-10-10 | 2017-03-31 | TOP, BA
PER-003-1 | Operating Personnel Credentials | R1. | Each Reliability Coordinator shall staff its Real-time operating positions performing Reliability Coordinator reliability-related tasks with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining a valid NERC Reliability Operator certificate | HIGH | Retired | 2012-10-01 | 2019-06-30 | RC
PER-003-1 | Operating Personnel Credentials | R1.1. | Areas of Competency | HIGH | Retired | 2012-10-01 | 2019-06-30 | RC
PER-003-1 | Operating Personnel Credentials | R1.1.1. | Resource and demand balancing | HIGH | Retired | 2012-10-01 | 2019-06-30 | RC
PER-003-1 | Operating Personnel Credentials | R1.1.2. | Transmission operations | HIGH | Retired | 2012-10-01 | 2019-06-30 | RC
PER-003-1 | Operating Personnel Credentials | R1.1.3. | Emergency preparedness and operations | HIGH | Retired | 2012-10-01 | 2019-06-30 | RC
PER-003-1 | Operating Personnel Credentials | R1.1.4. | System operations | HIGH | Retired | 2012-10-01 | 2019-06-30 | RC
PER-003-1 | Operating Personnel Credentials | R1.1.5. | Protection and control | HIGH | Retired | 2012-10-01 | 2019-06-30 | RC
PER-003-1 | Operating Personnel Credentials | R1.1.6. | Voltage and reactive | HIGH | Retired | 2012-10-01 | 2019-06-30 | RC
PER-003-1 | Operating Personnel Credentials | R1.1.7. | Interchange scheduling and coordination | HIGH | Retired | 2012-10-01 | 2019-06-30 | RC
PER-003-1 | Operating Personnel Credentials | R1.1.8. | Interconnection reliability operations and coordination | HIGH | Retired | 2012-10-01 | 2019-06-30 | RC
PER-003-1 | Operating Personnel Credentials | R2. | Each Transmission Operator shall staff its Real-time operating positions performing Transmission Operator reliability-related tasks with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining one of the following valid NERC certificates (1 | HIGH | Retired | 2012-10-01 | 2019-06-30 | TOP
PER-003-1 | Operating Personnel Credentials | R2.1. | Areas of Competency | HIGH | Retired | 2012-10-01 | 2019-06-30 | TOP
PER-003-1 | Operating Personnel Credentials | R2.1.1. | Transmission operations | HIGH | Retired | 2012-10-01 | 2019-06-30 | TOP
PER-003-1 | Operating Personnel Credentials | R2.1.2. | Emergency preparedness and operations | HIGH | Retired | 2012-10-01 | 2019-06-30 | TOP
PER-003-1 | Operating Personnel Credentials | R2.1.3. | System operations | HIGH | Retired | 2012-10-01 | 2019-06-30 | TOP
PER-003-1 | Operating Personnel Credentials | R2.1.4. | Protection and control | HIGH | Retired | 2012-10-01 | 2019-06-30 | TOP
PER-003-1 | Operating Personnel Credentials | R2.1.5. | Voltage and reactive | HIGH | Retired | 2012-10-01 | 2019-06-30 | TOP
PER-003-1 | Operating Personnel Credentials | R2.2. | Certificates • Reliability Operator • Balancing, Interchange and Transmission Operator • Transmission Operator | HIGH | Retired | 2012-10-01 | 2019-06-30 | TOP
PER-003-1 | Operating Personnel Credentials | R3. | Each Balancing Authority shall staff its Real-time operating positions performing Balancing Authority reliability-related tasks with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining one of the following valid NERC certificates (1) | HIGH | Retired | 2012-10-01 | 2019-06-30 | BA
PER-003-1 | Operating Personnel Credentials | R3.1. | Areas of Competency | HIGH | Retired | 2012-10-01 | 2019-06-30 | BA
PER-003-1 | Operating Personnel Credentials | R3.1.1. | Resources and demand balancing | HIGH | Retired | 2012-10-01 | 2019-06-30 | BA
PER-003-1 | Operating Personnel Credentials | R3.1.2. | Emergency preparedness and operations | HIGH | Retired | 2012-10-01 | 2019-06-30 | BA
PER-003-1 | Operating Personnel Credentials | R3.1.3. | System operations | HIGH | Retired | 2012-10-01 | 2019-06-30 | BA
PER-003-1 | Operating Personnel Credentials | R3.1.4. | Interchange scheduling and coordination | HIGH | Retired | 2012-10-01 | 2019-06-30 | BA
PER-003-1 | Operating Personnel Credentials | R3.2. | Certificates • Reliability Operator • Balancing, Interchange and Transmission Operator • Balancing and Interchange Operator | HIGH | Retired | 2012-10-01 | 2019-06-30 | BA
PER-003-2 | Operating Personnel Credentials | R1. | Each Reliability Coordinator shall staff its Real-time operating positions performing Reliability Coordinator reliability-related tasks with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining a valid NERC Reliability Operator certificate (1)(2): [Risk Factor: High][Time Horizon: Real-time Operations] | HIGH | Effective | 2019-07-01 |  | RC
PER-003-2 | Operating Personnel Credentials | R1.1. | Areas of Competency | HIGH | Effective | 2019-07-01 |  | RC
PER-003-2 | Operating Personnel Credentials | R1.1.1. | Resource and demand balancing | HIGH | Effective | 2019-07-01 |  | RC
PER-003-2 | Operating Personnel Credentials | R1.1.2. | Transmission operations | HIGH | Effective | 2019-07-01 |  | RC
PER-003-2 | Operating Personnel Credentials | R1.1.3. | Emergency preparedness and operations | HIGH | Effective | 2019-07-01 |  | RC
PER-003-2 | Operating Personnel Credentials | R1.1.4. | System operations | HIGH | Effective | 2019-07-01 |  | RC
PER-003-2 | Operating Personnel Credentials | R1.1.5. | Protection and control | HIGH | Effective | 2019-07-01 |  | RC
PER-003-2 | Operating Personnel Credentials | R1.1.6. | Voltage and reactive | HIGH | Effective | 2019-07-01 |  | RC
PER-003-2 | Operating Personnel Credentials | R1.1.7. | Interchange scheduling and coordination | HIGH | Effective | 2019-07-01 |  | RC
PER-003-2 | Operating Personnel Credentials | R1.1.8. | Interconnection reliability operations and coordination | HIGH | Effective | 2019-07-01 |  | RC
PER-003-2 | Operating Personnel Credentials | R2. | Each Transmission Operator shall staff its Real-time operating positions performing Transmission Operator reliability-related tasks with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining one of the following valid NERC certificates (1)(2): [Risk Factor: High][Time Horizon: Real-time Operations]: | HIGH | Effective | 2019-07-01 |  | TOP
PER-003-2 | Operating Personnel Credentials | R2.1. | Areas of Competency | HIGH | Effective | 2019-07-01 |  | TOP
PER-003-2 | Operating Personnel Credentials | R2.1.1. | Transmission operations | HIGH | Effective | 2019-07-01 |  | TOP
PER-003-2 | Operating Personnel Credentials | R2.1.2. | Emergency preparedness and operations | HIGH | Effective | 2019-07-01 |  | TOP
PER-003-2 | Operating Personnel Credentials | R2.1.3. | System operations | HIGH | Effective | 2019-07-01 |  | TOP
PER-003-2 | Operating Personnel Credentials | R2.1.4. | Protection and control | HIGH | Effective | 2019-07-01 |  | TOP
PER-003-2 | Operating Personnel Credentials | R2.1.5. | Voltage and reactive | HIGH | Effective | 2019-07-01 |  | TOP
PER-003-2 | Operating Personnel Credentials | R2.2. | Certificates  Reliability Operator  Balancing, Interchange and Transmission Operator  Transmission Operator | HIGH | Effective | 2019-07-01 |  | TOP
PER-003-2 | Operating Personnel Credentials | R3. | Each Balancing Authority shall staff its Real-time operating positions performing Balancing Authority reliability-related tasks with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining one of the following valid NERC certificates (1)(2): [Risk Factor: High][Time Horizon: Real-time Operations]: | HIGH | Effective | 2019-07-01 |  | BA
PER-003-2 | Operating Personnel Credentials | R3.1. | Areas of Competency | HIGH | Effective | 2019-07-01 |  | BA
PER-003-2 | Operating Personnel Credentials | R3.1.1. | Resources and demand balancing | HIGH | Effective | 2019-07-01 |  | BA
PER-003-2 | Operating Personnel Credentials | R3.1.2. | Emergency preparedness and operations | HIGH | Effective | 2019-07-01 |  | BA
PER-003-2 | Operating Personnel Credentials | R3.1.3. | System operations | HIGH | Effective | 2019-07-01 |  | BA
PER-003-2 | Operating Personnel Credentials | R3.1.4. | Interchange scheduling and coordination | HIGH | Effective | 2019-07-01 |  | BA
PER-003-2 | Operating Personnel Credentials | R3.2. | Certificates  Reliability Operator  Balancing, Interchange and Transmission Operator  Balancing and Interchange Operator | HIGH | Effective | 2019-07-01 |  | BA
PER-004-2 | Reliability Coordination - Staffing | R1. | Each Reliability Coordinator shall be staffed with adequately trained and NERC-certified Reliability Coordinator operators, 24 hours per day, seven days per week. | HIGH | Retired | 2011-04-01 | 2019-06-23 | RC
PER-004-2 | Reliability Coordination - Staffing | R2. | Reliability Coordinator operating personnel shall place particular attention on SOLs and IROLs and inter-tie facility limits. The Reliability Coordinator shall ensure protocols are in place to allow Reliability Coordinator operating personnel to have the best available information at all times. | HIGH | Retired | 2011-04-01 | 2019-06-23 | RC
PER-005-1 | System Personnel Training | R1. | Each Reliability Coordinator, Balancing Authority and Transmission Operator shall use a systematic approach to training to establish a training program for the BES company-specific reliability-related tasks performed by its System Operators and shall implement the program. [Time Horizon: Long-term Planning] | MEDIUM | Retired | 2011-04-01 | 2016-09-30 | TOP, RC, BA
PER-005-1 | System Personnel Training | R1.1. | Each Reliability Coordinator, Balancing Authority and Transmission Operator shall create a list of BES company-specific reliability-related tasks performed by its System Operators. | No Individual VRF Assigned | Retired | 2011-04-01 | 2016-09-30 | TOP, RC, BA
PER-005-1 | System Personnel Training | R1.1.1. | Each Reliability Coordinator, Balancing Authority and Transmission Operator shall update its list of BES company-specific reliability-related tasks performed by its System Operators each calendar year to identify new or modified tasks for inclusion in training. | No Individual VRF Assigned | Retired | 2011-04-01 | 2016-09-30 | TOP, RC, BA
PER-005-1 | System Personnel Training | R1.2. | Each Reliability Coordinator, Balancing Authority and Transmission Operator shall design and develop learning objectives and training materials based on the task list created in R1.1. | No Individual VRF Assigned | Retired | 2011-04-01 | 2016-09-30 | TOP, RC, BA
PER-005-1 | System Personnel Training | R1.3. | Each Reliability Coordinator, Balancing Authority and Transmission Operator shall deliver the training established in R1.2. | No Individual VRF Assigned | Retired | 2011-04-01 | 2016-09-30 | TOP, RC, BA
PER-005-1 | System Personnel Training | R1.4. | Each Reliability Coordinator, Balancing Authority and Transmission Operator shall conduct an annual evaluation of the training program established in R1, to identify any needed changes to the training program and shall implement the changes identified. | No Individual VRF Assigned | Retired | 2011-04-01 | 2016-09-30 | TOP, RC, BA
PER-005-1 | System Personnel Training | R2. | Each Reliability Coordinator, Balancing Authority and Transmission Operator shall verify each of its System Operator’s capabilities to perform each assigned task identified in R1.1 at least one time. [Time Horizon: Long-term Planning] | HIGH | Retired | 2011-04-01 | 2016-09-30 | TOP, RC, BA
PER-005-1 | System Personnel Training | R2.1. | Within six months of a modification of the BES company-specific reliability-related tasks, each Reliability Coordinator, Balancing Authority and Transmission Operator shall verify each of its System Operator’s capabilities to perform the new or modified tasks. | No Individual VRF Assigned | Retired | 2011-04-01 | 2016-09-30 | TOP, RC, BA
PER-005-1 | System Personnel Training | R3. | At least every 12 months each Reliability Coordinator, Balancing Authority and Transmission Operator shall provide each of its System Operators with at least 32 hours of emergency operations training applicable to its organization that reflects emergency operations topics, which includes system restoration using drills, exercises or other training required to maintain qualified personnel. [Time Horizon: Long-term Planning] | MEDIUM | Retired | 2011-04-01 | 2016-09-30 | TOP, RC, BA
PER-005-1 | System Personnel Training | R3.1. | Each Reliability Coordinator, Balancing Authority and Transmission Operator that has operational authority or control over Facilities with established IROLs or has established operating guides or protection systems to mitigate IROL violations shall provide each System Operator with emergency operations training using simulation technology such as a simulator, virtual technology, or other technology that replicates the operational behavior of the BES during normal and emergency conditions. | No Individual VRF Assigned | Retired | 2011-04-01 | 2016-09-30 | TOP, RC, BA
PER-005-2 | Operations Personnel Training | R1. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall use a systematic approach to develop and implement a training program for its System Operators as follows: | MEDIUM | Effective | 2016-10-01 |  | TOP, RC, BA
PER-005-2 | Operations Personnel Training | R1.1. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall create a list of Bulk Electric System (BES) company-specific Real-time reliability-related tasks based on a defined and documented methodology. | MEDIUM | Effective | 2016-10-01 |  | TOP, RC, BA
PER-005-2 | Operations Personnel Training | R1.1.1. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall review, and update if necessary, its list of BES company-specific Real-time reliability-related tasks identified in part 1.1 each calendar year. | MEDIUM | Effective | 2016-10-01 |  | TOP, RC, BA
PER-005-2 | Operations Personnel Training | R1.2. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall design and develop training materials according to its training program, based on the BES company-specific Real-time reliability-related task list created in part 1.1. | MEDIUM | Effective | 2016-10-01 |  | TOP, RC, BA
PER-005-2 | Operations Personnel Training | R1.3. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall deliver training to its System Operators according to its training program. | MEDIUM | Effective | 2016-10-01 |  | TOP, RC, BA
PER-005-2 | Operations Personnel Training | R1.4. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall conduct an evaluation each calendar year of the training program established in Requirement R1 to identify any needed changes to the training program and shall implement the changes identified. | MEDIUM | Effective | 2016-10-01 |  | TOP, RC, BA
PER-005-2 | Operations Personnel Training | R2. | Each Transmission Owner shall use a systematic approach to develop and implement a training program for its personnel identified in Applicability Section 4.1.4.1 of this standard as follows: | MEDIUM | Effective | 2016-10-01 |  | TO
PER-005-2 | Operations Personnel Training | R2.1. | Each Transmission Owner shall create a list of BES company-specific Real-time reliability-related tasks based on a defined and documented methodology. | MEDIUM | Effective | 2016-10-01 |  | TO
PER-005-2 | Operations Personnel Training | R2.1.1. | Each Transmission Owner shall review, and update if necessary, its list of BES company-specific Real-time reliability-related tasks identified in part 2.1 each calendar year. | MEDIUM | Effective | 2016-10-01 |  | TO
PER-005-2 | Operations Personnel Training | R2.2. | Each Transmission Owner shall design and develop training materials according to its training program, based on the BES company-specific Real-time reliability-related task list created in part 2.1. | MEDIUM | Effective | 2016-10-01 |  | TO
PER-005-2 | Operations Personnel Training | R2.3. | Each Transmission Owner shall deliver training to its personnel identified in Applicability Section 4.1.4.1 of this standard according to its training program. | MEDIUM | Effective | 2016-10-01 |  | TO
PER-005-2 | Operations Personnel Training | R2.4. | Each Transmission Owner shall conduct an evaluation each calendar year of the training program established in Requirement R2 to identify any needed changes to the training program and shall implement the changes identified. | MEDIUM | Effective | 2016-10-01 |  | TO
PER-005-2 | Operations Personnel Training | R3. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, and Transmission Owner shall verify, at least once, the capabilities of its personnel, identified in Requirement R1 or Requirement R2, assigned to perform each of the BES company-specific Real-time reliability-related tasks identified under Requirement R1 part 1.1 or Requirement R2 part 2.1. | HIGH | Effective | 2016-10-01 |  | TOP, TO, RC, BA
PER-005-2 | Operations Personnel Training | R3.1. | Within six months of a modification or addition of a BES company-specific Real-time reliability-related task, each Reliability Coordinator, Balancing Authority, Transmission Operator, and Transmission Owner shall verify the capabilities of each of its personnel identified in Requirement R1 or Requirement R2 to perform the new or modified BES company-specific Real-time reliability-related tasks identified in Requirement R1 part 1.1 or Requirement R2 part 2.1. | HIGH | Effective | 2016-10-01 |  | TOP, TO, RC, BA
PER-005-2 | Operations Personnel Training | R4. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, and Transmission Owner that (1) has operational authority or control over Facilities with established Interconnection Reliability Operating Limits (IROLs), or (2) has established protection systems or operating guides to mitigate IROL violations, shall provide its personnel identified in Requirement R1 or Requirement R2 with emergency operations training using simulation technology such as a simulator, virtual technology, or other technology that replicates the operational behavior of the BES. | MEDIUM | Effective | 2016-10-01 |  | TOP, TO, RC, BA
PER-005-2 | Operations Personnel Training | R4.1. | A Reliability Coordinator, Balancing Authority, Transmission Operator, or Transmission Owner that did not previously meet the criteria of Requirement R4, shall comply with Requirement R4 within 12 months of meeting the criteria. | MEDIUM | Effective | 2016-10-01 |  | TOP, TO, RC, BA
PER-005-2 | Operations Personnel Training | R5. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have available for inspection evidence that Operations Support Personnel completed training in accordance with its systematic approach. This evidence may be documents such as training records showing successful completion of training. Documentation of training shall include employee name and date of training. | MEDIUM | Effective | 2016-10-01 |  | BA, RC, TOP
PER-005-2 | Operations Personnel Training | R5. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall use a systematic approach to develop and implement training for its identified Operations Support Personnel on how their job function(s) impact those BES company-specific Real-time reliability-related tasks identified by the entity pursuant to Requirement R1 part 1.1. | MEDIUM | Effective | 2016-10-01 |  | TOP, RC, BA
PER-005-2 | Operations Personnel Training | R5. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall use a systematic approach to develop and implement training for its identified Operations Support Personnel on how their job function(s) impact those BES company-specific Real-time reliability-related tasks identified by the entity pursuant to Requirement R1 part 1.1. | MEDIUM | Effective | 2016-10-01 |  | TOP, RC, BA
PER-005-2 | Operations Personnel Training | R5.1. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have available for inspection evidence (such as instructor observations, trainee feedback, supervisor feedback, course evaluations, learning assessments, or internal audit results) that it performed an evaluation each calendar year, as specified in Requirement R5 part 5.1. | MEDIUM | Effective | 2016-10-01 |  | BA, RC, TOP
PER-005-2 | Operations Personnel Training | R5.1. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall conduct an evaluation each calendar year of the training established in Requirement R5 to identify and implement changes to the training. | MEDIUM | Effective | 2016-10-01 |  | TOP, RC, BA
PER-005-2 | Operations Personnel Training | R5.1. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall conduct an evaluation each calendar year of the training established in Requirement R5 to identify and implement changes to the training. | MEDIUM | Effective | 2016-10-01 |  | TOP, RC, BA
PER-005-2 | Operations Personnel Training | R6. | Each Generator Operator shall use a systematic approach to develop and implement training to its personnel identified in Applicability Section 4.1.5.1 of this standard, on how their job function(s) impact the reliable operations of the BES during normal and emergency operations. | MEDIUM | Effective | 2016-10-01 |  | GOP
PER-005-2 | Operations Personnel Training | R6.1. | Each Generator Operator shall conduct an evaluation each calendar year of the training established in Requirement R6 to identify and implement changes to the training. | MEDIUM | Effective | 2016-10-01 |  | GOP
PER-006-1 | Specific Training for Personnel | R1. | Each Generator Operator shall provide training to personnel identified in Applicability section 4.1.1.1. on the operational functionality of Protection Systems and Remedial Action Schemes (RAS) that affect the output of the generating Facility(ies) it operates. | MEDIUM | Effective | 2021-04-01 |  | GOP
PRC-001-1.1 | System Protection Coordination | R1. | Each Transmission Operator, Balancing Authority, and Generator Operator shall be familiar with the purpose and limitations of Protection System schemes applied in its area. | HIGH | Retired | 2013-04-01 | 2015-07-15 | TOP, GOP, BA
PRC-001-1.1 | System Protection Coordination | R2. | Each Generator Operator and Transmission Operator shall notify reliability entities of relay or equipment failures as follows: | HIGH | Retired | 2013-04-01 | 2015-07-15 | TOP, GOP
PRC-001-1.1 | System Protection Coordination | R2.1. | If a protective relay or equipment failure reduces system reliability, the Generator Operator shall notify its Transmission Operator and Host Balancing Authority. The Generator Operator shall take corrective action as soon as possible. | HIGH | Retired | 2013-04-01 | 2015-07-15 | GOP
PRC-001-1.1 | System Protection Coordination | R2.2. | If a protective relay or equipment failure reduces system reliability, the Transmission Operator shall notify its Reliability Coordinator and affected Transmission Operators and Balancing Authorities. The Transmission Operator shall take corrective action as soon as possible. | HIGH | Retired | 2013-04-01 | 2015-07-15 | TOP
PRC-001-1.1 | System Protection Coordination | R3. | A Generator Operator or Transmission Operator shall coordinate new protective systems and changes as follows. | No Individual VRF Assigned | Retired | 2013-04-01 | 2015-07-15 | TOP, GOP
PRC-001-1.1 | System Protection Coordination | R3.1. | Each Generator Operator shall coordinate all new protective systems and all protective system changes with its Transmission Operator and Host Balancing Authority. | HIGH | Retired | 2013-04-01 | 2015-07-15 | GOP
PRC-001-1.1 | System Protection Coordination | R3.2. | Each Transmission Operator shall coordinate all new protective systems and all protective system changes with neighboring Transmission Operators and Balancing Authorities. | HIGH | Retired | 2013-04-01 | 2015-07-15 | TOP
PRC-001-1.1 | System Protection Coordination | R4. | Each Transmission Operator shall coordinate Protection Systems on major transmission lines and interconnections with neighboring Generator Operators, Transmission Operators, and Balancing Authorities. | HIGH | Retired | 2013-04-01 | 2015-07-15 | TOP
PRC-001-1.1 | System Protection Coordination | R5. | A Generator Operator or Transmission Operator shall coordinate changes in generation, transmission, load or operating conditions that could require changes in the Protection Systems of others: | HIGH | Retired | 2013-04-01 | 2015-07-15 | TOP, GOP
PRC-001-1.1 | System Protection Coordination | R5. | A Generator Operator or Transmission Operator shall coordinate changes in generation, transmission, load or operating conditions that could require changes in the Protection Systems of others: | HIGH | Retired | 2013-04-01 | 2015-07-15 | TOP, GOP
PRC-001-1.1 | System Protection Coordination | R5. | A Generator Operator or Transmission Operator shall coordinate changes in generation, transmission, load or operating conditions that could require changes in the Protection Systems of others: | HIGH | Retired | 2013-04-01 | 2015-07-15 | TOP, GOP
PRC-001-1.1 | System Protection Coordination | R5.1. | Each Generator Operator shall notify its Transmission Operator in advance of changes in generation or operating conditions that could require changes in the Transmission Operator’s Protection Systems. | HIGH | Retired | 2013-04-01 | 2015-07-15 | GOP
PRC-001-1.1 | System Protection Coordination | R5.2. | Each Transmission Operator shall notify neighboring Transmission Operators in advance of changes in generation, transmission, load, or operating conditions that could require changes in the other Transmission Operators’ Protection Systems. | HIGH | Retired | 2013-04-01 | 2015-07-15 | TOP
PRC-001-1.1 | System Protection Coordination | R5.2. | Each Transmission Operator shall notify neighboring Transmission Operators in advance of changes in generation, transmission, load, or operating conditions that could require changes in the other Transmission Operators’ Protection Systems. | HIGH | Retired | 2013-04-01 | 2015-07-15 | TOP
PRC-001-1.1 | System Protection Coordination | R5.2. | Each Transmission Operator shall notify neighboring Transmission Operators in advance of changes in generation, transmission, load, or operating conditions that could require changes in the other Transmission Operators’ Protection Systems. | HIGH | Retired | 2013-04-01 | 2015-07-15 | TOP
PRC-001-1.1 | System Protection Coordination | R6. | Each Transmission Operator and Balancing Authority shall monitor the status of each Special Protection System in their area, and shall notify affected Transmission Operators and Balancing Authorities of each change in status. | HIGH | Retired | 2013-04-01 | 2015-07-15 | TOP, BA
PRC-001-1.1(i) | System Protection Coordination | R1. | Each Transmission Operator, Balancing Authority, and Generator Operator shall be familiar with the purpose and limitations of Protection System schemes applied in its area. | HIGH | Retired |  |  | TOP, GOP, BA
PRC-001-1.1(i) | System Protection Coordination | R2. | Each Generator Operator and Transmission Operator shall notify reliability entities of relay or equipment failures as follows: | HIGH | Retired |  |  | TOP, GOP
PRC-001-1.1(i) | System Protection Coordination | R2.1. | If a protective relay or equipment failure reduces system reliability, the Generator Operator shall notify its Transmission Operator and Host Balancing Authority. The Generator Operator shall take corrective action as soon as possible. | HIGH | Retired |  |  | GOP
PRC-001-1.1(i) | System Protection Coordination | R2.2. | If a protective relay or equipment failure reduces system reliability, the Transmission Operator shall notify its Reliability Coordinator and affected Transmission Operators and Balancing Authorities. The Transmission Operator shall take corrective action as soon as possible. | HIGH | Retired |  |  | TOP
PRC-001-1.1(i) | System Protection Coordination | R3. | A Generator Operator or Transmission Operator shall coordinate new protective systems and changes as follows. | No Individual VRF Assigned | Retired |  |  | TOP, GOP
PRC-001-1.1(i) | System Protection Coordination | R3.1. | Each Generator Operator shall coordinate all new protective systems and all protective system changes with its Transmission Operator and Host Balancing Authority. | HIGH | Retired |  |  | GOP
PRC-001-1.1(i) | System Protection Coordination | R3.2. | Each Transmission Operator shall coordinate all new protective systems and all protective system changes with neighboring Transmission Operators and Balancing Authorities. | HIGH | Retired |  |  | TOP
PRC-001-1.1(i) | System Protection Coordination | R4. | Each Transmission Operator shall coordinate Protection Systems on major transmission lines and interconnections with neighboring Generator Operators, Transmission Operators, and Balancing Authorities. | HIGH | Retired |  |  | TOP
PRC-001-1.1(i) | System Protection Coordination | R5. | A Generator Operator or Transmission Operator shall coordinate changes in generation, transmission, load or operating conditions that could require changes in the Protection Systems of others: | HIGH | Retired |  |  | TOP, GOP
PRC-001-1.1(i) | System Protection Coordination | R5. | A Generator Operator or Transmission Operator shall coordinate changes in generation, transmission, load or operating conditions that could require changes in the Protection Systems of others: | HIGH | Retired |  |  | TOP, GOP
PRC-001-1.1(i) | System Protection Coordination | R5. | A Generator Operator or Transmission Operator shall coordinate changes in generation, transmission, load or operating conditions that could require changes in the Protection Systems of others: | HIGH | Retired |  |  | TOP, GOP
PRC-001-1.1(i) | System Protection Coordination | R5.1. | Each Generator Operator shall notify its Transmission Operator in advance of changes in generation or operating conditions that could require changes in the Transmission Operator’s Protection Systems. | HIGH | Retired |  |  | GOP
PRC-001-1.1(i) | System Protection Coordination | R5.2. | Each Transmission Operator shall notify neighboring Transmission Operators in advance of changes in generation, transmission, load, or operating conditions that could require changes in the other Transmission Operators’ Protection Systems. | HIGH | Retired |  |  | TOP
PRC-001-1.1(i) | System Protection Coordination | R5.2. | Each Transmission Operator shall notify neighboring Transmission Operators in advance of changes in generation, transmission, load, or operating conditions that could require changes in the other Transmission Operators’ Protection Systems. | HIGH | Retired |  |  | TOP
PRC-001-1.1(i) | System Protection Coordination | R5.2. | Each Transmission Operator shall notify neighboring Transmission Operators in advance of changes in generation, transmission, load, or operating conditions that could require changes in the other Transmission Operators’ Protection Systems. | HIGH | Retired |  |  | TOP
PRC-001-1.1(i) | System Protection Coordination | R6. | Each Transmission Operator and Balancing Authority shall monitor the status of each Remedial Action Scheme in their area, and shall notify affected Transmission Operators and Balancing Authorities of each change in status. | HIGH | Retired |  |  | TOP, BA
PRC-001-1.1(ii) | System Protection Coordination | R1. | Each Transmission Operator, Balancing Authority, and Generator Operator shall be familiar with the purpose and limitations of Protection System schemes applied in its area. | HIGH | Retired | 2015-07-16 | 2020-09-30 | TOP, GOP, BA
PRC-001-1.1(ii) | System Protection Coordination | R2. | Each Generator Operator and Transmission Operator shall notify reliability entities of relay or equipment failures as follows: | HIGH | Retired | 2015-07-16 | 2017-03-31 | TOP, GOP
PRC-001-1.1(ii) | System Protection Coordination | R2.1. | If a protective relay or equipment failure reduces system reliability, the Generator Operator shall notify its Transmission Operator and Host Balancing Authority. The Generator Operator shall take corrective action as soon as possible. | HIGH | Retired | 2015-07-16 | 2017-03-31 | GOP
PRC-001-1.1(ii) | System Protection Coordination | R2.2. | If a protective relay or equipment failure reduces system reliability, the Transmission Operator shall notify its Reliability Coordinator and affected Transmission Operators and Balancing Authorities. The Transmission Operator shall take corrective action as soon as possible. | HIGH | Retired | 2015-07-16 | 2017-03-31 | TOP
PRC-001-1.1(ii) | System Protection Coordination | R3. | A Generator Operator or Transmission Operator shall coordinate new protective systems and changes as follows. | HIGH | Retired | 2015-07-16 | 2020-09-30 | TOP, GOP
PRC-001-1.1(ii) | System Protection Coordination | R3.1. | Each Generator Operator shall coordinate all new protective systems and all protective system changes with its Transmission Operator and Host Balancing Authority. • Requirement R3.1 is not applicable to the individual generating units of dispersed power producing resources identified through Inclusion I4 of the Bulk Electric System definition. | HIGH | Retired | 2015-07-16 | 2020-09-30 | GOP
PRC-001-1.1(ii) | System Protection Coordination | R3.2. | Each Transmission Operator shall coordinate all new protective systems and all protective system changes with neighboring Transmission Operators and Balancing Authorities. | HIGH | Retired | 2015-07-16 | 2020-09-30 | TOP
PRC-001-1.1(ii) | System Protection Coordination | R4. | Each Transmission Operator shall coordinate Protection Systems on major transmission lines and interconnections with neighboring Generator Operators, Transmission Operators, and Balancing Authorities. | HIGH | Retired | 2015-07-16 | 2020-09-30 | TOP
PRC-001-1.1(ii) | System Protection Coordination | R5. | A Generator Operator or Transmission Operator shall coordinate changes in generation, transmission, load or operating conditions that could require changes in the Protection Systems of others: | HIGH | Retired | 2015-07-16 | 2017-03-31 | TOP, GOP
PRC-001-1.1(ii) | System Protection Coordination | R5. | A Generator Operator or Transmission Operator shall coordinate changes in generation, transmission, load or operating conditions that could require changes in the Protection Systems of others: | HIGH | Retired | 2015-07-16 | 2017-03-31 | TOP, GOP
PRC-001-1.1(ii) | System Protection Coordination | R5.1. | Each Generator Operator shall notify its Transmission Operator in advance of changes in generation or operating conditions that could require changes in the Transmission Operator’s Protection Systems. | HIGH | Retired | 2015-07-16 | 2017-03-31 | GOP
PRC-001-1.1(ii) | System Protection Coordination | R5.2. | Each Transmission Operator shall notify neighboring Transmission Operators in advance of changes in generation, transmission, load, or operating conditions that could require changes in the other Transmission Operators’ Protection Systems. | HIGH | Retired | 2015-07-16 | 2017-03-31 | TOP
PRC-001-1.1(ii) | System Protection Coordination | R5.2. | Each Transmission Operator shall notify neighboring Transmission Operators in advance of changes in generation, transmission, load, or operating conditions that could require changes in the other Transmission Operators’ Protection Systems. | HIGH | Retired | 2015-07-16 | 2017-03-31 | TOP
PRC-001-1.1(ii) | System Protection Coordination | R6. | Each Transmission Operator and Balancing Authority shall monitor the status of each Special Protection System in their area, and shall notify affected Transmission Operators and Balancing Authorities of each change in status. | HIGH | Retired | 2015-07-16 | 2017-03-31 | TOP, BA
PRC-001-2 | System Protection Coordination | R1. | Each Transmission Operator, Balancing Authority, and Generator Operator shall be familiar with the purpose and limitations of Protection System schemes applied in its area. | HIGH | Never Came Into Effect in Ontario |  |  | TOP, GOP, BA
PRC-001-2 | System Protection Coordination | R2. | A Generator Operator or Transmission Operator shall coordinate new protective systems and changes as follows. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TOP, GOP
PRC-001-2 | System Protection Coordination | R2.1. | Each Generator Operator shall coordinate all new protective systems and all protective system changes with its Transmission Operator and Host Balancing Authority. | HIGH | Never Came Into Effect in Ontario |  |  | GOP
PRC-001-2 | System Protection Coordination | R2.2. | Each Transmission Operator shall coordinate all new protective systems and all protective system changes with neighboring Transmission Operators and Balancing Authorities. | HIGH | Never Came Into Effect in Ontario |  |  | TOP
PRC-001-2 | System Protection Coordination | R3. | Each Transmission Operator shall coordinate Protection Systems on major transmission lines and interconnections with neighboring Generator Operators, Transmission Operators, and Balancing Authorities. | HIGH | Never Came Into Effect in Ontario |  |  | TOP, GOP
PRC-002-1 | Define Regional Disturbance Monitoring and Reporting Requirements | R1. | The Regional Reliability Organization shall establish the following installation requirements for sequence of event recording: | LOWER | Never Came Into Effect in Ontario
PRC-002-1 | Define Regional Disturbance Monitoring and Reporting Requirements | R1.1. | Location, monitoring and recording requirements, including the following: | LOWER | Never Came Into Effect in Ontario
PRC-002-1 | Define Regional Disturbance Monitoring and Reporting Requirements | R1.1.1. | Criteria for equipment location (e.g., by voltage, geographic area, station size, etc.). | LOWER | Never Came Into Effect in Ontario
PRC-002-1 | Define Regional Disturbance Monitoring and Reporting Requirements | R1.1.2. | Devices to be monitored. | LOWER | Never Came Into Effect in Ontario
PRC-002-1 | Define Regional Disturbance Monitoring and Reporting Requirements | R2. | The Regional Reliability Organization shall establish the following installation requirements for fault recording: | LOWER | Never Came Into Effect in Ontario
PRC-002-1 | Define Regional Disturbance Monitoring and Reporting Requirements | R2.1. | Location, monitoring and recording requirements, including the following: | LOWER | Never Came Into Effect in Ontario
PRC-002-1 | Define Regional Disturbance Monitoring and Reporting Requirements | R2.1.1. | Criteria for equipment location (e.g., by voltage, geographic area, station size, etc.). | LOWER | Never Came Into Effect in Ontario
PRC-002-1 | Define Regional Disturbance Monitoring and Reporting Requirements | R2.1.2. | Elements to be monitored at each location. | LOWER | Never Came Into Effect in Ontario
PRC-002-1 | Define Regional Disturbance Monitoring and Reporting Requirements | R2.1.3. | Electrical quantities to be recorded for each monitored element shall be sufficient to determine the following: | LOWER | Never Came Into Effect in Ontario
PRC-002-1 | Define Regional Disturbance Monitoring and Reporting Requirements | R2.1.3.1. | Three phase to neutral voltages. | LOWER | Never Came Into Effect in Ontario
PRC-002-1 | Define Regional Disturbance Monitoring and Reporting Requirements | R2.1.3.2. | Three phase currents and neutral currents. | LOWER | Never Came Into Effect in Ontario
PRC-002-1 | Define Regional Disturbance Monitoring and Reporting Requirements | R2.1.3.3. | Polarizing currents and voltages, if used. | LOWER | Never Came Into Effect in Ontario
PRC-002-1 | Define Regional Disturbance Monitoring and Reporting Requirements | R2.1.3.4. | Frequency. | LOWER | Never Came Into Effect in Ontario
PRC-002-1 | Define Regional Disturbance Monitoring and Reporting Requirements | R2.1.3.5. | Megawatts and megavars. | LOWER | Never Came Into Effect in Ontario
PRC-002-1 | Define Regional Disturbance Monitoring and Reporting Requirements | R2.2. | Technical requirements, including the following: | LOWER | Never Came Into Effect in Ontario
PRC-002-1 | Define Regional Disturbance Monitoring and Reporting Requirements | R2.2.1. | Recording duration requirements. | LOWER | Never Came Into Effect in Ontario
PRC-002-1 | Define Regional Disturbance Monitoring and Reporting Requirements | R2.2.2. | Minimum sampling rate of 16 samples per cycle. | LOWER | Never Came Into Effect in Ontario
PRC-002-1 | Define Regional Disturbance Monitoring and Reporting Requirements | R2.2.3. | Event triggering requirements. | LOWER | Never Came Into Effect in Ontario
PRC-002-1 | Define Regional Disturbance Monitoring and Reporting Requirements | R3. | The Regional Reliability Organization shall establish the following installation requirements for dynamic Disturbance recording: | LOWER | Never Came Into Effect in Ontario
PRC-002-1 | Define Regional Disturbance Monitoring and Reporting Requirements | R3.1. | Location, monitoring and recording requirements including the following: | LOWER | Never Came Into Effect in Ontario
PRC-002-1 | Define Regional Disturbance Monitoring and Reporting Requirements | R3.1.1. | Criteria for equipment location giving consideration to the following: - Site(s) in or near major load centers - Site(s) in or near major generation clusters - Site(s) in or near major voltage sensitive areas - Site(s) on both sides of major transmission interfaces - A major transmission junction - Elements associated with Interconnection Reliability Operating Limits - Major EHV interconnections between control areas - Coordination with neighboring regions within the interconnection | LOWER | Never Came Into Effect in Ontario
PRC-002-1 | Define Regional Disturbance Monitoring and Reporting Requirements | R3.1.2. | Elements and number of phases to be monitored at each location. | LOWER | Never Came Into Effect in Ontario
PRC-002-1 | Define Regional Disturbance Monitoring and Reporting Requirements | R3.1.3. | Electrical quantities to be recorded for each monitored element shall be sufficient to determine the following: | LOWER | Never Came Into Effect in Ontario
PRC-002-1 | Define Regional Disturbance Monitoring and Reporting Requirements | R3.1.3.1. | Voltage, current and frequency. | LOWER | Never Came Into Effect in Ontario
PRC-002-1 | Define Regional Disturbance Monitoring and Reporting Requirements | R3.1.3.2. | Megawatts and megavars. | LOWER | Never Came Into Effect in Ontario
PRC-002-1 | Define Regional Disturbance Monitoring and Reporting Requirements | R3.2. | Technical requirements, including the following: | LOWER | Never Came Into Effect in Ontario
PRC-002-1 | Define Regional Disturbance Monitoring and Reporting Requirements | R3.2.1. | Capability for continuous recording for devices installed after January 1, 2009. | LOWER | Never Came Into Effect in Ontario
PRC-002-1 | Define Regional Disturbance Monitoring and Reporting Requirements | R3.2.2. | Each device shall sample data at a rate of at least 960 samples per second and shall record the RMS value of electrical quantities at a rate of at least 6 records per second. | LOWER | Never Came Into Effect in Ontario
PRC-002-1 | Define Regional Disturbance Monitoring and Reporting Requirements | R4. | The Regional Reliability Organization shall establish requirements for facility owners to report Disturbance data recorded by their DME installations. The Disturbance data reporting requirements shall include the following: | LOWER | Never Came Into Effect in Ontario
PRC-002-1 | Define Regional Disturbance Monitoring and Reporting Requirements | R4.1. | Criteria for events that require the collection of data from DMEs. | LOWER | Never Came Into Effect in Ontario
PRC-002-1 | Define Regional Disturbance Monitoring and Reporting Requirements | R4.2. | List of entities that must be provided with recorded Disturbance data. | LOWER | Never Came Into Effect in Ontario
PRC-002-1 | Define Regional Disturbance Monitoring and Reporting Requirements | R4.3. | Timetable for response to data request. | LOWER | Never Came Into Effect in Ontario
PRC-002-1 | Define Regional Disturbance Monitoring and Reporting Requirements | R4.4. | Provision for reporting Disturbance data in a format which is capable of being viewed, read and analyzed with a generic COMTRADE1 analysis tool, | LOWER | Never Came Into Effect in Ontario
PRC-002-1 | Define Regional Disturbance Monitoring and Reporting Requirements | R4.5. | Naming of data files in conformance with the IEEE C37.232 Recommended Practice for Naming Time Sequence Data Files2. | LOWER | Never Came Into Effect in Ontario
PRC-002-1 | Define Regional Disturbance Monitoring and Reporting Requirements | R4.6. | Data content requirements and guidelines. | LOWER | Never Came Into Effect in Ontario
PRC-002-1 | Define Regional Disturbance Monitoring and Reporting Requirements | R5. | The Regional Reliability Organization shall provide its requirements (and any revisions to those requirements) including those for DME installation and Disturbance data reporting to the affected Transmission Owners and Generator Owners within 30 calendar days of approval of those requirements. | LOWER | Never Came Into Effect in Ontario
PRC-002-1 | Define Regional Disturbance Monitoring and Reporting Requirements | R6. | The Regional Reliability Organization shall periodically (at least every five years) review, update and approve its Regional requirements for Disturbance monitoring and reporting. | LOWER | Never Came Into Effect in Ontario
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R1. | Each Transmission Owner shall: [Violation Risk Factor: Lower ] [Time Horizon: Longterm Planning] | LOWER | Effective | 2016-07-01 |  | TO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R1.1. | Identify BES buses for which sequence of events recording (SER) and fault recording (FR) data is required by using the methodology in PRC-002-2, Attachment 1. | LOWER | Effective | 2016-07-01 |  | TO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R1.2. | Notify other owners of BES Elements connected to those BES buses, if any, within 90-calendar days of completion of Part 1.1, that those BES Elements require SER data and/or FR data. | LOWER | Effective | 2016-07-01 |  | TO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R1.3. | Re-evaluate all BES buses at least once every five calendar years in accordance with Part 1.1 and notify other owners, if any, in accordance with Part 1.2, and implement the re-evaluated list of BES buses as per the Implementation Plan. | LOWER | Effective | 2016-07-01 |  | TO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R10. | Each Transmission Owner and Generator Owner shall time synchronize all SER and FR data for the BES buses identified in Requirement R1 and DDR data for the BES Elements identified in Requirement R5 to meet the following: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | LOWER | Effective | 2021-07-01 |  | TO, GO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R10.1. | Synchronization to Coordinated Universal Time (UTC) with or without a local time offset. | LOWER | Effective | 2021-07-01 |  | TO, GO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R10.2. | Synchronized device clock accuracy within ± 2 milliseconds of UTC. | LOWER | Effective | 2021-07-01 |  | TO, GO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R11. | Each Transmission Owner and Generator Owner shall provide, upon request, all SER and FR data for the BES buses identified in Requirement R1 and DDR data for the BES Elements identified in Requirement R5 to the Responsible Entity, Regional Entity, or NERC in accordance with the following: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | LOWER | Effective | 2021-07-01 |  | TO, GO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R11.1. | Data will be retrievable for the period of 10-calendar days, inclusive of the day the data was recorded. | LOWER | Effective | 2021-07-01 |  | TO, GO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R11.2. | Data subject to Part 11.1 will be provided within 30-calendar days of a request unless an extension is granted by the requestor. | LOWER | Effective | 2021-07-01 |  | TO, GO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R11.3. | SER data will be provided in ASCII Comma Separated Value (CSV) format following Attachment 2. | LOWER | Effective | 2021-07-01 |  | TO, GO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R11.4. | FR and DDR data will be provided in electronic files that are formatted in conformance with C37.111, (IEEE Standard for Common Format for Transient Data Exchange (COMTRADE), revision C37.111-1999 or later. | LOWER | Effective | 2021-07-01 |  | TO, GO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R11.5. | Data files will be named in conformance with C37.232, IEEE Standard for Common Format for Naming Time Sequence Data Files (COMNAME), revision C37.232-2011 or later. | LOWER | Effective | 2021-07-01 |  | TO, GO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R12. | Each Transmission Owner and Generator Owner shall, within 90-calendar days of the discovery of a failure of the recording capability for the SER, FR or DDR data, either: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning]  Restore the recording capability, or  Submit a Corrective Action Plan (CAP) to the Regional Entity and implement it. | LOWER | Effective | 2016-10-01 |  | TO, GO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R2. | Each Transmission Owner and Generator Owner shall have SER data for circuit breaker position (open/close) for each circuit breaker it owns connected directly to the BES buses identified in Requirement R1 and associated with the BES Elements at those BES buses. [Violation Risk Factor: Lower ] [Time Horizon: Long-term Planning] | LOWER | Effective | 2021-07-01 |  | TO, GO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R3. | Each Transmission Owner and Generator Owner shall have FR data to determine the following electrical quantities for each triggered FR for the BES Elements it owns connected to the BES buses identified in Requirement R1: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | LOWER | Effective | 2021-07-01 |  | TO, GO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R3.1. | Phase-to-neutral voltage for each phase of each specified BES bus. | LOWER | Effective | 2021-07-01 |  | TO, GO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R3.2. | Each phase current and the residual or neutral current for the following BES Elements: | LOWER | Effective | 2021-07-01 |  | TO, GO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R3.2.1. | Transformers that have a low-side operating voltage of 100kV or above. | LOWER | Effective | 2021-07-01 |  | TO, GO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R3.2.2. | Transmission Lines. | LOWER | Effective | 2021-07-01 |  | TO, GO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R4. | Each Transmission Owner and Generator Owner shall have FR data as specified in Requirement R3 that meets the following: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | LOWER | Effective | 2021-07-01 |  | TO, GO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R4.1. | A single record or multiple records that include: • A pre-trigger record length of at least two cycles and a total record length of at least 30-cycles for the same trigger point, or • At least two cycles of the pre-trigger data, the first three cycles of the posttrigger data, and the final cycle of the fault as seen by the fault recorder. | LOWER | Effective | 2021-07-01 |  | TO, GO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R4.2. | A minimum recording rate of 16 samples per cycle. | LOWER | Effective | 2021-07-01 |  | TO, GO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R4.3. | Trigger settings for at least the following: | LOWER | Effective | 2021-07-01 |  | TO, GO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R4.3.1. | Neutral (residual) overcurrent. | LOWER | Effective | 2021-07-01 |  | TO, GO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R4.3.2. | Phase undervoltage or overcurrent. | LOWER | Effective | 2021-07-01 |  | TO, GO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R5. | Each Responsible Entity shall: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | LOWER | Effective | 2016-07-01 |  | PC
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R5. | Each Responsible Entity shall: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | LOWER | Effective | 2016-07-01 |  | PC
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R5. | Each Responsible Entity shall: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | LOWER | Effective | 2016-07-01 |  | PC
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R5.1. | Identify BES Elements for which dynamic Disturbance recording (DDR) data is required, including the following: | LOWER | Effective | 2016-07-01 |  | PC
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R5.1. | Identify BES Elements for which dynamic Disturbance recording (DDR) data is required, including the following: | LOWER | Effective | 2016-07-01 |  | PC
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R5.1.1. | Generating resource(s) with: | LOWER | Effective | 2016-07-01 |  | PC
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R5.1.1.1. | Gross individual nameplate rating greater than or equal to 500 MVA. | LOWER | Effective | 2016-07-01 |  | PC
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R5.1.1.2. | Gross individual nameplate rating greater than or equal to 300 MVA where the gross plant/facility aggregate nameplate rating is greater than or equal to 1,000 MVA. | LOWER | Effective | 2016-07-01 |  | PC
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R5.1.2. | Any one BES Element that is part of a stability (angular or voltage) related System Operating Limit (SOL). | LOWER | Effective | 2016-07-01 |  | PC
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R5.1.3. | Each terminal of a high voltage direct current (HVDC) circuit with a nameplate rating greater than or equal to 300 MVA, on the alternating current (AC) portion of the converter. | LOWER | Effective | 2016-07-01 |  | PC
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R5.1.4. | One or more BES Elements that are part of an Interconnection Reliability Operating Limit (IROL). | LOWER | Effective | 2016-07-01 |  | PC
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R5.1.5. | Any one BES Element within a major voltage sensitive area as defined by an area with an in-service undervoltage load shedding (UVLS) program. | LOWER | Effective | 2016-07-01 |  | PC
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R5.2. | Identify a minimum DDR coverage, inclusive of those BES Elements identified in Part 5.1, of at least: | LOWER | Effective | 2016-07-01 |  | PC
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R5.2.1. | One BES Element; and | LOWER | Effective | 2016-07-01 |  | PC
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R5.2.2. | One BES Element per 3,000 MW of the Responsible Entity’s historical simultaneous peak System Demand. | LOWER | Effective | 2016-07-01 |  | PC
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R5.3. | Notify all owners of identified BES Elements, within 90-calendar days of completion of Part 5.1, that their respective BES Elements require DDR data when requested. | LOWER | Effective | 2016-07-01 |  | PC
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R5.4. | Re-evaluate all BES Elements at least once every five calendar years in accordance with Parts 5.1 and 5.2, and notify owners in accordance with Part 5.3 to implement the re-evaluated list of BES Elements as per the Implementation Plan. | LOWER | Effective | 2016-07-01 |  | PC
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R5.4. | Re-evaluate all BES Elements at least once every five calendar years in accordance with Parts 5.1 and 5.2, and notify owners in accordance with Part 5.3 to implement the re-evaluated list of BES Elements as per the Implementation Plan. | LOWER | Effective | 2016-07-01 |  | PC
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R6. | Each Transmission Owner shall have DDR data to determine the following electrical quantities for each BES Element it owns for which it received notification as identified in Requirement R5: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning ] | LOWER | Effective | 2021-07-01 |  | TO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R6.1. | One phase-to-neutral or positive sequence voltage. | LOWER | Effective | 2021-07-01 |  | TO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R6.2. | The phase current for the same phase at the same voltage corresponding to the voltage in Requirement R6, Part 6.1, or the positive sequence current. | LOWER | Effective | 2021-07-01 |  | TO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R6.3. | Real Power and Reactive Power flows expressed on a three phase basis corresponding to all circuits where current measurements are required. | LOWER | Effective | 2021-07-01 |  | TO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R6.4. | Frequency of any one of the voltage(s) in Requirement R6, Part 6.1. | LOWER | Effective | 2021-07-01 |  | TO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R7. | Each Generator Owner shall have DDR data to determine the following electrical quantities for each BES Element it owns for which it received notification as identified in Requirement R5: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | LOWER | Effective | 2021-07-11 |  | GO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R7.1. | One phase-to-neutral, phase-to-phase, or positive sequence voltage at either the generator step-up transformer (GSU) high-side or low-side voltage level. | LOWER | Effective | 2021-07-01 |  | GO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R7.2. | The phase current for the same phase at the same voltage corresponding to the voltage in Requirement R7, Part 7.1, phase current(s) for any phase-to-phase voltages, or positive sequence current. | LOWER | Effective | 2021-07-01 |  | GO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R7.3. | Real Power and Reactive Power flows expressed on a three phase basis corresponding to all circuits where current measurements are required. | LOWER | Effective | 2021-07-01 |  | GO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R7.4. | Frequency of at least one of the voltages in Requirement R7, Part 7.1. | LOWER | Effective | 2021-07-01 |  | GO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R8. | Each Transmission Owner and Generator Owner responsible for DDR data for the BES Elements identified in Requirement R5 shall have continuous data recording and storage. If the equipment was installed prior to the effective date of this standard and is not capable of continuous recording, triggered records must meet the following: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | LOWER | Effective | 2021-07-01 |  | TO, GO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R8.1. | Triggered record lengths of at least three minutes. | LOWER | Effective | 2021-07-01 |  | TO, GO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R8.2. | At least one of the following three triggers:  Off nominal frequency trigger set at: Low High o Eastern Interconnection <59.75 Hz >61.0 Hz o Western Interconnection <59.55 Hz >61.0 Hz o ERCOT Interconnection <59.35 Hz >61.0 Hz o Hydro-Quebec Interconnection <58.55 Hz >61.5 Hz  Rate of change of frequency trigger set at: o Eastern Interconnection < -0.03125 Hz/sec > 0.125 Hz/sec o Western Interconnection < -0.05625 Hz/sec > 0.125 Hz/sec o ERCOT Interconnection < -0.08125 Hz/sec > 0.125 Hz/sec o Hydro-Quebec Interconnection < -0.18125 Hz/sec > 0.1875 Hz/sec  Undervoltage trigger set no lower than 85 percent of normal operating voltage for a duration of 5 seconds. | LOWER | Effective | 2021-07-01 |  | TO, GO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R9. | Each Transmission Owner and Generator Owner responsible for DDR data for the BES Elements identified in Requirement R5 shall have DDR data that meet the following: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | LOWER | Effective | 2021-07-01 |  | TO, GO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R9.1. | Input sampling rate of at least 960 samples per second. | LOWER | Effective | 2021-07-01 |  | TO, GO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R9.2. | Output recording rate of electrical quantities of at least 30 times per second. | LOWER | Effective | 2021-07-01 |  | TO, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R1. | Each Transmission Owner shall: [Violation Risk Factor: Lower ] [Time Horizon: Longterm Planning] | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R1.1. | Identify BES buses for which sequence of events recording (SER) and fault recording (FR) data is required by using the methodology in PRC-002-3, Attachment 1. | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R1.2. | Notify other owners of BES Elements connected to those BES buses, if any, within 90-calendar days of completion of Part 1.1, that those BES Elements require SER data and/or FR data. | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R1.3. | Re-evaluate all BES buses at least once every five calendar years in accordance with Part 1.1 and notify other owners, if any, in accordance with Part 1.2, and implement the re-evaluated list of BES buses as per the Implementation Plan. | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R10. | Each Transmission Owner and Generator Owner shall time synchronize all SER and FR data for the BES buses identified in Requirement R1 and DDR data for the BES Elements identified in Requirement R5 to meet the following: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R10.1. | Synchronization to Coordinated Universal Time (UTC) with or without a local time offset. | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R10.2. | Synchronized device clock accuracy within ± 2 milliseconds of UTC. | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R11. | Each Transmission Owner and Generator Owner shall provide, upon request, all SER and FR data for the BES buses identified in Requirement R1 and DDR data for the BES Elements identified in Requirement R5 to the Reliability Coordinator, Regional Entity, or NERC in accordance with the following: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R11.1. | Data will be retrievable for the period of 10-calendar days, inclusive of the day the data was recorded. | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R11.2. | Data subject to Part 11.1 will be provided within 30-calendar days of a request unless an extension is granted by the requestor. | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R11.3. | SER data will be provided in ASCII Comma Separated Value (CSV) format following Attachment 2. | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R11.4. | FR and DDR data will be provided in electronic files that are formatted in conformance with C37.111, (IEEE Standard for Common Format for Transient Data Exchange (COMTRADE), revision C37.111-1999 or later. | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R11.5. | Data files will be named in conformance with C37.232, IEEE Standard for Common Format for Naming Time Sequence Data Files (COMNAME), revision C37.232-2011 or later. | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R12. | Each Transmission Owner and Generator Owner shall, within 90-calendar days of the discovery of a failure of the recording capability for the SER, FR or DDR data, either: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning]  Restore the recording capability, or  Submit a Corrective Action Plan (CAP) to the Regional Entity and implement it. | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R2. | Each Transmission Owner and Generator Owner shall have SER data for circuit breaker position (open/close) for each circuit breaker it owns connected directly to the BES buses identified in Requirement R1 and associated with the BES Elements at those BES buses. [Violation Risk Factor: Lower ] [Time Horizon: Long-term Planning] | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R3. | Each Transmission Owner and Generator Owner shall have FR data to determine the following electrical quantities for each triggered FR for the BES Elements it owns connected to the BES buses identified in Requirement R1: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R3.1. | Phase-to-neutral voltage for each phase of each specified BES bus. | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R3.2. | Each phase current and the residual or neutral current for the following BES Elements: | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R3.2.1. | Transformers that have a low-side operating voltage of 100kV or above. | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R3.2.2. | Transmission Lines. | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R4. | Each Transmission Owner and Generator Owner shall have FR data as specified in Requirement R3 that meets the following: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R4.1. | A single record or multiple records that include: • A pre-trigger record length of at least two cycles and a total record length of at least 30-cycles for the same trigger point, or • At least two cycles of the pre-trigger data, the first three cycles of the posttrigger data, and the final cycle of the fault as seen by the fault recorder. | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R4.2. | A minimum recording rate of 16 samples per cycle. | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R4.3. | Trigger settings for at least the following: | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R4.3.1. | Neutral (residual) overcurrent. | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R4.3.2. | Phase undervoltage or overcurrent. | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R5. | Each Reliability Coordinator shall: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R5.1. | Identify BES Elements for which dynamic Disturbance recording (DDR) data is required, including the following: | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R5.1.1. | Generating resource(s) with: | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R5.1.1.1. | Gross individual nameplate rating greater than or equal to 500 MVA. | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R5.1.1.2. | Gross individual nameplate rating greater than or equal to 300 MVA where the gross plant/facility aggregate nameplate rating is greater than or equal to 1,000 MVA. | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R5.1.2. | Any one BES Element that is part of a stability (angular or voltage) related System Operating Limit (SOL). | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R5.1.3. | Each terminal of a high voltage direct current (HVDC) circuit with a nameplate rating greater than or equal to 300 MVA, on the alternating current (AC) portion of the converter. | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R5.1.4. | One or more BES Elements that are part of an Interconnection Reliability Operating Limit (IROL). | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R5.1.5. | Any one BES Element within a major voltage sensitive area as defined by an area with an in-service undervoltage load shedding (UVLS) program. | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R5.2. | Identify a minimum DDR coverage, inclusive of those BES Elements identified in Part 5.1, of at least: | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R5.2.1. | One BES Element; and | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R5.2.2. | One BES Element per 3,000 MW of the Reliability Coordinator’s historical simultaneous peak System Demand. | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R5.3. | Notify all owners of identified BES Elements, within 90-calendar days of completion of Part 5.1, that their respective BES Elements require DDR data when requested. | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R5.4. | Re-evaluate all BES Elements at least once every five calendar years in accordance with Parts 5.1 and 5.2, and notify owners in accordance with Part 5.3 to implement the re-evaluated list of BES Elements as per the Implementation Plan. | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R6. | Each Transmission Owner shall have DDR data to determine the following electrical quantities for each BES Element it owns for which it received notification as identified in Requirement R5: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning ] | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R6.1. | One phase-to-neutral or positive sequence voltage. | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R6.2. | The phase current for the same phase at the same voltage corresponding to the voltage in Requirement R6, Part 6.1, or the positive sequence current. | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R6.3. | Real Power and Reactive Power flows expressed on a three phase basis corresponding to all circuits where current measurements are required. | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R6.4. | Frequency of any one of the voltage(s) in Requirement R6, Part 6.1. | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R7. | Each Generator Owner shall have DDR data to determine the following electrical quantities for each BES Element it owns for which it received notification as identified in Requirement R5: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R7.1. | One phase-to-neutral, phase-to-phase, or positive sequence voltage at either the generator step-up transformer (GSU) high-side or low-side voltage level. | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R7.2. | The phase current for the same phase at the same voltage corresponding to the voltage in Requirement R7, Part 7.1, phase current(s) for any phase-to-phase voltages, or positive sequence current. | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R7.3. | Real Power and Reactive Power flows expressed on a three phase basis corresponding to all circuits where current measurements are required. | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R7.4. | Frequency of at least one of the voltages in Requirement R7, Part 7.1. | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R8. | Each Transmission Owner and Generator Owner responsible for DDR data for the BES Elements identified in Requirement R5 shall have continuous data recording and storage. If the equipment was installed prior to the effective date of this standard and is not capable of continuous recording, triggered records must meet the following: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R8.1. | Triggered record lengths of at least three minutes. | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R8.2. | At least one of the following three triggers:  Off nominal frequency trigger set at: Low High o Eastern Interconnection <59.75 Hz >61.0 Hz o Western Interconnection <59.55 Hz >61.0 Hz o ERCOT Interconnection <59.35 Hz >61.0 Hz o Hydro-Quebec Interconnection <58.55 Hz >61.5 Hz  Rate of change of frequency trigger set at: o Eastern Interconnection < -0.03125 Hz/sec > 0.125 Hz/sec o Western Interconnection < -0.05625 Hz/sec > 0.125 Hz/sec o ERCOT Interconnection < -0.08125 Hz/sec > 0.125 Hz/sec o Hydro-Quebec Interconnection < -0.18125 Hz/sec > 0.1875 Hz/sec  Undervoltage trigger set no lower than 85 percent of normal operating voltage for a duration of 5 seconds. | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R9. | Each Transmission Owner and Generator Owner responsible for DDR data for the BES Elements identified in Requirement R5 shall have DDR data that meet the following: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R9.1. | Input sampling rate of at least 960 samples per second. | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-3 | Disturbance Monitoring and Reporting Requirements | R9.2. | Output recording rate of electrical quantities of at least 30 times per second. | LOWER | Effective | 2024-04-01 |  | TO, RC, GO
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R1. | Each Transmission Owner shall: [Violation Risk Factor: Lower] [Time Horizon: Longterm Planning] | LOWER | Future Effective | 2024-07-01 |  | TO
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R1.1. | Identify BES buses for which sequence of events recording (SER) and fault recording (FR) data is required by using the methodology in PRC-002-4, Attachment 1. | LOWER | Future Effective | 2024-07-01 |  | TO
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R1.2. | Notify the other owners of BES Elements directly connected1 to those BES buses, that SER or FR data is required for those BES Elements, only if the Transmission Owner who identified the BES buses in Part 1.1 does not have SER or FR data. This notification is required within 90 calendar days of completion of Part 1.1. | LOWER | Future Effective | 2024-07-01 |  | TO
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R1.3. | Re-evaluate all BES buses at least once every five calendar years in accordance with Part 1.1 and notify other owners in accordance with Part 1.2. | LOWER | Future Effective | 2024-07-01 |  | TO
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R10. | Each Transmission Owner and Generator Owner shall time synchronize all SER and FR data for the BES buses identified in Requirement R1 and DDR data for the BES Elements identified in Requirement R5 to meet the following: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | LOWER | Future Effective | 2024-07-01 |  | GO, TO
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R10.1. | Synchronization to Coordinated Universal Time (UTC) with or without a local time offset. | LOWER | Future Effective | 2024-07-01 |  | GO, TO
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R10.2. | Synchronized device clock accuracy within ± 2 milliseconds of UTC. | LOWER | Future Effective | 2024-07-01 |  | GO, TO
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R11. | Each Transmission Owner and Generator Owner shall provide, upon request, all SER and FR data for the BES buses identified in Requirement R1 and DDR data for the BES Elements identified in Requirement R5 to the Reliability Coordinator, Regional Entity, or NERC in accordance with the following: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | LOWER | Future Effective | 2024-07-01 |  | TO, GO
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R11.1. | Data will be retrievable for the period of 10 calendar days, inclusive of the day the data was recorded. | LOWER | Future Effective | 2024-07-01 |  | TO, GO
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R11.2. | Data subject to Part 11.1 will be provided within 30 calendar days of a request unless an extension is granted by the requestor. | LOWER | Future Effective | 2024-07-01 |  | TO, GO
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R11.3. | SER data will be provided in ASCII Comma Separated Value (CSV) format following Attachment 2. | LOWER | Future Effective | 2024-07-01 |  | TO, GO
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R11.4. | FR and DDR data will be provided in electronic files that are formatted in conformance with C37.111, (IEEE Standard Common Format for Transient Data Exchange (COMTRADE), revision C37.111-1999 or later. | LOWER | Future Effective | 2024-07-01 |  | TO, GO
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R11.5. | Data files will be named in conformance with C37.232, IEEE Standard for Common Format for Naming Time Sequence Data Files (COMNAME), revision C37.232-2011 or later. | LOWER | Future Effective | 2024-07-01 |  | TO, GO
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R12. | Each Transmission Owner and Generator Ownershall, within 90 calendar days of the discovery of a failure of the recording capability for the SER, FR or DDR data, either: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] • Restore the recording capability, or • Submit a Corrective Action Plan (CAP) to the Regional Entity and implement it. | LOWER | Future Effective | 2024-07-01 |  | TO, GO
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R13. | Each Transmission Owner and Generator Ownershall: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | LOWER | Future Effective | 2024-07-01 |  | TO, GO
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R13.1. | Within three (3) calendar years of completing a re-evaluation or receiving notification under Requirement R1, Part 1.3, have SER or FR data as applicable for BES Elements directly connected to the identified BES buses. | LOWER | Future Effective | 2024-07-01 |  | TO, GO
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R13.2. | Within three (3) calendar years of receiving notification under Requirement R5, Part 5.4, have DDR data for BES Elements identified during the re-evaluation. | LOWER | Future Effective | 2024-07-01 |  | TO, GO
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R2. | Each Transmission Owner and Generator Owner shall have SER data for circuit breaker position (open/close) for each circuit breaker it owns directly connected to the BES buses identified in Requirement R1 and associated with the BES Elements at those BES buses. [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | LOWER | Future Effective | 2024-07-01 |  | GO, TO
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R3. | Each Transmission Owner and Generator Owner shall have FR data to determine the following electrical quantities for each triggered FR for the BES Elements it owns directly connected to the BES buses identified in Requirement R1: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | LOWER | Future Effective | 2024-07-01 |  | GO, TO
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R3.1. | Phase-to-neutral voltage for each phase of each specified BES bus. | LOWER | Future Effective | 2024-07-01 |  | GO, TO
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R3.2. | Each phase current and the residual or neutral current for the following BES Elements: | LOWER | Future Effective | 2024-07-01 |  | GO, TO
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R3.2.1. | Transformers that have a low-side operating voltage of 100 kV or above. | LOWER | Future Effective | 2024-07-01 |  | GO, TO
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R3.2.2. | Transmission Lines. | LOWER | Future Effective | 2024-07-01 |  | GO, TO
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R4. | Each Transmission Owner and Generator Owner shall have FR data as specified in Requirement R3 that meets the following: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | LOWER | Future Effective | 2024-07-01 |  | GO, TO
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R4.1. | A single record or multiple records that include: • A pre-trigger record length of at least two cycles and a total record length of at least 30 cycles for the same trigger point, or • At least two cycles of the pre-trigger data, the first three cycles of the posttrigger data, and the final cycle of the fault as seen by the fault | LOWER | Future Effective | 2024-07-01 |  | GO, TO
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R4.2. | A minimum recording rate of 16 samples per cycle. | LOWER | Future Effective | 2024-07-01 |  | GO, TO
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R4.3. | Trigger settings for at least the following: | LOWER | Future Effective | 2024-07-01 |  | GO, TO
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R4.3.1. | Neutral (residual) overcurrent. | LOWER | Future Effective | 2024-07-01 |  | GO, TO
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R4.3.2. | Phase undervoltage or overcurrent. | LOWER | Future Effective | 2024-07-01 |  | GO, TO
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R5. | Each Reliability Coordinatorshall: [Violation Risk Factor: Lower] [Time Horizon: Longterm Planning] | LOWER | Future Effective | 2024-07-01 |  | RC
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R5.1. | Identify BES Elements for which dynamic Disturbance recording (DDR) data is required, including the following: | LOWER | Future Effective | 2024-07-01 |  | RC
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R5.1.1. | Generating resource(s) with: | LOWER | Future Effective | 2024-07-01 |  | RC
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R5.1.1.1. | Gross individual nameplate rating greater than or equal to 500 MVA. | LOWER | Future Effective | 2024-07-01 |  | RC
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R5.1.1.2. | Gross individual nameplate rating greater than or equal to 300 MVA where the gross plant/facility aggregate nameplate rating is greater than or equal to 1,000 MVA. | LOWER | Future Effective | 2024-07-01 |  | RC
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R5.1.2. | Any one BES Element that is part of a stability (angular or voltage) related System Operating Limit (SOL). | LOWER | Future Effective | 2024-07-01 |  | RC
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R5.1.3. | Each terminal of a high voltage direct current (HVDC) circuit with a nameplate rating greater than or equal to 300 MVA, on the alternating current (AC) portion of the converter. | LOWER | Future Effective | 2024-07-01 |  | RC
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R5.1.4. | One or more BES Elements that are part of an Interconnection Reliability Operating Limit (IROL). | LOWER | Future Effective | 2024-07-01 |  | RC
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R5.1.5. | Any one BES Element within a major voltage sensitive area as defined by an area with an in-service undervoltage load shedding (UVLS) program. | LOWER | Future Effective | 2024-07-01 |  | RC
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R5.2. | Identify a minimum DDR coverage, inclusive of those BES Elements identified in Part 5.1, of at least: | LOWER | Future Effective | 2024-07-01 |  | RC
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R5.2.1. | One BES Element; and | LOWER | Future Effective | 2024-07-01 |  | RC
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R5.2.2. | One BES Element per 3,000 MW of the Reliability Coordinator’s historical simultaneous peak System Demand. | LOWER | Future Effective | 2024-07-01 |  | RC
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R5.3. | Notify all owners of identified BES Elements, within 90 calendar days of completion of Part 5.1, that their respective BES Elements require DDR data. | LOWER | Future Effective | 2024-07-01 |  | RC
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R5.4. | Re-evaluate all BES Elements within its Reliability Coordinator Area at least once every five calendar years in accordance with Parts 5.1 and 5.2, and notify owners in accordance with Part 5.3. | LOWER | Future Effective | 2024-07-01 |  | RC
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R6. | Each Transmission Owner shall have DDR data to determine the following electrical quantities for each BES Element it owns for which it received notification as identified in Requirement R5: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | LOWER | Future Effective | 2024-07-01 |  | TO
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R6.1. | One phase-to-neutral or positive sequence voltage. | LOWER | Future Effective | 2024-07-01 |  | TO
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R6.2. | The phase current for the same phase at the same voltage corresponding to the voltage in Requirement R6, Part 6.1, or the positive sequence current. | LOWER | Future Effective | 2024-07-01 |  | TO
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R6.3. | Real Power and Reactive Power flows expressed on a three phase basis corresponding to all circuits where current measurements are required. | LOWER | Future Effective | 2024-07-01 |  | TO
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R6.4. | Frequency of any one of the voltage(s) in Requirement R6, Part 6.1. | LOWER | Future Effective | 2024-07-01 |  | TO
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R7. | Each Generator Owner shall have DDR data to determine the following electrical quantities for each BES Element it owns for which it received notification as identified in Requirement R5: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | LOWER | Future Effective | 2024-07-01 |  | GO
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R7.1. | One phase-to-neutral, phase-to-phase, or positive sequence voltage at either the generator step-up transformer (GSU) high-side or low-side voltage level. | LOWER | Future Effective | 2024-07-01 |  | GO
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R7.2. | The phase current for the same phase at the same voltage corresponding to the voltage in Requirement R7, Part 7.1, phase current(s) for any phase-to-phase voltages, or positive sequence current. | LOWER | Future Effective | 2024-07-01 |  | GO
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R7.3. | Real Power and Reactive Power flows expressed on a three phase basis corresponding to all circuits where current measurements are required. | LOWER | Future Effective | 2024-07-01 |  | GO
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R7.4. | Frequency of at least one of the voltages in Requirement R7, Part 7.1. | LOWER | Future Effective | 2024-07-01 |  | GO
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R8. | Each Transmission Owner and Generator Owner responsible for DDR data for the BES Elements identified in Requirement R5 shall have continuous data recording and storage. If the equipment was installed prior to the effective date of the Reliability Standard PRC-002-22 and is not capable of continuous recording, triggered records must meet the following: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | LOWER | Future Effective | 2024-07-01 |  | GO, TO
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R8.1. | Triggered record lengths of at least three minutes. | LOWER | Future Effective | 2024-07-01 |  | GO, TO
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R8.2. | At least one of the following three triggers: • Off nominal frequency triggerset at: Low High o Eastern Interconnectio <59.75 Hz >61.0 Hz o Western Interconnection <59.55 Hz >61.0 Hz o ERCOT Interconnection <59.35 Hz >61.0 Hz o Hydro-Quebec Interconnection <58.55 Hz >61.5 Hz • Rate of change of frequency trigger set at: Low High o Eastern Interconnection < -0.03125 Hz/sec >0.125 Hz/sec o Western Interconnection < -0.05625 Hz/sec >0.125 Hz/sec o ERCOT Interconnection < -0.08125 Hz/sec >0.125 Hz/sec o Hydro-Quebec Interconnection < -0.18125 Hz/sec >0.1875 Hz/sec • Undervoltage trigger set no lower than 85 percent of normal operating voltage for a duration of 5 seconds. | LOWER | Future Effective | 2024-07-01 |  | GO, TO
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R9. | Each Transmission Owner and Generator Owner responsible for DDR data for the BES Elements identified in Requirement R5 shall have DDR data that meet the following: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | LOWER | Future Effective | 2024-07-01 |  | GO, TO
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R9.1. | Input sampling rate of at least 960 samples per second. | LOWER | Future Effective | 2024-07-01 |  | GO, TO
PRC-002-4 | Disturbance Monitoring and Reporting Requirements | R9.2. | Output recording rate of electrical quantities of at least 30 times per second. | LOWER | Future Effective | 2024-07-01 |  | GO, TO
PRC-003-1 | Regional Procedure for Analysis of Misoperations of Transmission and Generation Protection Systems | R1. | Each Regional Reliability Organization shall establish, document and maintain its procedures for, review, analysis, reporting and mitigation of transmission and generation Protection System Misoperations. These procedures shall include the following elements: |  | Never Came Into Effect in Ontario
PRC-003-1 | Regional Procedure for Analysis of Misoperations of Transmission and Generation Protection Systems | R1.1. | The Protection Systems to be reviewed and analyzed for Misoperations (due to theirpotential impact on BES reliability). |  | Never Came Into Effect in Ontario
PRC-003-1 | Regional Procedure for Analysis of Misoperations of Transmission and Generation Protection Systems | R1.2. | Data reporting requirements (periodicity and format) for Misoperations. |  | Never Came Into Effect in Ontario
PRC-003-1 | Regional Procedure for Analysis of Misoperations of Transmission and Generation Protection Systems | R1.3. | Process for review, analysis follow up, and documentation of Corrective Action Plans for Misoperations. |  | Never Came Into Effect in Ontario
PRC-003-1 | Regional Procedure for Analysis of Misoperations of Transmission and Generation Protection Systems | R1.4. | Identification of the Regional Reliability Organization group responsible for the procedures and the process for approval of the procedures. |  | Never Came Into Effect in Ontario
PRC-003-1 | Regional Procedure for Analysis of Misoperations of Transmission and Generation Protection Systems | R2. | Each Regional Reliability Organization shall maintain and periodically update documentation of its procedures for review, analysis, reporting, and mitigation of transmission and generation Protection System Misoperations. |  | Never Came Into Effect in Ontario
PRC-003-1 | Regional Procedure for Analysis of Misoperations of Transmission and Generation Protection Systems | R3. | Each Regional Reliability Organization shall distribute procedures in Requirement 1 and any changes to those procedures, to the affected Transmission Owners, Distribution Providers that own transmission Protection Systems, and Generator Owners within 30 calendar days of approval of those procedures. |  | Never Came Into Effect in Ontario
PRC-004-2 | Analysis and Mitigation of Transmission and Generation Protection System Misoperations | R1. | The Transmission Owner and any Distribution Provider that owns a transmission Protection System shall each analyze its transmission Protection System Misoperations and shall develop and implement a Corrective Action Plan to avoid future Misoperations of a similar nature according to the Regional Entity’s procedures. | HIGH | Retired |  |  | TO, DP
PRC-004-2 | Analysis and Mitigation of Transmission and Generation Protection System Misoperations | R2. | The Generator Owner shall analyze its generator Protection System Misoperations, and shall develop and implement a Corrective Action Plan to avoid future Misoperations of a similar nature according to the Regional Entity’s procedures. | HIGH | Retired |  |  | GO
PRC-004-2 | Analysis and Mitigation of Transmission and Generation Protection System Misoperations | R3. | The Transmission Owner, any Distribution Provider that owns a transmission Protection System, and the Generator Owner shall each provide to its Regional Entity, documentation of its Misoperations analyses and Corrective Action Plans according to the Regional Entity’s procedures. | LOWER | Retired |  |  | TO, GO, DP
PRC-004-2.1(i)a | Analysis and Mitigation of Transmission and Generation Protection System Misoperations | R1. | The Transmission Owner and any Distribution Provider that owns a transmission Protection System shall each analyze its transmission Protection System Misoperations and shall develop and implement a Corrective Action Plan to avoid future Misoperations of a similar nature according to the Regional Entity’s procedures. | HIGH | Retired | 2015-06-14 | 2016-06-30 | TO, DP
PRC-004-2.1(i)a | Analysis and Mitigation of Transmission and Generation Protection System Misoperations | R2. | The Generator Owner shall analyze its generator and generator interconnection Facility Protection System Misoperations, and shall develop and implement a Corrective Action Plan to avoid future Misoperations of a similar nature according to the Regional Entity’s procedures.  For Misoperations occurring on the Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES facilities, this requirement does not apply. | HIGH | Retired | 2015-06-14 | 2016-06-30 | GO
PRC-004-2.1(i)a | Analysis and Mitigation of Transmission and Generation Protection System Misoperations | R3. | The Transmission Owner, any Distribution Provider that owns a transmission Protection System, and the Generator Owner shall each provide to its Regional Entity, documentation of its Misoperations analyses and Corrective Action Plans according to the Regional Entity’s procedures.  For Misoperations occurring on the Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES facilities, this requirement does not apply. | LOWER | Retired | 2015-06-14 | 2016-06-30 | TO, GO, DP
PRC-004-2.1a | Analysis and Mitigation of Transmission and Generation Protection System Misoperations | R1. | The Transmission Owner and any Distribution Provider that owns a transmission Protection System shall each analyze its transmission Protection System Misoperations and shall develop and implement a Corrective Action Plan to avoid future Misoperations of a similar nature according to the Regional Entity’s procedures. | HIGH | Retired | 2013-11-25 | 2015-06-13 | TO, DP
PRC-004-2.1a | Analysis and Mitigation of Transmission and Generation Protection System Misoperations | R2. | The Generator Owner shall analyze its generator and generator interconnection Facility Protection System Misoperations, and shall develop and implement a Corrective Action Plan to avoid future Misoperations of a similar nature according to the Regional Entity’s procedures. | HIGH | Retired | 2013-11-25 | 2015-06-13 | GO
PRC-004-2.1a | Analysis and Mitigation of Transmission and Generation Protection System Misoperations | R3. | The Transmission Owner, any Distribution Provider that owns a transmission Protection System, and the Generator Owner shall each provide to its Regional Entity, documentation of its Misoperations analyses and Corrective Action Plans according to the Regional Entity’s procedures. | LOWER | Retired | 2013-11-25 | 2015-06-13 | TO, GO, DP
PRC-004-3 | Protection System Misoperation Identification and Correction | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated under the circumstances in Parts 1.1 through 1.3 shall, within 120 calendar days of the BES interrupting device operation, identify whether its Protection System component(s) caused a Misoperation: [Violation Risk Factor: Medium][Time Horizon: Operations Assessment, Operations Planning] | MEDIUM | Retired |  |  | TO, GO, DP
PRC-004-3 | Protection System Misoperation Identification and Correction | R1.1. | The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and | MEDIUM | Retired |  |  | TO, GO, DP
PRC-004-3 | Protection System Misoperation Identification and Correction | R1.2. | The BES interrupting device owner owns all or part of the Composite Protection System; and | MEDIUM | Retired |  |  | TO, GO, DP
PRC-004-3 | Protection System Misoperation Identification and Correction | R1.3. | The BES interrupting device owner identified that its Protection System component(s) caused the BES interrupting device(s) operation or was caused by manual intervention in response to its Protection System failure to operate. | MEDIUM | Retired |  |  | TO, GO, DP
PRC-004-3 | Protection System Misoperation Identification and Correction | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated shall, within 120 calendar days of the BES interrupting device operation, provide notification as described in Parts 2.1 and 2.2. [Violation Risk Factor: Medium][Time Horizon: Operations Assessment, Operations Planning] | MEDIUM | Retired |  |  | TO, GO, DP
PRC-004-3 | Protection System Misoperation Identification and Correction | R2.1. | For a BES interrupting device operation by a Composite Protection System or by manual intervention in response to a Protection System failure to operate, notification of the operation shall be provided to the other owner(s) that share Misoperation identification responsibility for the Composite Protection System under the following circumstances: | MEDIUM | Retired |  |  | TO, GO, DP
PRC-004-3 | Protection System Misoperation Identification and Correction | R2.1.1. | The BES interrupting device owner shares the Composite Protection System ownership with any other owner; and | MEDIUM | Retired |  |  | TO, GO, DP
PRC-004-3 | Protection System Misoperation Identification and Correction | R2.1.2. | The BES interrupting device owner has determined that a Misoperation occurred or cannot rule out a Misoperation; and | MEDIUM | Retired |  |  | TO, GO, DP
PRC-004-3 | Protection System Misoperation Identification and Correction | R2.1.3. | The BES interrupting device owner has determined that its Protection System component(s) did not cause the BES interrupting device(s) operation or cannot determine whether its Protection System components caused the BES interrupting device(s) operation. | MEDIUM | Retired |  |  | TO, GO, DP
PRC-004-3 | Protection System Misoperation Identification and Correction | R2.2. | For a BES interrupting device operation by a Protection System component intended to operate as backup protection for a condition on another entity’s BES Element, notification of the operation shall be provided to the other Protection System owner(s) for which that backup protection was provided. | MEDIUM | Retired |  |  | TO, GO, DP
PRC-004-3 | Protection System Misoperation Identification and Correction | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that receives notification, pursuant to Requirement R2 shall, within the later of 60 calendar days of notification or 120 calendar days of the BES interrupting device(s) operation, identify whether its Protection System component(s) caused a Misoperation. [Violation Risk Factor: Medium][Time Horizon: Operations Assessment, Operations Planning] | MEDIUM | Retired |  |  | TO, GO, DP
PRC-004-3 | Protection System Misoperation Identification and Correction | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that receives notification, pursuant to Requirement R2 shall, within the later of 60 calendar days of notification or 120 calendar days of the BES interrupting device(s) operation, identify whether its Protection System component(s) caused a Misoperation. [Violation Risk Factor: Medium][Time Horizon: Operations Assessment, Operations Planning] | MEDIUM | Retired |  |  | TO, GO, DP
PRC-004-3 | Protection System Misoperation Identification and Correction | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns the Protection System component(s) that caused the Misoperation shall, within 60 calendar days of first identifying a cause of the Misoperation: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning, Long-Term Planning]  Develop a Corrective Action Plan (CAP) for the identified Protection System component(s), and an evaluation of the CAP’s applicability to the entity’s other Protection Systems including other locations; or  Explain in a declaration why corrective actions are beyond the entity’s control or would not improve BES reliability, and that no further corrective actions will be taken. | MEDIUM | Retired |  |  | TO, GO, DP
PRC-004-3 | Protection System Misoperation Identification and Correction | R6. | Each Transmission Owner, Generator Owner, and Distribution Provider shall implement each CAP developed in Requirement R5, and update each CAP if actions or timetables change, until completed. [Violation Risk Factor: Medium][Time Horizon: Operations Planning, Long-Term Planning] | MEDIUM | Retired |  |  | TO, GO, DP
PRC-004-3(i) | Protection System Misoperation Identification and Correction | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated under the circumstances in Parts 1.1 through 1.3 shall, within 120 calendar days of the BES interrupting device operation, identify whether its Protection System component(s) caused a Misoperation: [Violation Risk Factor: High][Time Horizon: Operations Assessment, Operations Planning] | HIGH | Retired |  |  | TO, GO, DP
PRC-004-3(i) | Protection System Misoperation Identification and Correction | R1.1. | The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and | HIGH | Retired |  |  | TO, GO, DP
PRC-004-3(i) | Protection System Misoperation Identification and Correction | R1.2. | The BES interrupting device owner owns all or part of the Composite Protection System; and | HIGH | Retired |  |  | TO, GO, DP
PRC-004-3(i) | Protection System Misoperation Identification and Correction | R1.3. | The BES interrupting device owner identified that its Protection System component(s) caused the BES interrupting device(s) operation or was caused by manual intervention in response to its Protection System failure to operate. | HIGH | Retired |  |  | TO, GO, DP
PRC-004-3(i) | Protection System Misoperation Identification and Correction | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated shall, within 120 calendar days of the BES interrupting device operation, provide notification as described in Parts 2.1 and 2.2. [Violation Risk Factor: High][Time Horizon: Operations Assessment, Operations Planning] | HIGH | Retired |  |  | TO, GO, DP
PRC-004-3(i) | Protection System Misoperation Identification and Correction | R2.1. | For a BES interrupting device operation by a Composite Protection System or by manual intervention in response to a Protection System failure to operate, notification of the operation shall be provided to the other owner(s) that share Misoperation identification responsibility for the Composite Protection System under the following circumstances: | HIGH | Retired |  |  | TO, GO, DP
PRC-004-3(i) | Protection System Misoperation Identification and Correction | R2.1.1. | The BES interrupting device owner shares the Composite Protection System ownership with any other owner; and | HIGH | Retired |  |  | TO, GO, DP
PRC-004-3(i) | Protection System Misoperation Identification and Correction | R2.1.2. | The BES interrupting device owner has determined that a Misoperation occurred or cannot rule out a Misoperation; and | HIGH | Retired |  |  | TO, GO, DP
PRC-004-3(i) | Protection System Misoperation Identification and Correction | R2.1.3. | The BES interrupting device owner has determined that its Protection System component(s) did not cause the BES interrupting device(s) operation or cannot determine whether its Protection System components caused the BES interrupting device(s) operation. | HIGH | Retired |  |  | TO, GO, DP
PRC-004-3(i) | Protection System Misoperation Identification and Correction | R2.2. | For a BES interrupting device operation by a Protection System component intended to operate as backup protection for a condition on another entity’s BES Element, notification of the operation shall be provided to the other Protection System owner(s) for which that backup protection was provided. | HIGH | Retired |  |  | TO, GO, DP
PRC-004-3(i) | Protection System Misoperation Identification and Correction | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that receives notification, pursuant to Requirement R2 shall, within the later of 60 calendar days of notification or 120 calendar days of the BES interrupting device(s) operation, identify whether its Protection System component(s) caused a Misoperation. [Violation Risk Factor: High][Time Horizon: Operations Assessment, Operations Planning] | HIGH | Retired |  |  | TO, GO, DP
PRC-004-3(i) | Protection System Misoperation Identification and Correction | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that has not determined the cause(s) of a Misoperation, for a Misoperation identified in accordance with Requirement R1 or R3, shall perform investigative action(s) to determine the cause(s) of the Misoperation at least once every two full calendar quarters after the Misoperation was first identified, until one of the following completes the investigation: [Violation Risk Factor: High] [Time Horizon: Operations Assessment, Operations Planning] ● The identification of the cause(s) of the Misoperation; or ● A declaration that no cause was identified. | HIGH | Retired |  |  | TO, GO, DP
PRC-004-3(i) | Protection System Misoperation Identification and Correction | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns the Protection System component(s) that caused the Misoperation shall, within 60 calendar days of first identifying a cause of the Misoperation: [Violation Risk Factor: High] [Time Horizon: Operations Planning, Long-Term Planning] ● Develop a Corrective Action Plan (CAP) for the identified Protection System component(s), and an evaluation of the CAP’s applicability to the entity’s other Protection Systems including other locations; or ● Explain in a declaration why corrective actions are beyond the entity’s control or would not improve BES reliability, and that no further corrective actions will be taken. | HIGH | Retired |  |  | TO, GO, DP
PRC-004-3(i) | Protection System Misoperation Identification and Correction | R6. | Each Transmission Owner, Generator Owner, and Distribution Provider shall implement each CAP developed in Requirement R5, and update each CAP if actions or timetables change, until completed. [Violation Risk Factor: High][Time Horizon: Operations Planning, Long-Term Planning] | HIGH | Retired |  |  | TO, GO, DP
PRC-004-4 | Protection System Misoperation Identification and Correction | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated under the circumstances in Parts 1.1 through 1.3 shall, within 120 calendar days of the BES interrupting device operation, identify whether its Protection System component(s) caused a Misoperation: [Violation Risk Factor: Medium][Time Horizon: Operations Assessment, Operations Planning] | MEDIUM | Retired |  |  | TO, GO, DP
PRC-004-4 | Protection System Misoperation Identification and Correction | R1.1. | The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and | MEDIUM | Retired |  |  | TO, GO, DP
PRC-004-4 | Protection System Misoperation Identification and Correction | R1.2. | The BES interrupting device owner owns all or part of the Composite Protection System; and | MEDIUM | Retired |  |  | TO, GO, DP
PRC-004-4 | Protection System Misoperation Identification and Correction | R1.3. | The BES interrupting device owner identified that its Protection System component(s) caused the BES interrupting device(s) operation or was caused by manual intervention in response to its Protection System failure to operate. | MEDIUM | Retired |  |  | TO, GO, DP
PRC-004-4 | Protection System Misoperation Identification and Correction | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated shall, within 120 calendar days of the BES interrupting device operation, provide notification as described in Parts 2.1 and 2.2. [Violation Risk Factor: Medium][Time Horizon: Operations Assessment, Operations Planning] | MEDIUM | Retired |  |  | TO, GO, DP
PRC-004-4 | Protection System Misoperation Identification and Correction | R2.1. | For a BES interrupting device operation by a Composite Protection System or by manual intervention in response to a Protection System failure to operate, notification of the operation shall be provided to the other owner(s) that share Misoperation identification responsibility for the Composite Protection System under the following circumstances: | MEDIUM | Retired |  |  | TO, GO, DP
PRC-004-4 | Protection System Misoperation Identification and Correction | R2.1.1. | The BES interrupting device owner shares the Composite Protection System ownership with any other owner; and | MEDIUM | Retired |  |  | TO, GO, DP
PRC-004-4 | Protection System Misoperation Identification and Correction | R2.1.2. | The BES interrupting device owner has determined that a Misoperation occurred or cannot rule out a Misoperation; and | MEDIUM | Retired |  |  | TO, GO, DP
PRC-004-4 | Protection System Misoperation Identification and Correction | R2.1.3. | The BES interrupting device owner has determined that its Protection System component(s) did not cause the BES interrupting device(s) operation or cannot determine whether its Protection System components caused the BES interrupting device(s) operation. | MEDIUM | Retired |  |  | TO, GO, DP
PRC-004-4 | Protection System Misoperation Identification and Correction | R2.2. | For a BES interrupting device operation by a Protection System component intended to operate as backup protection for a condition on another entity’s BES Element, notification of the operation shall be provided to the other Protection System owner(s) for which that backup protection was provided. | MEDIUM | Retired |  |  | TO, GO, DP
PRC-004-4 | Protection System Misoperation Identification and Correction | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that receives notification, pursuant to Requirement R2 shall, within the later of 60 calendar days of notification or 120 calendar days of the BES interrupting device(s) operation, identify whether its Protection System component(s) caused a Misoperation. [Violation Risk Factor: Medium][Time Horizon: Operations Assessment, Operations Planning] | MEDIUM | Retired |  |  | TO, GO, DP
PRC-004-4 | Protection System Misoperation Identification and Correction | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that has not determined the cause(s) of a Misoperation, for a Misoperation identified in accordance with Requirement R1 or R3, shall perform investigative action(s) to determine the cause(s) of the Misoperation at least once every two full calendar quarters after the Misoperation was first identified, until one of the following completes the investigation: [Violation Risk Factor: Medium] [Time Horizon: Operations Assessment, Operations Planning]  The identification of the cause(s) of the Misoperation; or  A declaration that no cause was identified. | MEDIUM | Retired |  |  | TO, GO, DP
PRC-004-4 | Protection System Misoperation Identification and Correction | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns the Protection System component(s) that caused the Misoperation shall, within 60 calendar days of first identifying a cause of the Misoperation: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning, Long-Term Planning]  Develop a Corrective Action Plan (CAP) for the identified Protection System component(s), and an evaluation of the CAP’s applicability to the entity’s other Protection Systems including other locations; or  Explain in a declaration why corrective actions are beyond the entity’s control or would not improve BES reliability, and that no further corrective actions will be taken. | MEDIUM | Retired |  |  | TO, GO, DP
PRC-004-4 | Protection System Misoperation Identification and Correction | R6. | Each Transmission Owner, Generator Owner, and Distribution Provider shall implement each CAP developed in Requirement R5, and update each CAP if actions or timetables change, until completed. [Violation Risk Factor: Medium][Time Horizon: Operations Planning, Long-Term Planning] | MEDIUM | Retired |  |  | TO, GO, DP
PRC-004-4(i) | Protection System Misoperation Identification and Correction | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated under the circumstances in Parts 1.1 through 1.3 shall, within 120 calendar days of the BES interrupting device operation, identify whether its Protection System component(s) caused a Misoperation: [Violation Risk Factor: High][Time Horizon: Operations Assessment, Operations Planning] | HIGH | Retired | 2016-07-01 | 2017-04-01 | TO, GO, DP
PRC-004-4(i) | Protection System Misoperation Identification and Correction | R1.1. | The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and | HIGH | Retired | 2016-07-01 | 2017-04-01 | TO, GO, DP
PRC-004-4(i) | Protection System Misoperation Identification and Correction | R1.2. | The BES interrupting device owner owns all or part of the Composite Protection System; and | HIGH | Retired | 2016-07-01 | 2017-04-01 | TO, GO, DP
PRC-004-4(i) | Protection System Misoperation Identification and Correction | R1.3. | The BES interrupting device owner identified that its Protection System component(s) caused the BES interrupting device(s) operation or was caused by manual intervention in response to its Protection System failure to operate. | HIGH | Retired | 2016-07-01 | 2017-04-01 | TO, GO, DP
PRC-004-4(i) | Protection System Misoperation Identification and Correction | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated shall, within 120 calendar days of the BES interrupting device operation, provide notification as described in Parts 2.1 and 2.2. [Violation Risk Factor: High][Time Horizon: Operations Assessment, Operations Planning] | HIGH | Retired | 2016-07-01 | 2017-04-01 | TO, GO, DP
PRC-004-4(i) | Protection System Misoperation Identification and Correction | R2.1. | For a BES interrupting device operation by a Composite Protection System or by manual intervention in response to a Protection System failure to operate, notification of the operation shall be provided to the other owner(s) that share Misoperation identification responsibility for the Composite Protection System under the following circumstances: | HIGH | Retired | 2016-07-01 | 2017-04-01 | TO, GO, DP
PRC-004-4(i) | Protection System Misoperation Identification and Correction | R2.1.1. | The BES interrupting device owner shares the Composite Protection System ownership with any other owner; and | HIGH | Retired | 2016-07-01 | 2017-04-01 | TO, GO, DP
PRC-004-4(i) | Protection System Misoperation Identification and Correction | R2.1.2. | The BES interrupting device owner has determined that a Misoperation occurred or cannot rule out a Misoperation; and | HIGH | Retired | 2016-07-01 | 2017-04-01 | TO, GO, DP
PRC-004-4(i) | Protection System Misoperation Identification and Correction | R2.1.3. | The BES interrupting device owner has determined that its Protection System component(s) did not cause the BES interrupting device(s) operation or cannot determine whether its Protection System components caused the BES interrupting device(s) operation. | HIGH | Retired | 2016-07-01 | 2017-04-01 | TO, GO, DP
PRC-004-4(i) | Protection System Misoperation Identification and Correction | R2.2. | For a BES interrupting device operation by a Protection System component intended to operate as backup protection for a condition on another entity’s BES Element, notification of the operation shall be provided to the other Protection System owner(s) for which that backup protection was provided. | HIGH | Retired | 2016-07-01 | 2017-04-01 | TO, GO, DP
PRC-004-4(i) | Protection System Misoperation Identification and Correction | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that receives notification, pursuant to Requirement R2 shall, within the later of 60 calendar days of notification or 120 calendar days of the BES interrupting device(s) operation, identify whether its Protection System component(s) caused a Misoperation. [Violation Risk Factor: High][Time Horizon: Operations Assessment, Operations Planning] | HIGH | Retired | 2016-07-01 | 2017-04-01 | TO, GO, DP
PRC-004-4(i) | Protection System Misoperation Identification and Correction | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that has not determined the cause(s) of a Misoperation, for a Misoperation identified in accordance with Requirement R1 or R3, shall perform investigative action(s) to determine the cause(s) of the Misoperation at least once every two full calendar quarters after the Misoperation was first identified, until one of the following completes the investigation: [Violation Risk Factor: High] [Time Horizon: Operations Assessment, Operations Planning] ● The identification of the cause(s) of the Misoperation; or ● A declaration that no cause was identified. | HIGH | Retired | 2016-07-01 | 2017-04-01 | TO, GO, DP
PRC-004-4(i) | Protection System Misoperation Identification and Correction | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns the Protection System component(s) that caused the Misoperation shall, within 60 calendar days of first identifying a cause of the Misoperation: [Violation Risk Factor: High] [Time Horizon: Operations Planning, Long-Term Planning] ● Develop a Corrective Action Plan (CAP) for the identified Protection System component(s), and an evaluation of the CAP’s applicability to the entity’s other Protection Systems including other locations; or ● Explain in a declaration why corrective actions are beyond the entity’s control or would not improve BES reliability, and that no further corrective actions will be taken. | HIGH | Retired | 2016-07-01 | 2017-04-01 | TO, GO, DP
PRC-004-4(i) | Protection System Misoperation Identification and Correction | R6. | Each Transmission Owner, Generator Owner, and Distribution Provider shall implement each CAP developed in Requirement R5, and update each CAP if actions or timetables change, until completed. [Violation Risk Factor: High][Time Horizon: Operations Planning, Long-Term Planning] | HIGH | Retired | 2016-07-01 | 2017-04-01 | TO, GO, DP
PRC-004-5 | Protection System Misoperation Identification and Correction | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated under the circumstances in Parts 1.1 through 1.3 shall, within 120 calendar days of the BES interrupting device operation, identify whether its Protection System component(s) caused a Misoperation: [Violation Risk Factor: Medium][Time Horizon: Operations Assessment, Operations Planning] | MEDIUM | Retired |  |  | TO, GO, DP
PRC-004-5 | Protection System Misoperation Identification and Correction | R1.1. | The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and | MEDIUM | Retired |  |  | TO, GO, DP
PRC-004-5 | Protection System Misoperation Identification and Correction | R1.2. | The BES interrupting device owner owns all or part of the Composite Protection System; and | MEDIUM | Retired |  |  | TO, GO, DP
PRC-004-5 | Protection System Misoperation Identification and Correction | R1.3. | The BES interrupting device owner identified that its Protection System component(s) caused the BES interrupting device(s) operation or was caused by manual intervention in response to its Protection System failure to operate. | MEDIUM | Retired |  |  | TO, GO, DP
PRC-004-5 | Protection System Misoperation Identification and Correction | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated shall, within 120 calendar days of the BES interrupting device operation, provide notification as described in Parts 2.1 and 2.2. [Violation Risk Factor: Medium][Time Horizon: Operations Assessment, Operations Planning] | MEDIUM | Retired |  |  | TO, GO, DP
PRC-004-5 | Protection System Misoperation Identification and Correction | R2.1. | For a BES interrupting device operation by a Composite Protection System or by manual intervention in response to a Protection System failure to operate, notification of the operation shall be provided to the other owner(s) that share Misoperation identification responsibility for the Composite Protection System under the following circumstances: | MEDIUM | Retired |  |  | TO, GO, DP
PRC-004-5 | Protection System Misoperation Identification and Correction | R2.1.1. | The BES interrupting device owner shares the Composite Protection System ownership with any other owner; and | MEDIUM | Retired |  |  | TO, GO, DP
PRC-004-5 | Protection System Misoperation Identification and Correction | R2.1.2. | The BES interrupting device owner has determined that a Misoperation occurred or cannot rule out a Misoperation; and | MEDIUM | Retired |  |  | TO, GO, DP
PRC-004-5 | Protection System Misoperation Identification and Correction | R2.1.3. | The BES interrupting device owner has determined that its Protection System component(s) did not cause the BES interrupting device(s) operation or cannot determine whether its Protection System components caused the BES interrupting device(s) operation. | MEDIUM | Retired |  |  | TO, GO, DP
PRC-004-5 | Protection System Misoperation Identification and Correction | R2.2. | For a BES interrupting device operation by a Protection System component intended to operate as backup protection for a condition on another entity’s BES Element, notification of the operation shall be provided to the other Protection System owner(s) for which that backup protection was provided. | MEDIUM | Retired |  |  | TO, GO, DP
PRC-004-5 | Protection System Misoperation Identification and Correction | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that receives notification, pursuant to Requirement R2 shall, within the later of 60 calendar days of notification or 120 calendar days of the BES interrupting device(s) operation, identify whether its Protection System component(s) caused a Misoperation. [Violation RisK Factor: Medium][Time Horizon: Operations Assessment, Operations Planning] | MEDIUM | Retired |  |  | TO, GO, DP
PRC-004-5 | Protection System Misoperation Identification and Correction | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that has not determined the cause(s) of a Misoperation, for a Misoperation identified in accordance with Requirement R1 or R3, shall perform investigative action(s) to determine the cause(s) of the Misoperation at least once every two full calendar quarters after the Misoperation was first identified, until one of the following completes the investigation: [Violation Risk Factor: Medium] [Time Horizon: Operations Assessment, Operations Planning]  The identification of the cause(s) of the Misoperation; or  A declaration that no cause was identified. | MEDIUM | Retired |  |  | TO, GO, DP
PRC-004-5 | Protection System Misoperation Identification and Correction | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns the Protection System component(s) that caused the Misoperation shall, within 60 calendar days of first identifying a cause of the Misoperation: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning, Long‐Term Planning]  Develop a Corrective Action Plan (CAP) for the identified Protection System component(s), and an evaluation of the CAP’s applicability to the entity’s other Protection Systems including other locations; or  Explain in a declaration why corrective actions are beyond the entity’s control or would not improve BES reliability, and that no further corrective actions will be taken. | MEDIUM | Retired |  |  | TO, GO, DP
PRC-004-5 | Protection System Misoperation Identification and Correction | R6. | Each Transmission Owner, Generator Owner, and Distribution Provider shall implement each CAP developed in Requirement R5, and update each CAP if actions or timetables change, until completed. [Violation Risk Factor: Medium][Time Horizon: Operations Planning, Long‐Term Planning] | MEDIUM | Retired |  |  | TO, GO, DP
PRC-004-5(i) | Protection System Misoperation Identification and Correction | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated under the circumstances in Parts 1.1 through 1.3 shall, within 120 calendar days of the BES interrupting device operation, identify whether its Protection System component(s) caused a Misoperation: [Violation Risk Factor: High][Time Horizon: Operations Assessment, Operations Planning] | HIGH | Retired | 2017-04-02 | 2021-03-31 | TO, GO, DP
PRC-004-5(I) | Protection System Misoperation Identification and Correction | R1.1. | The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and | HIGH | Retired | 2017-04-02 | 2021-03-31 | TO, GO, DP
PRC-004-5(I) | Protection System Misoperation Identification and Correction | R1.2. | The BES interrupting device owner owns all or part of the Composite Protection System; and | HIGH | Retired | 2017-04-02 | 2021-03-31 | TO, GO, DP
PRC-004-5(I) | Protection System Misoperation Identification and Correction | R1.3. | The BES interrupting device owner identified that its Protection System component(s) caused the BES interrupting device(s) operation or was caused by manual intervention in response to its Protection System failure to operate. | HIGH | Retired | 2017-04-02 | 2021-03-31 | TO, GO, DP
PRC-004-5(I) | Protection System Misoperation Identification and Correction | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated shall, within 120 calendar days of the BES interrupting device operation, provide notification as described in Parts 2.1 and 2.2. [Violation Risk Factor: High][Time Horizon: Operations Assessment, Operations Planning] | HIGH | Retired | 2017-04-02 | 2021-03-31 | TO, GO, DP
PRC-004-5(I) | Protection System Misoperation Identification and Correction | R2.1. | For a BES interrupting device operation by a Composite Protection System or by manual intervention in response to a Protection System failure to operate, notification of the operation shall be provided to the other owner(s) that share Misoperation identification responsibility for the Composite Protection System under the following circumstances: | HIGH | Retired | 2017-04-02 | 2021-03-31 | TO, GO, DP
PRC-004-5(I) | Protection System Misoperation Identification and Correction | R2.1.1. | The BES interrupting device owner shares the Composite Protection System ownership with any other owner; and | HIGH | Retired | 2017-04-02 | 2021-03-31 | TO, GO, DP
PRC-004-5(I) | Protection System Misoperation Identification and Correction | R2.1.2. | The BES interrupting device owner has determined that a Misoperation occurred or cannot rule out a Misoperation; and | HIGH | Retired | 2017-04-02 | 2021-03-31 | TO, GO, DP
PRC-004-5(I) | Protection System Misoperation Identification and Correction | R2.1.3. | The BES interrupting device owner has determined that its Protection System component(s) did not cause the BES interrupting device(s) operation or cannot determine whether its Protection System components caused the BES interrupting device(s) operation. | HIGH | Retired | 2017-04-02 | 2021-03-31 | TO, GO, DP
PRC-004-5(I) | Protection System Misoperation Identification and Correction | R2.2. | For a BES interrupting device operation by a Protection System component intended to operate as backup protection for a condition on another entity’s BES Element, notification of the operation shall be provided to the other Protection System owner(s) for which that backup protection was provided. | HIGH | Retired | 2017-04-02 | 2021-03-31 | TO, GO, DP
PRC-004-5(I) | Protection System Misoperation Identification and Correction | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that receives notification, pursuant to Requirement R2 shall, within the later of 60 calendar days of notification or 120 calendar days of the BES interrupting device(s) operation, identify whether its Protection System component(s) caused a Misoperation. [Violation Risk Factor: High][Time Horizon: Operations Assessment, Operations Planning] | HIGH | Retired | 2017-04-02 | 2021-03-31 | TO, GO, DP
PRC-004-5(I) | Protection System Misoperation Identification and Correction | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that has not determined the cause(s) of a Misoperation, for a Misoperation identified in accordance with Requirement R1 or R3, shall perform investigative action(s) to determine the cause(s) of the Misoperation at least once every two full calendar quarters after the Misoperation was first identified, until one of the following completes the investigation: [Violation Risk Factor: High] [Time Horizon: Operations Assessment, Operations Planning] ● The identification of the cause(s) of the Misoperation; or ● A declaration that no cause was identified. | HIGH | Retired | 2017-04-02 | 2021-03-31 | TO, GO, DP
PRC-004-5(I) | Protection System Misoperation Identification and Correction | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns the Protection System component(s) that caused the Misoperation shall, within 60 calendar days of first identifying a cause of the Misoperation: [Violation Risk Factor: High] [Time Horizon: Operations Planning, Long‐Term Planning] ● Develop a Corrective Action Plan (CAP) for the identified Protection System component(s), and an evaluation of the CAP’s applicability to the entity’s other Protection Systems including other locations; or ● Explain in a declaration why corrective actions are beyond the entity’s control or would not improve BES reliability, and that no further corrective actions will be taken. | HIGH | Retired | 2017-04-02 | 2021-03-31 | TO, GO, DP
PRC-004-5(I) | Protection System Misoperation Identification and Correction | R6. | Each Transmission Owner, Generator Owner, and Distribution Provider shall implement each CAP developed in Requirement R5, and update each CAP if actions or timetables change, until completed. [Violation Risk Factor: High][Time Horizon: Operations Planning, Long‐Term Planning] | HIGH | Retired | 2017-04-02 | 2021-03-31 | TO, GO, DP
PRC-004-6 | Protection System Misoperation Identification and Correction | R.1. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated under the circumstances in Parts 1.1 through 1.3 shall, within 120 calendar days of the BES interrupting device operation, identify whether its Protection System component(s) caused a Misoperation: [Violation Risk Factor: High][Time Horizon: Operations Assessment, Operations Planning] | HIGH | Effective | 2021-04-01 |  | DP, GO, TO
PRC-004-6 | Protection System Misoperation Identification and Correction | R1.1. | The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and | HIGH | Effective | 2021-04-01 |  | DP, GO, TO
PRC-004-6 | Protection System Misoperation Identification and Correction | R1.2. | The BES interrupting device owner owns all or part of the Composite Protection System; and | HIGH | Effective | 2021-04-01 |  | DP, TO, GO
PRC-004-6 | Protection System Misoperation Identification and Correction | R1.3. | The BES interrupting device owner identified that its Protection System component(s) caused the BES interrupting device(s) operation or was caused by manual intervention in response to its Protection System failure to operate. | HIGH | Effective | 2021-04-01 |  | DP, TO, GO
PRC-004-6 | Protection System Misoperation Identification and Correction | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated shall, within 120 calendar days of the BES interrupting device operation, provide notification as described in Parts 2.1 and 2.2. [Violation Risk Factor: High][Time Horizon: Operations Assessment, Operations Planning] | HIGH | Effective | 2021-04-01 |  | DP, TO, GO
PRC-004-6 | Protection System Misoperation Identification and Correction | R2.1. | For a BES interrupting device operation by a Composite Protection System or by manual intervention in response to a Protection System failure to operate, notification of the operation shall be provided to the other owner(s) that share Misoperation identification responsibility for the Composite Protection System under the following circumstances: | HIGH | Effective | 2021-04-01 |  | DP, TO, GO
PRC-004-6 | Protection System Misoperation Identification and Correction | R2.1.1. | The BES interrupting device owner shares the Composite Protection System ownership with any other owner; and | HIGH | Effective | 2021-04-01 |  | DP, TO, GO
PRC-004-6 | Protection System Misoperation Identification and Correction | R2.1.2. | The BES interrupting device owner has determined that a Misoperation occurred or cannot rule out a Misoperation; and | HIGH | Effective | 2021-04-01 |  | DP, TO, GO
PRC-004-6 | Protection System Misoperation Identification and Correction | R2.1.3. | The BES interrupting device owner has determined that its Protection System component(s) did not cause the BES interrupting device(s) operation or cannot determine whether its Protection System components caused the BES interrupting device(s) operation. | HIGH | Effective | 2021-04-01 |  | DP, TO, GO
PRC-004-6 | Protection System Misoperation Identification and Correction | R2.2. | For a BES interrupting device operation by a Protection System component intended to operate as backup protection for a condition on another entity’s BES Element, notification of the operation shall be provided to the other Protection System owner(s) for which that backup protection was provided. | HIGH | Effective | 2021-04-01 |  | DP, TO, GO
PRC-004-6 | Protection System Misoperation Identification and Correction | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that receives notification, pursuant to Requirement R2 shall, within the later of 60 calendar days of notification or 120 calendar days of the BES interrupting device(s) operation, identify whether its Protection System component(s) caused a Misoperation. [Violation Risk Factor: High][Time Horizon: Operations Assessment, Operations Planning] | HIGH | Effective | 2021-04-01 |  | DP, TO, GO
PRC-004-6 | Protection System Misoperation Identification and Correction | R4. | Reserved | HIGH | Effective | 2021-04-01 |  | DP, TO, GO
PRC-004-6 | Protection System Misoperation Identification and Correction | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns the Protection System component(s) that caused the Misoperation shall, within 60 calendar days of first identifying a cause of the Misoperation: [Violation Risk Factor: High] [Time Horizon: Operations Planning, Long‐Term Planning] ● Develop a Corrective Action Plan (CAP) for the identified Protection System component(s), and an evaluation of the CAP’s applicability to the entity’s other Protection Systems including other locations; or ● Explain in a declaration why corrective actions are beyond the entity’s control or would not improve BES reliability, and that no further corrective actions will be taken. | HIGH | Effective | 2021-04-01 |  | DP, TO, GO
PRC-004-6 | Protection System Misoperation Identification and Correction | R6. | Each Transmission Owner, Generator Owner, and Distribution Provider shall implement each CAP developed in Requirement R5, and update each CAP if actions or timetables change, until completed. [Violation Risk Factor: High][Time Horizon: Operations Planning, Long‐Term Planning] | HIGH | Effective | 2021-04-01 |  | DP, TO, GO
PRC-005-1.1b | Transmission and Generation Protection System Maintenance and Testing | R1. | Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation or generator interconnection Facility Protection System shall have a Protection System maintenance and testing program for Protection Systems that affect the reliability of the BES. The program shall include: | HIGH | Effective | 2013-11-25 | 2027-03-31 | TO, GO, DP
PRC-005-1.1b | Transmission and Generation Protection System Maintenance and Testing | R1.1. | Maintenance and testing intervals and their basis. | HIGH | Effective | 2013-11-25 | 2027-03-31 | TO, GO, DP
PRC-005-1.1b | Transmission and Generation Protection System Maintenance and Testing | R1.2. | Summary of maintenance and testing procedures. | HIGH | Effective | 2013-11-25 | 2027-03-31 | TO, GO, DP
PRC-005-1.1b | Transmission and Generation Protection System Maintenance and Testing | R2. | Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation or generator interconnection Facility Protection System shall provide documentation of its Protection System maintenance and testing program and the implementation of that program to its Regional Entity on request (within 30 calendar days). The documentation of the program implementation shall include: | LOWER | Effective | 2013-11-25 | 2027-03-31 | TO, GO, DP
PRC-005-1.1b | Transmission and Generation Protection System Maintenance and Testing | R2.1. | Evidence Protection System devices were maintained and tested within the defined intervals | HIGH | Effective | 2013-11-25 | 2027-03-31 | TO, GO, DP
PRC-005-1.1b | Transmission and Generation Protection System Maintenance and Testing | R2.2. | Date each Protection System device was last tested/maintained. | HIGH | Effective | 2013-11-25 | 2027-03-31 | TO, GO, DP
PRC-005-2 | Protection System Maintenance | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a Protection System Maintenance Program (PSMP) for its Protection Systems identified in Section 4.2. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] The PSMP shall: | MEDIUM | Retired | 2015-04-01 | 2015-06-13 | TO, GO, DP
PRC-005-2 | Protection System Maintenance | R1.1. | Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. | MEDIUM | Retired | 2015-04-01 | 2015-06-13 | TO, GO, DP
PRC-005-2 | Protection System Maintenance | R1.2. | Include the applicable monitored Component attributes applied to each Protection System Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, and Table 3 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System Components | MEDIUM | Retired | 2015-04-01 | 2015-06-13 | TO, GO, DP
PRC-005-2 | Protection System Maintenance | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals in its PSMP shall follow the procedure established in PRC-005 Attachment A to establish and maintain its performance-based intervals. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Retired | 2015-04-01 | 2015-06-13 | TO, GO, DP
PRC-005-2 | Protection System Maintenance | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes timebased maintenance program(s) shall maintain its Protection System Components that are included within the time-based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, and Table 3. [Violation Risk Factor: High] [Time Horizon: Operations Planning] | HIGH | Retired | 2015-04-01 | 2015-06-13 | TO, GO, DP
PRC-005-2 | Protection System Maintenance | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance program(s) in accordance with Requirement R2 shall implement and follow its PSMP for its Protection System Components that are included within the performance-based program(s). [Violation Risk Factor: High] [Time Horizon: Operations Planning] | HIGH | Retired | 2015-04-01 | 2015-06-13 | TO, GO, DP
PRC-005-2 | Protection System Maintenance | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider shall demonstrate efforts to correct identified Unresolved Maintenance Issues. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Retired | 2015-04-01 | 2015-06-13 | TO, GO, DP
PRC-005-2(i) | Protection System Maintenance | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a Protection System Maintenance Program (PSMP) for its Protection Systems identified in Section 4.2. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] The PSMP shall: | MEDIUM | Retired | 2015-06-14 | 2016-03-17 | TO, GO, DP
PRC-005-2(i) | Protection System Maintenance | R1.1. | Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. | MEDIUM | Retired | 2015-06-14 | 2016-03-17 | TO, GO, DP
PRC-005-2(i) | Protection System Maintenance | R1.2. | Include the applicable monitored Component attributes applied to each Protection System Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, and Table 3 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System Components. | MEDIUM | Retired | 2015-06-14 | 2016-03-17 | TO, GO, DP
PRC-005-2(i) | Protection System Maintenance | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals in its PSMP shall follow the procedure established in PRC-005 Attachment A to establish and maintain its performance-based intervals. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Retired | 2015-06-14 | 2016-03-17 | TO, GO, DP
PRC-005-2(i) | Protection System Maintenance | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time-based maintenance program(s) shall maintain its Protection System Components that are included within the time-based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, and Table 3. [Violation Risk Factor: High] [Time Horizon: Operations Planning] | HIGH | Retired | 2015-06-14 | 2016-03-17 | TO, GO, DP
PRC-005-2(i) | Protection System Maintenance | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance program(s) in accordance with Requirement R2 shall implement and follow its PSMP for its Protection System Components that are included within the performance-based program(s). [Violation Risk Factor: High] [Time Horizon: Operations Planning] | HIGH | Retired | 2015-06-14 | 2016-03-17 | TO, GO, DP
PRC-005-2(i) | Protection System Maintenance | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider shall demonstrate efforts to correct identified Unresolved Maintenance Issues. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Retired | 2015-06-14 | 2016-03-17 | TO, GO, DP
PRC-005-2(ii) | Protection System Maintenance | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a Protection System Maintenance Program (PSMP) for its Protection Systems identified in Section 4.2. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] The PSMP shall: | MEDIUM | Retired |  |  | TO, GO, DP
PRC-005-2(ii) | Protection System Maintenance | R1.1. | Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. | MEDIUM | Retired |  |  | TO, GO, DP
PRC-005-2(ii) | Protection System Maintenance | R1.2. | Include the applicable monitored Component attributes applied to each Protection System Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, and Table 3 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System Components | MEDIUM | Retired |  |  | TO, GO, DP
PRC-005-2(ii) | Protection System Maintenance | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals in its PSMP shall follow the procedure established in PRC-005 Attachment A to establish and maintain its performance-based intervals. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Retired |  |  | TO, GO, DP
PRC-005-2(ii) | Protection System Maintenance | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes timebased maintenance program(s) shall maintain its Protection System Components that are included within the time-based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, and Table 3. [Violation Risk Factor: High] [Time Horizon: Operations Planning] | HIGH | Retired |  |  | TO, GO, DP
PRC-005-2(ii) | Protection System Maintenance | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance program(s) in accordance with Requirement R2 shall implement and follow its PSMP for its Protection System Components that are included within the performance-based program(s). [Violation Risk Factor: High] [Time Horizon: Operations Planning] | HIGH | Retired |  |  | TO, GO, DP
PRC-005-2(ii) | Protection System Maintenance | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider shall demonstrate efforts to correct identified Unresolved Maintenance Issues. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Retired |  |  | TO, GO, DP
PRC-005-3 | Protection System and Automatic Reclosing Maintenance | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a Protection System Maintenance Program (PSMP) for its Protection Systems and Automatic Reclosing identified in Facilities Section 4.2. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Never Came Into Effect in Ontario | 2024-04-01 |  | TO, GO, DP
PRC-005-3 | Protection System and Automatic Reclosing Maintenance | R1.1. | The PSMP shall: Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System and Automatic Reclosing Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. | MEDIUM | Never Came Into Effect in Ontario | 2024-04-01 |  | TO, GO, DP
PRC-005-3 | Protection System and Automatic Reclosing Maintenance | R1.2. | Include the applicable monitored Component attributes applied to each Protection System and Automatic Reclosing Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, Table 3, and Table 4-1 through 4-2 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System and Automatic Reclosing Components. | MEDIUM | Never Came Into Effect in Ontario | 2024-04-01 |  | TO, GO, DP
PRC-005-3 | Protection System and Automatic Reclosing Maintenance | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses performancebased maintenance intervals in its PSMP shall follow the procedure established in PRC-005 Attachment A to establish and maintain its performance-based intervals. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Never Came Into Effect in Ontario | 2024-04-01 |  | TO, GO, DP
PRC-005-3 | Protection System and Automatic Reclosing Maintenance | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes timebased maintenance program(s) shall maintain its Protection System and Automatic Reclosing Components that are included within the time-based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, Table 3, and Table 4-1 through 4-2. [Violation Risk Factor: High] [Time Horizon: Operations Planning] | HIGH | Never Came Into Effect in Ontario | 2024-04-01 |  | TO, GO, DP
PRC-005-3 | Protection System and Automatic Reclosing Maintenance | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance program(s) in accordance with Requirement R2 shall implement and follow its PSMP for its Protection System and Automatic Reclosing Components that are included within the performance-based program(s). [Violation Risk Factor: High] [Time Horizon: Operations Planning] | HIGH | Never Came Into Effect in Ontario | 2024-04-01 |  | TO, GO, DP
PRC-005-3 | Protection System and Automatic Reclosing Maintenance | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider shall demonstrate efforts to correct identified Unresolved Maintenance Issues. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Never Came Into Effect in Ontario | 2024-04-01 |  | TO, GO, DP
PRC-005-3(i) | Protection System and Automatic Reclosing Maintenance | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a Protection System Maintenance Program (PSMP) for its Protection Systems and Automatic Reclosing identified in Facilities Section 4.2. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] The PSMP shall: | MEDIUM | Never Came Into Effect in Ontario |  |  | TO, GO, DP
PRC-005-3(i) | Protection System and Automatic Reclosing Maintenance | R1.1. | Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System and Automatic Reclosing Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. | MEDIUM | Never Came Into Effect in Ontario |  |  | TO, GO, DP
PRC-005-3(i) | Protection System and Automatic Reclosing Maintenance | R1.2. | Include the applicable monitored Component attributes applied to each Protection System and Automatic Reclosing Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, Table 3, and Table 4-1 through 4-2 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System and Automatic Reclosing Components. | MEDIUM | Never Came Into Effect in Ontario |  |  | TO, GO, DP
PRC-005-3(i) | Protection System and Automatic Reclosing Maintenance | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals in its PSMP shall follow the procedure established in PRC-005 Attachment A to establish and maintain its performance-based intervals. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Never Came Into Effect in Ontario |  |  | TO, GO, DP
PRC-005-3(i) | Protection System and Automatic Reclosing Maintenance | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time-based maintenance program(s) shall maintain its Protection System and Automatic Reclosing Components that are included within the time-based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, Table 3, and Table 4-1 through 4-2. [Violation Risk Factor: High] [Time Horizon: Operations Planning] | HIGH | Never Came Into Effect in Ontario |  |  | TO, GO, DP
PRC-005-3(i) | Protection System and Automatic Reclosing Maintenance | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance program(s) in accordance with Requirement R2 shall implement and follow its PSMP for its Protection System and Automatic Reclosing Components that are included within the performance-based program(s). [Violation Risk Factor: High] [Time Horizon: Operations Planning] | HIGH | Never Came Into Effect in Ontario |  |  | TO, GO, DP
PRC-005-3(i) | Protection System and Automatic Reclosing Maintenance | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider shall demonstrate efforts to correct identified Unresolved Maintenance Issues. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Never Came Into Effect in Ontario |  |  | TO, GO, DP
PRC-005-3(ii) | Protection System and Automatic Reclosing Maintenance | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a Protection System Maintenance Program (PSMP) for its Protection Systems and Automatic Reclosing identified in Facilities Section 4.2. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Retired |  |  | TO, GO, DP
PRC-005-3(ii) | Protection System and Automatic Reclosing Maintenance | R1.1. | The PSMP shall: Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System and Automatic Reclosing Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. | MEDIUM | Retired |  |  | TO, GO, DP
PRC-005-3(ii) | Protection System and Automatic Reclosing Maintenance | R1.2. | Include the applicable monitored Component attributes applied to each Protection System and Automatic Reclosing Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, Table 3, and Table 4-1 through 4-2 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System and Automatic Reclosing Components. | MEDIUM | Retired |  |  | TO, GO, DP
PRC-005-3(ii) | Protection System and Automatic Reclosing Maintenance | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses performancebased maintenance intervals in its PSMP shall follow the procedure established in PRC-005 Attachment A to establish and maintain its performance-based intervals. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Retired |  |  | TO, GO, DP
PRC-005-3(ii) | Protection System and Automatic Reclosing Maintenance | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes timebased maintenance program(s) shall maintain its Protection System and Automatic Reclosing Components that are included within the time-based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, Table 3, and Table 4-1 through 4-2. [Violation Risk Factor: High] [Time Horizon: Operations Planning] | HIGH | Retired |  |  | TO, GO, DP
PRC-005-3(ii) | Protection System and Automatic Reclosing Maintenance | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance program(s) in accordance with Requirement R2 shall implement and follow its PSMP for its Protection System and Automatic Reclosing Components that are included within the performance-based program(s). [Violation Risk Factor: High] [Time Horizon: Operations Planning] | HIGH | Retired |  |  | TO, GO, DP
PRC-005-3(ii) | Protection System and Automatic Reclosing Maintenance | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider shall demonstrate efforts to correct identified Unresolved Maintenance Issues. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Retired |  |  | TO, GO, DP
PRC-005-4 | Protection System , Automatic Reclosing and Sudden Pressure Relaying Maintenance | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a Protection System Maintenance Program (PSMP) for its Protection Systems, Automatic Reclosing, and Sudden Pressure Relaying identified in Section 4.2, Facilities. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] The PSMP shall: | MEDIUM | Never Came Into Effect in Ontario |  |  | TO, GO, DP
PRC-005-4 | Protection System , Automatic Reclosing and Sudden Pressure Relaying Maintenance | R1.1. | Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. | MEDIUM | Never Came Into Effect in Ontario |  |  | TO, GO, DP
PRC-005-4 | Protection System , Automatic Reclosing and Sudden Pressure Relaying Maintenance | R1.2. | Include the applicable monitored Component attributes applied to each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, Table 3, Table 4-1 through 4-2, and Table 5 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components. | MEDIUM | Never Came Into Effect in Ontario |  |  | TO, GO, DP
PRC-005-4 | Protection System , Automatic Reclosing and Sudden Pressure Relaying Maintenance | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals in its PSMP shall follow the procedure established in PRC-005 Attachment A to establish and maintain its performance-based intervals. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Never Came Into Effect in Ontario |  |  | TO, GO, DP
PRC-005-4 | Protection System , Automatic Reclosing and Sudden Pressure Relaying Maintenance | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time-based maintenance program(s) shall maintain its Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components that are included within the time-based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, Table 3, Table 4-1 through 4-2, and Table 5. [Violation Risk Factor: High] [Time Horizon: Operations Planning] | HIGH | Never Came Into Effect in Ontario |  |  | TO, GO, DP
PRC-005-4 | Protection System , Automatic Reclosing and Sudden Pressure Relaying Maintenance | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance program(s) in accordance with Requirement R2 shall implement and follow its PSMP for its Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components that are included within the performance-based program(s). [Violation Risk Factor: High] [Time Horizon: Operations Planning] | HIGH | Never Came Into Effect in Ontario |  |  | TO, GO, DP
PRC-005-4 | Protection System , Automatic Reclosing and Sudden Pressure Relaying Maintenance | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider shall demonstrate efforts to correct identified Unresolved Maintenance Issues. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Never Came Into Effect in Ontario |  |  | TO, GO, DP
PRC-005-5 | Protection System , Automatic Reclosing and Sudden Pressure Relaying Maintenance | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a Protection System Maintenance Program (PSMP) for its Protection Systems, Automatic Reclosing, and Sudden Pressure Relaying identified in Section 4.2, Facilities. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] The PSMP shall: | MEDIUM | Retired |  |  | TO, GO, DP
PRC-005-5 | Protection System , Automatic Reclosing and Sudden Pressure Relaying Maintenance | R1.1. | Identify which maintenance method (time‐based, performance‐based per PRC‐005 Attachment A, or a combination) is used to address each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time‐based program as described in Table 1‐4 and Table 3. | MEDIUM | Retired |  |  | TO, GO, DP
PRC-005-5 | Protection System , Automatic Reclosing and Sudden Pressure Relaying Maintenance | R1.2. | Include the applicable monitored Component attributes applied to each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type consistent with the maintenance intervals specified in Tables 1‐1 through 1‐5, Table 2, Table 3, Table 4‐1 through 4‐2, and Table 5 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components. | MEDIUM | Retired |  |  | TO, GO, DP
PRC-005-5 | Protection System , Automatic Reclosing and Sudden Pressure Relaying Maintenance | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance‐based maintenance intervals in its PSMP shall follow the procedure established in PRC‐005 Attachment A to establish and maintain its performance‐based intervals. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Retired |  |  | TO, GO, DP
PRC-005-5 | Protection System , Automatic Reclosing and Sudden Pressure Relaying Maintenance | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time‐based maintenance program(s) shall maintain its Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components that are included within the time‐based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1‐1 through 1‐5, Table 2, Table 3, Table 4‐1 through 4‐2, and Table 5. [Violation Risk Factor: High] [Time Horizon: Operations Planning] | HIGH | Retired |  |  | TO, GO, DP
PRC-005-5 | Protection System , Automatic Reclosing and Sudden Pressure Relaying Maintenance | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance‐based maintenance program(s) in accordance with Requirement R2 shall implement and follow its PSMP for its Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components that are included within the performancebased program(s). [Violation Risk Factor: High] [Time Horizon: Operations Planning] | HIGH | Retired |  |  | TO, GO, DP
PRC-005-5 | Protection System , Automatic Reclosing and Sudden Pressure Relaying Maintenance | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider shall demonstrate efforts to correct identified Unresolved Maintenance Issues. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Retired |  |  | TO, GO, DP
PRC-005-6 | Protection System , Automatic Reclosing and Sudden Pressure Relaying Maintenance | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a Protection System Maintenance Program (PSMP) for its Protection Systems, Automatic Reclosing, and Sudden Pressure Relaying identified in Section 4.2, Facilities. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] The PSMP shall: | MEDIUM | Effective | 2017-04-01 |  | TO, GO, DP
PRC-005-6 | Protection System , Automatic Reclosing and Sudden Pressure Relaying Maintenance | R1.1. | Identify which maintenance method (time‐based, performance‐based per PRC‐005 Attachment A, or a combination) is used to address each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time‐based program as described in Table 1‐4 and Table 3. | MEDIUM | Effective | 2017-04-01 |  | TO, GO, DP
PRC-005-6 | Protection System , Automatic Reclosing and Sudden Pressure Relaying Maintenance | R1.2. | Include the applicable monitored Component attributes applied to each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type consistent with the maintenance intervals specified in Tables 1‐1 through 1‐5, Table 2, Table 3, Table 4‐1 through 4‐3, and Table 5 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components. | MEDIUM | Effective | 2017-04-01 |  | TO, GO, DP
PRC-005-6 | Protection System , Automatic Reclosing and Sudden Pressure Relaying Maintenance | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance‐based maintenance intervals in its PSMP shall follow the procedure established in PRC‐005 Attachment A to establish and maintain its performance‐based intervals. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Effective | 2017-04-01 |  | TO, GO, DP
PRC-005-6 | Protection System , Automatic Reclosing and Sudden Pressure Relaying Maintenance | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time‐based maintenance program(s) shall maintain its Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components that are included within the time‐based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1‐1 through 1‐5, Table 2, Table 3, Table 4‐1 through 4‐3, and Table 5. [Violation Risk Factor: High] [Time Horizon: Operations Planning] | HIGH | Effective | 2019-04-01 |  | TO, GO, DP
PRC-005-6 | Protection System , Automatic Reclosing and Sudden Pressure Relaying Maintenance | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance‐based maintenance program(s) in accordance with Requirement R2 shall implement and follow its PSMP for its Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components that are included within the performancebased program(s). [Violation Risk Factor: High] [Time Horizon: Operations Planning] | HIGH | Effective | 2019-04-01 |  | TO, GO, DP
PRC-005-6 | Protection System , Automatic Reclosing and Sudden Pressure Relaying Maintenance | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider shall demonstrate efforts to correct identified Unresolved Maintenance Issues. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Effective | 2017-04-01 |  | TO, GO, DP
PRC-006-1 | Automatic Underfrequency Load Shedding | R1. | Each Planning Coordinator shall develop and document criteria, including consideration of historical events and system studies, to select portions of the Bulk Electric System (BES), including interconnected portions of the BES in adjacent Planning Coordinator areas and Regional Entity areas that may form islands. | HIGH | Retired | 2013-10-01 | 2015-12-31 | PC
PRC-006-1 | Automatic Underfrequency Load Shedding | R10. | Each Transmission Owner shall provide automatic switching of its existing capacitor banks, Transmission Lines, and reactors to control over-voltage as a result of underfrequency load shedding if required by the UFLS program and schedule for application determined by the Planning Coordinator(s) in each Planning Coordinator area in which the Transmission Owner owns transmission. | HIGH | Retired | 2013-10-01 | 2015-12-31 | TO
PRC-006-1 | Automatic Underfrequency Load Shedding | R11. | Each Planning Coordinator, in whose area a BES islanding event results in system frequency excursions below the initializing set points of the UFLS program, shall conduct and document an assessment of the event within one year of event actuation to evaluate: | MEDIUM | Retired | 2013-10-01 | 2015-12-31 | PC
PRC-006-1 | Automatic Underfrequency Load Shedding | R11.1. | The performance of the UFLS equipment, | MEDIUM | Retired | 2013-10-01 | 2015-12-31 | PC
PRC-006-1 | Automatic Underfrequency Load Shedding | R11.2. | The effectiveness of the UFLS program. | MEDIUM | Retired | 2013-10-01 | 2015-12-31 | PC
PRC-006-1 | Automatic Underfrequency Load Shedding | R12. | Each Planning Coordinator, in whose islanding event assessment (per R11) UFLS program deficiencies are identified, shall conduct and document a UFLS design assessment to consider the identified deficiencies within two years of event actuation. | MEDIUM | Retired | 2013-10-01 | 2015-12-31 | PC
PRC-006-1 | Automatic Underfrequency Load Shedding | R13. | Each Planning Coordinator, in whose area a BES islanding event occurred that also included the area(s) or portions of area(s) of other Planning Coordinator(s) in the same islanding event and that resulted in system frequency excursions below the initializing set points of the UFLS program, shall coordinate its event assessment (in accordance with Requirement R11) with all other Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event through one of the following: [VRF: Medium][Time Horizon: Operations Assessment] • Conduct a joint event assessment per Requirement R11 among the Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, or • Conduct an independent event assessment per Requirement R11 that reaches conclusions and recommendations consistent with those of the event assessments of the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, or • Conduct an independent event assessment per Requirement R11 and where the assessment fails to reach conclusions and recommendations consistent with those of the event assessments of the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, identify differences in the assessments that likely resulted in the differences in the conclusions and recommendations and report these differences to the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event and the ERO. | MEDIUM | Retired | 2013-10-01 | 2015-12-31 | PC
PRC-006-1 | Automatic Underfrequency Load Shedding | R14. | Each Planning Coordinator shall respond to written comments submitted by UFLS entities and Transmission Owners within its Planning Coordinator area following a comment period and before finalizing its UFLS program, indicating in the written response to comments whether changes will be made or reasons why changes will not be made to the following | LOWER | Retired | 2013-10-01 | 2015-12-31 | PC
PRC-006-1 | Automatic Underfrequency Load Shedding | R14.1. | UFLS program, including a schedule for implementation | LOWER | Retired | 2013-10-01 | 2015-12-31 | PC
PRC-006-1 | Automatic Underfrequency Load Shedding | R14.2. | UFLS design assessment | LOWER | Retired | 2013-10-01 | 2015-12-31 | PC
PRC-006-1 | Automatic Underfrequency Load Shedding | R14.3. | Format and schedule of UFLS data submittal | LOWER | Retired | 2013-10-01 | 2015-12-31 | PC
PRC-006-1 | Automatic Underfrequency Load Shedding | R2. | Each Planning Coordinator shall identify one or more islands to serve as a basis for designing its UFLS program including: | HIGH | Retired | 2013-10-01 | 2015-12-31 | PC
PRC-006-1 | Automatic Underfrequency Load Shedding | R2.1. | Those islands selected by applying the criteria in Requirement R1, and | HIGH | Retired | 2013-10-01 | 2015-12-31 | PC
PRC-006-1 | Automatic Underfrequency Load Shedding | R2.2. | Any portions of the BES designed to detach from the Interconnection (planned islands) as a result of the operation of a relay scheme or Special Protection System, and | HIGH | Retired | 2013-10-01 | 2015-12-31 | PC
PRC-006-1 | Automatic Underfrequency Load Shedding | R2.3. | A single island that includes all portions of the BES in either the Regional Entity area or the Interconnection in which the Planning Coordinator’s area resides. If a Planning Coordinator’s area resides in multiple Regional Entity areas, each of those Regional Entity areas shall be identified as an island. Planning Coordinators may adjust island boundaries to differ from Regional Entity area boundaries by mutual consent where necessary for the sole purpose of producing contiguous regional islands more suitable for simulation. | HIGH | Retired | 2013-10-01 | 2015-12-31 | PC
PRC-006-1 | Automatic Underfrequency Load Shedding | R3. | Each Planning Coordinator shall develop a UFLS program, including notification of and a schedule for implementation by UFLS entities within its area, that meets the following performance characteristics in simulations of underfrequency conditions resulting from an imbalance scenario, where an imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s). | HIGH | Retired | 2013-10-01 | 2015-12-31 | PC
PRC-006-1 | Automatic Underfrequency Load Shedding | R3. | Each Planning Coordinator shall develop a UFLS program, including notification of and a schedule for implementation by UFLS entities within its area, that meets the following performance characteristics in simulations of underfrequency conditions resulting from an imbalance scenario, where an imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s). | MEDIUM | Retired | 2013-10-01 | 2015-12-31 | PC
PRC-006-1 | Automatic Underfrequency Load Shedding | R3.1. | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-1 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and | MEDIUM | Retired | 2013-10-01 | 2015-12-31 | PC
PRC-006-1 | Automatic Underfrequency Load Shedding | R3.2. | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-1 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and | MEDIUM | Retired | 2013-10-01 | 2015-12-31 | PC
PRC-006-1 | Automatic Underfrequency Load Shedding | R3.3. | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each generator bus and generator step-up transformer high-side bus associated with each of the following: | MEDIUM | Retired | 2013-10-01 | 2015-12-31 | PC
PRC-006-1 | Automatic Underfrequency Load Shedding | R3.3.1. | Individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES | MEDIUM | Retired | 2013-10-01 | 2015-12-31 | PC
PRC-006-1 | Automatic Underfrequency Load Shedding | R3.3.2. | Generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES | MEDIUM | Retired | 2013-10-01 | 2015-12-31 | PC
PRC-006-1 | Automatic Underfrequency Load Shedding | R3.3.3. | Facilities consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA gross nameplate rating. | MEDIUM | Retired | 2013-10-01 | 2015-12-31 | PC
PRC-006-1 | Automatic Underfrequency Load Shedding | R4. | Each Planning Coordinator shall conduct and document a UFLS design assessment at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement R3 for each island identified in Requirement R2. The simulation shall model each of the following: | HIGH | Retired | 2013-10-01 | 2015-12-31 | PC
PRC-006-1 | Automatic Underfrequency Load Shedding | R4.1. | Underfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-1 - Attachment 1. | HIGH | Retired | 2013-10-01 | 2015-12-31 | PC
PRC-006-1 | Automatic Underfrequency Load Shedding | R4.2. | Underfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-1 - Attachment 1. | HIGH | Retired | 2013-10-01 | 2015-12-31 | PC
PRC-006-1 | Automatic Underfrequency Load Shedding | R4.3. | Underfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-1 - Attachment 1. | HIGH | Retired | 2013-10-01 | 2015-12-31 | PC
PRC-006-1 | Automatic Underfrequency Load Shedding | R4.4. | Overfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-1 — Attachment 1. | HIGH | Retired | 2013-10-01 | 2015-12-31 | PC
PRC-006-1 | Automatic Underfrequency Load Shedding | R4.5. | Overfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-1 — Attachment 1. | HIGH | Retired | 2013-10-01 | 2015-12-31 | PC
PRC-006-1 | Automatic Underfrequency Load Shedding | R4.6. | Overfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-1 — Attachment 1. | HIGH | Retired | 2013-10-01 | 2015-12-31 | PC
PRC-006-1 | Automatic Underfrequency Load Shedding | R4.7. | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. | HIGH | Retired | 2013-10-01 | 2015-12-31 | PC
PRC-006-1 | Automatic Underfrequency Load Shedding | R5. | Each Planning Coordinator, whose area or portions of whose area is part of an island identified by it or another Planning Coordinator which includes multiple Planning Coordinator areas or portions of those areas, shall coordinate its UFLS program design with all other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island through one of the following: • Develop a common UFLS program design and schedule for implementation per Requirement R3 among the Planning Coordinators whose areas or portions of whose areas are part of the same identified island, or • Conduct a joint UFLS design assessment per Requirement R4 among the Planning Coordinators whose areas or portions of whose areas are part of the same identified island, or • Conduct an independent UFLS design assessment per Requirement R4 for the identified island, and in the event the UFLS design assessment fails to meet Requirement R3, identify modifications to the UFLS program(s) to meet Requirement R3 and report these modifications as recommendations to the other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island and the ERO. | HIGH | Retired | 2013-10-01 | 2015-12-31 | PC
PRC-006-1 | Automatic Underfrequency Load Shedding | R6. | Each Planning Coordinator shall maintain a UFLS database containing data necessary to model its UFLS program for use in event analyses and assessments of the UFLS program at least once each calendar year, with no more than 15 months between maintenance activities. | LOWER | Retired | 2013-10-01 | 2015-12-31 | PC
PRC-006-1 | Automatic Underfrequency Load Shedding | R7. | Each Planning Coordinator shall provide its UFLS database containing data necessary to model its UFLS program to other Planning Coordinators within its Interconnection within 30 calendar days of a request. | LOWER | Retired | 2013-10-01 | 2015-12-31 | PC
PRC-006-1 | Automatic Underfrequency Load Shedding | R8. | Each UFLS entity shall provide data to its Planning Coordinator(s) according to the format and schedule specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. | LOWER | Retired | 2013-10-01 | 2015-12-31 | TO, DP
PRC-006-1 | Automatic Underfrequency Load Shedding | R9. | Each UFLS entity shall provide automatic tripping of Load in accordance with the UFLS program design and schedule for application determined by its Planning Coordinator(s) in each Planning Coordinator area in which it owns assets. | HIGH | Retired | 2013-10-01 | 2015-12-31 | TO, DP
PRC-006-1(i) | Automatic Underfrequency Load Shedding | R1. | Each Planning Coordinator shall develop and document criteria, including consideration of historical events and system studies, to select portions of the Bulk Electric System (BES), including interconnected portions of the BES in adjacent Planning Coordinator areas and Regional Entity areas that may form islands. | HIGH | Retired |  |  | PC
PRC-006-1(i) | Automatic Underfrequency Load Shedding | R10. | Each Transmission Owner shall provide automatic switching of its existing capacitor banks, Transmission Lines, and reactors to control over-voltage as a result of underfrequency load shedding if required by the UFLS program and schedule for application determined by the Planning Coordinator(s) in each Planning Coordinator area in which the Transmission Owner owns transmission. | HIGH | Retired |  |  | TO
PRC-006-1(i) | Automatic Underfrequency Load Shedding | R11. | Each Planning Coordinator, in whose area a BES islanding event results in system frequency excursions below the initializing set points of the UFLS program, shall conduct and document an assessment of the event within one year of event actuation to evaluate: | MEDIUM | Retired |  |  | PC
PRC-006-1(i) | Automatic Underfrequency Load Shedding | R11.1. | The performance of the UFLS equipment, | MEDIUM | Retired |  |  | PC
PRC-006-1(i) | Automatic Underfrequency Load Shedding | R11.2. | The effectiveness of the UFLS program. | MEDIUM | Retired |  |  | PC
PRC-006-1(i) | Automatic Underfrequency Load Shedding | R12. | Each Planning Coordinator, in whose islanding event assessment (per R11) UFLS program deficiencies are identified, shall conduct and document a UFLS design assessment to consider the identified deficiencies within two years of event actuation. | MEDIUM | Retired |  |  | PC
PRC-006-1(i) | Automatic Underfrequency Load Shedding | R13. | Each Planning Coordinator, in whose area a BES islanding event occurred that also included the area(s) or portions of area(s) of other Planning Coordinator(s) in the same islanding event and that resulted in system frequency excursions below the initializing set points of the UFLS program, shall coordinate its event assessment (in accordance with Requirement R11) with all other Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event through one of the following: [VRF: Medium][Time Horizon: Operations Assessment] • Conduct a joint event assessment per Requirement R11 among the Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, or • Conduct an independent event assessment per Requirement R11 that reaches conclusions and recommendations consistent with those of the event assessments of the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, or • Conduct an independent event assessment per Requirement R11 and where the assessment fails to reach conclusions and recommendations consistent with those of the event assessments of the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, identify differences in the assessments that likely resulted in the differences in the conclusions and recommendations and report these differences to the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event and the ERO. | MEDIUM | Retired |  |  | PC
PRC-006-1(i) | Automatic Underfrequency Load Shedding | R14. | Each Planning Coordinator shall respond to written comments submitted by UFLS entities and Transmission Owners within its Planning Coordinator area following a comment period and before finalizing its UFLS program, indicating in the written response to comments whether changes will be made or reasons why changes will not be made to the following | LOWER | Retired |  |  | PC
PRC-006-1(i) | Automatic Underfrequency Load Shedding | R14.1. | UFLS program, including a schedule for implementation | LOWER | Retired |  |  | PC
PRC-006-1(i) | Automatic Underfrequency Load Shedding | R14.2. | UFLS design assessment | LOWER | Retired |  |  | PC
PRC-006-1(i) | Automatic Underfrequency Load Shedding | R14.3. | Format and schedule of UFLS data submittal | LOWER | Retired |  |  | PC
PRC-006-1(i) | Automatic Underfrequency Load Shedding | R2. | Each Planning Coordinator shall identify one or more islands to serve as a basis for designing its UFLS program including: | HIGH | Retired |  |  | PC
PRC-006-1(i) | Automatic Underfrequency Load Shedding | R2.1. | Those islands selected by applying the criteria in Requirement R1, and | HIGH | Retired |  |  | PC
PRC-006-1(i) | Automatic Underfrequency Load Shedding | R2.2. | Any portions of the BES designed to detach from the Interconnection (planned islands) as a result of the operation of a relay scheme or Remedial Action Scheme, and | HIGH | Retired |  |  | PC
PRC-006-1(i) | Automatic Underfrequency Load Shedding | R2.3. | A single island that includes all portions of the BES in either the Regional Entity area or the Interconnection in which the Planning Coordinator’s area resides. If a Planning Coordinator’s area resides in multiple Regional Entity areas, each of those Regional Entity areas shall be identified as an island. Planning Coordinators may adjust island boundaries to differ from Regional Entity area boundaries by mutual consent where necessary for the sole purpose of producing contiguous regional islands more suitable for simulation. | HIGH | Retired |  |  | PC
PRC-006-1(i) | Automatic Underfrequency Load Shedding | R3. | Each Planning Coordinator shall develop a UFLS program, including notification of and a schedule for implementation by UFLS entities within its area, that meets the following performance characteristics in simulations of underfrequency conditions resulting from an imbalance scenario, where an imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s). | HIGH | Retired |  |  | PC
PRC-006-1(i) | Automatic Underfrequency Load Shedding | R3. | Each Planning Coordinator shall develop a UFLS program, including notification of and a schedule for implementation by UFLS entities within its area, that meets the following performance characteristics in simulations of underfrequency conditions resulting from an imbalance scenario, where an imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s). | MEDIUM | Retired |  |  | PC
PRC-006-1(i) | Automatic Underfrequency Load Shedding | R3.1. | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-1(i) - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and | MEDIUM | Retired |  |  | PC
PRC-006-1(i) | Automatic Underfrequency Load Shedding | R3.2. | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-1(i) - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and | MEDIUM | Retired |  |  | PC
PRC-006-1(i) | Automatic Underfrequency Load Shedding | R3.3. | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each generator bus and generator step-up transformer high-side bus associated with each of the following: | MEDIUM | Retired |  |  | PC
PRC-006-1(i) | Automatic Underfrequency Load Shedding | R3.3.1. | Individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES | MEDIUM | Retired |  |  | PC
PRC-006-1(i) | Automatic Underfrequency Load Shedding | R3.3.2. | Generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES | MEDIUM | Retired |  |  | PC
PRC-006-1(i) | Automatic Underfrequency Load Shedding | R3.3.3. | Facilities consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA gross nameplate rating. | MEDIUM | Retired |  |  | PC
PRC-006-1(i) | Automatic Underfrequency Load Shedding | R4. | Each Planning Coordinator shall conduct and document a UFLS design assessment at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement R3 for each island identified in Requirement R2. The simulation shall model each of the following: | HIGH | Retired |  |  | PC
PRC-006-1(i) | Automatic Underfrequency Load Shedding | R4.1. | Underfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-1(i) - Attachment 1. | HIGH | Retired |  |  | PC
PRC-006-1(i) | Automatic Underfrequency Load Shedding | R4.2. | Underfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-1(i) - Attachment 1. | HIGH | Retired |  |  | PC
PRC-006-1(i) | Automatic Underfrequency Load Shedding | R4.3. | Underfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-1(i) - Attachment 1. | HIGH | Retired |  |  | PC
PRC-006-1(i) | Automatic Underfrequency Load Shedding | R4.4. | Overfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-1(i) — Attachment 1. | HIGH | Retired |  |  | PC
PRC-006-1(i) | Automatic Underfrequency Load Shedding | R4.5. | Overfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-1(i) — Attachment 1. | HIGH | Retired |  |  | PC
PRC-006-1(i) | Automatic Underfrequency Load Shedding | R4.6. | Overfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-1(i) — Attachment 1. | HIGH | Retired |  |  | PC
PRC-006-1(i) | Automatic Underfrequency Load Shedding | R4.7. | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. | HIGH | Retired |  |  | PC
PRC-006-1(i) | Automatic Underfrequency Load Shedding | R5. | Each Planning Coordinator, whose area or portions of whose area is part of an island identified by it or another Planning Coordinator which includes multiple Planning Coordinator areas or portions of those areas, shall coordinate its UFLS program design with all other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island through one of the following: • Develop a common UFLS program design and schedule for implementation per Requirement R3 among the Planning Coordinators whose areas or portions of whose areas are part of the same identified island, or • Conduct a joint UFLS design assessment per Requirement R4 among the Planning Coordinators whose areas or portions of whose areas are part of the same identified island, or • Conduct an independent UFLS design assessment per Requirement R4 for the identified island, and in the event the UFLS design assessment fails to meet Requirement R3, identify modifications to the UFLS program(s) to meet Requirement R3 and report these modifications as recommendations to the other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island and the ERO. | HIGH | Retired |  |  | PC
PRC-006-1(i) | Automatic Underfrequency Load Shedding | R6. | Each Planning Coordinator shall maintain a UFLS database containing data necessary to model its UFLS program for use in event analyses and assessments of the UFLS program at least once each calendar year, with no more than 15 months between maintenance activities. | LOWER | Retired |  |  | PC
PRC-006-1(i) | Automatic Underfrequency Load Shedding | R7. | Each Planning Coordinator shall provide its UFLS database containing data necessary to model its UFLS program to other Planning Coordinators within its Interconnection within 30 calendar days of a request. | LOWER | Retired |  |  | PC
PRC-006-1(i) | Automatic Underfrequency Load Shedding | R8. | Each UFLS entity shall provide data to its Planning Coordinator(s) according to the format and schedule specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. | LOWER | Retired |  |  | TO, DP
PRC-006-1(i) | Automatic Underfrequency Load Shedding | R9. | Each UFLS entity shall provide automatic tripping of Load in accordance with the UFLS program design and schedule for application determined by its Planning Coordinator(s) in each Planning Coordinator area in which it owns assets. | HIGH | Retired |  |  | TO, DP
PRC-006-2 | Automatic Underfrequency Load Shedding | R1. | Each Planning Coordinator shall develop and document criteria, including consideration of historical events and system studies, to select portions of the Bulk Electric System (BES), including interconnected portions of the BES in adjacent Planning Coordinator areas and Regional Entity areas that may form islands. | MEDIUM | Retired | 2016-01-01 | 2017-09-30 | PC
PRC-006-2 | Automatic Underfrequency Load Shedding | R10. | Each Transmission Owner shall provide automatic switching of its existing capacitor banks, Transmission Lines, and reactors to control over-voltage as a result of underfrequency load shedding if required by the UFLS program and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) in each Planning Coordinator area in which the Transmission Owner owns transmission. | HIGH | Retired | 2016-01-01 | 2017-09-30 | TO
PRC-006-2 | Automatic Underfrequency Load Shedding | R11. | Each Planning Coordinator, in whose area a BES islanding event results in system frequency excursions below the initializing set points of the UFLS program, shall conduct and document an assessment of the event within one year of event actuation to evaluate: | MEDIUM | Retired | 2016-01-01 | 2017-09-30 | PC
PRC-006-2 | Automatic Underfrequency Load Shedding | R11.1. | The performance of the UFLS equipment, | MEDIUM | Retired | 2016-01-01 | 2017-09-30 | PC
PRC-006-2 | Automatic Underfrequency Load Shedding | R11.2. | The effectiveness of the UFLS program. | MEDIUM | Retired | 2016-01-01 | 2017-09-30 | PC
PRC-006-2 | Automatic Underfrequency Load Shedding | R12. | Each Planning Coordinator, in whose islanding event assessment (per R11) UFLS program deficiencies are identified, shall conduct and document a UFLS design assessment to consider the identified deficiencies within two years of event actuation. | MEDIUM | Retired | 2016-01-01 | 2017-09-30 | PC
PRC-006-2 | Automatic Underfrequency Load Shedding | R13. | Each Planning Coordinator, in whose area a BES islanding event occurred that also included the area(s) or portions of area(s) of other Planning Coordinator(s) in the same islanding event and that resulted in system frequency excursions below the initializing set points of the UFLS program, shall coordinate its event assessment (in accordance with Requirement R11) with all other Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event through one of the following: • Conduct a joint event assessment per Requirement R11 among the Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, or • Conduct an independent event assessment per Requirement R11 that reaches conclusions and recommendations consistent with those of the event assessments of the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, or • Conduct an independent event assessment per Requirement R11 and where the assessment fails to reach conclusions and recommendations consistent with those of the event assessments of the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, identify differences in the assessments that likely resulted in the differences in the conclusions and recommendations and report these differences to the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event and the ERO. | MEDIUM | Retired | 2016-01-01 | 2017-09-30 | PC
PRC-006-2 | Automatic Underfrequency Load Shedding | R14. | Each Planning Coordinator shall respond to written comments submitted by UFLS entities and Transmission Owners within its Planning Coordinator area following a comment period and before finalizing its UFLS program, indicating in the written response to comments whether changes will be made or reasons why changes will not be made to the following | LOWER | Retired | 2016-01-01 | 2017-09-30 | PC
PRC-006-2 | Automatic Underfrequency Load Shedding | R14.1. | UFLS program, including a schedule for implementation | LOWER | Retired | 2016-01-01 | 2017-09-30 | PC
PRC-006-2 | Automatic Underfrequency Load Shedding | R14.2. | UFLS design assessment | LOWER | Retired | 2016-01-01 | 2017-09-30 | PC
PRC-006-2 | Automatic Underfrequency Load Shedding | R14.3. | Format and schedule of UFLS data submittal | LOWER | Retired | 2016-01-01 | 2017-09-30 | PC
PRC-006-2 | Automatic Underfrequency Load Shedding | R15. | Each Planning Coordinator that conducts a UFLS design assessment under Requirement R4, R5, or R12 and determines that the UFLS program does not meet the performance characteristics in Requirement R3, shall develop a Corrective Action Plan and a schedule for implementation by the UFLS entities within its area. | HIGH | Retired | 2016-01-01 | 2017-09-30 | PC
PRC-006-2 | Automatic Underfrequency Load Shedding | R15.1. | For UFLS design assessments performed under Requirement R4 or R5, the Corrective Action Plan shall be developed within the five-year time frame identified in Requirement R4. | HIGH | Retired | 2016-01-01 | 2017-09-30 | PC
PRC-006-2 | Automatic Underfrequency Load Shedding | R15.2. | For UFLS design assessments performed under Requirement R12, the Corrective Action Plan shall be developed within the two-year time frame identified in Requirement R12. | HIGH | Retired | 2016-01-01 | 2017-09-30 | PC
PRC-006-2 | Automatic Underfrequency Load Shedding | R2. | Each Planning Coordinator shall identify one or more islands to serve as a basis for designing its UFLS program including: | MEDIUM | Retired | 2016-01-01 | 2017-09-30 | PC
PRC-006-2 | Automatic Underfrequency Load Shedding | R2.1. | Those islands selected by applying the criteria in Requirement R1, and | MEDIUM | Retired | 2016-01-01 | 2017-09-30 | PC
PRC-006-2 | Automatic Underfrequency Load Shedding | R2.2. | Any portions of the BES designed to detach from the Interconnection (planned islands) as a result of the operation of a relay scheme or Special Protection System, and | MEDIUM | Retired | 2016-01-01 | 2017-09-30 | PC
PRC-006-2 | Automatic Underfrequency Load Shedding | R2.3. | A single island that includes all portions of the BES in either the Regional Entity area or the Interconnection in which the Planning Coordinator’s area resides. If a Planning Coordinator’s area resides in multiple Regional Entity areas, each of those Regional Entity areas shall be identified as an island. Planning Coordinators may adjust island boundaries to differ from Regional Entity area boundaries by mutual consent where necessary for the sole purpose of producing contiguous regional islands more suitable for simulation. | MEDIUM | Retired | 2016-01-01 | 2017-09-30 | PC
PRC-006-2 | Automatic Underfrequency Load Shedding | R3. | Each Planning Coordinator shall develop a UFLS program, including notification of and a schedule for implementation by UFLS entities within its area, that meets the following performance characteristics in simulations of underfrequency conditions resulting from an imbalance scenario, where an imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s) | HIGH | Retired | 2016-01-01 | 2017-09-30 | PC
PRC-006-2 | Automatic Underfrequency Load Shedding | R3. | Each Planning Coordinator shall develop a UFLS program, including notification of and a schedule for implementation by UFLS entities within its area, that meets the following performance characteristics in simulations of underfrequency conditions resulting from an imbalance scenario, where an imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s) | HIGH | Retired | 2016-01-01 | 2017-09-30 | PC
PRC-006-2 | Automatic Underfrequency Load Shedding | R3.1. | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-2 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and | HIGH | Retired | 2016-01-01 | 2017-09-30 | PC
PRC-006-2 | Automatic Underfrequency Load Shedding | R3.2. | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-2 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and | HIGH | Retired | 2016-01-01 | 2017-09-30 | PC
PRC-006-2 | Automatic Underfrequency Load Shedding | R3.3. | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each generator bus and generator step-up transformer high-side bus associated with each of the following: • Individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES • Generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES • Facilities consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA gross nameplate rating. | HIGH | Retired | 2016-01-01 | 2017-09-30 | PC
PRC-006-2 | Automatic Underfrequency Load Shedding | R4. | Each Planning Coordinator shall conduct and document a UFLS design assessment at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement R3 for each island identified in Requirement R2. The simulation shall model each of the following: | HIGH | Retired | 2016-01-01 | 2017-09-30 | PC
PRC-006-2 | Automatic Underfrequency Load Shedding | R4.1. | Underfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-2 - Attachment 1. | HIGH | Retired | 2016-01-01 | 2017-09-30 | PC
PRC-006-2 | Automatic Underfrequency Load Shedding | R4.2. | Underfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-2 - Attachment 1. | HIGH | Retired | 2016-01-01 | 2017-09-30 | PC
PRC-006-2 | Automatic Underfrequency Load Shedding | R4.3. | Underfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-2 - Attachment 1. | HIGH | Retired | 2016-01-01 | 2017-09-30 | PC
PRC-006-2 | Automatic Underfrequency Load Shedding | R4.4. | Overfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-2 — Attachment 1. | HIGH | Retired | 2016-01-01 | 2017-09-30 | PC
PRC-006-2 | Automatic Underfrequency Load Shedding | R4.5. | Overfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-2 — Attachment 1. | HIGH | Retired | 2016-01-01 | 2017-09-30 | PC
PRC-006-2 | Automatic Underfrequency Load Shedding | R4.6. | Overfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-2 — Attachment 1. | HIGH | Retired | 2016-01-01 | 2017-09-30 | PC
PRC-006-2 | Automatic Underfrequency Load Shedding | R4.7. | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment | HIGH | Retired | 2016-01-01 | 2017-09-30 | PC
PRC-006-2 | Automatic Underfrequency Load Shedding | R5. | Each Planning Coordinator, whose area or portions of whose area is part of an island identified by it or another Planning Coordinator which includes multiple Planning Coordinator areas or portions of those areas, shall coordinate its UFLS program design with all other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island through one of the following: • Develop a common UFLS program design and schedule for implementation per Requirement R3 among the Planning Coordinators whose areas or portions of whose areas are part of the same identified island, or • Conduct a joint UFLS design assessment per Requirement R4 among the Planning Coordinators whose areas or portions of whose areas are part of the same identified island, or • Conduct an independent UFLS design assessment per Requirement R4 for the identified island, and in the event the UFLS design assessment fails to meet Requirement R3, identify modifications to the UFLS program(s) to meet Requirement R3 and report these modifications as recommendations to the other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island and the ERO. | HIGH | Retired | 2016-01-01 | 2017-09-30 | PC
PRC-006-2 | Automatic Underfrequency Load Shedding | R6. | Each Planning Coordinator shall maintain a UFLS database containing data necessary to model its UFLS program for use in event analyses and assessments of the UFLS program at least once each calendar year, with no more than 15 months between maintenance activities. | LOWER | Retired | 2016-01-01 | 2017-09-30 | PC
PRC-006-2 | Automatic Underfrequency Load Shedding | R7. | Each Planning Coordinator shall provide its UFLS database containing data necessary to model its UFLS program to other Planning Coordinators within its Interconnection within 30 calendar days of a request. | LOWER | Retired | 2016-01-01 | 2017-09-30 | PC
PRC-006-2 | Automatic Underfrequency Load Shedding | R8. | Each UFLS entity shall provide data to its Planning Coordinator(s) according to the format and schedule specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. | LOWER | Retired | 2016-01-01 | 2017-09-30 | TO, DP
PRC-006-2 | Automatic Underfrequency Load Shedding | R9. | Each UFLS entity shall provide automatic tripping of Load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, as determined by its Planning Coordinator(s) in each Planning Coordinator area in which it owns assets. | HIGH | Retired | 2016-01-01 | 2017-09-30 | TO, DP
PRC-006-3 | Automatic Underfrequency Load Shedding | R1. | Each Planning Coordinator shall develop and document criteria, including consideration of historical events and system studies, to select portions of the Bulk Electric System (BES), including interconnected portions of the BES in adjacent Planning Coordinator areas and Regional Entity areas that may form islands. | MEDIUM | Retired | 2017-10-01 | 2021-03-31 | PC
PRC-006-3 | Automatic Underfrequency Load Shedding | R10. | Each Transmission Owner shall provide automatic switching of its existing capacitor banks, Transmission Lines, and reactors to control over-voltage as a result of underfrequency load shedding if required by the UFLS program and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) in each Planning Coordinator area in which the Transmission Owner owns transmission. | HIGH | Retired | 2017-10-01 | 2021-03-31 | TO
PRC-006-3 | Automatic Underfrequency Load Shedding | R11. | Each Planning Coordinator, in whose area a BES islanding event results in system frequency excursions below the initializing set points of the UFLS program, shall conduct and document an assessment of the event within one year of event actuation to evaluate: | MEDIUM | Retired | 2017-10-01 | 2021-03-31 | PC
PRC-006-3 | Automatic Underfrequency Load Shedding | R11.1. | The performance of the UFLS equipment, | MEDIUM | Retired | 2017-10-01 | 2021-03-31 | PC
PRC-006-3 | Automatic Underfrequency Load Shedding | R11.2. | The effectiveness of the UFLS program. | MEDIUM | Retired | 2017-10-01 | 2021-03-31 | PC
PRC-006-3 | Automatic Underfrequency Load Shedding | R12. | Each Planning Coordinator, in whose islanding event assessment (per R11) UFLS program deficiencies are identified, shall conduct and document a UFLS design assessment to consider the identified deficiencies within two years of event actuation. | MEDIUM | Retired | 2017-10-01 | 2021-03-31 | PC
PRC-006-3 | Automatic Underfrequency Load Shedding | R13. | Each Planning Coordinator, in whose area a BES islanding event occurred that also included the area(s) or portions of area(s) of other Planning Coordinator(s) in the same islanding event and that resulted in system frequency excursions below the initializing set points of the UFLS program, shall coordinate its event assessment (in accordance with Requirement R11) with all other Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event through one of the following: • Conduct a joint event assessment per Requirement R11 among the Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, or • Conduct an independent event assessment per Requirement R11 that reaches conclusions and recommendations consistent with those of the event assessments of the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, or • Conduct an independent event assessment per Requirement R11 and where the assessment fails to reach conclusions and recommendations consistent with those of the event assessments of the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, identify differences in the assessments that likely resulted in the differences in the conclusions and recommendations and report these differences to the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event and the ERO. | MEDIUM | Retired | 2017-10-01 | 2021-03-31 | PC
PRC-006-3 | Automatic Underfrequency Load Shedding | R14. | Each Planning Coordinator shall respond to written comments submitted by UFLS entities and Transmission Owners within its Planning Coordinator area following a comment period and before finalizing its UFLS program, indicating in the written response to comments whether changes will be made or reasons why changes will not be made to the following | LOWER | Retired | 2017-10-01 | 2021-03-31 | PC
PRC-006-3 | Automatic Underfrequency Load Shedding | R14.1. | UFLS program, including a schedule for implementation | LOWER | Retired | 2017-10-01 | 2021-04-30 | PC
PRC-006-3 | Automatic Underfrequency Load Shedding | R14.2. | UFLS design assessment | LOWER | Retired | 2017-10-01 | 2021-04-30 | PC
PRC-006-3 | Automatic Underfrequency Load Shedding | R14.3. | Format and schedule of UFLS data submittal | LOWER | Retired | 2017-10-01 | 2021-04-30 | PC
PRC-006-3 | Automatic Underfrequency Load Shedding | R15. | Each Planning Coordinator that conducts a UFLS design assessment under Requirement R4, R5, or R12 and determines that the UFLS program does not meet the performance characteristics in Requirement R3, shall develop a Corrective Action Plan and a schedule for implementation by the UFLS entities within its area. | HIGH | Retired | 2017-10-01 | 2021-04-30 | PC
PRC-006-3 | Automatic Underfrequency Load Shedding | R15.1. | For UFLS design assessments performed under Requirement R4 or R5, the Corrective Action Plan shall be developed within the five-year time frame identified in Requirement R4. | HIGH | Retired | 2017-10-01 | 2021-04-30 | PC
PRC-006-3 | Automatic Underfrequency Load Shedding | R15.2. | For UFLS design assessments performed under Requirement R12, the Corrective Action Plan shall be developed within the two-year time frame identified in Requirement R12. | HIGH | Retired | 2017-10-01 | 2021-04-30 | PC
PRC-006-3 | Automatic Underfrequency Load Shedding | R2. | Each Planning Coordinator shall identify one or more islands to serve as a basis for designing its UFLS program including: | MEDIUM | Retired | 2017-10-01 | 2021-03-31 | PC
PRC-006-3 | Automatic Underfrequency Load Shedding | R2.1. | Those islands selected by applying the criteria in Requirement R1, and | MEDIUM | Retired | 2017-10-01 | 2021-03-31 | PC
PRC-006-3 | Automatic Underfrequency Load Shedding | R2.2. | Any portions of the BES designed to detach from the Interconnection (planned islands) as a result of the operation of a relay scheme or Special Protection System, and | MEDIUM | Retired | 2017-10-01 | 2021-03-31 | PC
PRC-006-3 | Automatic Underfrequency Load Shedding | R2.3. | A single island that includes all portions of the BES in either the Regional Entity area or the Interconnection in which the Planning Coordinator’s area resides. If a Planning Coordinator’s area resides in multiple Regional Entity areas, each of those Regional Entity areas shall be identified as an island. Planning Coordinators may adjust island boundaries to differ from Regional Entity area boundaries by mutual consent where necessary for the sole purpose of producing contiguous regional islands more suitable for simulation. | MEDIUM | Retired | 2017-10-01 | 2021-03-31 | PC
PRC-006-3 | Automatic Underfrequency Load Shedding | R3. | Each Planning Coordinator shall develop a UFLS program, including notification of and a schedule for implementation by UFLS entities within its area, that meets the following performance characteristics in simulations of underfrequency conditions resulting from an imbalance scenario, where an imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s) | HIGH | Retired | 2017-10-01 | 2021-03-31 | PC
PRC-006-3 | Automatic Underfrequency Load Shedding | R3. | Each Planning Coordinator shall develop a UFLS program, including notification of and a schedule for implementation by UFLS entities within its area, that meets the following performance characteristics in simulations of underfrequency conditions resulting from an imbalance scenario, where an imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s) | HIGH | Retired | 2017-10-01 | 2021-03-31 | PC
PRC-006-3 | Automatic Underfrequency Load Shedding | R3.1. | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-2 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and | HIGH | Retired | 2017-10-01 | 2021-03-31 | PC
PRC-006-3 | Automatic Underfrequency Load Shedding | R3.2. | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-2 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and | HIGH | Retired | 2017-10-01 | 2021-03-31 | PC
PRC-006-3 | Automatic Underfrequency Load Shedding | R3.3. | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each generator bus and generator step-up transformer high-side bus associated with each of the following: • Individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES • Generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES • Facilities consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA gross nameplate rating. | HIGH | Retired | 2017-10-01 | 2021-03-31 | PC
PRC-006-3 | Automatic Underfrequency Load Shedding | R4. | Each Planning Coordinator shall conduct and document a UFLS design assessment at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement R3 for each island identified in Requirement R2. The simulation shall model each of the following: | HIGH | Retired | 2017-10-01 | 2021-03-31 | PC
PRC-006-3 | Automatic Underfrequency Load Shedding | R4.1. | Underfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-2 - Attachment 1. | HIGH | Retired | 2017-10-01 | 2021-03-31 | PC
PRC-006-3 | Automatic Underfrequency Load Shedding | R4.2. | Underfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-2 - Attachment 1. | HIGH | Retired | 2017-10-01 | 2021-03-31 | PC
PRC-006-3 | Automatic Underfrequency Load Shedding | R4.3. | Underfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-2 - Attachment 1. | HIGH | Retired | 2017-10-01 | 2021-03-31 | PC
PRC-006-3 | Automatic Underfrequency Load Shedding | R4.4. | Overfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-2 — Attachment 1. | HIGH | Retired | 2017-10-01 | 2021-03-31 | PC
PRC-006-3 | Automatic Underfrequency Load Shedding | R4.5. | Overfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-2 — Attachment 1. | HIGH | Retired | 2017-10-01 | 2021-03-31 | PC
PRC-006-3 | Automatic Underfrequency Load Shedding | R4.6. | Overfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-2 — Attachment 1. | HIGH | Retired | 2017-10-01 | 2021-03-31 | PC
PRC-006-3 | Automatic Underfrequency Load Shedding | R4.7. | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment | HIGH | Retired | 2017-10-01 | 2021-03-31 | PC
PRC-006-3 | Automatic Underfrequency Load Shedding | R5. | Each Planning Coordinator, whose area or portions of whose area is part of an island identified by it or another Planning Coordinator which includes multiple Planning Coordinator areas or portions of those areas, shall coordinate its UFLS program design with all other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island through one of the following: • Develop a common UFLS program design and schedule for implementation per Requirement R3 among the Planning Coordinators whose areas or portions of whose areas are part of the same identified island, or • Conduct a joint UFLS design assessment per Requirement R4 among the Planning Coordinators whose areas or portions of whose areas are part of the same identified island, or • Conduct an independent UFLS design assessment per Requirement R4 for the identified island, and in the event the UFLS design assessment fails to meet Requirement R3, identify modifications to the UFLS program(s) to meet Requirement R3 and report these modifications as recommendations to the other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island and the ERO. | HIGH | Retired | 2017-10-01 | 2021-03-31 | PC
PRC-006-3 | Automatic Underfrequency Load Shedding | R6. | Each Planning Coordinator shall maintain a UFLS database containing data necessary to model its UFLS program for use in event analyses and assessments of the UFLS program at least once each calendar year, with no more than 15 months between maintenance activities. | LOWER | Retired | 2017-10-01 | 2021-03-31 | PC
PRC-006-3 | Automatic Underfrequency Load Shedding | R6. | Each Planning Coordinator shall maintain a UFLS database containing data necessary to model its UFLS program for use in event analyses and assessments of the UFLS program at least once each calendar year, with no more than 15 months between maintenance activities. | LOWER | Retired | 2017-10-01 | 2021-03-31 | PC
PRC-006-3 | Automatic Underfrequency Load Shedding | R7. | Each Planning Coordinator shall provide its UFLS database containing data necessary to model its UFLS program to other Planning Coordinators within its Interconnection within 30 calendar days of a request. | LOWER | Retired | 2017-10-01 | 2021-03-31 | PC
PRC-006-3 | Automatic Underfrequency Load Shedding | R8. | Each UFLS entity shall provide data to its Planning Coordinator(s) according to the format and schedule specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. | LOWER | Retired | 2017-10-01 | 2021-03-31 | TO, DP
PRC-006-3 | Automatic Underfrequency Load Shedding | R9. | Each UFLS entity shall provide automatic tripping of Load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, as determined by its Planning Coordinator(s) in each Planning Coordinator area in which it owns assets. | HIGH | Retired | 2017-10-01 | 2021-03-31 | TO, DP
PRC-006-4 | Automatic Underfrequency Load Shedding | R1. | Each Planning Coordinator shall develop and document criteria, including consideration of historical events and system studies, to select portions of the Bulk Electric System (BES), including interconnected portions of the BES in adjacent Planning Coordinator areas and Regional Entity areas that may form islands. [VRF: Medium][Time Horizon: Long-term Planning] | MEDIUM | Effective | 2021-04-01 |  | DP, TO, PC
PRC-006-4 | Automatic Underfrequency Load Shedding | R10. | Each Transmission Owner shall provide automatic switching of its existing capacitor banks, Transmission Lines, and reactors to control over-voltage as a result of underfrequency load shedding if required by the UFLS program and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) in each Planning Coordinator area in which the Transmission Owner owns transmission. [VRF: High][Time Horizon: Long-term Planning] | HIGH | Effective | 2021-04-01 |  | DP, TO, PC
PRC-006-4 | Automatic Underfrequency Load Shedding | R11. | Each Planning Coordinator, in whose area a BES islanding event results in system frequency excursions below the initializing set points of the UFLS program, shall conduct and document an assessment of the event within one year of event actuation to evaluate: [VRF: Medium][Time Horizon: Operations Assessment] | MEDIUM | Effective | 2021-04-01 |  | DP, TO, PC
PRC-006-4 | Automatic Underfrequency Load Shedding | R11.1. | The performance of the UFLS equipment, | MEDIUM | Effective | 2021-04-01 |  | DP, TO, PC
PRC-006-4 | Automatic Underfrequency Load Shedding | R11.2. | The effectiveness of the UFLS program. | MEDIUM | Effective | 2021-04-01 |  | DP, TO, PC
PRC-006-4 | Automatic Underfrequency Load Shedding | R12. | Each Planning Coordinator, in whose islanding event assessment (per R11) UFLS program deficiencies are identified, shall conduct and document a UFLS design assessment to consider the identified deficiencies within two years of event actuation. [VRF: Medium][Time Horizon: Operations Assessment] | MEDIUM | Effective | 2021-04-01 |  | DP, TO, PC
PRC-006-4 | Automatic Underfrequency Load Shedding | R13. | Each Planning Coordinator, in whose area a BES islanding event occurred that also included the area(s) or portions of area(s) of other Planning Coordinator(s) in the same islanding event and that resulted in system frequency excursions below the initializing set points of the UFLS program, shall coordinate its event assessment (in accordance with Requirement R11) with all other Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event through one of the following: [VRF: Medium][Time Horizon: Operations Assessment] • Conduct a joint event assessment per Requirement R11 among the Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, or • Conduct an independent event assessment per Requirement R11 that reaches conclusions and recommendations consistent with those of the event assessments of the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, or • Conduct an independent event assessment per Requirement R11 and where the assessment fails to reach conclusions and recommendations consistent with those of the event assessments of the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, identify differences in the assessments that likely resulted in the differences in the conclusions and recommendations and report these differences to the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event and the ERO. | MEDIUM | Effective | 2021-04-01 |  | DP, TO, PC
PRC-006-4 | Automatic Underfrequency Load Shedding | R14. | Each Planning Coordinator shall respond to written comments submitted by UFLS entities and Transmission Owners within its Planning Coordinator area following a comment period and before finalizing its UFLS program, indicating in the written response to comments whether changes will be made or reasons why changes will not be made to the following [VRF: Lower][Time Horizon: Long-term Planning]: | LOWER | Effective | 2021-04-01 |  | DP, TO, PC
PRC-006-4 | Automatic Underfrequency Load Shedding | R14.1. | UFLS program, including a schedule for implementation | LOWER | Effective | 2021-04-01 |  | DP, TO, PC
PRC-006-4 | Automatic Underfrequency Load Shedding | R14.2. | UFLS design assessment | LOWER | Effective | 2021-04-01 |  | DP, TO, PC
PRC-006-4 | Automatic Underfrequency Load Shedding | R14.3. | Format and schedule of UFLS data submittal | LOWER | Effective | 2021-04-01 |  | DP, TO, PC
PRC-006-4 | Automatic Underfrequency Load Shedding | R15. | Each Planning Coordinator that conducts a UFLS design assessment under Requirement R4, R5, or R12 and determines that the UFLS program does not meet the performance characteristics in Requirement R3, shall develop a Corrective Action Plan and a schedule for implementation by the UFLS entities within its area. [VRF: High][Time Horizon: Long-term Planning] | HIGH | Effective | 2021-04-01 |  | DP, TO, PC
PRC-006-4 | Automatic Underfrequency Load Shedding | R15.1. | For UFLS design assessments performed under Requirement R4 or R5, the Corrective Action Plan shall be developed within the five-year time frame identified in Requirement R4. | HIGH | Effective | 2021-04-01 |  | DP, TO, PC
PRC-006-4 | Automatic Underfrequency Load Shedding | R15.2. | For UFLS design assessments performed under Requirement R12, the Corrective Action Plan shall be developed within the two-year time frame identified in Requirement R12. | HIGH | Effective | 2021-04-01 |  | DP, TO, PC
PRC-006-4 | Automatic Underfrequency Load Shedding | R2. | Each Planning Coordinator shall identify one or more islands to serve as a basis for designing its UFLS program including: [VRF: Medium][Time Horizon: Long-term Planning] | MEDIUM | Effective | 2021-04-01 |  | DP, TO, PC
PRC-006-4 | Automatic Underfrequency Load Shedding | R2.1. | Those islands selected by applying the criteria in Requirement R1, and | MEDIUM | Effective | 2021-04-01 |  | DP, TO, PC
PRC-006-4 | Automatic Underfrequency Load Shedding | R2.2. | Any portions of the BES designed to detach from the Interconnection (planned islands) as a result of the operation of a relay scheme or Special Protection System, and | MEDIUM | Effective | 2021-04-01 |  | DP, TO, PC
PRC-006-4 | Automatic Underfrequency Load Shedding | R2.3. | A single island that includes all portions of the BES in either the Regional Entity area or the Interconnection in which the Planning Coordinator’s area resides. If a Planning Coordinator’s area resides in multiple Regional Entity areas, each of those Regional Entity areas shall be identified as an island. Planning Coordinators may adjust island boundaries to differ from Regional Entity area boundaries by mutual consent where necessary for the sole purpose of producing contiguous regional islands more suitable for simulation. | MEDIUM | Effective | 2021-04-01 |  | DP, TO, PC
PRC-006-4 | Automatic Underfrequency Load Shedding | R3. | Each Planning Coordinator shall develop a UFLS program, including notification of and a schedule for implementation by UFLS entities within its area, that meets the following performance characteristics in simulations of underfrequency conditions resulting from an imbalance scenario, where an imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s). [VRF: High][Time Horizon: Long-term Planning] | HIGH | Effective | 2021-04-01 |  | DP, TO, PC
PRC-006-4 | Automatic Underfrequency Load Shedding | R3. | Each Planning Coordinator shall develop a UFLS program, including notification of and a schedule for implementation by UFLS entities within its area, that meets the following performance characteristics in simulations of underfrequency conditions resulting from an imbalance scenario, where an imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s). [VRF: High][Time Horizon: Long-term Planning] | HIGH | Effective | 2021-04-01 |  | DP, TO, PC
PRC-006-4 | Automatic Underfrequency Load Shedding | R3.1. | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-4 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and | HIGH | Effective | 2021-04-01 |  | DP, TO, PC
PRC-006-4 | Automatic Underfrequency Load Shedding | R3.2. | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-4 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and | HIGH | Effective | 2021-04-01 |  | DP, TO, PC
PRC-006-4 | Automatic Underfrequency Load Shedding | R3.3. | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each generator bus and generator step-up transformer high-side bus associated with each of the following: • Individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES • Generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES • Facilities consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA gross nameplate rating. | HIGH | Effective | 2021-04-01 |  | DP, TO, PC
PRC-006-4 | Automatic Underfrequency Load Shedding | R4. | Each Planning Coordinator shall conduct and document a UFLS design assessment at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement R3 for each island identified in Requirement R2. The simulation shall model each of the following: [VRF: High][Time Horizon: Long-term Planning] | HIGH | Effective | 2021-04-01 |  | DP, TO, PC
PRC-006-4 | Automatic Underfrequency Load Shedding | R4.1. | Underfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-4 - Attachment 1. | HIGH | Effective | 2021-04-01 |  | DP, TO, PC
PRC-006-4 | Automatic Underfrequency Load Shedding | R4.2. | Underfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-4 - Attachment 1. | HIGH | Effective | 2021-04-01 |  | DP, TO, PC
PRC-006-4 | Automatic Underfrequency Load Shedding | R4.3. | Underfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-4 - Attachment 1. | HIGH | Effective | 2021-04-01 |  | DP, TO, PC
PRC-006-4 | Automatic Underfrequency Load Shedding | R4.4. | Overfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-4 — Attachment 1. | HIGH | Effective | 2021-04-01 |  | DP, TO, PC
PRC-006-4 | Automatic Underfrequency Load Shedding | R4.5. | Overfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-4 — Attachment 1. | HIGH | Effective | 2021-04-01 |  | DP, TO, PC
PRC-006-4 | Automatic Underfrequency Load Shedding | R4.6. | Overfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-4 — Attachment 1. | HIGH | Effective | 2021-04-01 |  | DP, TO, PC
PRC-006-4 | Automatic Underfrequency Load Shedding | R4.7. | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. | HIGH | Effective | 2021-04-01 |  | DP, TO, PC
PRC-006-4 | Automatic Underfrequency Load Shedding | R5. | Each Planning Coordinator, whose area or portions of whose area is part of an island identified by it or another Planning Coordinator which includes multiple Planning Coordinator areas or portions of those areas, shall coordinate its UFLS program design with all other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island through one of the following: [VRF: High][Time Horizon: Long-term Planning] • Develop a common UFLS program design and schedule for implementation per Requirement R3 among the Planning Coordinators whose areas or portions of whose areas are part of the same identified island, or • Conduct a joint UFLS design assessment per Requirement R4 among the Planning Coordinators whose areas or portions of whose areas are part of the same identified island, or • Conduct an independent UFLS design assessment per Requirement R4 for the identified island, and in the event the UFLS design assessment fails to meet Requirement R3, identify modifications to the UFLS program(s) to meet Requirement R3 and report these modifications as recommendations to the other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island and the ERO. | HIGH | Effective | 2021-04-01 |  | DP, TO, PC
PRC-006-4 | Automatic Underfrequency Load Shedding | R6. | Each Planning Coordinator shall maintain a UFLS database containing data necessary to model its UFLS program for use in event analyses and assessments of the UFLS program at least once each calendar year, with no more than 15 months between maintenance activities. [VRF: Lower][Time Horizon: Long-term Planning] | LOWER | Effective | 2021-04-01 |  | DP, TO, PC
PRC-006-4 | Automatic Underfrequency Load Shedding | R6. | Each Planning Coordinator shall maintain a UFLS database containing data necessary to model its UFLS program for use in event analyses and assessments of the UFLS program at least once each calendar year, with no more than 15 months between maintenance activities. [VRF: Lower][Time Horizon: Long-term Planning] | LOWER | Effective | 2021-04-01 |  | DP, TO, PC
PRC-006-4 | Automatic Underfrequency Load Shedding | R7. | Each Planning Coordinator shall provide its UFLS database containing data necessary to model its UFLS program to other Planning Coordinators within its Interconnection within 30 calendar days of a request. [VRF: Lower][Time Horizon: Long-term Planning] | LOWER | Effective | 2021-04-01 |  | DP, TO, PC
PRC-006-4 | Automatic Underfrequency Load Shedding | R8. | Each UFLS entity shall provide data to its Planning Coordinator(s) according to the format and schedule specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. [VRF: Lower][Time Horizon: Long-term Planning] | LOWER | Effective | 2021-04-01 |  | DP, TO, PC
PRC-006-4 | Automatic Underfrequency Load Shedding | R9. | Each UFLS entity shall provide automatic tripping of Load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, as determined by its Planning Coordinator(s) in each Planning Coordinator area in which it owns assets. [VRF: High][Time Horizon: Long-term Planning] | HIGH | Effective | 2021-04-01 |  | DP, TO, PC
PRC-006-5 | Automatic Underfrequency Load Shedding | R1. | Each Planning Coordinator shall develop and document criteria, including consideration of historical events and system studies, to select portions of the Bulk Electric System (BES), including interconnected portions of the BES in adjacent Planning Coordinator areas and Regional Entity areas that may form islands. [VRF: Medium][Time Horizon: Long-term Planning] | MEDIUM | Effective | 2024-04-01 |  | PC
PRC-006-5 | Automatic Underfrequency Load Shedding | R10. | Each Transmission Owner shall provide automatic switching of its existing capacitor banks, Transmission Lines, and reactors to control over-voltage as a result of underfrequency load shedding if required by the UFLS program and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) in each Planning Coordinator area in which the Transmission Owner owns transmission. [VRF: High][Time Horizon: Long-term Planning] | HIGH | Effective | 2024-04-01 |  | TO
PRC-006-5 | Automatic Underfrequency Load Shedding | R11. | Each Planning Coordinator, in whose area a BES islanding event results in system frequency excursions below the initializing set points of the UFLS program, shall conduct and document an assessment of the event within one year of event actuation to evaluate: [VRF: Medium][Time Horizon: Operations Assessment] | MEDIUM | Effective | 2024-04-01 |  | PC
PRC-006-5 | Automatic Underfrequency Load Shedding | R11.1. | The performance of the UFLS equipment, | MEDIUM | Effective | 2024-04-01 |  | PC
PRC-006-5 | Automatic Underfrequency Load Shedding | R11.2. | The effectiveness of the UFLS program. | MEDIUM | Effective | 2024-04-01 |  | PC
PRC-006-5 | Automatic Underfrequency Load Shedding | R12. | Each Planning Coordinator, in whose islanding event assessment (per R11) UFLS program deficiencies are identified, shall conduct and document a UFLS design assessment to consider the identified deficiencies within two years of event actuation. [VRF: Medium][Time Horizon: Operations Assessment] | MEDIUM | Effective | 2024-04-01 |  | PC
PRC-006-5 | Automatic Underfrequency Load Shedding | R13. | Each Planning Coordinator, in whose area a BES islanding event occurred that also included the area(s) or portions of area(s) of other Planning Coordinator(s) in the same islanding event and that resulted in system frequency excursions below the initializing set points of the UFLS program, shall coordinate its event assessment (in accordance with Requirement R11) with all other Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event through one of the following: [VRF: Medium][Time Horizon: Operations Assessment] • Conduct a joint event assessment per Requirement R11 among the Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, or • Conduct an independent event assessment per Requirement R11 that reaches conclusions and recommendations consistent with those of the event assessments of the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, or • Conduct an independent event assessment per Requirement R11 and where the assessment fails to reach conclusions and recommendations consistent with those of the event assessments of the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, identify differences in the assessments that likely resulted in the differences in the conclusions and recommendations and report these differences to the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event and the ERO. | MEDIUM | Effective | 2024-04-01 |  | PC
PRC-006-5 | Automatic Underfrequency Load Shedding | R14. | Each Planning Coordinator shall respond to written comments submitted by UFLS entities and Transmission Owners within its Planning Coordinator area following a comment period and before finalizing its UFLS program, indicating in the written response to comments whether changes will be made or reasons why changes will not be made to the following [VRF: Lower][Time Horizon: Long-term Planning]: | LOWER | Effective | 2024-04-01 |  | PC
PRC-006-5 | Automatic Underfrequency Load Shedding | R14.1. | UFLS program, including a schedule for implementation | LOWER | Effective | 2024-04-01 |  | PC
PRC-006-5 | Automatic Underfrequency Load Shedding | R14.2. | UFLS design assessment | LOWER | Effective | 2024-04-01 |  | PC
PRC-006-5 | Automatic Underfrequency Load Shedding | R14.3. | Format and schedule of UFLS data submittal | LOWER | Effective | 2024-04-01 |  | PC
PRC-006-5 | Automatic Underfrequency Load Shedding | R15. | Each Planning Coordinator that conducts a UFLS design assessment under Requirement R4, R5, or R12 and determines that the UFLS program does not meet the performance characteristics in Requirement R3, shall develop a Corrective Action Plan and a schedule for implementation by the UFLS entities within its area. [VRF: High][Time Horizon: Long-term Planning] | HIGH | Effective | 2024-04-01 |  | PC
PRC-006-5 | Automatic Underfrequency Load Shedding | R15.1. | For UFLS design assessments performed under Requirement R4 or R5, the Corrective Action Plan shall be developed within the five-year time frame identified in Requirement R4. | HIGH | Effective | 2024-04-01 |  | PC
PRC-006-5 | Automatic Underfrequency Load Shedding | R15.2. | For UFLS design assessments performed under Requirement R12, the Corrective Action Plan shall be developed within the two-year time frame identified in Requirement R12. | HIGH | Effective | 2024-04-01 |  | PC
PRC-006-5 | Automatic Underfrequency Load Shedding | R2. | Each Planning Coordinator shall identify one or more islands to serve as a basis for designing its UFLS program including: [VRF: Medium][Time Horizon: Long-term Planning] | MEDIUM | Effective | 2024-04-01 |  | PC
PRC-006-5 | Automatic Underfrequency Load Shedding | R2.1. | Those islands selected by applying the criteria in Requirement R1, and | MEDIUM | Effective | 2024-04-01 |  | PC
PRC-006-5 | Automatic Underfrequency Load Shedding | R2.2. | Any portions of the BES designed to detach from the Interconnection (planned islands) as a result of the operation of a relay scheme or Special Protection System, and | MEDIUM | Effective | 2024-04-01 |  | PC
PRC-006-5 | Automatic Underfrequency Load Shedding | R2.3. | A single island that includes all portions of the BES in either the Regional Entity area or the Interconnection in which the Planning Coordinator’s area resides. If a Planning Coordinator’s area resides in multiple Regional Entity areas, each of those Regional Entity areas shall be identified as an island. Planning Coordinators may adjust island boundaries to differ from Regional Entity area boundaries by mutual consent where necessary for the sole purpose of producing contiguous regional islands more suitable for simulation. | MEDIUM | Effective | 2024-04-01 |  | PC
PRC-006-5 | Automatic Underfrequency Load Shedding | R3. | Each Planning Coordinator shall develop a UFLS program, including notification of and a schedule for implementation by UFLS entities within its area, that meets the following performance characteristics in simulations of underfrequency conditions resulting from an imbalance scenario, where an imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s). [VRF: High][Time Horizon: Long-term Planning] | HIGH | Effective | 2024-04-01 |  | PC
PRC-006-5 | Automatic Underfrequency Load Shedding | R3.1. | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-5 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and | HIGH | Effective | 2024-04-01 |  | PC
PRC-006-5 | Automatic Underfrequency Load Shedding | R3.2. | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-5 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and | HIGH | Effective | 2024-04-01 |  | PC
PRC-006-5 | Automatic Underfrequency Load Shedding | R3.3. | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each generator bus and generator step-up transformer high-side bus associated with each of the following: • Individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES • Generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES • Facilities consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA gross nameplate rating. | HIGH | Effective | 2024-04-01 |  | PC
PRC-006-5 | Automatic Underfrequency Load Shedding | R4. | Each Planning Coordinator shall conduct and document a UFLS design assessment at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement R3 for each island identified in Requirement R2. The simulation shall model each of the following: [VRF: High][Time Horizon: Long-term Planning] | HIGH | Effective | 2024-04-01 |  | PC
PRC-006-5 | Automatic Underfrequency Load Shedding | R4.1. | Underfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-5 - Attachment 1. | HIGH | Effective | 2024-04-01 |  | PC
PRC-006-5 | Automatic Underfrequency Load Shedding | R4.2. | Underfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-5 - Attachment 1. | HIGH | Effective | 2024-04-01 |  | PC
PRC-006-5 | Automatic Underfrequency Load Shedding | R4.3. | Underfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-5 - Attachment 1. | HIGH | Effective | 2024-04-01 |  | PC
PRC-006-5 | Automatic Underfrequency Load Shedding | R4.4. | Overfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-5 — Attachment 1. | HIGH | Effective | 2024-04-01 |  | PC
PRC-006-5 | Automatic Underfrequency Load Shedding | R4.5. | Overfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-5 — Attachment 1. | HIGH | Effective | 2024-04-01 |  | PC
PRC-006-5 | Automatic Underfrequency Load Shedding | R4.6. | Overfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-5 — Attachment 1. | HIGH | Effective | 2024-04-01 |  | PC
PRC-006-5 | Automatic Underfrequency Load Shedding | R4.7. | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. | HIGH | Effective | 2024-04-01 |  | PC
PRC-006-5 | Automatic Underfrequency Load Shedding | R5. | Each Planning Coordinator, whose area or portions of whose area is part of an island identified by it or another Planning Coordinator which includes multiple Planning Coordinator areas or portions of those areas, shall coordinate its UFLS program design with all other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island through one of the following: [VRF: High][Time Horizon: Long-term Planning]Develop a common UFLS program design and schedule for implementation per Requirement R3 among the Planning Coordinators whose areas or portions of whose areas are part of the same identified island, or • Conduct a joint UFLS design assessment per Requirement R4 among the Planning Coordinators whose areas or portions of whose areas are part of the same identified island, or • Conduct an independent UFLS design assessment per Requirement R4 for the identified island, and in the event the UFLS design assessment fails to meet Requirement R3, identify modifications to the UFLS program(s) to meet Requirement R3 and report these modifications as recommendations to the other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island and the ERO. | HIGH | Effective | 2024-04-01 |  | PC
PRC-006-5 | Automatic Underfrequency Load Shedding | R6. | Each Planning Coordinator shall maintain a UFLS database containing data necessary to model its UFLS program for use in event analyses and assessments of the UFLS program at least once each calendar year, with no more than 15 months between maintenance activities. [VRF: Lower][Time Horizon: Long-term Planning] | LOWER | Effective | 2024-04-01 |  | PC
PRC-006-5 | Automatic Underfrequency Load Shedding | R7. | Each Planning Coordinator shall provide its UFLS database containing data necessary to model its UFLS program to other Planning Coordinators within its Interconnection within 30 calendar days of a request. [VRF: Lower][Time Horizon: Long-term Planning] | LOWER | Effective | 2024-04-01 |  | PC
PRC-006-5 | Automatic Underfrequency Load Shedding | R8. | Each UFLS entity shall provide data to its Planning Coordinator(s) according to the format and schedule specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. [VRF: Lower][Time Horizon: Long-term Planning] | LOWER | Effective | 2024-04-01 |  | TO, DP
PRC-006-5 | Automatic Underfrequency Load Shedding | R9. | Each UFLS entity shall provide automatic tripping of Load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, as determined by its Planning Coordinator(s) in each Planning Coordinator area in which it owns assets. [VRF: High][Time Horizon: Long-term Planning] | HIGH | Effective | 2024-04-01 |  | TO, DP
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R1. | Each Planning Coordinator shall establish requirements for entities aggregating their UFLS programs for each anticipated island and requirements for compensatory load shedding based on islanding criteria (required by the NERC PRC Standard on UFLS). [Violation Risk Factor: Medium] [Time Horizon: Long Term Planning] | MEDIUM | Retired | 2017-04-01 | 2020-06-30 | PC
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R10. | Each Distribution Provider and Transmission Owner shall implement the inhibit threshold settings based on the notification provided by the Planning Coordinator in accordance with Requirement R9. [Violation Risk Factor: High] [Time Horizon: Operations Planning] | HIGH | Retired | 2017-04-01 | 2020-06-30 | TO, DP
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R11. | Each Distribution Provider and Transmission Owner shall develop and submit an implementation plan within 90 days of the request from the Planning Coordinator for approval by the Planning Coordinator in accordance with R9. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Retired | 2017-04-01 | 2020-06-30 | DP
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R12. | Each Transmission Owner and Distribution Provider shall annually provide documentation, with no more than 15 months between updates, to its Planning Coordinator of the actual net Load that would have been shed by the UFLS relays at each UFLS stage coincident with their integrated hourly peak net Load during the previous year, as determined by measuring actual metered Load through the switches that would be opened by the UFLS relays. [Violation Risk Factor: Lower] [Time Horizon: Long Term Planning] | LOWER | Retired | 2017-04-01 | 2020-06-30 | TO, DP
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R13. | Each Generator Owner shall set each generator underfrequency trip relay, if so equipped, below the appropriate generator underfrequency trip protection settings threshold curve in Figure 1, except as otherwise exempted in Requirements R16 and R19. [Violation Risk Factor: High] [Time Horizon: Long Term Planning] | HIGH | Retired | 2017-04-01 | 2020-06-30 | GO
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R14. | Each Generator Owner shall transmit the generator underfrequency trip setting and time delay to its Planning Coordinator within 45 days of the Planning Coordinator’s request. [Violation Risk Factor: High] [Time Horizon: Operations Planning] | HIGH | Retired | 2017-04-01 | 2020-06-30 | GO
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R15. | Each Generator Owner with a new generating unit, scheduled to be in service on or after the effective date of this Standard, or an existing generator increasing its net capability by greater than 10% shall: [Violation Risk Factor: High] [Time Horizon: Long Term Planning] | HIGH | Retired | 2017-04-01 | 2020-06-30 | GO
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R15.1. | Design measures to prevent the generating unit from tripping directly or indirectly for underfrequency conditions above the appropriate generator tripping threshold curve in Figure 1. | HIGH | Retired | 2017-04-01 | 2020-06-30 | GO
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R15.2. | Design auxiliary system(s) or devices used for the control and protection of auxiliary system(s), necessary for the generating unit operation such that they will not trip the generating unit during underfrequency conditions above the appropriate generator underfrequency trip protection settings threshold curve in Figure 1. | HIGH | Retired | 2017-04-01 | 2020-06-30 | GO
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R16. | Each Generator Owner of existing non-nuclear units in service prior to the effective date of this standard that have underfrequency protections set to trip above the appropriate curve in Figure 1 shall: [Violation Risk Factor: High] [Time Horizon: Long Term Planning] | HIGH | Retired | 2017-04-01 | 2020-06-30 | GO
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R16.1. | Set the underfrequency protection to operate at the lowest frequency allowed by the plant design and licensing limitations. | HIGH | Retired | 2017-04-01 | 2020-06-30 | GO
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R16.2. | Transmit the existing underfrequency settings and any changes to the underfrequency settings along with the technical basis for the settings to the Planning Coordinator. | HIGH | Retired | 2017-04-01 | 2020-06-30 | GO
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R16.3. | Have compensatory load shedding, as provided by a Distribution Provider or Transmission Owner that is adequate to compensate for the loss of their generator due to early tripping. | HIGH | Retired | 2017-04-01 | 2020-06-30 | GO
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R17. | Each Planning Coordinator in Ontario, Quebec and the Maritime provinces shall apply the criteria described in Attachment A to determine the compensatory load shedding that is required in Requirement R16.3 for generating units in its respective NPCC area. [Violation Risk Factor: High] [Time Horizon: Long Term Planning] | HIGH | Retired | 2017-04-01 | 2020-06-30 | PC
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R18. | Each Generator Owner, Distribution Provider or Transmission Owner within the Planning Coordinator area of ISO-NE or the New York ISO shall apply the criteria described in Attachment B to determine the compensatory load shedding that is required in Requirement R16.3 for generating units in its respective NPCC area. [Violation Risk Factor: High] [Time Horizon: Long Term Planning] | HIGH | Effective | 2017-04-01 |  | TO, GO, DP
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R19. | Each Generator Owner of existing nuclear generating plants with units that have underfrequency relay threshold settings above the Eastern Interconnection generator tripping curve in Figure 1, based on their licensing design basis, shall: [Violation Risk Factor: High] [Time Horizon: Long Term Planning] | HIGH | Effective | 2017-04-01 |  | GO
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R19.1. | Set the underfrequency protection to operate at as low a frequency as possible in accordance with the plant design and licensing limitations but not greater than 57.8Hz. | HIGH | Effective | 2017-04-01 |  | GO
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R19.2. | Set the frequency trip setting upper tolerance to no greater than + 0.1 Hz. | HIGH | Effective | 2017-04-01 |  | GO
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R19.3. | Transmit the initial frequency trip setting and any changes to the setting and the technical basis for the settings to the Planning Coordinator. | HIGH | Effective | 2017-04-01 |  | GO
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R2. | Each Planning Coordinator shall, within 30 days of completion of its system studies required by the NERC PRC Standard on UFLS, identify to the Regional Entity the generation facilities within its Planning Coordinator Area necessary to support the UFLS program performance characteristics. [Violation Risk Factor: Medium] [Time Horizon: Long Term Planning] | MEDIUM | Retired | 2017-04-01 | 2020-06-30 | PC
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R20. | The Planning Coordinator shall update its UFLS program database as specified by the NERC PRC Standard on UFLS. This database shall include the following information: [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Effective | 2017-04-01 |  | PC
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R20. | The Planning Coordinator shall update its UFLS program database as specified by the NERC PRC Standard on UFLS. This database shall include the following information: [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Effective | 2017-04-01 |  | PC
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R20.1. | For each UFLS relay, including those used for compensatory load shedding, the amount and location of load shed at peak, the corresponding frequency threshold and time delay settings. | LOWER | Effective | 2017-04-01 |  | PC
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R20.1. | For each UFLS relay, including those used for compensatory load shedding, the amount and location of load shed at peak, the corresponding frequency threshold and time delay settings. | LOWER | Effective | 2017-04-01 |  | PC
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R20.2. | The buses at which the Load is modeled in the NPCC library power flow case. | LOWER | Effective | 2017-04-01 |  | PC
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R20.2. | The buses at which the Load is modeled in the NPCC library power flow case. | LOWER | Effective | 2017-04-01 |  | PC
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R20.3. | A list of all generating units that may be tripped for underfrequency conditions above the appropriate generator underfrequency trip protection settings threshold curve in Figure 1, including the frequency trip threshold and time delay for each protection system. | LOWER | Effective | 2017-04-01 |  | PC
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R20.3. | A list of all generating units that may be tripped for underfrequency conditions above the appropriate generator underfrequency trip protection settings threshold curve in Figure 1, including the frequency trip threshold and time delay for each protection system. | LOWER | Effective | 2017-04-01 |  | PC
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R20.4. | The location and amount of additional elements to be switched for voltage control that are coordinated with UFLS program tripping. | LOWER | Effective | 2017-04-01 |  | PC
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R20.4. | The location and amount of additional elements to be switched for voltage control that are coordinated with UFLS program tripping. | LOWER | Effective | 2017-04-01 |  | PC
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R20.5. | A list of all UFLS relay inhibit functions along with the corresponding settings and locations of these relays. | LOWER | Effective | 2017-04-01 |  | PC
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R20.5. | A list of all UFLS relay inhibit functions along with the corresponding settings and locations of these relays. | LOWER | Effective | 2017-04-01 |  | PC
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R21. | Each Planning Coordinator shall notify each Distribution Provider, Transmission Owner, and Generator Owner within its Planning Coordinator area of changes to load distribution needed to satisfy UFLS program performance characteristics as specified by the NERC PRC Standard on UFLS.[Violation Risk Factor: High] [Time Horizon: Long Term Planning] | HIGH | Retired | 2017-04-01 | 2020-06-30 | PC
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R22. | Each Distribution Provider, Transmission Owner and Generator Owner shall implement the load distribution changes based on the notification provided by the Planning Coordinator in accordance with Requirement R21. [Violation Risk Factor: High] [Time Horizon: Long Term Planning] | HIGH | Retired | 2017-04-01 | 2020-06-30 | TO, GO, DP
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R23. | Each Distribution Provider, Transmission Owner and Generator Owner shall develop and submit an implementation plan within 90 days of the request from the Planning Coordinator for approval by the Planning Coordinator in accordance with Requirement R21. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Retired | 2017-04-01 | 2020-06-30 | TO, GO, DP
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R3. | Each Planning Coordinator shall provide to the Transmission Owner, Distribution Provider, and Generator Owner within 30 days upon written request the requirements for entities aggregating the UFLS programs and requirements for compensatory load shedding program derived from each Planning Coordinator’s system studies as determined by Requirement R1. [Violation Risk Factor: Low] [Time Horizon: Long Term Planning] | LOWER | Retired | 2017-04-01 | 2020-06-30 | PC
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R4. | Each Distribution Provider and Transmission Owner in the Eastern Interconnection portion of NPCC shall implement an automatic UFLS program reflecting normal operating conditions excluding outages for its Facilities based on frequency thresholds, total nominal operating time and amounts specified in Attachment C, Tables 1 through 3, or shall collectively implement by mutual agreement with one or more Distribution Providers and Transmission Owners within the same island identified in Requirement R1 and acting as a single entity, provide an aggregated automatic UFLS program that sheds their coincident peak aggregated net Load, based on frequency thresholds, total nominal operating time and amounts specified in Attachment C, Tables 1 through 3. [Violation Risk Factor: High] [Time Horizon: Long Term Planning] | HIGH | Retired | 2017-04-01 | 2020-06-30 | TO, DP
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R5. | Each Distribution Provider or Transmission Owner that must arm its load to trip on underfrequency in order to meet its requirements as specified and by doing so exceeds the tolerances and/or deviates from the number of stages and frequency set points of the UFLS program as specified in the tables contained in Requirement R4 above, as applicable depending on its total peak net Load shall: [Violation Risk Factor: High] [Time Horizon: Long Term Planning] | HIGH | Retired | 2017-04-01 | 2020-06-30 | TO, DP
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R5.1. | Inform its Planning Coordinator of the need to exceed the stated tolerances or the number of stages as shown in UFLS Attachment C, Table 1 if applicable and | HIGH | Retired | 2017-04-01 | 2020-06-30 | TO, DP
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R5.2. | Provide its Planning Coordinator with a technical study that demonstrates that the Distribution Providers or Transmission Owners specific deviations from the requirements of UFLS Attachment C, Table 1 will not have a significant adverse impact on the bulk power system. | HIGH | Retired | 2017-04-01 | 2020-06-30 | TO, DP
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R5.3. | Inform its Planning Coordinator of the need to exceed the stated tolerances of UFLS Attachment C, Table 2 or Table 3, and in the case of Attachment C, Table 2 only, the need to deviate from providing two stages of UFLS, if applicable, and | HIGH | Retired | 2017-04-01 | 2020-06-30 | TO, DP
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R5.4. | Provide its Planning Coordinator with an analysis demonstrating that no alternative load shedding solution is available that would allow the Distribution Provider or Transmission Owner to comply with UFLS Attachment C Table 2 or Attachment C Table 3. | HIGH | Retired | 2017-04-01 | 2020-06-30 | TO, DP
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R6. | Each Distribution Provider and Transmission Owner in the Québec Interconnection portion of NPCC shall implement an automatic UFLS program for its Facilities based on the frequency thresholds, slopes, total nominal operating time and amounts specified in Attachment C, Table 4 or shall collectively implement by mutual agreement with one or more Distribution Providers and Transmission Owners within the same island, identified in Requirement R1, an aggregated automatic UFLS program that sheds Load based on the frequency thresholds, slopes, total nominal operating time and amounts specified in Attachment C, Table 4. [Violation Risk Factor: High] [Time Horizon: Long Term Planning] | HIGH | Retired | 2017-04-01 | 2020-06-30 | TO, DP
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R7. | Each Distribution Provider and Transmission Owner shall set each underfrequency relay that is part of its region’s UFLS program with the following minimum time delay: | HIGH | Retired | 2017-04-01 | 2020-06-30 | TO, DP
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R7.1. | Eastern Interconnection – 100 ms | HIGH | Retired | 2017-04-01 | 2020-06-30 | TO, DP
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R7.2. | Québec Interconnection – 200 ms [Violation Risk Factor: High] [Time Horizon: Long Term Planning] | HIGH | Retired | 2017-04-01 | 2020-06-30 | TO, DP
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R8. | Each Planning Coordinator shall develop and review once per calendar year settings for inhibit thresholds (such as but not limited to voltage, current and time) to be utilized within its region's UFLS program. [Violation Risk Factor: Medium] [Time Horizon: Long Term Planning] | MEDIUM | Retired | 2017-04-01 | 2020-06-30 | PC
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R9. | Each Planning Coordinator shall provide each Transmission Owner and Distribution Provider within its Planning Coordinator area the applicable inhibit thresholds within 30 days of the initial determination of those inhibit thresholds and within 30 days of any changes to those thresholds. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Retired | 2017-04-01 | 2020-06-30 | PC
PRC-006-NPCC-2 | Automatic Underfrequency Load Shedding | R1. | Each Planning Coordinator in the Eastern Interconnection portion of NPCC shall design an UFLS program, pertaining to islands wholly within the NPCC Region, having performance characteristics that prevents the frequency from remaining below 59.5 Hz for more than 30 seconds in accordance with Figure 1 [Violation Risk Factor: High] [Time Horizon: Long Term Planning | HIGH | Effective | 2020-07-01 |  | PC
PRC-006-NPCC-2 | Automatic Underfrequency Load Shedding | R10. | Each Generator Owner shall set each generator underfrequency trip relay, if so equipped, on or below the appropriate generator underfrequency trip protection setting threshold curve in Figure 2, except as otherwise exempted in Requirements R13 and R16. [Violation Risk Factor: High] [Time Horizon: Long Term Planning] | HIGH | Effective | 2020-07-01 |  | GO
PRC-006-NPCC-2 | Automatic Underfrequency Load Shedding | R11. | Each Generator Owner shall transmit the generator underfrequency trip setting and time delay within 45 calendar days of the Planning Coordinator’s request. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Effective | 2020-07-01 |  | GO
PRC-006-NPCC-2 | Automatic Underfrequency Load Shedding | R12. | Each Generator Owner with a new generating unit, or an existing generator increasing its net capability by greater than 10% shall: [Violation Risk Factor: Medium] [Time Horizon: Long Term Planning] | MEDIUM | Effective | 2020-07-01 |  | GO
PRC-006-NPCC-2 | Automatic Underfrequency Load Shedding | R12.1. | Design measures to prevent the generating unit from tripping directly or indirectly for underfrequency conditions above the appropriate generator tripping threshold curve in Figure 2. | MEDIUM | Effective | 2020-07-01 |  | GO
PRC-006-NPCC-2 | Automatic Underfrequency Load Shedding | R12.2. | Design auxiliary system(s) or devices used for the control and protection of auxiliary system(s), necessary for the generating unit operation such that they will not trip the generating unit during underfrequency conditions above the appropriate generator underfrequency trip protection setting threshold curve in Figure 2. | MEDIUM | Effective | 2020-07-01 |  | GO
PRC-006-NPCC-2 | Automatic Underfrequency Load Shedding | R13. | For existing non-nuclear units in service prior to July 1, 2015, that have underfrequency protections set to trip above the appropriate curve in Figure 2: [Violation Risk Factor: High] [Time Horizon: Long Term Planning] | HIGH | Effective | 2020-07-01 |  | GO
PRC-006-NPCC-2 | Automatic Underfrequency Load Shedding | R13.1. | Each Generator Owner shall set the underfrequency protection to operate at the lowest frequency allowed by the plant design and licensing limitations | HIGH | Effective | 2020-07-01 |  | GO
PRC-006-NPCC-2 | Automatic Underfrequency Load Shedding | R13.2. | Each Generator Owner shall transmit the existing underfrequency settings and any changes to the underfrequency settings along with the technical basis for the settings to the Planning Coordinator | HIGH | Effective | 2020-07-01 |  | GO
PRC-006-NPCC-2 | Automatic Underfrequency Load Shedding | R13.3. | Each Planning Coordinator in Ontario, Québec and the Maritime Provinces shall arrange for compensatory load shedding, in accordance with Attachment A and as provided by a Distribution Provider or Transmission Owner, that is adequate to compensate for the loss of generator(s) due to early tripping that is within the UFLS island identified by the Planning Coordinator in Requirement R2 | HIGH | Effective | 2020-07-01 |  | TO, PC, DP, GO
PRC-006-NPCC-2 | Automatic Underfrequency Load Shedding | R13.4. | Each Generator Owner in the ISO-NE Planning Coordinator area and in NYISO Planning Coordinator area shall arrange for compensatory load shedding, in accordance with Attachment B and as provided by a Distribution Provider or Transmission Owner, that is adequate to compensate for the loss of generator(s) due to early tripping that is within the UFLS island identified by the Planning Coordinator in Requirement R2. | HIGH | Effective | 2020-07-01 |  | TO, PC, DP, GO
PRC-006-NPCC-2 | Automatic Underfrequency Load Shedding | R14. | Each Planning Coordinator in Ontario, Quebec and the Maritime provinces shall apply the criteria described in Attachment A to determine the compensatory load shedding that is required in Requirement R13.3 for generating units in its respective NPCC area. [Violation Risk Factor: High] [Time Horizon: Long Term Planning] | HIGH | Effective | 2020-07-01 |  | PC
PRC-006-NPCC-2 | Automatic Underfrequency Load Shedding | R15. | Each Generator Owner, Distribution Provider or Transmission Owner within the ISONE Planning Coordinator area and in NYISO Planning Coordinator Area shall apply the criteria described in Attachment B to determine the compensatory load shedding that is required in Requirement R13.4 for generating units in its respective NPCC area. [Violation Risk Factor: High] [Time Horizon: Long Term Planning] | HIGH | Effective | 2020-07-01
PRC-006-NPCC-2 | Automatic Underfrequency Load Shedding | R16. | Each Generator Owner of existing nuclear generating plants with units that have underfrequency relay threshold settings above the Eastern Interconnection generator tripping curve in Figure 2 based on their licensing design shall: [Violation Risk Factor: High] [Time Horizon: Long Term Planning] | HIGH | Effective | 2020-07-01 |  | GO
PRC-006-NPCC-2 | Automatic Underfrequency Load Shedding | R16.1. | Set the underfrequency protection to operate at a frequency setting that is as low as possible in accordance with the plant design and licensing limitations but not greater than 57.8 Hz. | HIGH | Effective | 2020-07-01 |  | GO
PRC-006-NPCC-2 | Automatic Underfrequency Load Shedding | R16.2. | Set the frequency trip setting upper tolerance to no greater than + 0.1 Hz. | HIGH | Effective | 2020-07-01 |  | GO
PRC-006-NPCC-2 | Automatic Underfrequency Load Shedding | R16.3. | Transmit the initial frequency trip setting and any changes to the setting and the technical basis for the settings to the Planning Coordinator. | HIGH | Effective | 2020-07-01 |  | GO
PRC-006-NPCC-2 | Automatic Underfrequency Load Shedding | R2. | Each Planning Coordinator shall provide UFLS island boundaries, as identified per the NERC continent-wide PRC-006 Standard on UFLS, to Distribution Providers, Generator Owners, and Transmission Owners within 30 calendar days of receipt of a request. [Violation Risk Factor: Lower] [Time Horizon: Long Term Planning] | Lower | Effective | 2020-07-01 |  | DP, TO, GO, PC
PRC-006-NPCC-2 | Automatic Underfrequency Load Shedding | R3. | Each Distribution Provider and Transmission Owner in the Eastern Interconnection portion of NPCC shall implement an automatic UFLS program, reflecting normal operating conditions, excluding outages. The automatic UFLS program shall be implemented on an island basis for each identified island per the NERC continent-wide PRC-006 Standard on UFLS as follows: [Violation Risk Factor: High] [Time Horizon: Long Term Planning]  The UFLS program shall be implemented by each Distribution Provider and Transmission Owner according to the frequency thresholds, nominal operating times, and load shedding amounts specified in Attachment C, Tables 1-3; or  The UFLS program shall be implemented collectively by multiple Distribution Providers or Transmission Owners, as long as they reside in the same UFLS island identified by the Planning Coordinator per Requirement R2. These multiple Distribution Providers or Transmission Owners, via mutual agreement, shall act as a single entity to provide an aggregated automatic UFLS program that sheds their coincident peak aggregated net Load according to the frequency thresholds, total nominal operating time, and load shedding amounts specified in Attachment C, Tables 1-3. | HIGH | Effective | 2021-07-01 |  | PC, TO, DP
PRC-006-NPCC-2 | Automatic Underfrequency Load Shedding | R4. | Each Distribution Provider or Transmission Owner in the Eastern Interconnection portion of NPCC that does not meet the UFLS program parameters specified in Attachment C, Table 1-3, and each Distribution Provider or Transmission Owner in the Quebec Interconnection that does not meet the UFLS program parameters specified by its Planning Coordinator shall: [Violation Risk Factor: High] [Time Horizon: Long Term Planning]  Within 30 calendar days of determining that it does not meet the specified parameters, notify its Planning Coordinator that it does not meet the UFLS program parameters; and  Within the following 180 calendar days from notification of the Planning Coordinator, (1) develop a Corrective Action Plan and a schedule for implementation that is mutually agreed upon with its Planning Coordinator or (2) provide its Planning Coordinator with a technical study that demonstrates that the deviations from the program parameters will not result in failure of UFLS performance criteria being met for any island. The technical study must be acceptable to the Planning Coordinator prior to implementing deviations from program parameters and shall demonstrate coordination with UFLS programs of all entities residing within the same island(s) identified by the Planning Coordinator in Requirement R2. The technical study shall also demonstrate coordination with other UFLS programs of adjoining Planning Coordinators, or (3) provide its Planning Coordinator with an analysis demonstrating that no alternative load shedding solution is available that would allow the Distribution Provider or Transmission Owner to comply with UFLS Attachment C Table 2 or Attachment C Table 3. | HIGH | Effective | 2020-07-01 |  | PC, TO, DP
PRC-006-NPCC-2 | Automatic Underfrequency Load Shedding | R5. | Each Planning Coordinator shall develop and review settings for inhibit thresholds at least once per five calendar years (such as, but not limited to, voltage, current and time) to be utilized within its region’s UFLS program. [Violation Risk Factor: Medium] [Time Horizon: Long Term Planning] | MEDIUM | Effective | 2020-07-01 |  | PC
PRC-006-NPCC-2 | Automatic Underfrequency Load Shedding | R6. | Each Planning Coordinator shall provide each Transmission Owner and Distribution Provider within its Planning Coordinator area the applicable inhibit thresholds within 30 calendar days of any changes. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Effective | 2020-07-01 |  | DP, TO, PC
PRC-006-NPCC-2 | Automatic Underfrequency Load Shedding | R7. | Each Distribution Provider and Transmission Owner that receives a notification pursuant to Requirement R6 shall develop and submit an implementation plan with respect to inhibit thresholds for approval by the Planning Coordinator within 90 calendar days of the request from the Planning Coordinator. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Effective | 2020-07-01 |  | PC, TO, DP
PRC-006-NPCC-2 | Automatic Underfrequency Load Shedding | R8. | Each Distribution Provider and Transmission Owner shall implement the inhibit thresholds provided by the Planning Coordinator in accordance with Requirement R6 and based on the Planning Coordinator approved implementation plan in accordance with R7. [Violation Risk Factor: High] [Time Horizon: Operation Planning] | HIGH | Effective | 2020-07-01 |  | PC, DP
PRC-006-NPCC-2 | Automatic Underfrequency Load Shedding | R9. | Each Transmission Owner and Distribution Provider shall annually provide documentation, with no more than 15 calendar months between updates, to its Planning Coordinator of the actual net Load that would have been shed by the UFLS relays at each UFLS stage. The actual net Load shall be coincident with the entity’s integrated hourly peak net Load during the previous year, as determined by measuring or calculating Load through the switches that would disconnect load if triggered by the UFLS relays. If measured data is unavailable then calculated data may be used. [Violation Risk Factor: Lower] [Time Horizon: Long Term Planning] | LOWER | Effective | 2020-07-01 |  | TO, PC, DP
PRC-008-0 | Implementation and Documentation of Underfrequency Load Shedding Equipment Maintenance Program | R1. | The Transmission Owner and Distribution Provider with a UFLS program (as required by its Regional Reliability Organization) shall have a UFLS equipment maintenance and testing program in place. This UFLS equipment maintenance and testing program shall include UFLS equipment identification, the schedule for UFLS equipment testing, and the schedule for UFLS equipment maintenance. | MEDIUM | Effective | 2005-02-08 | 2027-03-31 | TO, DP
PRC-008-0 | Implementation and Documentation of Underfrequency Load Shedding Equipment Maintenance Program | R2. | The Transmission Owner and Distribution Provider with a UFLS program (as required by its Regional Reliability Organization) shall implement its UFLS equipment maintenance and testing program and shall provide UFLS maintenance and testing program results to its Regional Reliability Organization and NERC on request (within 30 calendar days). | MEDIUM | Effective | 2005-02-08 | 2027-03-31 | TO, DP
PRC-010-0 | Technical Assessment of the Design and Effectiveness of Undervoltage Load Shedding Program | R1. | The Load-Serving Entity, Transmission Owner, Transmission Operator, and Distribution Provider that owns or operates a UVLS program shall periodically (at least every five years or as required by changes in system conditions) conduct and document an assessment of the effectiveness of the UVLS program. This assessment shall be conducted with the associated Transmission Planner(s) and Planning Authority(ies). | MEDIUM | Retired | 2005-02-08 | 2017-03-31 | TOP, TO, DP
PRC-010-0 | Technical Assessment of the Design and Effectiveness of Undervoltage Load Shedding Program | R1.1. | This assessment shall include, but is not limited to: | MEDIUM | Retired | 2005-02-08 | 2017-03-31 | TOP, TO, DP
PRC-010-0 | Technical Assessment of the Design and Effectiveness of Undervoltage Load Shedding Program | R1.1.1. | Coordination of the UVLS programs with other protection and control systems in the Region and with other Regional Reliability Organizations, as appropriate. | MEDIUM | Retired | 2005-02-08 | 2017-03-31 | TOP, TO, DP
PRC-010-0 | Technical Assessment of the Design and Effectiveness of Undervoltage Load Shedding Program | R1.1.2. | Simulations that demonstrate that the UVLS programs performance is consistent with Reliability Standards TPL-001-0, TPL-002-0, TPL-003-0 and TPL-004-0. | MEDIUM | Retired | 2005-02-08 | 2017-03-31 | TOP, TO, DP
PRC-010-0 | Technical Assessment of the Design and Effectiveness of Undervoltage Load Shedding Program | R1.1.3. | A review of the voltage set points and timing. | MEDIUM | Retired | 2005-02-08 | 2017-03-31 | TOP, TO, DP
PRC-010-1 | Undervoltage Load Shedding | R1. | Each Planning Coordinator or Transmission Planner that is developing a UVLS Program shall evaluate its effectiveness and subsequently provide the UVLS Program’s specifications and implementation schedule to the UVLS entities responsible for implementing the UVLS Program. The evaluation shall include, but is not limited to, studies and analyses that show: [Violation Risk Factor: High] [Time Horizon: Long‐term Planning] | HIGH | Retired | 2017-04-01 | 2017-04-01 | TP, PC
PRC-010-1 | Undervoltage Load Shedding | R1.1. | The implementation of the UVLS Program resolves the identified undervoltage issues that led to its development and design. | HIGH | Retired | 2017-04-01 | 2017-04-01 | TP, PC
PRC-010-1 | Undervoltage Load Shedding | R1.2. | The UVLS Program is integrated through coordination with generator voltage ride‐through capabilities and other protection and control systems, including, but not limited to, transmission line protection, autoreclosing, Remedial Action Schemes, and other undervoltage‐based load shedding programs. | HIGH | Retired | 2017-04-01 | 2017-04-01 | TP, PC
PRC-010-1 | Undervoltage Load Shedding | R2. | Each UVLS entity shall adhere to the UVLS Program specifications and implementation schedule determined by its Planning Coordinator or Transmission Planner associated with UVLS Program development per Requirement R1 or with any Corrective Action Plans per Requirement R5. [Violation Risk Factor: High] [Time Horizon: Long‐term Planning] | HIGH | Retired | 2017-04-01 | 2017-04-01 | TO, DP
PRC-010-1 | Undervoltage Load Shedding | R3. | Each Planning Coordinator or Transmission Planner shall perform a comprehensive assessment to evaluate the effectiveness of each of its UVLS Programs at least once every 60 calendar months. Each assessment shall include, but is not limited to, studies and analyses that evaluate whether: [Violation Risk Factor: Medium] [Time Horizon: Long‐term Planning] | MEDIUM | Retired | 2017-04-01 | 2017-04-01 | TP, PC
PRC-010-1 | Undervoltage Load Shedding | R3.1. | The UVLS Program resolves the identified undervoltage issues for which the UVLS Program is designed. | MEDIUM | Retired | 2017-04-01 | 2017-04-01 | TP, PC
PRC-010-1 | Undervoltage Load Shedding | R3.2. | The UVLS Program is integrated through coordination with generator voltage ride‐through capabilities and other protection and control systems, including, but not limited to, transmission line protection, autoreclosing, Remedial Action Schemes, and other undervoltage‐based load shedding programs. | MEDIUM | Retired | 2017-04-01 | 2017-04-01 | TP, PC
PRC-010-1 | Undervoltage Load Shedding | R4. | Each Planning Coordinator or Transmission Planner shall, within 12 calendar months of an event that resulted in a voltage excursion for which its UVLS Program was designed to operate, perform an assessment to evaluate whether its UVLS Program resolved the undervoltage issues associated with the event. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Retired | 2017-04-01 | 2017-04-01 | TP, PC
PRC-010-1 | Undervoltage Load Shedding | R5. | Each Planning Coordinator or Transmission Planner that identifies deficiencies in its UVLS Program during an assessment performed in either Requirement R3 or R4 shall develop a Corrective Action Plan to address the deficiencies and subsequently provide the Corrective Action Plan, including an implementation schedule, to UVLS entities within three calendar months of completing the assessment. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Retired | 2017-04-01 | 2017-04-01 | TP, PC
PRC-010-1 | Undervoltage Load Shedding | R6. | Each Planning Coordinator that has a UVLS Program in its area shall update a database containing data necessary to model the UVLS Program(s) in its area for use in event analyses and assessments of the UVLS Program at least once each calendar year. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Retired | 2017-04-01 | 2017-04-01 | PC
PRC-010-1 | Undervoltage Load Shedding | R7. | Each UVLS entity shall provide data to its Planning Coordinator according to the format and schedule specified by the Planning Coordinator to support maintenance of a UVLS Program database. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Retired | 2017-04-01 | 2017-04-01 | TO, DP
PRC-010-1 | Undervoltage Load Shedding | R8. | Each Planning Coordinator that has a UVLS Program in its area shall provide its UVLS Program database to other Planning Coordinators and Transmission Planners within its Interconnection, and other functional entities with a reliability need, within 30 calendar days of a written request. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Retired | 2017-04-01 | 2017-04-01 | PC
PRC-010-2 | Undervoltage Load Shedding | R1. | Each Planning Coordinator or Transmission Planner that is developing a UVLS Program shall evaluate its effectiveness and subsequently provide the UVLS Program’s specifications and implementation schedule to the UVLS entities responsible for implementing the UVLS Program. The evaluation shall include, but is not limited to, studies and analyses that show: [Violation Risk Factor: High] [Time Horizon: Long‐term Planning] | HIGH | Effective | 2017-04-02 |  | TP, PC
PRC-010-2 | Undervoltage Load Shedding | R1.1. | The implementation of the UVLS Program resolves the identified undervoltage issues that led to its development and design. | HIGH | Effective | 2017-04-02 |  | TP, PC
PRC-010-2 | Undervoltage Load Shedding | R1.2. | The UVLS Program is integrated through coordination with generator voltage ride‐through capabilities and other protection and control systems, including, but not limited to, transmission line protection, autoreclosing, Remedial Action Schemes, and other undervoltage‐based load shedding programs. | HIGH | Effective | 2017-04-02 |  | TP, PC
PRC-010-2 | Undervoltage Load Shedding | R2. | Each UVLS entity shall adhere to the UVLS Program specifications and implementation schedule determined by its Planning Coordinator or Transmission Planner associated with UVLS Program development per Requirement R1 or with any Corrective Action Plans per Requirement R5. [Violation Risk Factor: High] [Time Horizon: Long‐term Planning] | HIGH | Effective | 2017-04-02 |  | TO, DP
PRC-010-2 | Undervoltage Load Shedding | R3. | Each Planning Coordinator or Transmission Planner shall perform a comprehensive assessment to evaluate the effectiveness of each of its UVLS Programs at least once every 60 calendar months. Each assessment shall include, but is not limited to, studies and analyses that evaluate whether: [Violation Risk Factor: Medium] [Time Horizon: Long‐term Planning] | MEDIUM | Effective | 2017-04-02 |  | TP, PC
PRC-010-2 | Undervoltage Load Shedding | R3.1. | The UVLS Program resolves the identified undervoltage issues for which the UVLS Program is designed. | MEDIUM | Effective | 2017-04-02 |  | TP, PC
PRC-010-2 | Undervoltage Load Shedding | R3.2. | The UVLS Program is integrated through coordination with generator voltage ride‐through capabilities and other protection and control systems, including, but not limited to, transmission line protection, autoreclosing, Remedial Action Schemes, and other undervoltage‐based load shedding programs. | MEDIUM | Effective | 2017-04-02 |  | TP, PC
PRC-010-2 | Undervoltage Load Shedding | R4. | Each Planning Coordinator or Transmission Planner shall, within 12 calendar months of an event that resulted in a voltage excursion for which its UVLS Program was designed to operate, perform an assessment to evaluate: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Effective | 2017-04-02 |  | TP, PC
PRC-010-2 | Undervoltage Load Shedding | R4.1. | Whether its UVLS Program resolved the undervoltage issues associated with the event, and | MEDIUM | Effective | 2017-04-02 |  | TP, PC
PRC-010-2 | Undervoltage Load Shedding | R4.2. | The performance (i.e., operation and non‐operation) of the UVLS Program equipment. | MEDIUM | Effective | 2017-04-02 |  | TP, PC
PRC-010-2 | Undervoltage Load Shedding | R5. | Each Planning Coordinator or Transmission Planner that identifies deficiencies during an assessment performed in either Requirement R3 or R4 shall develop a Corrective Action Plan to address the deficiencies and subsequently provide the Corrective Action Plan, including an implementation schedule, to UVLS entities within three calendar months of completing the assessment. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Effective | 2017-04-02 |  | TP, PC
PRC-010-2 | Undervoltage Load Shedding | R6. | Each Planning Coordinator that has a UVLS Program in its area shall update a database containing data necessary to model the UVLS Program(s) in its area for use in event analyses and assessments of the UVLS Program at least once each calendar year. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Effective | 2017-04-02 |  | PC
PRC-010-2 | Undervoltage Load Shedding | R7. | Each UVLS entity shall provide data to its Planning Coordinator according to the format and schedule specified by the Planning Coordinator to support maintenance of a UVLS Program database. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Effective | 2017-04-02 |  | TO, DP
PRC-010-2 | Undervoltage Load Shedding | R8. | Each Planning Coordinator that has a UVLS Program in its area shall provide its UVLS Program database to other Planning Coordinators and Transmission Planners within its Interconnection, and other functional entities with a reliability need, within 30 calendar days of a written request. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Effective | 2017-04-02 |  | PC
PRC-011-0 | Undervoltage Load Shedding System Maintenance and Testing | R1. | The Transmission Owner and Distribution Provider that owns a UVLS system shall have a UVLS equipment maintenance and testing program in place. This program shall include: | MEDIUM | Effective | 2005-02-08 | 2027-03-31 | TO, DP
PRC-011-0 | Undervoltage Load Shedding System Maintenance and Testing | R1.1. | The UVLS system identification which shall include but is not limited to: | MEDIUM | Effective | 2005-02-08 | 2027-03-31 | TO, DP
PRC-011-0 | Undervoltage Load Shedding System Maintenance and Testing | R1.1.1. | Relays. | MEDIUM | Effective | 2005-02-08 | 2027-03-31 | TO, DP
PRC-011-0 | Undervoltage Load Shedding System Maintenance and Testing | R1.1.2. | Instrument transformers. | MEDIUM | Effective | 2005-02-08 | 2027-03-31 | TO, DP
PRC-011-0 | Undervoltage Load Shedding System Maintenance and Testing | R1.1.3. | Communications systems, where appropriate. | MEDIUM | Effective | 2005-02-08 | 2027-03-31 | TO, DP
PRC-011-0 | Undervoltage Load Shedding System Maintenance and Testing | R1.1.4. | Batteries. | MEDIUM | Effective | 2005-02-08 | 2027-03-31 | TO, DP
PRC-011-0 | Undervoltage Load Shedding System Maintenance and Testing | R1.2. | Documentation of maintenance and testing intervals and their basis. | MEDIUM | Effective | 2005-02-08 | 2027-03-31 | TO, DP
PRC-011-0 | Undervoltage Load Shedding System Maintenance and Testing | R1.3. | Summary of testing procedure. | MEDIUM | Effective | 2005-02-08 | 2027-03-31 | TO, DP
PRC-011-0 | Undervoltage Load Shedding System Maintenance and Testing | R1.4. | Schedule for system testing. | MEDIUM | Effective | 2005-02-08 | 2027-03-31 | TO, DP
PRC-011-0 | Undervoltage Load Shedding System Maintenance and Testing | R1.5. | Schedule for system maintenance. | MEDIUM | Effective | 2005-02-08 | 2027-03-31 | TO, DP
PRC-011-0 | Undervoltage Load Shedding System Maintenance and Testing | R1.6. | Date last tested/maintained. | MEDIUM | Effective | 2005-02-08 | 2027-03-31 | TO, DP
PRC-011-0 | Undervoltage Load Shedding System Maintenance and Testing | R2. | The Transmission Owner and Distribution Provider that owns a UVLS system shall provide documentation of its UVLS equipment maintenance and testing program and the implementation of that UVLS equipment maintenance and testing program to its Regional Reliability Organization and NERC on request (within 30 calendar days). | LOWER | Effective | 2005-02-08 | 2027-03-31 | TO, DP
PRC-012-0 | Special Protection System Review Procedure | R1. | Each Regional Reliability Organization with a Transmission Owner, Generator Owner, or Distribution Providers that uses or is planning to use an SPS shall have a documented Regional Reliability Organization SPS review procedure to ensure that SPSs comply with Regional criteria and NERC Reliability Standards. The Regional SPS review procedure shall include: | MEDIUM | Never Came Into Effect in Ontario
PRC-012-0 | Special Protection System Review Procedure | R1.1. | Description of the process for submitting a proposed SPS for Regional Reliability Organization review. | MEDIUM | Never Came Into Effect in Ontario
PRC-012-0 | Special Protection System Review Procedure | R1.2. | Requirements to provide data that describes design, operation, and modeling of an SPS. | MEDIUM | Never Came Into Effect in Ontario
PRC-012-0 | Special Protection System Review Procedure | R1.3. | Requirements to demonstrate that the SPS shall be designed so that a single SPS component failure, when the SPS was intended to operate, does not prevent the interconnected transmission system from meeting the performance requirements defined in Reliability Standards TPL-001-0, TPL-002-0, and TPL-003-0. | MEDIUM | Never Came Into Effect in Ontario
PRC-012-0 | Special Protection System Review Procedure | R1.4. | Requirements to demonstrate that the inadvertent operation of an SPS shall meet the same performance requirement (TPL-001-0, TPL-002-0, and TPL-003-0) as that required of the contingency for which it was designed, and not exceed TPL-003-0. | MEDIUM | Never Came Into Effect in Ontario
PRC-012-0 | Special Protection System Review Procedure | R1.5. | Requirements to demonstrate the proposed SPS will coordinate with other protection and control systems and applicable Regional Reliability Organization Emergency procedures. | MEDIUM | Never Came Into Effect in Ontario
PRC-012-0 | Special Protection System Review Procedure | R1.6. | Regional Reliability Organization definition of misoperation. | MEDIUM | Never Came Into Effect in Ontario
PRC-012-0 | Special Protection System Review Procedure | R1.7. | Requirements for analysis and documentation of corrective action plans for all SPS misoperations. | MEDIUM | Never Came Into Effect in Ontario
PRC-012-0 | Special Protection System Review Procedure | R1.8. | Identification of the Regional Reliability Organization group responsible for the Regional Reliability Organization’s review procedure and the process for Regional Reliability Organization approval of the procedure. | MEDIUM | Never Came Into Effect in Ontario
PRC-012-0 | Special Protection System Review Procedure | R1.9. | Determination, as appropriate, of maintenance and testing requirements. | MEDIUM | Never Came Into Effect in Ontario
PRC-012-0 | Special Protection System Review Procedure | R2. | The Regional Reliability Organization shall provide affected Regional Reliability Organizations and NERC with documentation of its SPS review procedure on request (within 30 calendar days). | LOWER | Never Came Into Effect in Ontario
PRC-012-1 | Remedial Action Scheme Review Procedure | R1. | Each Regional Reliability Organization with a Transmission Owner, Generator Owner, or Distribution Providers that uses or is planning to use a RAS shall have a documented Regional Reliability Organization RAS review procedure to ensure that RAS comply with Regional criteria and NERC Reliability Standards. The Regional RAS review procedure shall include: | MEDIUM | Never Came Into Effect in Ontario
PRC-012-1 | Remedial Action Scheme Review Procedure | R1.1. | Description of the process for submitting a proposed RAS for Regional Reliability Organization review. | MEDIUM | Never Came Into Effect in Ontario
PRC-012-1 | Remedial Action Scheme Review Procedure | R1.2. | Requirements to provide data that describes design, operation, and modeling of a RAS. | MEDIUM | Never Came Into Effect in Ontario
PRC-012-1 | Remedial Action Scheme Review Procedure | R1.3. | Requirements to demonstrate that the RAS shall be designed so that a single RAS component failure, when the RAS was intended to operate, does not prevent the interconnected transmission system from meeting the performance requirements defined in Reliability Standards TPL-001-0, TPL-002-0, and TPL-003-0. | MEDIUM | Never Came Into Effect in Ontario
PRC-012-1 | Remedial Action Scheme Review Procedure | R1.4. | Requirements to demonstrate that the inadvertent operation of a RAS shall meet the same performance requirement (TPL-001-0, TPL-002-0, and TPL-003-0) as that required of the contingency for which it was designed, and not exceed TPL-003-0. | MEDIUM | Never Came Into Effect in Ontario
PRC-012-1 | Remedial Action Scheme Review Procedure | R1.5. | Requirements to demonstrate the proposed RAS will coordinate with other protection and control systems and applicable Regional Reliability Organization Emergency procedures. | MEDIUM | Never Came Into Effect in Ontario
PRC-012-1 | Remedial Action Scheme Review Procedure | R1.6. | Regional Reliability Organization definition of misoperation. | MEDIUM | Never Came Into Effect in Ontario
PRC-012-1 | Remedial Action Scheme Review Procedure | R1.7. | Requirements for analysis and documentation of corrective action plans for all RAS misoperations | MEDIUM | Never Came Into Effect in Ontario
PRC-012-1 | Remedial Action Scheme Review Procedure | R1.8. | Identification of the Regional Reliability Organization group responsible for the Regional Reliability Organization’s review procedure and the process for Regional Reliability Organization approval of the procedure. | MEDIUM | Never Came Into Effect in Ontario
PRC-012-1 | Remedial Action Scheme Review Procedure | R1.9. | Determination, as appropriate, of maintenance and testing requirements. | MEDIUM | Never Came Into Effect in Ontario
PRC-012-1 | Remedial Action Scheme Review Procedure | R2. | The Regional Reliability Organization shall provide affected Regional Reliability Organizations and NERC with documentation of its RAS review procedure on request (within 30 calendar days). | LOWER | Never Came Into Effect in Ontario
PRC-012-2 | Remedial Action Schemes | R1. | Prior to placing a new or functionally modified RAS in service or retiring an existing RAS, each RAS-entity shall provide the information identified in Attachment 1 for review to the Reliability Coordinator(s) where the RAS is located. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Effective | 2021-01-01 |  | PC, RC, TO, GO, DP
PRC-012-2 | Remedial Action Schemes | R2. | Each Reliability Coordinator that receives Attachment 1 information pursuant to Requirement R1 shall, within four full calendar months of receipt or on a mutually agreed upon schedule, perform a review of the RAS in accordance with Attachment 2, and provide written feedback to each RAS-entity. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Effective | 2021-01-01 |  | GO, TO, DP, PC, RC
PRC-012-2 | Remedial Action Schemes | R3. | Prior to placing a new or functionally modified RAS in service or retiring an existing RAS, each RAS‐entity that receives feedback from the reviewing Reliability Coordinator(s) identifying reliability issue(s) shall resolve each issue to obtain approval of the RAS from each reviewing Reliability Coordinator. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Effective | 2021-01-01 |  | PC, RC, TO, GO, DP
PRC-012-2 | Remedial Action Schemes | R4. | Each Planning Coordinator, at least once every five full calendar years, shall: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2021-01-01 |  | GO, TO, DP, PC, RC
PRC-012-2 | Remedial Action Schemes | R4.1. | Perform an evaluation of each RAS within its planning area to determine whether: | MEDIUM | Effective | 2021-01-01 |  | GO, TO, DP, PC, RC
PRC-012-2 | Remedial Action Schemes | R4.1.1. | The RAS mitigates the System condition(s) or Contingency(ies) for which it was designed. | MEDIUM | Effective | 2021-01-01 |  | GO, TO, DP, PC, RC
PRC-012-2 | Remedial Action Schemes | R4.1.2. | The RAS avoids adverse interactions with other RAS, and protection and control systems. | MEDIUM | Effective | 2021-01-01 |  | GO, TO, DP, PC, RC
PRC-012-2 | Remedial Action Schemes | R4.1.3. | For limited impact1 RAS, the inadvertent operation of the RAS or the failure of the RAS to operate does not cause or contribute to BES Cascading, uncontrolled separation, angular instability, voltage instability, voltage collapse, or unacceptably damped oscillations. | MEDIUM | Effective | 2021-01-01 |  | GO, TO, DP, PC, RC
PRC-012-2 | Remedial Action Schemes | R4.1.4. | Except for limited impact RAS, the possible inadvertent operation of the RAS, resulting from any single RAS component malfunction satisfies all of the following: | MEDIUM | Effective | 2021-01-01 |  | GO, TO, DP, PC, RC
PRC-012-2 | Remedial Action Schemes | R4.1.4.1. | The BES shall remain stable. | MEDIUM | Effective | 2021-01-01 |  | GO, TO, DP, PC, RC
PRC-012-2 | Remedial Action Schemes | R4.1.4.2. | Cascading shall not occur. | MEDIUM | Effective | 2021-01-01 |  | GO, TO, DP, PC, RC
PRC-012-2 | Remedial Action Schemes | R4.1.4.3. | Applicable Facility Ratings shall not be exceeded. | MEDIUM | Effective | 2021-01-01 |  | GO, TO, DP, PC, RC
PRC-012-2 | Remedial Action Schemes | R4.1.4.4. | BES voltages shall be within post-Contingency voltage limits and post-Contingency voltage deviation limits as established | MEDIUM | Effective | 2021-01-01 |  | GO, TO, DP, PC, RC
PRC-012-2 | Remedial Action Schemes | R4.1.4.5. | Transient voltage responses shall be within acceptable limits as established by the Transmission Planner and the Planning Coordinator. | MEDIUM | Effective | 2021-01-01 |  | GO, TO, DP, PC, RC
PRC-012-2 | Remedial Action Schemes | R4.1.5. | Except for limited impact RAS, a single component failure in the RAS, when the RAS is intended to operate does not prevent the BES from meeting the same performance requirements (defined in Reliability Standard TPL-001-4 or its successor) as those required for the events and conditions for which the RAS is designed. | MEDIUM | Effective | 2021-01-01 |  | GO, TO, DP, PC, RC
PRC-012-2 | Remedial Action Schemes | R4.2. | Provide the results of the RAS evaluation including any identified deficiencies to each reviewing Reliability Coordinator and RAS-entity, and each impacted Transmission Planner and Planning Coordinator. | MEDIUM | Effective | 2021-01-01 |  | GO, TO, DP, PC, RC
PRC-012-2 | Remedial Action Schemes | R5. | Each RAS-entity, within 120 full calendar days of a RAS operation or a failure of its RAS to operate when expected, or on a mutually agreed upon schedule with its reviewing Reliability Coordinator(s), shall: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Effective | 2021-01-01 |  | PC, RC, TO, GO, DP
PRC-012-2 | Remedial Action Schemes | R5.1. | Participate in analyzing the RAS operational performance to determine whether: | MEDIUM | Effective | 2021-01-01 |  | PC, RC, TO, GO, DP
PRC-012-2 | Remedial Action Schemes | R5.1.1. | The System events and/or conditions appropriately triggered the RAS. | MEDIUM | Effective | 2021-01-01 |  | PC, RC, DP, GO, TO
PRC-012-2 | Remedial Action Schemes | R5.1.2. | The RAS responded as designed. | MEDIUM | Effective | 2021-01-01 |  | PC, RC, DP, GO, TO
PRC-012-2 | Remedial Action Schemes | R5.1.3. | The RAS was effective in mitigating BES performance issues it was designed to address. | MEDIUM | Effective | 2021-01-01 |  | PC, RC, DP, GO, TO
PRC-012-2 | Remedial Action Schemes | R5.1.4. | The RAS operation resulted in any unintended or adverse BES response. | MEDIUM | Effective | 2021-01-01 |  | PC, RC, DP, GO, TO
PRC-012-2 | Remedial Action Schemes | R5.2. | Provide the results of RAS operational performance analysis that identified any deficiencies to its reviewing Reliability Coordinator(s). | MEDIUM | Effective | 2021-01-01 |  | PC, RC, TO, GO, DP
PRC-012-2 | Remedial Action Schemes | R6. | Each RAS-entity shall participate in developing a Corrective Action Plan (CAP) and submit the CAP to its reviewing Reliability Coordinator(s) within six full calendar months of: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning, Long-term Planning] • Being notified of a deficiency in its RAS pursuant to Requirement R4, or • Notifying the Reliability Coordinator of a deficiency pursuant to Requirement R5, Part 5.2, or • Identifying a deficiency in its RAS pursuant to Requirement R8. | MEDIUM | Effective | 2021-01-01 |  | PC, RC, TO, GO, DP
PRC-012-2 | Remedial Action Schemes | R7. | Each RAS-entity shall, for each of its CAPs developed pursuant to Requirement R6: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning, Long-term Planning] | MEDIUM | Effective | 2021-01-01 |  | PC, RC, TO, GO, DP
PRC-012-2 | Remedial Action Schemes | R7.1. | Implement the CAP. | MEDIUM | Effective | 2021-01-01 |  | PC, RC, TO, GO, DP
PRC-012-2 | Remedial Action Schemes | R7.2. | Update the CAP if actions or timetables change. | MEDIUM | Effective | 2021-01-01 |  | PC, RC, TO, GO, DP
PRC-012-2 | Remedial Action Schemes | R7.3. | Notify each reviewing Reliability Coordinator if CAP actions or timetables change and when the CAP is completed. | MEDIUM | Effective | 2021-01-01 |  | PC, RC, TO, GO, DP
PRC-012-2 | Remedial Action Schemes | R8. | Each RAS-entity shall participate in performing a functional test of each of its RAS to verify the overall RAS performance and the proper operation of non-Protection System components: [Violation Risk Factor: High] [Time Horizon: Long-term Planning] • At least once every six full calendar years for all RAS not designated as limited impact, or • At least once every twelve full calendar years for all RAS designated as limited impact | HIGH | Effective | 2021-01-01 |  | PC, RC, TO, GO, DP
PRC-012-2 | Remedial Action Schemes | R9. | Each Reliability Coordinator shall update a RAS database containing, at a minimum, the information in Attachment 3 at least once every twelve full calendar months. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Effective | 2021-01-01 |  | GO, TO, DP, PC, RC
PRC-013-0 | Special Protection System Database. | R1. | The Regional Reliability Organization that has a Transmission Owner, Generator Owner, or Distribution Provider with an SPS installed shall maintain an SPS database. The database shall include the following types of information: | LOWER | Never Came Into Effect in Ontario
PRC-013-0 | Special Protection System Database. | R1.1. | Design Objectives — Contingencies and system conditions for which the SPS was designed, | LOWER | Never Came Into Effect in Ontario
PRC-013-0 | Special Protection System Database. | R1.2. | Operation — The actions taken by the SPS in response to Disturbance conditions, and | LOWER | Never Came Into Effect in Ontario
PRC-013-0 | Special Protection System Database. | R1.3. | Modeling — Information on detection logic or relay settings that control operation of the SPS. | LOWER | Never Came Into Effect in Ontario
PRC-013-0 | Special Protection System Database. | R2. | The Regional Reliability Organization shall provide to affected Regional Reliability Organization(s) and NERC documentation of its database or the information therein on request (within 30 calendar days). | LOWER | Never Came Into Effect in Ontario
PRC-013-1 | Remedial Action Scheme Database | R1. | The Regional Reliability Organization that has a Transmission Owner, Generator Owner, or Distribution Provider with a RAS installed shall maintain a RAS database. The database shall include the following types of information: | LOWER | Never Came Into Effect in Ontario
PRC-013-1 | Remedial Action Scheme Database | R1.1. | Design Objectives — Contingencies and system conditions for which the RAS was designed, | LOWER | Never Came Into Effect in Ontario
PRC-013-1 | Remedial Action Scheme Database | R1.2. | Operation —The actions taken by the RAS in response to Disturbance conditions, and | LOWER | Never Came Into Effect in Ontario
PRC-013-1 | Remedial Action Scheme Database | R1.3. | Modeling — Information on detection logic or relay settings that control operation of the RAS. | LOWER | Never Came Into Effect in Ontario
PRC-013-1 | Remedial Action Scheme Database | R2. | The Regional Reliability Organization shall provide to affected Regional Reliability Organization(s) and NERC documentation of its database or the information therein on request (within 30 calendar days). | LOWER | Never Came Into Effect in Ontario
PRC-014-0 | Special Protection System Assessment | R1. | The Regional Reliability Organization shall assess the operation, coordination, and effectiveness of all SPSs installed in its Region at least once every five years for compliance with NERC Reliability Standards and Regional criteria. | MEDIUM | Never Came Into Effect in Ontario
PRC-014-0 | Special Protection System Assessment | R2. | The Regional Reliability Organization shall provide either a summary report or a detailed report of its assessment of the operation, coordination, and effectiveness of all SPSs installed in its Region to affected Regional Reliability Organizations or NERC on request (within 30 calendar days). | LOWER | Never Came Into Effect in Ontario
PRC-014-0 | Special Protection System Assessment | R3. | The documentation of the Regional Reliability Organization’s SPS assessment shall include the following elements: | LOWER | Never Came Into Effect in Ontario
PRC-014-0 | Special Protection System Assessment | R3.1. | Identification of group conducting the assessment and the date the assessment was performed. | LOWER | Never Came Into Effect in Ontario
PRC-014-0 | Special Protection System Assessment | R3.2. | Study years, system conditions, and contingencies analyzed in the technical studies on which the assessment is based and when those technical studies were performed. | LOWER | Never Came Into Effect in Ontario
PRC-014-0 | Special Protection System Assessment | R3.3. | Identification of SPSs that were found not to comply with NERC standards and Regional Reliability Organization criteria. | LOWER | Never Came Into Effect in Ontario
PRC-014-0 | Special Protection System Assessment | R3.4. | Discussion of any coordination problems found between a SPS and other protection and control systems. | LOWER | Never Came Into Effect in Ontario
PRC-014-0 | Special Protection System Assessment | R3.5. | Provide corrective action plans for non-compliant SPSs. |  | Never Came Into Effect in Ontario
PRC-014-1 | Remedial Action Scheme Assessment | R1. | The Regional Reliability Organization shall assess the operation, coordination, and effectiveness of all RAS installed in its Region at least once every five years for compliance with NERC Reliability Standards and Regional criteria. | MEDIUM | Never Came Into Effect in Ontario
PRC-014-1 | Remedial Action Scheme Assessment | R2. | The Regional Reliability Organization shall provide either a summary report or a detailed report of its assessment of the operation, coordination, and effectiveness of all RAS installed in its Region to affected Regional Reliability Organizations or NERC on request (within 30 calendar days). | LOWER | Never Came Into Effect in Ontario
PRC-014-1 | Remedial Action Scheme Assessment | R3. | The documentation of the Regional Reliability Organization’s RAS assessment shall include the following elements: | LOWER | Never Came Into Effect in Ontario
PRC-014-1 | Remedial Action Scheme Assessment | R3.1. | Identification of group conducting the assessment and the date the assessment was performed. | LOWER | Never Came Into Effect in Ontario
PRC-014-1 | Remedial Action Scheme Assessment | R3.2. | Study years, system conditions, and contingencies analyzed in the technical studies on which the assessment is based and when those technical studies were performed. | LOWER | Never Came Into Effect in Ontario
PRC-014-1 | Remedial Action Scheme Assessment | R3.3. | Identification of RAS that were found not to comply with NERC standards and Regional Reliability Organization criteria. | LOWER | Never Came Into Effect in Ontario
PRC-014-1 | Remedial Action Scheme Assessment | R3.4. | Discussion of any coordination problems found between a RAS and other protection and control systems. | LOWER | Never Came Into Effect in Ontario
PRC-014-1 | Remedial Action Scheme Assessment | R3.5. | Provide corrective action plans for non-compliant RAS. |  | Never Came Into Effect in Ontario
PRC-015-0 | Special Protection System Data and Documentation | R1. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall maintain a list of and provide data for existing and proposed SPSs as specified in Reliability Standard PRC-013-0_R 1. | MEDIUM | Retired | 2005-02-08 | 2017-03-31 | TO, GO, DP
PRC-015-0 | Special Protection System Data and Documentation | R2. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall have evidence it reviewed new or functionally modified SPSs in accordance with the Regional Reliability Organization’s procedures as defined in Reliability Standard PRC-012-0_R1 prior to being placed in service. | MEDIUM | Retired | 2005-02-08 | 2017-03-31 | TO, GO, DP
PRC-015-0 | Special Protection System Data and Documentation | R3. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall provide documentation of SPS data and the results of studies that show compliance of new or functionally modified SPSs with NERC Reliability Standards and Regional Reliability Organization criteria to affected Regional Reliability Organizations and NERC on request (within 30 calendar days). | LOWER | Retired | 2005-02-08 | 2017-03-31 | TO, GO, DP
PRC-015-1 | Remedial Action Scheme Data and Documentation | R1. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall maintain a list of and provide data for existing and proposed RAS as specified in Reliability Standard PRC-013-1 R1. | MEDIUM | Effective | 2017-04-01 |  | TO, GO, DP
PRC-015-1 | Remedial Action Scheme Data and Documentation | R2. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall have evidence it reviewed new or functionally modified RAS in accordance with the Regional Reliability Organization’s procedures as defined in Reliability Standard PRC-012-1_R1 prior to being placed in service. | MEDIUM | Effective | 2017-04-01 |  | TO, GO, DP
PRC-015-1 | Remedial Action Scheme Data and Documentation | R3. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall provide documentation of RAS data and the results of Studies that show compliance of new or functionally modified RAS with NERC Reliability Standards and Regional Reliability Organization criteria to affected Regional Reliability Organizations and NERC on request (within 30 calendar days). | LOWER | Effective | 2017-04-01 |  | TO, GO, DP
PRC-016-0.1 | Special Protection System Misoperations | R1. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall analyze its SPS operations and maintain a record of all misoperations in accordance with the Regional SPS review procedure specified in Reliability Standard PRC-012-0_R1. | MEDIUM | Retired | 2009-09-13 | 2017-03-31 | TO, GO, DP
PRC-016-0.1 | Special Protection System Misoperations | R2. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall take corrective actions to avoid future misoperations. | MEDIUM | Retired | 2009-09-13 | 2017-03-31 | TO, GO, DP
PRC-016-0.1 | Special Protection System Misoperations | R3. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall provide documentation of the misoperation analyses and the corrective action plans to its Regional Reliability Organization and NERC on request (within 90 calendar days). | LOWER | Retired | 2009-09-13 | 2017-03-31 | TO, GO, DP
PRC-016-1 | Remedial Action Scheme Misoperations | R1. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall analyze its RAS operations and maintain a record of all misoperations in accordance with the Regional RAS review procedure specified in Reliability Standard PRC-012-1_R1. | MEDIUM | Effective | 2017-04-01 |  | TO, GO, DP
PRC-016-1 | Remedial Action Scheme Misoperations | R2. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall take corrective actions to avoid future misoperations. | MEDIUM | Effective | 2017-04-01 |  | TO, GO, DP
PRC-016-1 | Remedial Action Scheme Misoperations | R3. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall provide documentation of the misoperation analyses and the corrective action plans to its Regional Reliability Organization and NERC on request (within 90 calendar days). | LOWER | Effective | 2017-04-01 |  | TO, GO, DP
PRC-017-0 | Special Protection System Maintenance and Testing | R1. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall have a system maintenance and testing program(s) in place. The program(s) shall include: | HIGH | Effective | 2005-02-08 | 2028-06-30 | TO, GO, DP
PRC-017-0 | Special Protection System Maintenance and Testing | R1.1. | SPS identification shall include but is not limited to: | HIGH | Effective | 2005-02-08 | 2028-06-30 | TO, GO, DP
PRC-017-0 | Special Protection System Maintenance and Testing | R1.1.1. | Relays. | HIGH | Effective | 2005-02-08 | 2028-06-30 | TO, GO, DP
PRC-017-0 | Special Protection System Maintenance and Testing | R1.1.2. | Instrument transformers. | HIGH | Effective | 2005-02-08 | 2028-06-30 | TO, GO, DP
PRC-017-0 | Special Protection System Maintenance and Testing | R1.1.3. | Communications systems, where appropriate. | HIGH | Effective | 2005-02-08 | 2028-06-30 | TO, GO, DP
PRC-017-0 | Special Protection System Maintenance and Testing | R1.1.4. | Batteries. | HIGH | Effective | 2005-02-08 | 2028-06-30 | TO, GO, DP
PRC-017-0 | Special Protection System Maintenance and Testing | R1.2. | Documentation of maintenance and testing intervals and their basis. | HIGH | Effective | 2005-02-08 | 2028-06-30 | TO, GO, DP
PRC-017-0 | Special Protection System Maintenance and Testing | R1.3. | Summary of testing procedure. | HIGH | Effective | 2005-02-08 | 2028-06-30 | TO, GO, DP
PRC-017-0 | Special Protection System Maintenance and Testing | R1.4. | Schedule for system testing. | HIGH | Effective | 2005-02-08 | 2028-06-30 | TO, GO, DP
PRC-017-0 | Special Protection System Maintenance and Testing | R1.5. | Schedule for system maintenance. | HIGH | Effective | 2005-02-08 | 2028-06-30 | TO, GO, DP
PRC-017-0 | Special Protection System Maintenance and Testing | R1.6. | Date last tested/maintained. | MEDIUM | Effective | 2005-02-08 | 2028-06-30 | TO, GO, DP
PRC-017-0 | Special Protection System Maintenance and Testing | R2. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall provide documentation of the program and its implementation to the appropriate Regional Reliability Organizations and NERC on request (within 30 calendar days). | LOWER | Effective | 2005-02-08 | 2028-06-30 | TO, GO, DP
PRC-017-1 | Remedial Action Scheme Maintenance and Testing | R1. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall have a system maintenance and testing program(s) in place. The program(s) shall include: | HIGH | Effective | 2017-04-01 | 2027-03-31 | TO, GO, DP
PRC-017-1 | Remedial Action Scheme Maintenance and Testing | R1.1. | RAS identification shall include but is not limited to: | HIGH | Effective | 2017-04-01 | 2027-03-31 | TO, GO, DP
PRC-017-1 | Remedial Action Scheme Maintenance and Testing | R1.1.1. | Relays. | HIGH | Effective | 2017-04-01 | 2027-03-31 | TO, GO, DP
PRC-017-1 | Remedial Action Scheme Maintenance and Testing | R1.1.2. | Instrument transformers. | HIGH | Effective | 2017-04-01 | 2027-03-31 | TO, GO, DP
PRC-017-1 | Remedial Action Scheme Maintenance and Testing | R1.1.3. | Communications systems, where appropriate. | HIGH | Effective | 2017-04-01 | 2027-03-31 | TO, GO, DP
PRC-017-1 | Remedial Action Scheme Maintenance and Testing | R1.1.4. | Batteries. | HIGH | Effective | 2017-04-01 | 2027-03-31 | TO, GO, DP
PRC-017-1 | Remedial Action Scheme Maintenance and Testing | R1.2. | Documentation of maintenance and testing intervals and their basis. | HIGH | Effective | 2017-04-01 | 2027-03-31 | TO, GO, DP
PRC-017-1 | Remedial Action Scheme Maintenance and Testing | R1.3. | Summary of testing procedure. | HIGH | Effective | 2017-04-01 | 2027-03-31 | TO, GO, DP
PRC-017-1 | Remedial Action Scheme Maintenance and Testing | R1.4. | Schedule for system testing. | HIGH | Effective | 2017-04-01 | 2027-03-31 | TO, GO, DP
PRC-017-1 | Remedial Action Scheme Maintenance and Testing | R1.5. | Schedule for system maintenance. | HIGH | Effective | 2017-04-01 | 2027-03-31 | TO, GO, DP
PRC-017-1 | Remedial Action Scheme Maintenance and Testing | R1.6. | Date last tested/maintained. | MEDIUM | Effective | 2017-04-01 | 2027-03-31 | TO, GO, DP
PRC-017-1 | Remedial Action Scheme Maintenance and Testing | R2. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall provide documentation of the program and its implementation to the appropriate Regional Reliability Organizations and NERC on request (within 30 calendar days). | LOWER | Effective | 2017-04-01 | 2027-03-31 | TO, GO, DP
PRC-018-1 | Disturbance Monitoring Equipment Installation and Data Reporting | R1. | Each Transmission Owner and Generator Owner required to install DMEs by its Regional Reliability Organization (reliability standard PRC-002 Requirements 1-3) shall have DMEs installed that meet the following requirements: | LOWER | Retired | 2007-02-02 | 2022-06-30 | TO, GO
PRC-018-1 | Disturbance Monitoring Equipment Installation and Data Reporting | R1.1. | Internal Clocks in DME devices shall be synchronized to within 2 milliseconds or less of Universal Coordinated Time scale (UTC) | LOWER | Retired | 2007-02-02 | 2022-06-30 | TO, GO
PRC-018-1 | Disturbance Monitoring Equipment Installation and Data Reporting | R1.2. | Recorded data from each Disturbance shall be retrievable for ten calendar days.. | LOWER | Retired | 2007-02-02 | 2022-06-30 | TO, GO
PRC-018-1 | Disturbance Monitoring Equipment Installation and Data Reporting | R2. | The Transmission Owner and Generator Owner shall each install DMEs in accordance with its Regional Reliability Organization’s installation requirements (reliability standard PRC-002 Requirements 1 through 3). | LOWER | Retired | 2007-02-02 | 2022-06-30 | TO, GO
PRC-018-1 | Disturbance Monitoring Equipment Installation and Data Reporting | R3. | The Transmission Owner and Generator Owner shall each maintain, and report to its Regional Reliability Organization on request, the following data on the DMEs installed to meet that region’s installation requirements (reliability standard PRC-002 Requirements1.1, 2.1 and 3.1): | LOWER | Retired | 2007-02-02 | 2022-06-30 | TO, GO
PRC-018-1 | Disturbance Monitoring Equipment Installation and Data Reporting | R3.1. | Type of DME (sequence of event recorder, fault recorder, or dynamic disturbance recorder). | LOWER | Retired | 2007-02-02 | 2022-06-30 | TO, GO
PRC-018-1 | Disturbance Monitoring Equipment Installation and Data Reporting | R3.2. | Make and model of equipment. | LOWER | Retired | 2007-02-02 | 2022-06-30 | TO, GO
PRC-018-1 | Disturbance Monitoring Equipment Installation and Data Reporting | R3.3. | Installation location. | LOWER | Retired | 2007-02-02 | 2022-06-30 | TO, GO
PRC-018-1 | Disturbance Monitoring Equipment Installation and Data Reporting | R3.4. | Operational status. | LOWER | Retired | 2007-02-02 | 2022-06-30 | TO, GO
PRC-018-1 | Disturbance Monitoring Equipment Installation and Data Reporting | R3.5. | Date last tested. | LOWER | Retired | 2007-02-02 | 2022-06-30 | TO, GO
PRC-018-1 | Disturbance Monitoring Equipment Installation and Data Reporting | R3.6. | Monitored elements, such as transmission circuit, bus section, etc. | LOWER | Retired | 2007-02-02 | 2022-06-30 | TO, GO
PRC-018-1 | Disturbance Monitoring Equipment Installation and Data Reporting | R3.7. | Monitored devices, such as circuit breaker, disconnect status, alarms, etc. | LOWER | Retired | 2007-02-02 | 2022-06-30 | TO, GO
PRC-018-1 | Disturbance Monitoring Equipment Installation and Data Reporting | R3.8. | Monitored electrical quantities, such as voltage, current, etc. | LOWER | Retired | 2007-02-02 | 2022-06-30 | TO, GO
PRC-018-1 | Disturbance Monitoring Equipment Installation and Data Reporting | R4. | The Transmission Owner and Generator Owner shall each provide Disturbance data (recorded by DMEs) in accordance with its Regional Reliability Organization’s requirements (reliability standard PRC-002 Requirement 4). | LOWER | Retired | 2007-02-02 | 2022-06-30 | TO, GO
PRC-018-1 | Disturbance Monitoring Equipment Installation and Data Reporting | R5. | The Transmission Owner and Generator Owner shall each archive all data recorded by DMEs for Regional Reliability Organization-identified events for at least three years. | LOWER | Retired | 2007-02-02 | 2022-06-30 | TO, GO
PRC-018-1 | Disturbance Monitoring Equipment Installation and Data Reporting | R6. | Each Transmission Owner and Generator Owner that is required by its Regional Reliability Organization to have DMEs shall have a maintenance and testing program for those DMEs that includes: | LOWER | Retired | 2007-02-02 | 2022-06-30 | TO, GO
PRC-018-1 | Disturbance Monitoring Equipment Installation and Data Reporting | R6.1. | Maintenance and testing intervals and their basis. | LOWER | Retired | 2007-02-02 | 2022-06-30 | TO, GO
PRC-018-1 | Disturbance Monitoring Equipment Installation and Data Reporting | R6.2. | Summary of maintenance and testing procedures. | LOWER | Retired | 2007-02-02 | 2022-06-30 | TO, GO
PRC-019-1 | Coordination of Generating Unit or Plant Capabilities, Voltage Regulating Controls, and Protection | R1. | At a maximum of every five calendar years, each Generator Owner and Transmission Owner with applicable Facilities shall coordinate the voltage regulating system controls, (including in-service1 limiters and protection functions) with the applicable equipment capabilities and settings of the applicable Protection System devices and functions. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Retired |  |  | TO, GO
PRC-019-1 | Coordination of Generating Unit or Plant Capabilities, Voltage Regulating Controls, and Protection | R1.1. | Assuming the normal automatic voltage regulator control loop and steady-state system operating conditions, verify the following coordination items for each applicable Facility: | MEDIUM | Retired |  |  | TO, GO
PRC-019-1 | Coordination of Generating Unit or Plant Capabilities, Voltage Regulating Controls, and Protection | R1.1.1. | The in-service limiters are set to operate before the Protection System of the applicable Facility in order to avoid disconnecting the generator unnecessarily. | MEDIUM | Retired |  |  | TO, GO
PRC-019-1 | Coordination of Generating Unit or Plant Capabilities, Voltage Regulating Controls, and Protection | R1.1.2. | The applicable in-service Protection System devices are set to operate to isolate or de-energize equipment in order to limit the extent of damage when operating conditions exceed equipment capabilities or stability limits. | MEDIUM | Retired |  |  | TO, GO
PRC-019-1 | Coordination of Generating Unit or Plant Capabilities, Voltage Regulating Controls, and Protection | R2. | Within 90 calendar days following the identification or implementation of systems, equipment or setting changes that will affect the coordination described in Requirement R1, each Generator Owner and Transmission Owner with applicable Facilities shall perform the coordination as described in Requirement R1. These possible systems, equipment or settings changes include, but are not limited to the following [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning]:  Voltage regulating settings or equipment changes;  Protection System settings or component changes;  Generating or synchronous condenser equipment capability changes; or  Generator or synchronous condenser step-up transformer changes. | MEDIUM | Retired |  |  | TO, GO
PRC-019-2 | Coordination of Generating Unit or Plant Capabilities, Voltage Regulating Controls, and Protection | R1. | At a maximum of every five calendar years, each Generator Owner and Transmission Owner with applicable Facilities shall coordinate the voltage regulating system controls, (including in-service1 limiters and protection functions) with the applicable equipment capabilities and settings of the applicable Protection System devices and functions. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2016-07-01 |  | TO, GO
PRC-019-2 | Coordination of Generating Unit or Plant Capabilities, Voltage Regulating Controls, and Protection | R1.1. | Assuming the normal automatic voltage regulator control loop and steady-state system operating conditions, verify the following coordination items for each applicable Facility: | MEDIUM | Effective | 2016-07-01 |  | TO, GO
PRC-019-2 | Coordination of Generating Unit or Plant Capabilities, Voltage Regulating Controls, and Protection | R1.1.1. | The in-service limiters are set to operate before the Protection System of the applicable Facility in order to avoid disconnecting the generator unnecessarily. | MEDIUM | Effective | 2016-07-01 |  | TO, GO
PRC-019-2 | Coordination of Generating Unit or Plant Capabilities, Voltage Regulating Controls, and Protection | R1.1.2. | The applicable in-service Protection System devices are set to operate to isolate or de-energize equipment in order to limit the extent of damage when operating conditions exceed equipment capabilities or stability limits. | MEDIUM | Effective | 2016-07-01 |  | TO, GO
PRC-019-2 | Coordination of Generating Unit or Plant Capabilities, Voltage Regulating Controls, and Protection | R2. | Within 90 calendar days following the identification or implementation of systems, equipment or setting changes that will affect the coordination described in Requirement R1, each Generator Owner and Transmission Owner with applicable Facilities shall perform the coordination as described in Requirement R1. These possible systems, equipment or settings changes include, but are not limited to the following [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning]: • Voltage regulating settings or equipment changes; • Protection System settings or component changes; • Generating or synchronous condenser equipment capability changes; or • Generator or synchronous condenser step-up transformer changes. | MEDIUM | Effective | 2016-07-01 |  | TO, GO
PRC-020-1 | Under-Voltage Load Shedding Program Database | R1. | The Regional Reliability Organization shall establish, maintain and annually update a database for UVLS programs implemented by entities within the region to mitigate the risk of voltage collapse or voltage instability in the BES. This database shall include the following items: |  | Never Came Into Effect in Ontario
PRC-020-1 | Under-Voltage Load Shedding Program Database | R1.1. | Owner and operator of the UVLS program. |  | Never Came Into Effect in Ontario
PRC-020-1 | Under-Voltage Load Shedding Program Database | R1.2. | Size and location of customer load, or percent of connected load, to be interrupted. |  | Never Came Into Effect in Ontario
PRC-020-1 | Under-Voltage Load Shedding Program Database | R1.3. | Corresponding voltage set points and overall scheme clearing times. |  | Never Came Into Effect in Ontario
PRC-020-1 | Under-Voltage Load Shedding Program Database | R1.4. | Time delay from initiation to trip signal. |  | Never Came Into Effect in Ontario
PRC-020-1 | Under-Voltage Load Shedding Program Database | R1.5. | Breaker operating times. |  | Never Came Into Effect in Ontario
PRC-020-1 | Under-Voltage Load Shedding Program Database | R1.6. | Any other schemes that are part of or impact the UVLS programs such as related generation protection, islanding schemes, automatic load restoration schemes, UFLS and Special Protection Systems. |  | Never Came Into Effect in Ontario
PRC-020-1 | Under-Voltage Load Shedding Program Database | R2. | The Regional Reliability Organization shall provide the information in its UVLS database to the Planning Authority, the Transmission Planner, or other Regional Reliability Organizations and to NERC within 30 calendar days of a request. |  | Never Came Into Effect in Ontario
PRC-020-2 | Under-Voltage Load Shedding Program Database | R1. | The Regional Reliability Organization shall establish, maintain and annually update a database for UVLS programs implemented by entities within the region to mitigate the risk of voltage collapse or voltage instability in the BES. This database shall include the following items: |  | Never Came Into Effect in Ontario
PRC-020-2 | Under-Voltage Load Shedding Program Database | R1.1. | Owner and operator of the UVLS program. |  | Never Came Into Effect in Ontario
PRC-020-2 | Under-Voltage Load Shedding Program Database | R1.2. | Size and location of customer load, or percent of connected load, to be interrupted. |  | Never Came Into Effect in Ontario
PRC-020-2 | Under-Voltage Load Shedding Program Database | R1.3. | Corresponding voltage set points and overall scheme clearing times. |  | Never Came Into Effect in Ontario
PRC-020-2 | Under-Voltage Load Shedding Program Database | R1.4. | Time delay from initiation to trip signal. |  | Never Came Into Effect in Ontario
PRC-020-2 | Under-Voltage Load Shedding Program Database | R1.5. | Breaker operating times. |  | Never Came Into Effect in Ontario
PRC-020-2 | Under-Voltage Load Shedding Program Database | R1.6. | Any other schemes that are part of or impact the UVLS programs such as related generation protection, islanding schemes, automatic load restoration schemes, UFLS and Remedial Action Schemes. |  | Never Came Into Effect in Ontario
PRC-020-2 | Under-Voltage Load Shedding Program Database | R2. | The Regional Reliability Organization shall provide the information in its UVLS database to the Planning Authority, the Transmission Planner, or other Regional Reliability Organizations and to NERC within 30 calendar days of a request. |  | Never Came Into Effect in Ontario
PRC-021-1 | Under-Voltage Load Shedding Program Data | R1. | Each Transmission Owner and Distribution Provider that owns a UVLS program to mitigate the risk of voltage collapse or voltage instability in the BES shall annually update its UVLS data to support the Regional UVLS program database. The following data shall be provided to the Regional Reliability Organization for each installed UVLS system: | LOWER | Retired | 2006-02-07 | 2017-03-31 | TO, DP
PRC-021-1 | Under-Voltage Load Shedding Program Data | R1.1. | Size and location of customer load, or percent of connected load, to be interrupted. | LOWER | Retired | 2006-02-07 | 2017-03-31 | TO, DP
PRC-021-1 | Under-Voltage Load Shedding Program Data | R1.2. | Corresponding voltage set points and overall scheme clearing times. | MEDIUM | Retired | 2006-02-07 | 2017-03-31 | TO, DP
PRC-021-1 | Under-Voltage Load Shedding Program Data | R1.3. | Time delay from initiation to trip signal. | LOWER | Retired | 2006-02-07 | 2017-03-31 | TO, DP
PRC-021-1 | Under-Voltage Load Shedding Program Data | R1.4. | Breaker operating times. | LOWER | Retired | 2006-02-07 | 2017-03-31 | TO, DP
PRC-021-1 | Under-Voltage Load Shedding Program Data | R1.5. | Any other schemes that are part of or impact the UVLS programs such as related generation protection, islanding schemes, automatic load restoration schemes, UFLS and Special Protection Systems. | LOWER | Retired | 2006-02-07 | 2017-03-31 | TO, DP
PRC-021-1 | Under-Voltage Load Shedding Program Data | R2. | Each Transmission Owner and Distribution Provider that owns a UVLS program shall provide its UVLS program data to the Regional Reliability Organization within 30 calendar days of a request. | LOWER | Retired | 2006-02-07 | 2017-03-31 | TO, DP
PRC-021-2 | Under-Voltage Load Shedding Program Data | R1. | Each Transmission Owner and Distribution Provider that owns a UVLS program to mitigate the risk of voltage collapse or voltage instability in the BES shall annually update its UVLS data to support the Regional UVLS program database. The following data shall be provided to the Regional Reliability Organization for each installed UVLS system: | LOWER | Never Came Into Effect in Ontario |  | 2014-11-13 | TO, DP
PRC-021-2 | Under-Voltage Load Shedding Program Data | R1.1. | Size and location of customer load, or percent of connected load, to be interrupted. | LOWER | Never Came Into Effect in Ontario |  | 2014-11-13 | TO, DP
PRC-021-2 | Under-Voltage Load Shedding Program Data | R1.2. | Corresponding voltage set points and overall scheme clearing times. | MEDIUM | Never Came Into Effect in Ontario |  | 2014-11-13 | TO, DP
PRC-021-2 | Under-Voltage Load Shedding Program Data | R1.3. | Time delay from initiation to trip signal. | LOWER | Never Came Into Effect in Ontario |  | 2014-11-13 | TO, DP
PRC-021-2 | Under-Voltage Load Shedding Program Data | R1.4. | Breaker operating times. | LOWER | Never Came Into Effect in Ontario |  | 2014-11-13 | TO, DP
PRC-021-2 | Under-Voltage Load Shedding Program Data | R1.5. | Any other schemes that are part of or impact the UVLS programs such as related generation protection, islanding schemes, automatic load restoration schemes, UFLS and Remedial Action Schemes. | LOWER | Never Came Into Effect in Ontario |  | 2014-11-13 | TO, DP
PRC-021-2 | Under-Voltage Load Shedding Program Data | R2. | Each Transmission Owner and Distribution Provider that owns a UVLS program shall provide its UVLS program data to the Regional Reliability Organization within 30 calendar days of a request. | LOWER | Never Came Into Effect in Ontario |  | 2014-11-13 | TO, DP
PRC-022-1 | Under-Voltage Load Shedding Program Performance | R1. | Each Transmission Operator, Load-Serving Entity, and Distribution Provider that operates a UVLS program to mitigate the risk of voltage collapse or voltage instability in the BES shall analyze and document all UVLS operations and Misoperations. The analysis shall include: | MEDIUM | Retired | 2006-02-07 | 2017-03-31 | TOP, DP
PRC-022-1 | Under-Voltage Load Shedding Program Performance | R1.1. | A description of the event including initiating conditions. | LOWER | Retired | 2006-02-07 | 2017-03-31 | TOP, DP
PRC-022-1 | Under-Voltage Load Shedding Program Performance | R1.2. | A review of the UVLS set points and tripping times. | MEDIUM | Retired | 2006-02-07 | 2017-03-31 | TOP, DP
PRC-022-1 | Under-Voltage Load Shedding Program Performance | R1.3. | A simulation of the event, if deemed appropriate by the Regional Reliability Organization. For most events, analysis of sequence of events may be sufficient and dynamic simulations may not be needed. | LOWER | Retired | 2006-02-07 | 2017-03-31 | TOP, DP
PRC-022-1 | Under-Voltage Load Shedding Program Performance | R1.4. | A summary of the findings. | LOWER | Retired | 2006-02-07 | 2017-03-31 | TOP, DP
PRC-022-1 | Under-Voltage Load Shedding Program Performance | R1.5. | For any Misoperation, a Corrective Action Plan to avoid future Misoperations of a similar nature. | MEDIUM | Retired | 2006-02-07 | 2017-03-31 | TOP, DP
PRC-023-2(i) | Transmission Relay Loadability | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall use any one of the following criteria (Requirement R1, criteria 1 through 13) for any specific circuit terminal to prevent its phase protective relay settings from limiting transmission system loadability while maintaining reliable protection of the BES for all fault conditions. Each Transmission Owner, Generator Owner, and Distribution Provider shall evaluate relay loadability at 0.85 per unit voltage and a power factor angle of 30 degrees. (see standard for list of criteria. | HIGH | Never Came Into Effect in Ontario |  |  | TO, GO, DP
PRC-023-2(i) | Transmission Relay Loadability | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider shall set its out-of-step blocking elements to allow tripping of phase protective relays for faults that occur during the loading conditions used to verify transmission line relay loadability per Requirement R1. | HIGH | Never Came Into Effect in Ontario |  |  | TO, GO, DP
PRC-023-2(i) | Transmission Relay Loadability | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses a circuit capability with the practical limitations described in Requirement R1, criterion 6, 7, 8, 9, 12, or 13 shall use the calculated circuit capability as the Facility Rating of the circuit and shall obtain the agreement of the Planning Coordinator, Transmission Operator, and Reliability Coordinator with the calculated circuit capability. | MEDIUM | Never Came Into Effect in Ontario |  |  | TO, GO, DP
PRC-023-2(i) | Transmission Relay Loadability | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that chooses to use Requirement R1 criterion 2 as the basis for verifying transmission line relay loadability shall provide its Planning Coordinator, Transmission Operator, and Reliability Coordinator with an updated list of circuits associated with those transmission line relays at least once each calendar year, with no more than 15 months between reports. | LOWER | Never Came Into Effect in Ontario |  |  | TO, GO, DP
PRC-023-2(i) | Transmission Relay Loadability | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider that sets transmission line relays according to Requirement R1 criterion 12 shall provide an updated list of the circuits associated with those relays to its Regional Entity at least once each calendar year, with no more than 15 months between reports, to allow the ERO to compile a list of all circuits that have protective relay settings that limit circuit capability. | LOWER | Never Came Into Effect in Ontario |  |  | TO, GO, DP
PRC-023-2(i) | Transmission Relay Loadability | R6. | Each Planning Coordinator shall conduct an assessment at least once each calendar year, with no more than 15 months between assessments, by applying the criteria in Attachment B to determine the circuits in its Planning Coordinator area for which Transmission Owners, Generator Owners, and Distribution Providers must comply with Requirements R1 through R5. The Planning Coordinator shall: | HIGH | Never Came Into Effect in Ontario |  |  | PC
PRC-023-2(i) | Transmission Relay Loadability | R6.1. | Maintain a list of circuits subject to PRC-023-2(i) per application of Attachment B, including identification of the first calendar year in which any criterion in Attachment B applies. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | PC
PRC-023-2(i) | Transmission Relay Loadability | R6.2. | Provide the list of circuits to all Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within 30 calendar days of the establishment of the initial list and within 30 calendar days of any changes to that list. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | PC
PRC-023-3 | Transmission Relay Loadability | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall use any one of the following criteria (Requirement R1, criteria 1 through 13) for any specific circuit terminal to prevent its phase protective relay settings from limiting transmission system loadability while maintaining reliable protection of the BES for all fault conditions. Each Transmission Owner, Generator Owner, and Distribution Provider shall evaluate relay loadability at 0.85 per unit voltage and a power factor angle of 30 degrees. [Violation Risk Factor: High] [Time Horizon: Long Term Planning]. See detailed Criteria in the standard. | HIGH | Retired | 2014-10-01 | 2017-03-31 | TO, GO, DP
PRC-023-3 | Transmission Relay Loadability | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider shall set its out-of-step blocking elements to allow tripping of phase protective relays for faults that occur during the loading conditions used to verify transmission line relay loadability per Requirement R1. [Violation Risk Factor: High] [Time Horizon: Long Term Planning] | HIGH | Retired | 2014-10-01 | 2017-03-31 | TO, GO, DP
PRC-023-3 | Transmission Relay Loadability | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses a circuit capability with the practical limitations described in Requirement R1, criterion 7, 8, 9, 12, or 13 shall use the calculated circuit capability as the Facility Rating of the circuit and shall obtain the agreement of the Planning Coordinator, Transmission Operator, and Reliability Coordinator with the calculated circuit capability. [Violation Risk Factor: Medium] [Time Horizon: Long Term Planning] | MEDIUM | Retired | 2014-10-01 | 2017-03-31 | TO, GO, DP
PRC-023-3 | Transmission Relay Loadability | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that chooses to use Requirement R1 criterion 2 as the basis for verifying transmission line relay loadability shall provide its Planning Coordinator, Transmission Operator, and Reliability Coordinator with an updated list of circuits associated with those transmission line relays at least once each calendar year, with no more than 15 months between reports. [Violation Risk Factor: Lower] [Time Horizon: Long Term Planning] | LOWER | Retired | 2015-04-01 | 2017-03-31 | TO, GO, DP
PRC-023-3 | Transmission Relay Loadability | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider that sets transmission line relays according to Requirement R1 criterion 12 shall provide an updated list of the circuits associated with those relays to its Regional Entity at least once each calendar year, with no more than 15 months between reports, to allow the ERO to compile a list of all circuits that have protective relay settings that limit circuit capability. [Violation Risk Factor: Lower] [Time Horizon: Long Term Planning] | LOWER | Retired | 2014-10-01 | 2017-03-31 | TO, GO, DP
PRC-023-3 | Transmission Relay Loadability | R6. | Each Planning Coordinator shall conduct an assessment at least once each calendar year, with no more than 15 months between assessments, by applying the criteria in PRC-023-3, Attachment B to determine the circuits in its Planning Coordinator area for which Transmission Owners, Generator Owners, and Distribution Providers must comply with Requirements R1 through R5. The Planning Coordinator shall: [Violation Risk Factor: High] [Time Horizon: Long Term Planning] | HIGH | Retired | 2014-10-01 | 2017-03-31 | PC
PRC-023-3 | Transmission Relay Loadability | R6.1. | Maintain a list of circuits subject to PRC-023-3 per application of Attachment B, including identification of the first calendar year in which any criterion in PRC-023-3, Attachment B applies. | HIGH | Retired | 2014-10-01 | 2017-03-31 | PC
PRC-023-3 | Transmission Relay Loadability | R6.2. | Provide the list of circuits to all Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within 30 calendar days of the establishment of the initial list and within 30 calendar days of any changes to that list. | HIGH | Retired | 2014-10-01 | 2017-03-31 | PC
PRC-023-4 | Transmission Relay Loadability | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall use any one of the following criteria (Requirement R1, criteria 1 through 13) for any specific circuit terminal to prevent its phase protective relay settings from limiting transmission system loadability while maintaining reliable protection of the BES for all fault conditions. Each Transmission Owner, Generator Owner, and Distribution Provider shall evaluate relay loadability at 0.85 per unit voltage and a power factor angle of 30 degrees. [Violation Risk Factor: High] [Time Horizon: Long Term Planning]. See detailed Criteria in the standard. | HIGH | Effective | 2017-04-01 |  | TO, GO, DP
PRC-023-4 | Transmission Relay Loadability | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider shall set its out-of-step blocking elements to allow tripping of phase protective relays for faults that occur during the loading conditions used to verify transmission line relay loadability per Requirement R1. [Violation Risk Factor: High] [Time Horizon: Long Term Planning] | HIGH | Effective | 2017-04-01 |  | TO, GO, DP
PRC-023-4 | Transmission Relay Loadability | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses a circuit capability with the practical limitations described in Requirement R1, criterion 7, 8, 9, 12, or 13 shall use the calculated circuit capability as the Facility Rating of the circuit and shall obtain the agreement of the Planning Coordinator, Transmission Operator, and Reliability Coordinator with the calculated circuit capability. [Violation Risk Factor: Medium] [Time Horizon: Long Term Planning] | MEDIUM | Effective | 2017-04-01 |  | TO, GO, DP
PRC-023-4 | Transmission Relay Loadability | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that chooses to use Requirement R1 criterion 2 as the basis for verifying transmission line relay loadability shall provide its Planning Coordinator, Transmission Operator, and Reliability Coordinator with an updated list of circuits associated with those transmission line relays at least once each calendar year, with no more than 15 months between reports. [Violation Risk Factor: Lower] [Time Horizon: Long Term Planning] | LOWER | Effective | 2017-04-01 |  | TO, GO, DP
PRC-023-4 | Transmission Relay Loadability | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider that sets transmission line relays according to Requirement R1 criterion 12 shall provide an updated list of the circuits associated with those relays to its Regional Entity at least once each calendar year, with no more than 15 months between reports, to allow the ERO to compile a list of all circuits that have protective relay settings that limit circuit capability. [Violation Risk Factor: Lower] [Time Horizon: Long Term Planning] | LOWER | Effective | 2017-04-01 |  | TO, GO, DP
PRC-023-4 | Transmission Relay Loadability | R6. | Each Planning Coordinator shall conduct an assessment at least once each calendar year, with no more than 15 months between assessments, by applying the criteria in PRC-023-4, Attachment B to determine the circuits in its Planning Coordinator area for which Transmission Owners, Generator Owners, and Distribution Providers must comply with Requirements R1 through R5. The Planning Coordinator shall: [Violation Risk Factor: High] [Time Horizon: Long Term Planning] | HIGH | Effective | 2017-04-01 |  | PC
PRC-023-4 | Transmission Relay Loadability | R6. | Each Planning Coordinator shall conduct an assessment at least once each calendar year, with no more than 15 months between assessments, by applying the criteria in PRC-023-4, Attachment B to determine the circuits in its Planning Coordinator area for which Transmission Owners, Generator Owners, and Distribution Providers must comply with Requirements R1 through R5. The Planning Coordinator shall: [Violation Risk Factor: High] [Time Horizon: Long Term Planning] | HIGH | Effective | 2017-04-01 |  | PC
PRC-023-4 | Transmission Relay Loadability | R6.1. | Maintain a list of circuits subject to PRC-023-4 per application of Attachment B, including identification of the first calendar year in which any criterion in PRC-023-4, Attachment B applies. | HIGH | Effective | 2017-04-01 |  | PC
PRC-023-4 | Transmission Relay Loadability | R6.2. | Provide the list of circuits to all Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within 30 calendar days of the establishment of the initial list and within 30 calendar days of any changes to that list. | HIGH | Effective | 2017-04-01 |  | PC
PRC-023-5 | Transmission Relay Loadability | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall use any one of the following criteria (Requirement R1, criteria 1 through 13) for any specific circuit terminal to prevent its phase protective relay settings from limiting transmission system loadability while maintaining reliable protection of the BES for all fault conditions. Each Transmission Owner,Generator Owner, and Distribution Provider shall evaluate relay loadability at 0.85 per unit voltage and a power factor angle of 30 degrees. [Violation Risk Factor: High] [Time Horizon: Long Term Planning]. See detailed Criteria in the standard. | HIGH | Effective | 2024-04-01 |  | TO, PC, GO, DP
PRC-023-5 | Transmission Relay Loadability | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider shall set its out-of-step blocking elements to allow tripping of phase protective relays for faults that occur during the loading conditions used to verify transmission line relay loadability per Requirement R1. [Violation Risk Factor: High] [Time Horizon: Long Term Planning] | HIGH | Effective | 2024-04-01 |  | TO, PC, GO, DP
PRC-023-5 | Transmission Relay Loadability | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses a circuit capability with the practical limitations described in Requirement R1, criterion 7, 8, 9, 12, or 13 shall use the calculated circuit capability as the Facility Rating of the circuit and shall obtain the agreement of the Planning Coordinator, Transmission Operator, and Reliability Coordinator withthe calculated circuit capability. [Violation Risk Factor: Medium] [Time Horizon: Long Term Planning] | MEDIUM | Effective | 2024-04-01 |  | GO, DP, TO, PC
PRC-023-5 | Transmission Relay Loadability | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that chooses to use Requirement R1 criterion 2 as the basis for verifying transmission line relay loadability shall provide its Planning Coordinator, Transmission Operator, and Reliability Coordinator with an updated list of circuits associated with those transmission line relays at least once each calendaryear, with no more than 15 months between reports. [Violation Risk Factor: Lower] [Time Horizon: Long Term Planning] | LOWER | Effective | 2024-04-01 |  | TO, PC, GO, DP
PRC-023-5 | Transmission Relay Loadability | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider that sets transmission line relays according to Requirement R1 criterion 12 shall provide an updated list of the circuits associated with those relays to its Regional Entity at least once each calendar year, with no more than 15 months between reports, to allow the ERO to compile a list of all circuits that haveprotective relay settings that limit circuit capability. [Violation Risk Factor: Lower] [Time Horizon: Long Term Planning] | LOWER | Effective | 2024-04-01 |  | TO, PC, GO, DP
PRC-023-5 | Transmission Relay Loadability | R6. | Each Planning Coordinator shall conduct an assessment at least once each calendar year, with no more than 15 months between assessments, by applying the criteria in PRC-023-4, Attachment B to determine the circuits in its Planning Coordinator area for which Transmission Owners, Generator Owners, and Distribution Providers must comply with Requirements R1 through R5.The Planning Coordinator shall: [Violation Risk Factor: High] [Time Horizon: Long Term Planning] | HIGH | Effective | 2024-04-01 |  | TO, PC, GO, DP
PRC-023-5 | Transmission Relay Loadability | R6. | Each Planning Coordinator shall conduct an assessment at least once each calendar year, with no more than 15 months between assessments, by applying the criteria in PRC-023-4, Attachment B to determine the circuits in its Planning Coordinator area for which Transmission Owners, Generator Owners, and Distribution Providers must comply with Requirements R1 through R5. The Planning Coordinator shall: [Violation Risk Factor: High] [Time Horizon: Long Term Planning] | HIGH | Effective | 2024-04-01 |  | TO, PC, GO, DP
PRC-023-5 | Transmission Relay Loadability | R6.1. | Maintain a list of circuits subject to PRC-023-5 per application of Attachment B, including identification of the first calendar year in which any criterion in PRC-023-5, Attachment B applies. | HIGH | Effective | 2024-04-01 |  | TO, PC, GO, DP
PRC-023-5 | Transmission Relay Loadability | R6.2. | Provide the list of circuits to all Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within 30 calendar days of the establishment of the initial list and within 30 calendar days of any changes to that list. | HIGH | Effective | 2024-04-01 |  | TO, PC, GO, DP
PRC-023-6 | Transmission Relay Loadability | R1. | Each Transmission Owner, Generator Owner, and Distribution Providershall use any one of the following criteria (Requirement R1, criteria 1 through 13) for any specific circuit terminal to prevent its phase protective relay settings from limiting transmission system loadability while maintaining reliable protection of the BES for all fault conditions. Each Transmission Owner, Generator Owner, and Distribution Provider shall evaluate relay loadability at 0.85 per unit voltage and a power factor angle of 30 degrees. [Violation Risk Factor: High] [Time Horizon: Long Term Planning] Criteria: 1. Set transmission line relays so they do not operate at or below 150% of the highest seasonal Facility Rating of a circuit, for the available defined loading duration nearest 4 hours (expressed in amperes). 2. Set transmission line relays so they do not operate at or below 115% of the highest seasonal 15-minute Facility Ratingof a circuit (expressed in amperes). 3. Set transmission line relays so they do not operate at or below 115% of the maximum theoretical power transfer capability (using a 90-degree angle between the sending-end and receiving-end voltages and either reactance or complex impedance) of the circuit (expressed in amperes) using one of the following to perform the power transfer calculation: • An infinite source (zero source impedance) with a 1.00 per unit bus voltage at each end of the line. • An impedance at each end of the line, which reflects the actual system source impedance with a 1.05 per unit voltage behind each source impedance. 4. Set transmission line relays on series compensated transmission lines so they do not operate at or below the maximum power transfer capability of the line, determined as the greater of: • 115% of the highest emergency rating of the series capacitor. • 115% of the maximum power transfer capability of the circuit (expressed in amperes), calculated in accordance with Requirement R1, criterion 3, using the full lineinductive reactance. 5. Set transmission line relays on weak source systems so they do not operate at or below 170% of the maximum end-of-line three-phase fault magnitude (expressed in amperes). 6. Reserved. 7. Set transmission line relays applied at the load center terminal, remote from generation stations, so they do not operate at or below 115% of the maximum current flow from the load to the generation source under any system configuration.Set transmission line relays applied on the bulk system-end of transmission lines that serve load remote to the system so they do not operate at or below 115% of the maximum current flow from the system to the load under any system configuration. 9. Set transmission line relays applied on the load-end of transmission lines that serve load remote to the bulk system so they do not operate at or below 115% of the maximum current flow from the load to the system under any system configuration. 10. Set transformer fault protection relays and transmission line relays on transmission lines terminated only with a transformer so that the relays do not operate at or below the greater of: • 150% of the applicable maximum transformer nameplate rating (expressed in amperes), including the forced cooled ratings corresponding to all installed supplemental cooling equipment. • 115% of the highest operator established emergency transformerrating. 10.1 Set load-responsive transformer fault protection relays, if used, such that the protection settings do not expose the transformer to a fault level and duration that exceeds the transformer’s mechanical withstand capability. 11. For transformer overload protection relays that do not comply with the loadability component of Requirement R1, criterion 10 set the relays according to one of the following: • Set the relays to allow the transformer to be operated at an overload level of at least 150% of the maximum applicable nameplate rating, or 115% of the highest operator established emergency transformer rating, whichever is greater, for at least 15 minutes to provide time for the operator to take controlled action to relieve the overload. • Install supervision for the relays using either a top oil or simulated winding hot spot temperature element set no less than 100° C for the top oil temperature or no lessthan 140° C for the winding hot spot temperature. 12. When the desired transmission line capability is limited by the requirement to adequately protect the transmission line, set the transmission line distance relays to a maximum of 125% of the apparent impedance (at the impedance angle of the transmission line) subject to the following constraints: a. Set the maximum torque angle (MTA) to 90 degrees or the highestsupported by the manufacturer. b. Evaluate the relay loadability in amperes at the relay trip point at 0.85 per unit voltage and a power factor angle of 30 degrees. c. Include a relay setting component of 87% of the current calculated in Requirement R1, criterion 12 in the Facility Rating determination for the circuit. 13. Where other situations present practical limitations on circuit capability, set the phase protection relays so they do not operate at or below 115% of such limitations. | HIGH | Effective | 2024-04-01 |  | TO, GO, DP
PRC-023-6 | Transmission Relay Loadability | R2. | Reserved. | MEDIUM | Effective | 2024-04-01 |  | TO, GO, DP
PRC-023-6 | Transmission Relay Loadability | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses a circuit capability with the practical limitations described in Requirement R1, criterion 7, 8, 9, 12, or 13 shall use the calculated circuit capability as the Facility Rating of the circuit and shall obtain the agreement of the Planning Coordinator, Transmission Operator, and Reliability Coordinator with the calculated circuit capability. [Violation Risk Factor: Medium] [Time Horizon: Long Term Planning] | MEDIUM | Effective | 2024-04-01 |  | TO, GO, DP
PRC-023-6 | Transmission Relay Loadability | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that chooses to use Requirement R1 criterion 2 as the basis for verifying transmission line relay loadability shall provide its Planning Coordinator, Transmission Operator, and Reliability Coordinator with an updated list of circuits associated with those transmission line relays at least once each calendar year, with no more than 15 months between reports. [Violation Risk Factor: Lower] [Time Horizon: Long Term Planning] | LOWER | Effective | 2024-04-01 |  | TO, GO, DP
PRC-023-6 | Transmission Relay Loadability | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider that sets transmission line relays according to Requirement R1 criterion 12 shall provide an updated list of the circuits associated with those relays to its Regional Entity at least once each calendar year, with no more than 15 months between reports, to allow theERO to compile a list of all circuits that have protective relay settings that limit circuit capability. [Violation Risk Factor: Lower] [Time Horizon: Long Term Planning] | LOWER | Effective | 2024-04-01 |  | TO, GO, DP
PRC-023-6 | Transmission Relay Loadability | R6. | Each Planning Coordinator shall conduct an assessment at least once each calendar year, with no more than 15 months between assessments, by applying the criteria in PRC-023- 6, Attachment B to determine the circuits in its Planning Coordinator area for which Transmission Owners, Generator Owners, and Distribution Providers must comply with Requirements R1 through R5. The Planning Coordinator shall: [Violation Risk Factor: High] [Time Horizon: Long Term Planning] | HIGH | Effective | 2024-04-01 |  | PC
PRC-023-6 | Transmission Relay Loadability | R6.1. | Maintain a list of circuits subject to PRC-023-6 per application of Attachment B, including identification of the first calendar year in which any criterion in PRC-023- 6, Attachment B applies. | HIGH | Effective | 2024-04-01 |  | PC
PRC-023-6 | Transmission Relay Loadability | R6.2. | Provide the list of circuits to all Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within 30 calendar days of the establishment of the initial list and within 30 calendar days of any changes to that list. | HIGH | Effective | 2024-04-01 |  | PC
PRC-024-1 | Generator Frequency and Voltage Protective Relay Settings | R1. | Each Generator Owner that has generator frequency protective relaying1 • Generating unit(s) may trip if the protective functions (such as out-of-step functions or loss-of-field functions) operate due to an impending or actual loss of synchronism or, for asynchronous generating units, due to instability in power conversion control equipment. activated to trip its applicable generating unit(s) shall set its protective relaying such that the generator frequency protective relaying does not trip the applicable generating unit(s) within the “no trip zone” of PRC-024 Attachment 1, subject to the following exceptions: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] • Generating unit(s) may trip if clearing a system fault necessitates disconnecting (a) generating unit(s). • Generating unit(s) may trip within a portion of the “no trip zone” of PRC-024 Attachment 1 for documented and communicated regulatory or equipment limitations in accordance with Requirement R3. | MEDIUM | Retired | 2016-07-01 | 2016-06-30 | GO
PRC-024-1 | Generator Frequency and Voltage Protective Relay Settings | R2. | Each Generator Owner that has generator voltage protective relaying1 activated to trip its applicable generating unit(s) shall set its protective relaying such that the generator voltage protective relaying does not trip the applicable generating unit(s) as a result of a voltage excursion (at the point of interconnection2 • Generating unit(s) may trip in accordance with a Special Protection System (SPS) or Remedial Action Scheme (RAS). ) caused by an event on the transmission system external to the generating plant that remains within the “no trip zone” of PRC-024 Attachment 2. If the Transmission Planner allows less stringent voltage relay settings than those required to meet PRC-024 Attachment 2, then the Generator Owner shall set its protective relaying within the voltage recovery characteristics of a location-specific Transmission Planner’s study. Requirement R2 is subject to the following exceptions: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] • Generating unit(s) may trip if clearing a system fault necessitates disconnecting (a) generating unit(s). • Generating unit(s) may trip by action of protective functions (such as out-of-step functions or loss-of-field functions) that operate due to an impending or actual loss of synchronism or, for asynchronous generating units, due to instability in power conversion control equipment. • Generating unit(s) may trip within a portion of the “no trip zone” of PRC-024 Attachment 2 for documented and communicated regulatory or equipment limitations in accordance with Requirement R3. | MEDIUM | Retired | 2016-07-01 | 2016-06-30 | GO
PRC-024-1 | Generator Frequency and Voltage Protective Relay Settings | R3. | Each Generator Owner shall document each known regulatory or equipment limitation that prevents an applicable generating unit with generator frequency or voltage protective relays from meeting the relay setting criteria in Requirements R1 or R2 including (but not limited to) study results, experience from an actual event, or manufacturer’s advice. [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | LOWER | Retired | 2016-07-01 | 2016-06-30 | GO
PRC-024-1 | Generator Frequency and Voltage Protective Relay Settings | R3.1. | The Generator Owner shall communicate the documented regulatory or equipment limitation, or the removal of a previously documented regulatory or equipment limitation, to its Planning Coordinator and Transmission Planner within 30 calendar days of any of the following: • Identification of a regulatory or equipment limitation. • Repair of the equipment causing the limitation that removes the limitation. • Replacement of the equipment causing the limitation with equipment that removes the limitation. • Creation or adjustment of an equipment limitation caused by consumption of the cumulative turbine life-time frequency excursion allowance. | LOWER | Retired | 2016-07-01 | 2016-06-30 | GO
PRC-024-1 | Generator Frequency and Voltage Protective Relay Settings | R4. | Each Generator Owner shall provide its applicable generator protection trip settings associated with Requirements R1 and R2 to the Planning Coordinator or Transmission Planner that models the associated unit within 60 calendar days of receipt of a written request for the data and within 60 calendar days of any change to those previously requested trip settings unless directed by the requesting Planning Coordinator or Transmission Planner that the reporting of relay setting changes is not required. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Retired | 2016-07-01 | 2016-06-30 | GO
PRC-024-2 | Generator Frequency and Voltage Protective Relay Settings | R1. | Each Generator Owner that has generator frequency protective relaying1 activated to trip its applicable generating unit(s) shall set its protective relaying such that the generator frequency protective relaying does not trip the applicable generating unit(s) within the “no trip zone” of PRC-024 Attachment 1, subject to the following exceptions:2 [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] • Generating unit(s) may trip if the protective functions (such as out-of-step functions or loss-of-field functions) operate due to an impending or actual loss of synchronism or, for asynchronous generating units, due to instability in power conversion control equipment. • Generating unit(s) may trip if clearing a system fault necessitates disconnecting (a) generating unit(s). • Generating unit(s) may trip within a portion of the “no trip zone” of PRC-024 Attachment 1 for documented and communicated regulatory or equipment limitations in accordance with Requirement R3. | MEDIUM | Retired | 2016-07-01 | 2022-09-30 | GO
PRC-024-2 | Generator Frequency and Voltage Protective Relay Settings | R2. | Each Generator Owner that has generator voltage protective relaying1 activated to trip its applicable generating unit(s) shall set its protective relaying such that the generator voltage protective relaying does not trip the applicable generating unit(s) as a result of a voltage excursion (at the point of interconnection3) caused by an event on the transmission system external to the generating plant that remains within the “no trip zone” of PRC-024 Attachment 2.4 If the Transmission Planner allows less stringent voltage relay settings than those required to meet PRC-024 Attachment 2, then the Generator Owner shall set its protective relaying within the voltage recovery characteristics of a location-specific Transmission Planner’s study. Requirement R2 is subject to the following exceptions: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] • Generating unit(s) may trip in accordance with a Special Protection System (SPS) or Remedial Action Scheme (RAS). • Generating unit(s) may trip if clearing a system fault necessitates disconnecting (a) generating unit(s). • Generating unit(s) may trip by action of protective functions (such as out-of-step functions or loss-of-field functions) that operate due to an impending or actual loss of synchronism or, for asynchronous generating units, due to instability in power conversion control equipment. • Generating unit(s) may trip within a portion of the “no trip zone” of PRC-024 Attachment 2 for documented and communicated regulatory or equipment limitations in accordance with Requirement R3. | MEDIUM | Retired | 2016-07-01 | 2022-09-30 | GO
PRC-024-2 | Generator Frequency and Voltage Protective Relay Settings | R3. | Each Generator Owner shall document each known regulatory or equipment limitation, that prevents an applicable generating unit with generator frequency or voltage protective relays from meeting the relay setting criteria in Requirements R1 or R2 including (but not limited to) study results, experience from an actual event, or manufacturer’s advice. [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | LOWER | Retired | 2016-07-01 | 2022-09-30 | GO
PRC-024-2 | Generator Frequency and Voltage Protective Relay Settings | R3.1. | The Generator Owner shall communicate the documented regulatory or equipment limitation, or the removal of a previously documented regulatory or equipment limitation, to its Planning Coordinator and Transmission Planner within 30 calendar days of any of the following: • Identification of a regulatory or equipment limitation. • Repair of the equipment causing the limitation that removes the limitation. • Replacement of the equipment causing the limitation with equipment that removes the limitation. • Creation or adjustment of an equipment limitation caused by consumption of the cumulative turbine life-time frequency excursion allowance. | LOWER | Retired | 2016-07-01 | 2022-09-30 | GO
PRC-024-2 | Generator Frequency and Voltage Protective Relay Settings | R4. | Each Generator Owner shall provide its applicable generator protection trip settings associated with Requirements R1 and R2 to the Planning Coordinator or Transmission Planner that models the associated unit within 60 calendar days of receipt of a written request for the data and within 60 calendar days of any change to those previously requested trip settings unless directed by the requesting Planning Coordinator or Transmission Planner that the reporting of relay setting changes is not required. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Retired | 2016-07-01 | 2022-09-30 | GO
PRC-024-3 | Frequency and Voltage Protection Settings for Generating Resources | R1. | Each Generator Owner shall set its applicable frequency protection in accordance with PRC-024 Attachment 1 such that the applicable protection does not cause the generating resource to trip or cease injecting current within the “no trip zone” during a frequency excursion with the following exceptions: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2022-10-01 |  | GO
PRC-024-3 | Frequency and Voltage Protection Settings for Generating Resources | R2. | Each Generator Owner shall set its applicable voltage protection in accordance with PRC-024 Attachment 2, such that the applicable protection does not cause the generating resource to trip or cease injecting current within the “no trip zone” during a voltage excursion at the high side of the GSU or MPT, subject to the following exceptions: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] • If the Transmission Planner allows less stringent voltage protection settings than those required to meet PRC-024 Attachment 2, then the Generator Owner may set its protection within the voltage recovery characteristics of a location-specific Transmission Planner’s study. • Applicable voltage protection may be set to trip or cease injecting current during a voltage excursion within a portion of the “no trip zone” for documented and communicated regulatory or equipment limitations in accordance with Requirement R3 | MEDIUM | Effective | 2022-10-01 |  | GO
PRC-024-3 | Frequency and Voltage Protection Settings for Generating Resources | R3. | Each Generator Owner shall document each known regulatory or equipment limitation that prevents an applicable generating resource(s) with frequency or voltage protection from meeting the protection setting criteria in Requirements R1 or R2, including (but not limited to) study results, experience from an actual event, or manufacturer’s advice. [Violation Risk Factor: Lower] [Time Horizon: Long term Planning] | LOWER | Effective | 2022-10-01 |  | GO
PRC-024-3 | Frequency and Voltage Protection Settings for Generating Resources | R3.1. | The Generator Owner shall communicate the documented regulatory or equipment limitation, or the removal of a previously documented regulatory or equipment limitation, to its Planning Coordinator and Transmission Planner within 30 calendar days of any of the following: • Identification of a regulatory or equipment limitation. • Repair of the equipment causing the limitation that removes the limitation. • Replacement of the equipment causing the limitation with equipment that removes the limitation. • Creation or adjustment of an equipment limitation caused by consumption of the cumulative turbine life-time frequency excursion allowance. | LOWER | Effective | 2022-10-01 |  | GO
PRC-024-3 | Frequency and Voltage Protection Settings for Generating Resources | R4. | Each Generator Owner shall provide its applicable protection settings associated with Requirements R1 and R2 to the Planning Coordinator or Transmission Planner that models the associated generating resource(s) within 60 calendar days of receipt of a written request for the data and within 60 calendar days of any change to those previously requested settings unless directed by the requesting Planning Coordinator or Transmission Planner that the reporting of protection setting changes is not required. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Effective | 2022-10-01 |  | GO
PRC-025-1 | Generator Relay Loadability | R1. | Each Generator Owner, Transmission Owner, and Distribution Provider shall apply settings that are in accordance with PRC-025-1 – Attachment 1: Relay Settings, on each load-responsive protective relay while maintaining reliable fault protection. [Violation Risk Factor: High] [Time Horizon: Long-Term Planning] | HIGH | Retired | 2014-10-01 | 2018-09-30 | TO, GO, DP
PRC-025-2 | Generator Relay Loadability | R1. | Each Generator Owner, Transmission Owner, and Distribution Provider shall apply settings that are in accordance with PRC-025-2 – Attachment 1: Relay Settings, on each load-responsive protective relay while maintaining reliable fault protection. [Violation Risk Factor: High] [Time Horizon: Long-Term Planning] | HIGH | Effective | 2018-10-01 |  | TO, GO, DP
PRC-026-1 | Relay Performance During Stable Power Swings | R1. | Each Planning Coordinator shall, at least once each calendar year, provide notification of each generator, transformer, and transmission line BES Element in its area that meets one or more of the following criteria, if any, to the respective Generator Owner and Transmission Owner: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] Criteria: 1. Generator(s) where an angular stability constraint exists that is addressed by a System Operating Limit (SOL) or a Remedial Action Scheme (RAS) and those Elements terminating at the Transmission station associated with the generator(s). 2. An Element that is monitored as part of an SOL identified by the Planning Coordinator’s methodology1 based on an angular stability constraint. 3. An Element that forms the boundary of an island in the most recent underfrequency load shedding (UFLS) design assessment based on application of the Planning Coordinator’s criteria for identifying islands, only if the island is formed by tripping the Element due to angular instability. 4. An Element identified in the most recent annual Planning Assessment where relay tripping occurs due to a stable or unstable2 power swing during a simulated disturbance. | MEDIUM | Effective | 2018-01-01 |  | TO, PC, GO
PRC-026-1 | Relay Performance During Stable Power Swings | R2. | Each Generator Owner and Transmission Owner shall: [Violation Risk Factor: High] [Time Horizon: Operations Planning] | HIGH | Effective | 2020-01-01 |  | TO, GO
PRC-026-1 | Relay Performance During Stable Power Swings | R2.1. | Within 12 full calendar months of notification of a BES Element pursuant to Requirement R1, determine whether its load-responsive protective relay(s) applied to that BES Element meets the criteria in PRC-026-1 – Attachment B where an evaluation of that Element’s load-responsive protective relay(s) based on PRC-026-1 – Attachment B criteria has not been performed in the last five calendar years. | HIGH | Effective | 2020-01-01 |  | TO, GO
PRC-026-1 | Relay Performance During Stable Power Swings | R2.2. | Within 12 full calendar months of becoming aware4 of a generator, transformer, or transmission line BES Element that tripped in response to a stable or unstable5 power swing due to the operation of its protective relay(s), determine whether its load-responsive protective relay(s) applied to that BES Element meets the criteria in PRC-026-1 – Attachment B. | HIGH | Effective | 2020-01-01 |  | TO, GO
PRC-026-1 | Relay Performance During Stable Power Swings | R3. | Each Generator Owner and Transmission Owner shall, within six full calendar months of determining a load-responsive protective relay does not meet the PRC-026-1 – Attachment B criteria pursuant to Requirement R2, develop a Corrective Action Plan (CAP) to meet one of the following: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] • The Protection System meets the PRC-026-1 – Attachment B criteria, while maintaining dependable fault detection and dependable out-of-step tripping (if out-of-step tripping is applied at the terminal of the BES Element); or • The Protection System is excluded under the PRC-026-1 – Attachment A criteria (e.g., modifying the Protection System so that relay functions are supervised by power swing blocking or using relay systems that are immune to power swings), while maintaining dependable fault detection and dependable out-of-step tripping (if out-of-step tripping is applied at the terminal of the BES Element). | MEDIUM | Effective | 2020-01-01 |  | TO, GO
PRC-026-1 | Relay Performance During Stable Power Swings | R4. | Each Generator Owner and Transmission Owner shall implement each CAP developed pursuant to Requirement R3 and update each CAP if actions or timetables change until all actions are complete. [Violation Risk Factor: Medium][Time Horizon: Long-Term Planning] | MEDIUM | Effective | 2020-01-01 |  | TO, GO
PRC-026-2 | Relay Performance During Stable Power Swings | R1. | Each Planning Coordinator shall, at least once each calendar year, provide notification of each generator, transformer, and transmission line BES Element in its area that meets one or more of the following criteria, if any, to the respective Generator Owner and Transmission Owner: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning]Criteria:1. Generator(s) where an angular stability constraint, identified in Planning Assessments of the Near-Term Transmission Planning Horizon for a planning event, that is addressed by limiting the output of a generator or a Remedial Action Scheme (RAS), and those Elements terminating at the Transmission station associated with the generator(s).2. Elements associated with angular instability identified in Planning Assessments of the Near-Term Transmission Planning Horizon for a planning event.3. An Element that forms the boundary of an island in the most recent underfrequency load shedding (UFLS) design assessment based on application of the Planning Coordinator’s criteria for identifying islands, only if the island is formed by tripping the Element due to angular instability.4. An Element identified in the most recent annual Planning Assessment of the Near-Term Transmission Planning Horizon where relay tripping occurs due to a stable or unstable2 power swing during a simulated disturbance for a planning event. | MEDIUM | Effective | 2024-04-01 |  | TO, PC, GO
PRC-026-2 | Relay Performance During Stable Power Swings | R2. | Each Generator Owner and Transmission Owner shall: [Violation Risk Factor: High] [Time Horizon: Operations Planning] | HIGH | Effective | 2024-04-01 |  | TO, PC, GO
PRC-026-2 | Relay Performance During Stable Power Swings | R2.1. | Within 12 full calendar months of notification of a BES Element pursuant to Requirement R1, determine whether its load-responsive protective relay(s) applied to that BES Element meets the criteria in PRC-026-2 – Attachment B where an evaluation of that Element’s load-responsive protective relay(s) based on PRC-026-2 – Attachment B criteria has not been performed in the last five calendar years. | HIGH | Effective | 2024-04-01 |  | TO, PC, GO
PRC-026-2 | Relay Performance During Stable Power Swings | R2.2. | Within 12 full calendar months of becoming aware4 of a generator, transformer, or transmission line BES Element that tripped in response to a stable or unstable5 power swing due to the operation of its protective relay(s), determine whether its load-responsive protective relay(s) applied to that BES Element meets the criteria in PRC-026-2 – Attachment B. | HIGH | Effective | 2024-04-01 |  | TO, PC, GO
PRC-026-2 | Relay Performance During Stable Power Swings | R3. | Each Generator Owner and Transmission Owner shall, within six full calendar months of determining a load-responsive protective relay does not meet the PRC-026-2 – Attachment B criteria pursuant to Requirement R2, develop a Corrective Action Plan (CAP) to meet one of the following: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning]• The Protection System meets the PRC-026-2 – Attachment B criteria, while maintaining dependable fault detection and dependable out-of-step tripping (if out-of-step tripping is applied at the terminal of the BES Element); or• The Protection System is excluded under the PRC-026-2 – Attachment A criteria (e.g., modifying the Protection System so that relay functions are supervised by power swing blocking or using relay systems that are immune to power swings), while maintaining dependable fault detection and dependable out-of-step tripping (if out-of-step tripping is applied at the terminal of the BES Element). | MEDIUM | Effective | 2024-04-01 |  | TO, PC, GO
PRC-026-2 | Relay Performance During Stable Power Swings | R4. | Each Generator Owner and Transmission Owner shall implement each CAP developed pursuant to Requirement R3 and update each CAP if actions or timetables change until all actions are complete. [Violation Risk Factor: Medium][Time Horizon: Long-Term Planning] | MEDIUM | Effective | 2024-04-01 |  | TO, PC, GO
PRC-027-1 | Coordination of Protection Systems for Performance During Faults | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a process for developing new and revised Protection System settings for BES Elements, such that the Protection Systems operate in the intended sequence during Faults. The process shall include: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2021-04-01 |  | TO, GO, DP
PRC-027-1 | Coordination of Protection Systems for Performance During Faults | R1.1. | A review and update of short-circuit model data for the BES Elements under study. | MEDIUM | Effective | 2021-04-01 |  | TO, GO, DP
PRC-027-1 | Coordination of Protection Systems for Performance During Faults | R1.2. | A review of the developed Protection System settings. | MEDIUM | Effective | 2021-04-01 |  | TO, GO, DP
PRC-027-1 | Coordination of Protection Systems for Performance During Faults | R1.3. | For Protection System settings applied on BES Elements that electrically join Facilities owned by separate functional entities (Transmission Owners, Generator Owners, and Distribution Providers), provisions to: | MEDIUM | Effective | 2021-04-01 |  | TO, GO, DP
PRC-027-1 | Coordination of Protection Systems for Performance During Faults | R1.3.1. | Provide the proposed Protection System settings to the owner(s) of the electrically joined Facilities. | MEDIUM | Effective | 2021-04-01 |  | TO, GO, DP
PRC-027-1 | Coordination of Protection Systems for Performance During Faults | R1.3.2. | Respond to any owner(s) that provided its proposed Protection System settings pursuant to Requirement R1, Part 1.3.1 by identifying any coordination issue(s) or affirming that no coordination issue(s) were identified. | MEDIUM | Effective | 2021-04-01 |  | TO, GO, DP
PRC-027-1 | Coordination of Protection Systems for Performance During Faults | R1.3.3. | Verify that identified coordination issue(s) associated with the proposed Protection System settings for the associated BES Elements are addressed prior to implementation. | MEDIUM | Effective | 2021-04-01 |  | TO, GO, DP
PRC-027-1 | Coordination of Protection Systems for Performance During Faults | R1.3.4. | Communicate with the other owner(s) of the electrically joined Facilities regarding revised Protection System settings resulting from unforeseen circumstances that arise during implementation or commissioning, Misoperation investigations, maintenance activities, or emergency replacements required as a result of Protection System component failure. | MEDIUM | Effective | 2021-04-01 |  | TO, GO, DP
PRC-027-1 | Coordination of Protection Systems for Performance During Faults | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider shall, for each BES Element with Protection System functions identified in Attachment A: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] ● Option 1: Perform a Protection System Coordination Study in a time interval not to exceed six-calendar years; or ● Option 2: Compare present Fault current values to an established Fault current baseline and perform a Protection System Coordination Study when the comparison identifies a 15 percent or greater deviation in Fault current values (either three phase or phase to ground) at a bus to which the BES Element is connected, all in a time interval not to exceed six-calendar years;1 or, ● Option 3: Use a combination of the above. | MEDIUM | Effective | 2021-04-01 |  | TO, GO, DP
PRC-027-1 | Coordination of Protection Systems for Performance During Faults | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider shall utilize its process established in Requirement R1 to develop new and revised Protection System settings for BES Elements. [Violation Risk Factor: High] [Time Horizon: Operations Planning] | MEDIUM | Effective | 2021-04-01 |  | TO, GO, DP
TOP-001-1a | Reliability Responsibilities and Authorities | R1. | Each Transmission Operator shall have the responsibility and clear decision-making authority to take whatever actions are needed to ensure the reliability of its area and shall exercise specific authority to alleviate operating emergencies. | HIGH | Retired | 2011-11-21 | 2017-03-31 | TOP
TOP-001-1a | Reliability Responsibilities and Authorities | R2. | Each Transmission Operator shall take immediate actions to alleviate operating emergencies including curtailing transmission service or energy schedules, operating equipment (e.g., generators, phase shifters, breakers), shedding firm load, etc. | HIGH | Retired | 2011-11-21 | 2017-03-31 | TOP
TOP-001-1a | Reliability Responsibilities and Authorities | R3. | Each Transmission Operator, Balancing Authority, and Generator Operator shall comply with reliability directives issued by the Reliability Coordinator, and each Balancing Authority and Generator Operator shall comply with reliability directives issued by the Transmission Operator, unless such actions would violate safety, equipment, regulatory or statutory requirements. Under these circumstances the Transmission Operator, Balancing Authority, or Generator Operator shall immediately inform the Reliability Coordinator or Transmission Operator of the inability to perform the directive so that the Reliability Coordinator or Transmission Operator can implement alternate remedial actions. | HIGH | Retired | 2011-11-21 | 2017-03-31 | TOP, GOP, BA
TOP-001-1a | Reliability Responsibilities and Authorities | R4. | Each Distribution Provider and Load-Serving Entity shall comply with all reliability directives issued by the Transmission Operator, including shedding firm load, unless such actions would violate safety, equipment, regulatory or statutory requirements. Under these circumstances, the Distribution Provider or Load-Serving Entity shall immediately inform the Transmission Operator of the inability to perform the directive so that the Transmission Operator can implement alternate remedial actions. | HIGH | Retired | 2011-11-21 | 2017-03-31 | DP
TOP-001-1a | Reliability Responsibilities and Authorities | R5. | Each Transmission Operator shall inform its Reliability Coordinator and any other potentially affected Transmission Operators of real-time or anticipated emergency conditions, and take actions to avoid, when possible, or mitigate the emergency. | HIGH | Retired | 2011-11-21 | 2017-03-31 | TOP
TOP-001-1a | Reliability Responsibilities and Authorities | R6. | Each Transmission Operator, Balancing Authority, and Generator Operator shall render all available emergency assistance to others as requested, provided that the requesting entity has implemented its comparable emergency procedures, unless such actions would violate safety, equipment, or regulatory or statutory requirements. | HIGH | Retired | 2011-11-21 | 2017-03-31 | TOP, GOP, BA
TOP-001-1a | Reliability Responsibilities and Authorities | R7. | Each Transmission Operator and Generator Operator shall not remove Bulk Electric System facilities from service if removing those facilities would burden neighboring systems unless: | HIGH | Retired | 2011-11-21 | 2017-03-31 | TOP, GOP
TOP-001-1a | Reliability Responsibilities and Authorities | R7.1. | For a generator outage, the Generator Operator shall notify and coordinate with the Transmission Operator. The Transmission Operator shall notify the Reliability Coordinator and other affected Transmission Operators, and coordinate the impact of removing the Bulk Electric System facility. | HIGH | Retired | 2011-11-21 | 2017-03-31 | TOP, GOP
TOP-001-1a | Reliability Responsibilities and Authorities | R7.2. | For a transmission facility, the Transmission Operator shall notify and coordinate with its Reliability Coordinator. The Transmission Operator shall notify other affected Transmission Operators, and coordinate the impact of removing the Bulk Electric System facility. | HIGH | Retired | 2011-11-21 | 2017-03-31 | TOP
TOP-001-1a | Reliability Responsibilities and Authorities | R7.3. | When time does not permit such notifications and coordination, or when immediate action is required to prevent a hazard to the public, lengthy customer service interruption, or damage to facilities, the Generator Operator shall notify the Transmission Operator, and the Transmission Operator shall notify its Reliability Coordinator and adjacent Transmission Operators, at the earliest possible time. | HIGH | Retired | 2011-11-21 | 2017-03-31 | TOP, GOP
TOP-001-1a | Reliability Responsibilities and Authorities | R8. | During a system emergency, the Balancing Authority and Transmission Operator shall immediately take action to restore the Real and Reactive Power Balance. If the Balancing Authority or Transmission Operator is unable to restore Real and Reactive Power Balance it shall request emergency assistance from the Reliability Coordinator. If corrective action or emergency assistance is not adequate to mitigate the Real and Reactive Power Balance, then the Reliability Coordinator, Balancing Authority, and Transmission Operator shall implement firm load shedding. | HIGH | Retired | 2011-11-21 | 2017-03-31 | TOP, BA
TOP-001-2 | Transmission Operations | R1. | Each Balancing Authority, Generator Operator, Distribution Provider, and Load-Serving Entity shall comply with each Reliability Directive issued and identified as such by its Transmission Operator(s), unless such action would violate safety, equipment, regulatory, or statutory requirements. | HIGH | Never Came Into Effect in Ontario |  |  | TOP, GOP, DP, BA
TOP-001-2 | Transmission Operations | R10. | Each Transmission Operator shall inform its Reliability Coordinator of its actions to return the system to within limits when an IROL, or an SOL identified in Requirement R8, has been exceeded. | MEDIUM | Never Came Into Effect in Ontario |  |  | TOP, RC
TOP-001-2 | Transmission Operations | R11. | Each Transmission Operator shall act or direct others to act, to mitigate both the magnitude and duration of exceeding an IROL within the IROL’s Tv, or of an SOL identified in Requirement R8. | HIGH | Never Came Into Effect in Ontario |  |  | TOP
TOP-001-2 | Transmission Operations | R2. | Each Balancing Authority, Generator Operator, Distribution Provider, and Load-Serving Entity shall inform its Transmission Operator of its inability to perform an identified Reliability Directive issued by that Transmission Operator. | HIGH | Never Came Into Effect in Ontario |  |  | TOP, GOP, DP, BA
TOP-001-2 | Transmission Operations | R3. | Each Transmission Operator shall inform its Reliability Coordinator and Transmission Operator(s) that are known or expected to be affected by each actual and anticipated Emergency based on its assessment of its Operational Planning Analysis. | HIGH | Never Came Into Effect in Ontario |  |  | TOP, RC
TOP-001-2 | Transmission Operations | R4. | Each Transmission Operator shall render emergency assistance to other Transmission Operators, as requested and available, provided that the requesting entity has implemented its comparable emergency procedures, unless such actions would violate safety, equipment, regulatory, or statutory requirements. | HIGH | Never Came Into Effect in Ontario
TOP-001-2 | Transmission Operations | R5. | Each Transmission Operator shall inform its Reliability Coordinator and other Transmission Operators of its operations known or expected to result in an Adverse Reliability Impact on those respective Transmission Operator Areas unless conditions do not permit such communications. Examples of such operations are relay or equipment failures, and changes in generation, Transmission, or Load. | HIGH | Never Came Into Effect in Ontario |  |  | TOP, RC
TOP-001-2 | Transmission Operations | R6. | Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator and negatively impacted interconnected NERC registered entities of planned outages of telemetering equipment, control equipment and associated communication channels between the affected entities. | MEDIUM | Never Came Into Effect in Ontario |  |  | TOP, RC, BA
TOP-001-2 | Transmission Operations | R7. | Each Transmission Operator shall not operate outside any identified Interconnection Reliability Operating Limit (IROL) for a continuous duration exceeding its associated IROL Tv. | HIGH | Never Came Into Effect in Ontario |  |  | TOP
TOP-001-2 | Transmission Operations | R7.1. | For a generator outage, the Generator Operator shall notify and coordinate with the Transmission Operator. The Transmission Operator shall notify the Reliability Coordinator and other affected Transmission Operators, and coordinate the impact of removing the Bulk Electric System facility. | HIGH | Never Came Into Effect in Ontario |  |  | TOP, RC, GOP
TOP-001-2 | Transmission Operations | R8. | Each Transmission Operator shall inform its Reliability Coordinator of each SOL which, while not an IROL, has been identified by the Transmission Operator as supporting reliability internal to its Transmission Operator Area based on its assessment of its Operational Planning Analysis. | MEDIUM | Never Came Into Effect in Ontario |  |  | TOP, RC
TOP-001-2 | Transmission Operations | R9. | Each Transmission Operator shall not operate outside any System Operating Limit (SOL) identified in Requirement R8 for a continuous duration that would cause a violation of the Facility Rating or Stability criteria upon which it is based. | MEDIUM | Never Came Into Effect in Ontario |  |  | TOP
TOP-001-3 | Transmission Operations | R1. | Each Transmission Operator shall act to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. [Violation Risk Factor: High][Time Horizon: Same-Day Operations, Real-time Operations] | HIGH | Retired | 2017-04-01 | 2018-09-30 | TOP
TOP-001-3 | Transmission Operations | R10. | Each Transmission Operator shall perform the following as necessary for determining System Operating Limit (SOL) exceedances within its Transmission Operator Area: [Violation Risk Factor: High] [Time Horizon: Real-Time Operations] | HIGH | Retired | 2017-04-01 | 2018-09-30 | TOP
TOP-001-3 | Transmission Operations | R10.1. | Within its Transmission Operator Area, monitor Facilities and the status of Special Protection Systems, and | HIGH | Retired | 2017-04-01 | 2018-09-30 | TOP
TOP-001-3 | Transmission Operations | R10.2. | Outside its Transmission Operator Area, obtain and utilize status, voltages, and flow data for Facilities and the status of Special Protection Systems. | HIGH | Retired | 2017-04-01 | 2018-09-30 | TOP
TOP-001-3 | Transmission Operations | R11. | Each Balancing Authority shall monitor its Balancing Authority Area, including the status of Special Protection Systems that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. [Violation Risk Factor: High] [Time Horizon: Real- Time Operations] | HIGH | Retired | 2017-04-01 | 2018-09-30 | BA
TOP-001-3 | Transmission Operations | R12. | Each Transmission Operator shall not operate outside any identified Interconnection Reliability Operating Limit (IROL) for a continuous duration exceeding its associated IROL Tv. [Violation Risk Factor: High] [Time Horizon: Real-time Operations] | HIGH | Retired | 2017-04-01 | 2018-09-30 | TOP
TOP-001-3 | Transmission Operations | R13. | Each Transmission Operator shall ensure that a Real-time Assessment is performed at least once every 30 minutes. [Violation Risk Factor: High] [Time Horizon: Real-time Operations] | HIGH | Retired | 2017-04-01 | 2018-09-30 | TOP
TOP-001-3 | Transmission Operations | R14. | Each Transmission Operator shall initiate its Operating Plan to mitigate a SOL exceedance identified as part of its Real-time monitoring or Real-time Assessment. [Violation Risk Factor: High] [Time Horizon: Real-time Operations] | HIGH | Retired | 2017-04-01 | 2018-09-30 | TOP
TOP-001-3 | Transmission Operations | R15. | Each Transmission Operator shall inform its Reliability Coordinator of actions taken to return the System to within limits when a SOL has been exceeded. [Violation Risk Factor: Medium] [Time Horizon: Real-Time Operations] | MEDIUM | Retired | 2017-04-01 | 2018-09-30 | TOP
TOP-001-3 | Transmission Operations | R16. | Each Transmission Operator shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. [Violation Risk Factor: High] [Time Horizon: Operations Planning, Same-Day Operations, Real-time Operations] | HIGH | Retired | 2017-04-01 | 2018-09-30 | TOP
TOP-001-3 | Transmission Operations | R17. | Each Balancing Authority shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. [Violation Risk Factor: High] [Time Horizon: Operations Planning, Same-Day Operations, Real-time Operations] | HIGH | Retired | 2017-04-01 | 2018-09-30 | BA
TOP-001-3 | Transmission Operations | R18. | Each Transmission Operator shall operate to the most limiting parameter in instances where there is a difference in SOLs. [Violation Risk Factor: High] [Time Horizon: Operations Planning, Same-Day Operations, Real-time Operations] | HIGH | Retired | 2017-04-01 | 2018-09-30 | TOP
TOP-001-3 | Transmission Operations | R19. | Each Transmission Operator shall have data exchange capabilities with the entities that it has identified that it needs data from in order to maintain reliability in its Transmission Operator Area. [Violation Risk Factor: High] [Time Horizon: Operations Planning, Same-Day Operations, Real-time Operations] | HIGH | Retired | 2017-04-01 | 2018-09-30 | TOP
TOP-001-3 | Transmission Operations | R2. | Each Balancing Authority shall act to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. [Violation Risk Factor: High][Time Horizon: Same-Day Operations, Real-time Operations] | HIGH | Retired | 2017-04-01 | 2018-09-30 | BA
TOP-001-3 | Transmission Operations | R20. | Each Balancing Authority shall have data exchange capabilities with the entities that it has identified that it needs data from in order to maintain reliability in its Balancing Authority Area. [Violation Risk Factor: High] [Time Horizon: Operations Planning, Same-Day Operations, Real-time Operations] | HIGH | Retired | 2017-04-01 | 2018-09-30 | BA
TOP-001-3 | Transmission Operations | R3. | Each Balancing Authority, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Transmission Operator(s), unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. [Violation Risk Factor: High] [Time Horizon: Same-Day Operations, Real-Time Operations] | HIGH | Retired | 2017-04-01 | 2018-09-30 | GOP, DP, BA
TOP-001-3 | Transmission Operations | R4. | Each Balancing Authority, Generator Operator, and Distribution Provider shall inform its Transmission Operator of its inability to comply with an Operating Instruction issued by its Transmission Operator. [Violation Risk Factor: High] [Time Horizon: Same-Day Operations, Real-Time Operations] | HIGH | Retired | 2017-04-01 | 2018-09-30 | GOP, DP, BA
TOP-001-3 | Transmission Operations | R5. | Each Transmission Operator, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Balancing Authority, unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. [Violation Risk Factor: High] [Time Horizon: Same-Day Operations, Real-Time Operations] | HIGH | Retired | 2017-04-01 | 2018-09-30 | TOP, GOP, DP
TOP-001-3 | Transmission Operations | R6. | Each Transmission Operator, Generator Operator, and Distribution Provider shall inform its Balancing Authority of its inability to comply with an Operating Instruction issued by its Balancing Authority. [Violation Risk Factor: High] [Time Horizon: Same- Day Operations, Real-Time Operations] | HIGH | Retired | 2017-04-01 | 2018-09-30 | TOP, GOP, DP
TOP-001-3 | Transmission Operations | R7. | Each Transmission Operator shall assist other Transmission Operators within its Reliability Coordinator Area, if requested and able, provided that the requesting Transmission Operator has implemented its comparable Emergency procedures, unless such assistance cannot be physically implemented or would violate safety, equipment, regulatory, or statutory requirements. [Violation Risk Factor: High] [Time Horizon: Real-Time Operations] | HIGH | Retired | 2017-04-01 | 2018-09-30 | TOP
TOP-001-3 | Transmission Operations | R8. | Each Transmission Operator shall inform its Reliability Coordinator, known impacted Balancing Authorities, and known impacted Transmission Operators of its actual or expected operations that result in, or could result in, an Emergency. [Violation Risk Factor: High] [Time Horizon: Operations Planning, Same-Day Operations, Real-Time Operations] | HIGH | Retired | 2017-04-01 | 2018-09-30 | TOP
TOP-001-3 | Transmission Operations | R9. | Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between the affected entities. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning, Same-Day Operations, Real-Time Operations] | MEDIUM | Retired | 2017-04-01 | 2018-09-30 | TOP, BA
TOP-001-4 | Transmission Operations | R1. | Each Transmission Operator shall act to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. [Violation Risk Factor: High][Time Horizon: Same-Day Operations, Real-time Operations] | HIGH | Effective | 2018-10-01 |  | TOP
TOP-001-4 | Transmission Operations | R10. | Each Transmission Operator shall perform the following for determining System Operating Limit (SOL) exceedances within its Transmission Operator Area: [Violation Risk Factor: High] [Time Horizon: Real-Time Operations] | HIGH | Effective | 2018-10-01 |  | TOP
TOP-001-4 | Transmission Operations | R10.1. | Monitor Facilities within its Transmission Operator Area; | HIGH | Effective | 2018-10-01 |  | TOP
TOP-001-4 | Transmission Operations | R10.2. | Monitor the status of Remedial Action Schemes within its Transmission Operator Area; | HIGH | Effective | 2018-10-01 |  | TOP
TOP-001-4 | Transmission Operations | R10.3. | Monitor non-BES facilities within its Transmission Operator Area identified as necessary by the Transmission Operator; | HIGH | Effective | 2018-10-01 |  | TOP
TOP-001-4 | Transmission Operations | R10.4. | Obtain and utilize status, voltages, and flow data for Facilities outside its Transmission Operator Area identified as necessary by the Transmission Operator; | HIGH | Effective | 2018-10-01 |  | TOP
TOP-001-4 | Transmission Operations | R10.5. | Obtain and utilize the status of Remedial Action Schemes outside its Transmission Operator Area identified as necessary by the Transmission Operator; and | HIGH | Effective | 2018-10-01 |  | TOP
TOP-001-4 | Transmission Operations | R10.6. | Obtain and utilize status, voltages, and flow data for non-BES facilities outside its Transmission Operator Area identified as necessary by the Transmission Operator. | HIGH | Effective | 2018-10-01 |  | TOP
TOP-001-4 | Transmission Operations | R11. | Each Balancing Authority shall monitor its Balancing Authority Area, including the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. [Violation Risk Factor: High] [Time Horizon: Real-Time Operations] | HIGH | Effective | 2018-10-01 |  | BA
TOP-001-4 | Transmission Operations | R12. | Each Transmission Operator shall not operate outside any identified Interconnection Reliability Operating Limit (IROL) for a continuous duration exceeding its associated IROL Tv. [Violation Risk Factor: High] [Time Horizon: Real-time Operations] | HIGH | Effective | 2018-10-01 |  | TOP
TOP-001-4 | Transmission Operations | R13. | Each Transmission Operator shall ensure that a Real-time Assessment is performed at least once every 30 minutes. [Violation Risk Factor: High] [Time Horizon: Real-time Operations] | HIGH | Effective | 2018-10-01 |  | TOP
TOP-001-4 | Transmission Operations | R14. | Each Transmission Operator shall initiate its Operating Plan to mitigate a SOL exceedance identified as part of its Real-time monitoring or Real-time Assessment. [Violation Risk Factor: High] [Time Horizon: Real-time Operations] | HIGH | Effective | 2018-10-01 |  | TOP
TOP-001-4 | Transmission Operations | R15. | Each Transmission Operator shall inform its Reliability Coordinator of actions taken to return the System to within limits when a SOL has been exceeded. [Violation Risk Factor: Medium] [Time Horizon: Real-Time Operations] | MEDIUM | Effective | 2018-10-01 |  | TOP
TOP-001-4 | Transmission Operations | R16. | Each Transmission Operator shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. [Violation Risk Factor: High] [Time Horizon: Operations Planning, Same-Day Operations, Real-time Operations] | HIGH | Effective | 2018-10-01 |  | TOP
TOP-001-4 | Transmission Operations | R17. | Each Balancing Authority shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. [Violation Risk Factor: High] [Time Horizon: Operations Planning, Same-Day Operations, Real-time Operations] | HIGH | Effective | 2018-10-01 |  | BA
TOP-001-4 | Transmission Operations | R18. | Each Transmission Operator shall operate to the most limiting parameter in instances where there is a difference in SOLs. [Violation Risk Factor: High] [Time Horizon: Operations Planning, Same-Day Operations, Real-time Operations] | HIGH | Effective | 2018-10-01 |  | TOP
TOP-001-4 | Transmission Operations | R19. | Each Transmission Operator shall have data exchange capabilities with the entities it has identified it needs data from in order to perform its Operational Planning Analyses. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Effective | 2018-10-01 |  | TOP
TOP-001-4 | Transmission Operations | R2. | Each Balancing Authority shall act to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. [Violation Risk Factor: High][Time Horizon: Same-Day Operations, Real-time Operations] | HIGH | Effective | 2018-10-01 |  | BA
TOP-001-4 | Transmission Operations | R20. | Each Transmission Operator shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Balancing Authority, and the entities it has identified it needs data from in order for it to perform its Real-time monitoring and Real-time Assessments. [Violation Risk Factor: High] [Time Horizon: Same-Day Operations, Real-time Operations] | HIGH | Effective | 2018-10-01 |  | TOP
TOP-001-4 | Transmission Operations | R21. | Each Transmission Operator shall test its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Transmission Operator shall initiate action within two hours to restore redundant functionality. [Violation Risk Factor: Medium ] [Time Horizon: Operations Planning] | MEDIUM | Effective | 2018-10-01 |  | TOP
TOP-001-4 | Transmission Operations | R22. | Each Balancing Authority shall have data exchange capabilities with the entities it has identified it needs data from in order to develop its Operating Plan for next-day operations. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Effective | 2018-10-01 |  | BA
TOP-001-4 | Transmission Operations | R23. | Each Balancing Authority shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Transmission Operator, and the entities it has identified it needs data from in order for it to perform its Real-time monitoring and analysis functions. [Violation Risk Factor: High] [Time Horizon: Same-Day Operations, Real-time Operations] | HIGH | Effective | 2018-10-01 |  | BA
TOP-001-4 | Transmission Operations | R24. | Each Balancing Authority shall test its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Balancing Authority shall initiate action within two hours to restore redundant functionality. [Violation Risk Factor: Medium ] [Time Horizon: Operations Planning] | MEDIUM | Effective | 2018-10-01 |  | BA
TOP-001-4 | Transmission Operations | R3. | Each Balancing Authority, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Transmission Operator(s), unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. [Violation Risk Factor: High] [Time Horizon: Same-Day Operations, Real-Time Operations] | HIGH | Effective | 2018-10-01 |  | GOP, DP, BA
TOP-001-4 | Transmission Operations | R4. | Each Balancing Authority, Generator Operator, and Distribution Provider shall inform its Transmission Operator of its inability to comply with an Operating Instruction issued by its Transmission Operator. [Violation Risk Factor: High] [Time Horizon: Same-Day Operations, Real-Time Operations] | HIGH | Effective | 2018-10-01 |  | GOP, DP, BA
TOP-001-4 | Transmission Operations | R5. | Each Transmission Operator, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Balancing Authority, unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. [Violation Risk Factor: High] [Time Horizon: Same-Day Operations, Real-Time Operations] | HIGH | Effective | 2018-10-01 |  | TOP, GOP, DP
TOP-001-4 | Transmission Operations | R6. | Each Transmission Operator, Generator Operator, and Distribution Provider shall inform its Balancing Authority of its inability to comply with an Operating Instruction issued by its Balancing Authority. [Violation Risk Factor: High] [Time Horizon: Same-Day Operations, Real-Time Operations] | HIGH | Effective | 2018-10-01 |  | TOP, GOP, DP
TOP-001-4 | Transmission Operations | R7. | Each Transmission Operator shall assist other Transmission Operators within its Reliability Coordinator Area, if requested and able, provided that the requesting Transmission Operator has implemented its comparable Emergency procedures, unless such assistance cannot be physically implemented or would violate safety, equipment, regulatory, or statutory requirements. [Violation Risk Factor: High] [Time Horizon: Real-Time Operations] | HIGH | Effective | 2018-10-01 |  | TOP
TOP-001-4 | Transmission Operations | R8. | Each Transmission Operator shall inform its Reliability Coordinator, known impacted Balancing Authorities, and known impacted Transmission Operators of its actual or expected operations that result in, or could result in, an Emergency. [Violation Risk Factor: High] [Time Horizon: Operations Planning, Same-Day Operations, Real-Time Operations] | HIGH | Effective | 2018-10-01 |  | TOP
TOP-001-4 | Transmission Operations | R9. | Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between the affected entities. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning, Same-Day Operations, Real-Time Operations] | MEDIUM | Effective | 2018-10-01 |  | TOP, BA
TOP-001-5 | Transmission Operations | R1. | Each Transmission Operator shall act to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. [Violation Risk Factor: High][Time Horizon: Same‐Day Operations, Real‐time Operations] | HIGH | Effective | 2021-04-01 |  | GOP, DP, BA, TOP
TOP-001-5 | Transmission Operations | R10. | Each Transmission Operator shall perform the following for determining System Operating Limit (SOL) exceedances within its Transmission Operator Area: [Violation Risk Factor: High] [Time Horizon: Real‐Time Operations] | HIGH | Effective | 2021-04-01 |  | TOP, GOP, DP, BA
TOP-001-5 | Transmission Operations | R10.1. | Monitor Facilities within its Transmission Operator Area; | HIGH | Effective | 2021-04-01 |  | TOP, GOP, DP, BA
TOP-001-5 | Transmission Operations | R10.2. | Monitor the status of Remedial Action Schemes within its Transmission Operator Area; | HIGH | Effective | 2021-04-01 |  | TOP, GOP, DP, BA
TOP-001-5 | Transmission Operations | R10.3. | Monitor non‐BES facilities within its Transmission Operator Area identified as necessary by the Transmission Operator; | HIGH | Effective | 2021-04-01 |  | TOP, GOP, DP, BA
TOP-001-5 | Transmission Operations | R10.4. | Obtain and utilize status, voltages, and flow data for Facilities outside its Transmission Operator Area identified as necessary by the Transmission Operator; | HIGH | Effective | 2021-04-01 |  | TOP, GOP, DP, BA
TOP-001-5 | Transmission Operations | R10.5. | Obtain and utilize the status of Remedial Action Schemes outside its Transmission Operator Area identified as necessary by the Transmission Operator; and | HIGH | Effective | 2021-04-01 |  | TOP, GOP, DP, BA
TOP-001-5 | Transmission Operations | R10.6. | Obtain and utilize status, voltages, and flow data for non‐BES facilities outside its Transmission Operator Area identified as necessary by the Transmission Operator | HIGH | Effective | 2021-04-01 |  | TOP, GOP, DP, BA
TOP-001-5 | Transmission Operations | R11. | Each Balancing Authority shall monitor its Balancing Authority Area, including the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation‐Load‐interchange balance within its Balancing Authority Area and support Interconnection frequency. [Violation Risk Factor: High] [Time Horizon: Real‐Time Operations] | HIGH | Effective | 2021-04-01 |  | TOP, GOP, DP, BA
TOP-001-5 | Transmission Operations | R12. | Each Transmission Operator shall not operate outside any identified Interconnection Reliability Operating Limit (IROL) for a continuous duration exceeding its associated IROL Tv. [Violation Risk Factor: High] [Time Horizon: Real‐time Operations] | HIGH | Effective | 2021-04-01 |  | TOP, GOP, DP, BA
TOP-001-5 | Transmission Operations | R13. | . Each Transmission Operator shall ensure that a Real‐time Assessment is performed at least once every 30 minutes. [Violation Risk Factor: High] [Time Horizon: Real‐time Operations] | HIGH | Effective | 2021-04-01 |  | TOP, GOP, DP, BA
TOP-001-5 | Transmission Operations | R14. | Each Transmission Operator shall initiate its Operating Plan to mitigate a SOL exceedance identified as part of its Real‐time monitoring or Real‐time Assessment. [Violation Risk Factor: High] [Time Horizon: Real‐time Operations] | HIGH | Effective | 2021-04-01 |  | TOP, GOP, DP, BA
TOP-001-5 | Transmission Operations | R15. | Each Transmission Operator shall inform its Reliability Coordinator of actions taken to return the System to within limits when a SOL has been exceeded. [Violation Risk Factor: Medium] [Time Horizon: Real‐Time Operations] | MEDIUM | Effective | 2021-04-01 |  | TOP, GOP, DP, BA
TOP-001-5 | Transmission Operations | R16. | Each Transmission Operator shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. [Violation Risk Factor: High] [Time Horizon: Operations Planning, Same‐Day Operations, Real‐time Operations] | HIGH | Effective | 2021-04-01 |  | TOP, GOP, DP, BA
TOP-001-5 | Transmission Operations | R17. | Each Balancing Authority shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. [Violation Risk Factor: High] [Time Horizon: Operations Planning, Same‐Day Operations, Real‐time Operations] | HIGH | Effective | 2021-04-01 |  | TOP, GOP, DP, BA
TOP-001-5 | Transmission Operations | R18. | Each Transmission Operator shall operate to the most limiting parameter in instances where there is a difference in SOLs. [Violation Risk Factor: High] [Time Horizon: Operations Planning, Same‐Day Operations, Real‐time Operations] | HIGH | Effective | 2021-04-01 |  | TOP, GOP, DP, BA
TOP-001-5 | Transmission Operations | R19. | Reserved. | MEDIUM | Effective | 2021-04-01 |  | TOP, GOP, DP, BA
TOP-001-5 | Transmission Operations | R2. | Each Balancing Authority shall act to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. [Violation Risk Factor: High][Time Horizon: Same‐Day Operations, Real‐time Operations] | HIGH | Effective | 2021-04-01 |  | TOP, GOP, DP, BA
TOP-001-5 | Transmission Operations | R20. | Each Transmission Operator shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, for the exchange of Real‐time data with its Reliability Coordinator, Balancing Authority, and the entities it has identified it needs data from in order for it to perform its Real‐time monitoring and Real‐time Assessments. [Violation Risk Factor: High] [Time Horizon: Same‐Day Operations, Real‐time Operations] | HIGH | Effective | 2021-04-01 |  | TOP, GOP, DP, BA
TOP-001-5 | Transmission Operations | R21. | Each Transmission Operator shall test its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Transmission Operator shall initiate action within two hours to restore redundant functionality. [Violation Risk Factor: Medium ] [Time Horizon: Operations Planning] | MEDIUM | Effective | 2021-04-01 |  | TOP, GOP, DP, BA
TOP-001-5 | Transmission Operations | R22. | Reserved. | MEDIUM | Effective | 2021-04-01 |  | TOP, GOP, DP, BA
TOP-001-5 | Transmission Operations | R23. | Each Balancing Authority shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, for the exchange of Real‐time data with its Reliability Coordinator, Transmission Operator, and the entities it has identified it needs data from in order for it to perform its Real‐time monitoring and analysis functions. [Violation Risk Factor: High] [Time Horizon: Same‐Day Operations, Real‐time Operations] | HIGH | Effective | 2021-04-01 |  | TOP, GOP, DP, BA
TOP-001-5 | Transmission Operations | R24. | Each Balancing Authority shall test its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Balancing Authority shall initiate action within two hours to restore redundant functionality. [Violation Risk Factor: Medium ] [Time Horizon: Operations Planning] | HIGH | Effective | 2021-04-01 |  | TOP, GOP, DP, BA
TOP-001-5 | Transmission Operations | R3. | Each Balancing Authority, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Transmission Operator(s), unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. [Violation Risk Factor: High] [Time Horizon: Same‐Day Operations, Real‐Time Operations] recipient shall sign the NERC Confidentiality Agreement for “Electric System Reliability Data.” | HIGH | Effective | 2021-04-01 |  | TOP, GOP, DP, BA
TOP-001-5 | Transmission Operations | R4. | Each Balancing Authority, Generator Operator, and Distribution Provider shall inform its Transmission Operator of its inability to comply with an Operating Instruction issued by its Transmission Operator. [Violation Risk Factor: High] [Time Horizon: Same‐Day Operations, Real‐Time Operations] | HIGH | Effective | 2021-04-01 |  | TOP, GOP, DP, BA
TOP-001-5 | Transmission Operations | R5. | Each Transmission Operator, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Balancing Authority, unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. [Violation Risk Factor: High] [Time Horizon: Same‐Day Operations, Real‐Time Operations] | HIGH | Effective | 2021-04-01 |  | TOP, GOP, DP, BA
TOP-001-5 | Transmission Operations | R6. | Each Transmission Operator, Generator Operator, and Distribution Provider shall inform its Balancing Authority of its inability to comply with an Operating Instruction issued by its Balancing Authority. [Violation Risk Factor: High] [Time Horizon: Same‐ Day Operations, Real‐Time Operations] | HIGH | Effective | 2021-04-01 |  | TOP, GOP, DP, BA
TOP-001-5 | Transmission Operations | R7. | Each Transmission Operator shall assist other Transmission Operators within its Reliability Coordinator Area, if requested and able, provided that the requesting Transmission Operator has implemented its comparable Emergency procedures, unless such assistance cannot be physically implemented or would violate safety, equipment, regulatory, or statutory requirements. [Violation Risk Factor: High] [Time Horizon: Real‐Time Operations] | HIGH | Effective | 2021-04-01 |  | TOP, GOP, DP, BA
TOP-001-5 | Transmission Operations | R8. | Each Transmission Operator shall inform its Reliability Coordinator, known impacted Balancing Authorities, and known impacted Transmission Operators of its actual or expected operations that result in, or could result in, an Emergency. [Violation Risk Factor: High] [Time Horizon: Operations Planning, Same‐Day Operations, Real‐Time Operations] | HIGH | Effective | 2021-04-01 |  | TOP, GOP, DP, BA
TOP-001-5 | Transmission Operations | R9. | Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between the affected entities. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning, Same‐Day Operations, Real‐Time Operations] | MEDIUM | Effective | 2021-04-01 |  | TOP, GOP, DP, BA
TOP-001-6 | Transmission Operations | R1. | Each Transmission Operator shall act to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. [Violation Risk Factor: High][Time Horizon: Same‐Day Operations, Real‐time Operations] | HIGH | Effective | 2024-04-01 |  | TOP, GOP, DP, BA
TOP-001-6 | Transmission Operations | R10. | Each Transmission Operator shall perform the following for determining System Operating Limit (SOL) exceedances within its Transmission Operator Area: [Violation Risk Factor: High] [Time Horizon: Real‐Time Operations] | HIGH | Effective | 2024-04-01 |  | TOP, GOP, DP, BA
TOP-001-6 | Transmission Operations | R10.1. | Monitor Facilities within its Transmission Operator Area; | HIGH | Effective | 2024-04-01 |  | TOP, GOP, DP, BA
TOP-001-6 | Transmission Operations | R10.2. | Monitor the status of Remedial Action Schemes within its Transmission Operator Area; | HIGH | Effective | 2024-04-01 |  | TOP, GOP, DP, BA
TOP-001-6 | Transmission Operations | R10.3. | Monitor non‐BES facilities within its Transmission Operator Area identified as necessary by the Transmission Operator; | HIGH | Effective | 2024-04-01 |  | TOP, GOP, DP, BA
TOP-001-6 | Transmission Operations | R10.4. | Obtain and utilize status, voltages, and flow data for Facilities outside its Transmission Operator Area identified as necessary by the Transmission Operator; | HIGH | Effective | 2024-04-01 |  | TOP, GOP, DP, BA
TOP-001-6 | Transmission Operations | R10.5. | Obtain and utilize the status of Remedial Action Schemes outside its Transmission Operator Area identified as necessary by the Transmission Operator; and | HIGH | Effective | 2024-04-01 |  | TOP, GOP, DP, BA
TOP-001-6 | Transmission Operations | R10.6. | Obtain and utilize status, voltages, and flow data for non‐BES facilities outside its Transmission Operator Area identified as necessary by the Transmission Operator | HIGH | Effective | 2024-04-01 |  | TOP, GOP, DP, BA
TOP-001-6 | Transmission Operations | R11. | Each Balancing Authority shall monitor its Balancing Authority Area, including the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation‐Load‐interchange balance within its Balancing Authority Area and support I | HIGH | Effective | 2024-04-01 |  | TOP, GOP, DP, BA
TOP-001-6 | Transmission Operations | R12. | Each Transmission Operator shall not operate outside any identified Interconnection Reliability Operating Limit (IROL) for a continuous duration exceeding its associated IROL Tv. [Violation Risk Factor: High] [Time Horizon: Real‐time Operations] | HIGH | Effective | 2024-04-01 |  | TOP, GOP, DP, BA
TOP-001-6 | Transmission Operations | R13. | . Each Transmission Operator shall ensure that a Real‐time Assessment is performed at least once every 30 minutes. [Violation Risk Factor: High] [Time Horizon: Real‐time Operations] | HIGH | Effective | 2024-04-01 |  | TOP, GOP, DP, BA
TOP-001-6 | Transmission Operations | R14. | Each Transmission Operator shall initiate its Operating Plan to mitigate a SOL exceedance identified as part of its Real‐time monitoring or Real‐time Assessment. [Violation Risk Factor: High] [Time Horizon: Real‐time Operations] | HIGH | Effective | 2024-04-01 |  | TOP, GOP, DP, BA
TOP-001-6 | Transmission Operations | R15. | Each Transmission Operator shall inform its Reliability Coordinator of actions taken toreturn the System to within limits when a SOL has been exceeded in accordance with its Reliability Coordinator’s SOL methodology. [Violation Risk Factor: Medium] [Time | MEDIUM | Effective | 2024-04-01 |  | TOP, GOP, DP, BA
TOP-001-6 | Transmission Operations | R16. | Each Transmission Operator shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between af | HIGH | Effective | 2024-04-01 |  | TOP, GOP, DP, BA
TOP-001-6 | Transmission Operations | R17. | Each Balancing Authority shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affe | HIGH | Effective | 2024-04-01 |  | TOP, GOP, DP, BA
TOP-001-6 | Transmission Operations | R18. | Each Transmission Operator shall operate to the most limiting parameter in instances where there is a difference in SOLs. [Violation Risk Factor: High] [Time Horizon: Operations Planning, Same‐Day Operations, Real‐time Operations] | HIGH | Effective | 2024-04-01 |  | TOP, GOP, DP, BA
TOP-001-6 | Transmission Operations | R19. | Reserved. | MEDIUM | Effective | 2024-04-01 |  | TOP, GOP, DP, BA
TOP-001-6 | Transmission Operations | R2. | Each Balancing Authority shall act to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. [Violation Risk Factor: High][Time Horizon: Same‐Day Operations, Real‐time Operations] | HIGH | Effective | 2024-04-01 |  | TOP, GOP, DP, BA
TOP-001-6 | Transmission Operations | R20. | Each Transmission Operator shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, for the exchange of Real‐time data with its Reliability Coordinat | HIGH | Effective | 2024-04-01 |  | TOP, GOP, DP, BA
TOP-001-6 | Transmission Operations | R21. | Each Transmission Operator shall test its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Transmission Operator shall initiat | MEDIUM | Effective | 2024-04-01 |  | TOP, GOP, DP, BA
TOP-001-6 | Transmission Operations | R22. | Reserved. | MEDIUM | Effective | 2024-04-01 |  | TOP, GOP, DP, BA
TOP-001-6 | Transmission Operations | R23. | Each Balancing Authority shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, for the exchange of Real‐time data with its Reliability Coordinator, | HIGH | Effective | 2024-04-01 |  | TOP, GOP, DP, BA
TOP-001-6 | Transmission Operations | R24. | Each Balancing Authority shall test its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Balancing Authority shall initiate ac | HIGH | Effective | 2024-04-01 |  | TOP, GOP, DP, BA
TOP-001-6 | Transmission Operations | R25. | Each Transmission Operator shall use the applicable Reliability Coordinator’s SOL methodology when determining SOL exceedances for Real-time Assessments, Real time monitoring, and Operational Planning Analysis. [Violation Risk Factor: High ] [Time Horizon | HIGH | Effective | 2024-04-01 |  | TOP, GOP, DP, BA
TOP-001-6 | Transmission Operations | R3. | Each Balancing Authority, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Transmission Operator(s), unless such action cannot be physically implemented or it would violate safety, equipment, regulat | HIGH | Effective | 2024-04-01 |  | TOP, GOP, DP, BA
TOP-001-6 | Transmission Operations | R4. | Each Balancing Authority, Generator Operator, and Distribution Provider shall inform its Transmission Operator of its inability to comply with an Operating Instruction issued by its Transmission Operator. [Violation Risk Factor: High] [Time Horizon: Same‐ | HIGH | Effective | 2024-04-01 |  | TOP, GOP, DP, BA
TOP-001-6 | Transmission Operations | R5. | Each Transmission Operator, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Balancing Authority, unless such action cannot be physically implemented or it would violate safety, equipment, regulatory | HIGH | Effective | 2024-04-01 |  | TOP, GOP, DP, BA
TOP-001-6 | Transmission Operations | R6. | Each Transmission Operator, Generator Operator, and Distribution Provider shall inform its Balancing Authority of its inability to comply with an Operating Instruction issued by its Balancing Authority. [Violation Risk Factor: High] [Time Horizon: Same‐ D | HIGH | Effective | 2024-04-01 |  | TOP, GOP, DP, BA
TOP-001-6 | Transmission Operations | R7. | Each Transmission Operator shall assist other Transmission Operators within its Reliability Coordinator Area, if requested and able, provided that the requesting Transmission Operator has implemented its comparable Emergency procedures, unless such assist | HIGH | Effective | 2024-04-01 |  | TOP, GOP, DP, BA
TOP-001-6 | Transmission Operations | R8. | Each Transmission Operator shall inform its Reliability Coordinator, known impacted Balancing Authorities, and known impacted Transmission Operators of its actual or expected operations that result in, or could result in, an Emergency. [Violation Risk | HIGH | Effective | 2024-04-01 |  | TOP, GOP, DP, BA
TOP-001-6 | Transmission Operations | R9. | Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring | MEDIUM | Effective | 2024-04-01 |  | TOP, GOP, DP, BA
TOP-002-2.1b | Normal Operations Planning | R1. | Each Balancing Authority and Transmission Operator shall maintain a set of current plans that are designed to evaluate options and set procedures for reliable operation through a reasonable future time period. In addition, each Balancing Authority and Transmission Operator shall be responsible for using available personnel and system equipment to implement these plans to ensure that interconnected system reliability will be maintained. | MEDIUM | Retired | 2012-10-10 | 2017-03-31 | TOP, BA
TOP-002-2.1b | Normal Operations Planning | R1. | Each Balancing Authority and Transmission Operator shall maintain a set of current plans that are designed to evaluate options and set procedures for reliable operation through a reasonable future time period. In addition, each Balancing Authority and Transmission Operator shall be responsible for using available personnel and system equipment to implement these plans to ensure that interconnected system reliability will be maintained. | MEDIUM | Retired | 2012-10-10 | 2017-03-31 | TOP, BA
TOP-002-2.1b | Normal Operations Planning | R10. | Each Balancing Authority and Transmission Operator shall plan to meet all System Operating Limits (SOLs) and Interconnection Reliability Operating Limits (IROLs). | MEDIUM | Retired | 2012-10-10 | 2017-03-31 | TOP, BA
TOP-002-2.1b | Normal Operations Planning | R10. | Each Balancing Authority and Transmission Operator shall plan to meet all System Operating Limits (SOLs) and Interconnection Reliability Operating Limits (IROLs). | MEDIUM | Retired | 2012-10-10 | 2017-03-31 | TOP, BA
TOP-002-2.1b | Normal Operations Planning | R11. | The Transmission Operator shall perform seasonal, next-day, and current-day Bulk Electric System studies to determine SOLs. Neighboring Transmission Operators shall utilize identical SOLs for common facilities. The Transmission Operator shall update these Bulk Electric System studies as necessary to reflect current system conditions; and shall make the results of Bulk Electric System studies available to the Transmission Operators, Balancing Authorities (subject to confidentiality requirements), and to its Reliability Coordinator. | MEDIUM | Retired | 2012-10-10 | 2017-03-31 | TOP
TOP-002-2.1b | Normal Operations Planning | R11. | The Transmission Operator shall perform seasonal, next-day, and current-day Bulk Electric System studies to determine SOLs. Neighboring Transmission Operators shall utilize identical SOLs for common facilities. The Transmission Operator shall update these Bulk Electric System studies as necessary to reflect current system conditions; and shall make the results of Bulk Electric System studies available to the Transmission Operators, Balancing Authorities (subject to confidentiality requirements), and to its Reliability Coordinator. | MEDIUM | Retired | 2012-10-10 | 2017-03-31 | TOP
TOP-002-2.1b | Normal Operations Planning | R12. | The Transmission Service Provider shall include known SOLs or IROLs within its area and neighboring areas in the determination of transfer capabilities, in accordance with filed tariffs and/or regional Total Transfer Capability and Available Transfer Capability calculation processes. | MEDIUM | Retired | 2012-10-10 | 2017-03-31 | TSP
TOP-002-2.1b | Normal Operations Planning | R12. | The Transmission Service Provider shall include known SOLs or IROLs within its area and neighboring areas in the determination of transfer capabilities, in accordance with filed tariffs and/or regional Total Transfer Capability and Available Transfer Capability calculation processes. | MEDIUM | Retired | 2012-10-10 | 2017-03-31 | TSP
TOP-002-2.1b | Normal Operations Planning | R13. | At the request of the Balancing Authority or Transmission Operator, a Generator Operator shall perform generating real and reactive capability verification that shall include, among other variables, weather, ambient air and water conditions, and fuel quality and quantity, and provide the results to the Balancing Authority or Transmission Operator operating personnel as requested. | MEDIUM | Retired | 2012-10-10 | 2017-03-31 | GOP
TOP-002-2.1b | Normal Operations Planning | R14. | Generator Operators shall, without any intentional time delay, notify their Balancing Authority and Transmission Operator of changes in capabilities and characteristics including but not limited to: | MEDIUM | Retired | 2012-10-10 | 2017-03-31 | GOP
TOP-002-2.1b | Normal Operations Planning | R14.1. | Changes in real output capabilities. | MEDIUM | Retired | 2012-10-10 | 2017-03-31 | GOP
TOP-002-2.1b | Normal Operations Planning | R15. | Generation Operators shall, at the request of the Balancing Authority or Transmission Operator, provide a forecast of expected real power output to assist in operations planning (e.g., a seven-day forecast of real output). | LOWER | Retired | 2012-10-10 | 2017-03-31 | GOP
TOP-002-2.1b | Normal Operations Planning | R16. | Subject to standards of conduct and confidentiality agreements, Transmission Operators shall, without any intentional time delay, notify their Reliability Coordinator and Balancing Authority of changes in capabilities and characteristics including but not limited to: | MEDIUM | Retired | 2012-10-10 | 2017-03-31 | TOP
TOP-002-2.1b | Normal Operations Planning | R16. | Subject to standards of conduct and confidentiality agreements, Transmission Operators shall, without any intentional time delay, notify their Reliability Coordinator and Balancing Authority of changes in capabilities and characteristics including but not limited to: | MEDIUM | Retired | 2012-10-10 | 2017-03-31 | TOP
TOP-002-2.1b | Normal Operations Planning | R16.1. | Changes in transmission facility status. | HIGH | Retired | 2012-10-10 | 2017-03-31 | TOP
TOP-002-2.1b | Normal Operations Planning | R16.1. | Changes in transmission facility status. | HIGH | Retired | 2012-10-10 | 2017-03-31 | TOP
TOP-002-2.1b | Normal Operations Planning | R16.2. | Changes in transmission facility rating. | HIGH | Retired | 2012-10-10 | 2017-03-31 | TOP
TOP-002-2.1b | Normal Operations Planning | R16.2. | Changes in transmission facility rating. | HIGH | Retired | 2012-10-10 | 2017-03-31 | TOP
TOP-002-2.1b | Normal Operations Planning | R17. | Balancing Authorities and Transmission Operators shall, without any intentional time delay, communicate the information described in the requirements R1 to R16 above to their Reliability Coordinator. | HIGH | Retired | 2012-10-10 | 2017-03-31 | TOP, BA
TOP-002-2.1b | Normal Operations Planning | R17. | Balancing Authorities and Transmission Operators shall, without any intentional time delay, communicate the information described in the requirements R1 to R16 above to their Reliability Coordinator. | HIGH | Retired | 2012-10-10 | 2017-03-31 | TOP, BA
TOP-002-2.1b | Normal Operations Planning | R18. | Neighboring Balancing Authorities, Transmission Operators, Generator Operators, Transmission Service Providers and Load Serving Entities shall use uniform line identifiers when referring to transmission facilities of an interconnected network. | MEDIUM | Retired | 2012-10-10 | 2017-03-31 | TSP, TOP, GOP, BA
TOP-002-2.1b | Normal Operations Planning | R18. | Neighboring Balancing Authorities, Transmission Operators, Generator Operators, Transmission Service Providers and Load Serving Entities shall use uniform line identifiers when referring to transmission facilities of an interconnected network. | MEDIUM | Retired | 2012-10-10 | 2017-03-31 | TSP, TOP, GOP, BA
TOP-002-2.1b | Normal Operations Planning | R19. | Each Balancing Authority and Transmission Operator shall maintain accurate computer models utilized for analyzing and planning system operations. | MEDIUM | Retired | 2012-10-10 | 2017-03-31 | TOP, BA
TOP-002-2.1b | Normal Operations Planning | R2. | Each Balancing Authority and Transmission Operator shall ensure its operating personnel participate in the system planning and design study processes, so that these studies contain the operating personnel perspective and system operating personnel are aware of the planning purpose. | MEDIUM | Retired | 2012-10-10 | 2017-03-31 | TOP, BA
TOP-002-2.1b | Normal Operations Planning | R3. | Each Load Serving Entity and Generator Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal operations with its Host Balancing Authority and Transmission Service Provider. Each Balancing Authority and Transmission Service Provider shall coordinate its current-day, next-day, and seasonal operations with its Transmission Operator. | MEDIUM | Retired | 2012-10-10 | 2017-03-31 | TSP, GOP, BA
TOP-002-2.1b | Normal Operations Planning | R3. | Each Load Serving Entity and Generator Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal operations with its Host Balancing Authority and Transmission Service Provider. Each Balancing Authority and Transmission Service Provider shall coordinate its current-day, next-day, and seasonal operations with its Transmission Operator. | MEDIUM | Retired | 2012-10-10 | 2017-03-31 | TSP, GOP, BA
TOP-002-2.1b | Normal Operations Planning | R3. | Each Load Serving Entity and Generator Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal operations with its Host Balancing Authority and Transmission Service Provider. Each Balancing Authority and Transmission Service Provider shall coordinate its current-day, next-day, and seasonal operations with its Transmission Operator. | MEDIUM | Retired | 2012-10-10 | 2017-03-31 | TSP, GOP, BA
TOP-002-2.1b | Normal Operations Planning | R3. | Each Load Serving Entity and Generator Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal operations with its Host Balancing Authority and Transmission Service Provider. Each Balancing Authority and Transmission Service Provider shall coordinate its current-day, next-day, and seasonal operations with its Transmission Operator. | MEDIUM | Retired | 2012-10-10 | 2017-03-31 | TSP, GOP, BA
TOP-002-2.1b | Normal Operations Planning | R3. | Each Load Serving Entity and Generator Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal operations with its Host Balancing Authority and Transmission Service Provider. Each Balancing Authority and Transmission Service Provider shall coordinate its current-day, next-day, and seasonal operations with its Transmission Operator. | MEDIUM | Retired | 2012-10-10 | 2017-03-31 | TSP, GOP, BA
TOP-002-2.1b | Normal Operations Planning | R4. | Each Balancing Authority and Transmission Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal planning and operations with neighboring Balancing Authorities and Transmission Operators and with its Reliability Coordinator, so that normal Interconnection operation will proceed in an orderly and consistent manner. | MEDIUM | Retired | 2012-10-10 | 2017-03-31 | TOP, BA
TOP-002-2.1b | Normal Operations Planning | R4. | Each Balancing Authority and Transmission Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal planning and operations with neighboring Balancing Authorities and Transmission Operators and with its Reliability Coordinator, so that normal Interconnection operation will proceed in an orderly and consistent manner. | MEDIUM | Retired | 2012-10-10 | 2017-03-31 | TOP, BA
TOP-002-2.1b | Normal Operations Planning | R4. | Each Balancing Authority and Transmission Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal planning and operations with neighboring Balancing Authorities and Transmission Operators and with its Reliability Coordinator, so that normal Interconnection operation will proceed in an orderly and consistent manner. | MEDIUM | Retired | 2012-10-10 | 2017-03-31 | TOP, BA
TOP-002-2.1b | Normal Operations Planning | R4. | Each Balancing Authority and Transmission Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal planning and operations with neighboring Balancing Authorities and Transmission Operators and with its Reliability Coordinator, so that normal Interconnection operation will proceed in an orderly and consistent manner. | MEDIUM | Retired | 2012-10-10 | 2017-03-31 | TOP, BA
TOP-002-2.1b | Normal Operations Planning | R4. | Each Balancing Authority and Transmission Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal planning and operations with neighboring Balancing Authorities and Transmission Operators and with its Reliability Coordinator, so that normal Interconnection operation will proceed in an orderly and consistent manner. | MEDIUM | Retired | 2012-10-10 | 2017-03-31 | TOP, BA
TOP-002-2.1b | Normal Operations Planning | R5. | Each Balancing Authority and Transmission Operator shall plan to meet scheduled system configuration, generation dispatch, interchange scheduling and demand patterns. | MEDIUM | Retired | 2012-10-10 | 2017-03-31 | TOP, BA
TOP-002-2.1b | Normal Operations Planning | R5. | Each Balancing Authority and Transmission Operator shall plan to meet scheduled system configuration, generation dispatch, interchange scheduling and demand patterns. | MEDIUM | Retired | 2012-10-10 | 2017-03-31 | TOP, BA
TOP-002-2.1b | Normal Operations Planning | R6. | Each Balancing Authority and Transmission Operator shall plan to meet unscheduled changes in system configuration and generation dispatch (at a minimum N-1 Contingency planning) in accordance with NERC, Regional Reliability Organization, subregional, and local reliability requirements. | MEDIUM | Retired | 2012-10-10 | 2017-03-31 | TOP, BA
TOP-002-2.1b | Normal Operations Planning | R6. | Each Balancing Authority and Transmission Operator shall plan to meet unscheduled changes in system configuration and generation dispatch (at a minimum N-1 Contingency planning) in accordance with NERC, Regional Reliability Organization, subregional, and local reliability requirements. | MEDIUM | Retired | 2012-10-10 | 2017-03-31 | TOP, BA
TOP-002-2.1b | Normal Operations Planning | R7. | Each Balancing Authority shall plan to meet capacity and energy reserve requirements, including the deliverability/capability for any single Contingency. | MEDIUM | Retired | 2012-10-10 | 2017-03-31 | BA
TOP-002-2.1b | Normal Operations Planning | R7. | Each Balancing Authority shall plan to meet capacity and energy reserve requirements, including the deliverability/capability for any single Contingency. | MEDIUM | Retired | 2012-10-10 | 2017-03-31 | BA
TOP-002-2.1b | Normal Operations Planning | R8. | Each Balancing Authority shall plan to meet voltage and/or reactive limits, including the deliverability/capability for any single contingency. | MEDIUM | Retired | 2012-10-10 | 2017-03-31 | BA
TOP-002-2.1b | Normal Operations Planning | R8. | Each Balancing Authority shall plan to meet voltage and/or reactive limits, including the deliverability/capability for any single contingency. | MEDIUM | Retired | 2012-10-10 | 2017-03-31 | BA
TOP-002-2.1b | Normal Operations Planning | R9. | Each Balancing Authority shall plan to meet Interchange Schedules and ramps. | LOWER | Retired | 2012-10-10 | 2017-03-31 | BA
TOP-002-2.1b | Normal Operations Planning | R9. | Each Balancing Authority shall plan to meet Interchange Schedules and ramps. | LOWER | Retired | 2012-10-10 | 2017-03-31 | BA
TOP-002-3 | Operations Planning | R1. | Each Transmission Operator shall have an Operational Planning Analysis that represents projected System conditions that will allow it to assess whether the planned operations for the next day within its Transmission Operator Area will exceed any of its Facility Ratings or Stability Limits during anticipated normal and Contingency event conditions. | MEDIUM | Never Came Into Effect in Ontario |  |  | TOP
TOP-002-3 | Operations Planning | R2. | Each Transmission Operator shall develop a plan to operate within each Interconnection Reliability Operating Limit (IROL) and each System Operating Limit (SOL) which, while not an IROL, has been identified by the Transmission Operator as supporting reliability internal to its Transmission Operator Area, identified as a result of the Operational Planning Analysis performed in Requirement R1. | MEDIUM | Never Came Into Effect in Ontario |  |  | TOP
TOP-002-3 | Operations Planning | R3. | Each Transmission Operator shall notify all NERC registered entities identified in the plan(s) cited in Requirement R2 as to their role in those plan(s). | MEDIUM | Never Came Into Effect in Ontario |  |  | TOP
TOP-002-4 | Operations Planning | R1. | Each Transmission Operator shall have an Operational Planning Analysis that will allow it to assess whether its planned operations for the next day within its Transmission Operator Area will exceed any of its System Operating Limits (SOLs). [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Effective | 2017-04-01 |  | TOP
TOP-002-4 | Operations Planning | R1. | Each Transmission Operator shall have an Operational Planning Analysis that will allow it to assess whether its planned operations for the next day within its Transmission Operator Area will exceed any of its System Operating Limits (SOLs). [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Effective | 2017-04-01 |  | TOP
TOP-002-4 | Operations Planning | R2. | Each Transmission Operator shall have an Operating Plan(s) for next-day operations to address potential System Operating Limit (SOL) exceedances identified as a result of its Operational Planning Analysis as required in Requirement R1. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Effective | 2017-04-01 |  | TOP
TOP-002-4 | Operations Planning | R2. | Each Transmission Operator shall have an Operating Plan(s) for next-day operations to address potential System Operating Limit (SOL) exceedances identified as a result of its Operational Planning Analysis as required in Requirement R1. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Effective | 2017-04-01 |  | TOP
TOP-002-4 | Operations Planning | R3. | Each Transmission Operator shall notify entities identified in the Operating Plan(s) cited in Requirement R2 as to their role in those plan(s). [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Effective | 2017-04-01 |  | TOP
TOP-002-4 | Operations Planning | R3. | Each Transmission Operator shall notify entities identified in the Operating Plan(s) cited in Requirement R2 as to their role in those plan(s). [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Effective | 2017-04-01 |  | TOP
TOP-002-4 | Operations Planning | R4. | Each Balancing Authority shall have an Operating Plan(s) for the next-day that addresses: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Effective | 2017-04-01 |  | BA
TOP-002-4 | Operations Planning | R4.1. | Expected generation resource commitment and dispatch | MEDIUM | Effective | 2017-04-01 |  | BA
TOP-002-4 | Operations Planning | R4.2. | Interchange scheduling | MEDIUM | Effective | 2017-04-01 |  | BA
TOP-002-4 | Operations Planning | R4.3. | Demand patterns | MEDIUM | Effective | 2017-04-01 |  | BA
TOP-002-4 | Operations Planning | R4.4. | Capacity and energy reserve requirements, including deliverability capability | MEDIUM | Effective | 2017-04-01 |  | BA
TOP-002-4 | Operations Planning | R5. | Each Balancing Authority shall notify entities identified in the Operating Plan(s) cited in Requirement R4 as to their role in those plan(s). [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Effective | 2017-04-01 |  | BA
TOP-002-4 | Operations Planning | R5. | Each Balancing Authority shall notify entities identified in the Operating Plan(s) cited in Requirement R4 as to their role in those plan(s). [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Effective | 2017-04-01 |  | BA
TOP-002-4 | Operations Planning | R6. | Each Transmission Operator shall provide its Operating Plan(s) for next-day operations identified in Requirement R2 to its Reliability Coordinator. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Effective | 2017-04-01 |  | TOP
TOP-002-4 | Operations Planning | R6. | Each Transmission Operator shall provide its Operating Plan(s) for next-day operations identified in Requirement R2 to its Reliability Coordinator. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Effective | 2017-04-01 |  | TOP
TOP-002-4 | Operations Planning | R7. | Each Balancing Authority shall provide its Operating Plan(s) for next-day operations identified in Requirement R4 to its Reliability Coordinator. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Effective | 2017-04-01 |  | BA
TOP-002-4 | Operations Planning | R7. | Each Balancing Authority shall provide its Operating Plan(s) for next-day operations identified in Requirement R4 to its Reliability Coordinator. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Effective | 2017-04-01 |  | BA
TOP-002-5 | Operations Planning | R1. | Each Transmission Operator shall have an Operational Planning Analysis that will allow it to assess whether its planned operations for the next day within its Transmission Operator Area will exceed any of its System Operating Limits (SOLs). [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Future Effective | 2025-10-01 |  | TOP
TOP-002-5 | Operations Planning | R2. | Each Transmission Operator shall have an Operating Plan(s) for next-day operations to address potential System Operating Limit (SOL) exceedances identified as a result of its Operational Planning Analysis as required in Requirement R1. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Future Effective | 2025-10-01 |  | TOP
TOP-002-5 | Operations Planning | R3. | Each Transmission Operator shall notify entities identified in the Operating Plan(s) cited in Requirement R2 as to their role in those plan(s). [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Future Effective | 2025-10-01 |  | TOP
TOP-002-5 | Operations Planning | R4. | Each Balancing Authority shall have an Operating Plan(s) for the next day that addresses: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Future Effective | 2025-10-01 |  | BA
TOP-002-5 | Operations Planning | R4.1. | Expected generation resource commitment and dispatch; | MEDIUM | Future Effective | 2025-10-01 |  | BA
TOP-002-5 | Operations Planning | R4.2. | Interchange scheduling; | MEDIUM | Future Effective | 2025-10-01 |  | BA
TOP-002-5 | Operations Planning | R4.3. | Demand patterns; and | MEDIUM | Future Effective | 2025-10-01 |  | BA
TOP-002-5 | Operations Planning | R4.4. | Capacity and energy reserve requirements, including deliverability capability. | MEDIUM | Future Effective | 2025-10-01 |  | BA
TOP-002-5 | Operations Planning | R5. | Each Balancing Authority shall notify entities identified in the Operating Plan(s) cited in Requirement R4 as to their role in those plan(s). [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Future Effective | 2025-10-01 |  | BA
TOP-002-5 | Operations Planning | R6. | Each Transmission Operator shall provide its Operating Plan(s) for next day operations identified in Requirement R2 to its Reliability Coordinator. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Future Effective | 2025-10-01 |  | TOP
TOP-002-5 | Operations Planning | R7. | Each Balancing Authority shall provide its Operating Plan(s) for next day operations identified in Requirement R4 to its Reliability Coordinator. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Future Effective | 2025-10-01 |  | BA
TOP-002-5 | Operations Planning | R8. | Each Balancing Authority shall have an extreme cold weather Operating Process for its Balancing Authority Area, addressing preparations for and operations during extreme cold weather periods. The extreme cold weather Operating Process shall include, but is not limited to: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | MEDIUM | Future Effective | 2025-10-01 |  | BA
TOP-002-5 | Operations Planning | R8.1. | A methodology for identifying an extreme cold weather period within each Balancing Authority Area; | MEDIUM | Future Effective | 2025-10-01 |  | BA
TOP-002-5 | Operations Planning | R8.2. | A methodology to determine an adequate reserve margin during the extreme cold weather period considering the generating unit(s) operating limitations in previous extreme cold weather periods that includes, but is not limited to: | MEDIUM | Future Effective | 2025-10-01 |  | BA
TOP-002-5 | Operations Planning | R8.2.1. | Capability and availability; | MEDIUM | Future Effective | 2025-10-01 |  | BA
TOP-002-5 | Operations Planning | R8.2.2. | Fuel supply and inventory concerns; | MEDIUM | Future Effective | 2025-10-01 |  | BA
TOP-002-5 | Operations Planning | R8.2.3. | Start-up issues; | MEDIUM | Future Effective | 2025-10-01 |  | BA
TOP-002-5 | Operations Planning | R8.2.4. | Fuel switching capabilities; and | MEDIUM | Future Effective | 2025-10-01 |  | BA
TOP-002-5 | Operations Planning | R8.2.5. | Environmental constraints. | MEDIUM | Future Effective | 2025-10-01 |  | BA
TOP-002-5 | Operations Planning | R8.3. | A methodology to determine a five-day hourly forecast during the identified extreme cold weather periods that includes, but is not limited to: | MEDIUM | Future Effective | 2025-10-01 |  | BA
TOP-002-5 | Operations Planning | R8.3.1. | Expected generation resource commitment and dispatch; | MEDIUM | Future Effective | 2025-10-01 |  | BA
TOP-002-5 | Operations Planning | R8.3.2. | Demand patterns; | MEDIUM | Future Effective | 2025-10-01 |  | BA
TOP-002-5 | Operations Planning | R8.3.3. | Capacity and energy reserve requirements, including deliverability capability; and | MEDIUM | Future Effective | 2025-10-01 |  | BA
TOP-002-5 | Operations Planning | R8.3.4. | Weather forecast. | MEDIUM | Future Effective | 2025-10-01 |  | BA
TOP-003-1 | Planned Outage Coordination | R1. | Generator Operators and Transmission Operators shall provide planned outage information. | No Individual VRF Assigned | Retired | 2011-10-01 | 2016-12-31 | TOP, GOP
TOP-003-1 | Planned Outage Coordination | R1.1. | Each Generator Operator shall provide outage information daily to its Transmission Operator for scheduled generator outages planned for the next day (any foreseen outage of a generator greater than 50 MW). The Transmission Operator shall establish the outage reporting requirements. | MEDIUM | Retired | 2011-10-01 | 2016-12-31 | GOP
TOP-003-1 | Planned Outage Coordination | R1.2. | Each Transmission Operator shall provide outage information daily to affected Balancing Authorities and Transmission Operators for scheduled generator and bulk transmission outages planned for the next day (any foreseen outage of a transmission line or transformer greater than 100 kV or generator greater than 50 MW) that may collectively cause or contribute to an SOL or IROL violation or a regional operating area limitation. | MEDIUM | Retired | 2011-10-01 | 2016-12-31 | TOP
TOP-003-1 | Planned Outage Coordination | R1.3. | Such information shall be available by 1200 Central Standard Time for the Eastern Interconnection and 1200 Pacific Standard Time for the Western Interconnection. | MEDIUM | Retired | 2011-10-01 | 2016-12-31 | TOP
TOP-003-1 | Planned Outage Coordination | R2. | Each Transmission Operator, Balancing Authority, and Generator Operator shall plan and coordinate scheduled outages of system voltage regulating equipment, such as automatic voltage regulators on generators, supplementary excitation control, synchronous condensers, shunt and series capacitors, reactors, etc., among affected Balancing Authorities and Transmission Operators as required. | MEDIUM | Retired | 2011-10-01 | 2016-12-31 | TOP, GOP, BA
TOP-003-1 | Planned Outage Coordination | R3. | Each Transmission Operator, Balancing Authority, and Generator Operator shall plan and coordinate scheduled outages of telemetering and control equipment and associated communication channels between the affected areas. | MEDIUM | Retired | 2011-10-01 | 2016-12-31 | TOP, RC, GOP, BA
TOP-003-1 | Planned Outage Coordination | R4. | Each Reliability Coordinator shall resolve any scheduling of potential reliability conflicts. | MEDIUM | Retired | 2011-10-01 | 2016-12-31 | RC
TOP-003-2 | Operational Reliability Data | R1. | Each Transmission Operator shall create a documented specification for the data necessary for it to perform its Operational Planning Analyses and Real-time monitoring. The specification shall include: | LOWER | Never Came Into Effect in Ontario |  |  | TOP
TOP-003-2 | Operational Reliability Data | R1. | Each Transmission Operator shall create a documented specification for the data necessary for it to perform its Operational Planning Analyses and Real-time monitoring. The specification shall include: | LOWER | Never Came Into Effect in Ontario |  |  | TOP
TOP-003-2 | Operational Reliability Data | R1.1. | A list of data and information needed by the Transmission Operator to support its Operational Planning Analyses and Real-time monitoring. | LOWER | Never Came Into Effect in Ontario |  |  | TOP
TOP-003-2 | Operational Reliability Data | R1.1. | A list of data and information needed by the Transmission Operator to support its Operational Planning Analyses and Real-time monitoring. | LOWER | Never Came Into Effect in Ontario |  |  | TOP
TOP-003-2 | Operational Reliability Data | R1.2. | A mutually-agreeable format. | LOWER | Never Came Into Effect in Ontario |  |  | TOP
TOP-003-2 | Operational Reliability Data | R1.2. | A mutually-agreeable format. | LOWER | Never Came Into Effect in Ontario |  |  | TOP
TOP-003-2 | Operational Reliability Data | R1.3. | A periodicity for providing data. | LOWER | Never Came Into Effect in Ontario |  |  | TOP
TOP-003-2 | Operational Reliability Data | R1.3. | A periodicity for providing data. | LOWER | Never Came Into Effect in Ontario |  |  | TOP
TOP-003-2 | Operational Reliability Data | R1.4. | The deadline by which the respondent is to provide the indicated data. | LOWER | Never Came Into Effect in Ontario |  |  | TOP
TOP-003-2 | Operational Reliability Data | R1.4. | The deadline by which the respondent is to provide the indicated data. | LOWER | Never Came Into Effect in Ontario |  |  | TOP
TOP-003-2 | Operational Reliability Data | R2. | Each Balancing Authority shall create a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. The specification shall include: | LOWER | Never Came Into Effect in Ontario |  |  | TOP, BA
TOP-003-2 | Operational Reliability Data | R2. | Each Balancing Authority shall create a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. The specification shall include: | LOWER | Never Came Into Effect in Ontario |  |  | TOP, BA
TOP-003-2 | Operational Reliability Data | R2.1. | A list of data and information needed by the Balancing Authority to support its analysis functions and Real-time monitoring. | LOWER | Never Came Into Effect in Ontario |  |  | TOP, BA
TOP-003-2 | Operational Reliability Data | R2.1. | A list of data and information needed by the Balancing Authority to support its analysis functions and Real-time monitoring. | LOWER | Never Came Into Effect in Ontario |  |  | TOP, BA
TOP-003-2 | Operational Reliability Data | R2.2. | A mutually-agreeable format. | LOWER | Never Came Into Effect in Ontario |  |  | TOP, BA
TOP-003-2 | Operational Reliability Data | R2.2. | A mutually-agreeable format. | LOWER | Never Came Into Effect in Ontario |  |  | TOP, BA
TOP-003-2 | Operational Reliability Data | R2.3. | A periodicity for providing data. | LOWER | Never Came Into Effect in Ontario |  |  | TOP, BA
TOP-003-2 | Operational Reliability Data | R2.3. | A periodicity for providing data. | LOWER | Never Came Into Effect in Ontario |  |  | TOP, BA
TOP-003-2 | Operational Reliability Data | R2.4. | The deadline by which the respondent is to provide the indicated data. | LOWER | Never Came Into Effect in Ontario |  |  | TOP, BA
TOP-003-2 | Operational Reliability Data | R2.4. | The deadline by which the respondent is to provide the indicated data. | LOWER | Never Came Into Effect in Ontario |  |  | TOP, BA
TOP-003-2 | Operational Reliability Data | R3. | Each Transmission Operator shall distribute its data specification, as developed in Requirement R1,to entities that have data required by the Transmission Operator’s Operational Planning Analysis and Real-time monitoring process used in meeting its NERC-mandated reliability requirements. | LOWER | Never Came Into Effect in Ontario |  |  | TOP
TOP-003-2 | Operational Reliability Data | R3. | Each Transmission Operator shall distribute its data specification, as developed in Requirement R1,to entities that have data required by the Transmission Operator’s Operational Planning Analysis and Real-time monitoring process used in meeting its NERC-mandated reliability requirements. | LOWER | Never Came Into Effect in Ontario |  |  | TOP
TOP-003-2 | Operational Reliability Data | R4. | Each Balancing Authority shall distribute its data specification, as developed in Requirement R2, to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring process used in meeting its NERC-mandated reliability requirements. | LOWER | Never Came Into Effect in Ontario |  |  | TOP, BA
TOP-003-2 | Operational Reliability Data | R4. | Each Balancing Authority shall distribute its data specification, as developed in Requirement R2, to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring process used in meeting its NERC-mandated reliability requirements. | LOWER | Never Came Into Effect in Ontario |  |  | TOP, BA
TOP-003-2 | Operational Reliability Data | R5. | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Interchange Authority, Load-Serving Entity, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall satisfy the obligations of the documented specifications for data. | MEDIUM | Never Came Into Effect in Ontario |  |  | TOP, TO, GOP, GO, DP, BA
TOP-003-2 | Operational Reliability Data | R5. | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Interchange Authority, Load-Serving Entity, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall satisfy the obligations of the documented specifications for data. | MEDIUM | Never Came Into Effect in Ontario |  |  | TOP, TO, GOP, GO, DP, BA
TOP-003-3 | Operational Reliability Data | R1. | Each Transmission Operator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The data specification shall include, but not be limited to: [Violation Risk Factor: Low] [Time Horizon: Operations Planning] | LOWER | Retired | 2017-01-01 | 2021-03-31 | TOP
TOP-003-3 | Operational Reliability Data | R1. | Each Transmission Operator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The data specification shall include, but not be limited to: [Violation Risk Factor: Low] [Time Horizon: Operations Planning] | LOWER | Retired | 2017-01-01 | 2021-03-31 | TOP
TOP-003-3 | Operational Reliability Data | R1.1. | A list of data and information needed by the Transmission Operator to support its Operational Planning Analyses, Real-time monitoring, and Realtime Assessments including non-BES data and external network data as deemed necessary by the Transmission Operator. | LOWER | Retired | 2017-01-01 | 2021-03-31 | TOP
TOP-003-3 | Operational Reliability Data | R1.1. | A list of data and information needed by the Transmission Operator to support its Operational Planning Analyses, Real-time monitoring, and Realtime Assessments including non-BES data and external network data as deemed necessary by the Transmission Operator. | LOWER | Retired | 2017-01-01 | 2021-03-31 | TOP
TOP-003-3 | Operational Reliability Data | R1.2. | Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability. | LOWER | Retired | 2017-01-01 | 2021-03-31 | TOP
TOP-003-3 | Operational Reliability Data | R1.2. | Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability. | LOWER | Retired | 2017-01-01 | 2021-03-31 | TOP
TOP-003-3 | Operational Reliability Data | R1.3. | A periodicity for providing data. | LOWER | Retired | 2017-01-01 | 2021-03-31 | TOP
TOP-003-3 | Operational Reliability Data | R1.3. | A periodicity for providing data. | LOWER | Retired | 2017-01-01 | 2021-03-31 | TOP
TOP-003-3 | Operational Reliability Data | R1.4. | The deadline by which the respondent is to provide the indicated data. | LOWER | Retired | 2017-01-01 | 2021-03-31 | TOP
TOP-003-3 | Operational Reliability Data | R1.4. | The deadline by which the respondent is to provide the indicated data. | LOWER | Retired | 2017-01-01 | 2021-03-31 | TOP
TOP-003-3 | Operational Reliability Data | R2. | Each Balancing Authority shall maintain a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. The data specification shall include, but not be limited to: [Violation Risk Factor: Low] [Time Horizon: Operations Planning] | LOWER | Retired | 2017-01-01 | 2021-03-31 | BA
TOP-003-3 | Operational Reliability Data | R2. | Each Balancing Authority shall maintain a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. The data specification shall include, but not be limited to: [Violation Risk Factor: Low] [Time Horizon: Operations Planning] | LOWER | Retired | 2017-01-01 | 2021-03-31 | BA
TOP-003-3 | Operational Reliability Data | R2.1. | A list of data and information needed by the Balancing Authority to support its analysis functions and Real-time monitoring. | LOWER | Retired | 2017-01-01 | 2021-03-31 | BA
TOP-003-3 | Operational Reliability Data | R2.1. | A list of data and information needed by the Balancing Authority to support its analysis functions and Real-time monitoring. | LOWER | Retired | 2017-01-01 | 2021-03-31 | BA
TOP-003-3 | Operational Reliability Data | R2.2. | Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability. | LOWER | Retired | 2017-01-01 | 2021-03-31 | BA
TOP-003-3 | Operational Reliability Data | R2.2. | Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability. | LOWER | Retired | 2017-01-01 | 2021-03-31 | BA
TOP-003-3 | Operational Reliability Data | R2.3. | A periodicity for providing data. | LOWER | Retired | 2017-01-01 | 2021-03-31 | BA
TOP-003-3 | Operational Reliability Data | R2.3. | A periodicity for providing data. | LOWER | Retired | 2017-01-01 | 2021-03-31 | BA
TOP-003-3 | Operational Reliability Data | R2.4. | The deadline by which the respondent is to provide the indicated data. | LOWER | Retired | 2017-01-01 | 2021-03-31 | BA
TOP-003-3 | Operational Reliability Data | R2.4. | The deadline by which the respondent is to provide the indicated data. | LOWER | Retired | 2017-01-01 | 2021-03-31 | BA
TOP-003-3 | Operational Reliability Data | R3. | Each Transmission Operator shall distribute its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Realtime monitoring, and Real-time Assessment. [Violation Risk Factor: Low] [Time Horizon: Operations Planning] | LOWER | Retired | 2017-01-01 | 2021-03-31 | TOP
TOP-003-3 | Operational Reliability Data | R3. | Each Transmission Operator shall distribute its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Realtime monitoring, and Real-time Assessment. [Violation Risk Factor: Low] [Time Horizon: Operations Planning] | LOWER | Retired | 2017-01-01 | 2021-03-31 | TOP
TOP-003-3 | Operational Reliability Data | R4. | Each Balancing Authority shall distribute its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. [Violation Risk Factor: Low] [Time Horizon: Operations Planning] | LOWER | Retired | 2017-01-01 | 2021-03-31 | BA
TOP-003-3 | Operational Reliability Data | R4. | Each Balancing Authority shall distribute its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. [Violation Risk Factor: Low] [Time Horizon: Operations Planning] | LOWER | Retired | 2017-01-01 | 2021-03-31 | BA
TOP-003-3 | Operational Reliability Data | R5. | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Load-Serving Entity, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall satisfy the obligations of the documented specifications using: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning, Same-Day Operations, Real-time Operations] | MEDIUM | Retired | 2017-04-01 | 2021-03-31 | TOP, TO, GOP, GO, DP, BA
TOP-003-3 | Operational Reliability Data | R5. | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Load-Serving Entity, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall satisfy the obligations of the documented specifications using: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning, Same-Day Operations, Real-time Operations] | MEDIUM | Retired | 2017-04-01 | 2021-03-31 | TOP, TO, GOP, GO, DP, BA
TOP-003-3 | Operational Reliability Data | R5.1. | A mutually agreeable format | MEDIUM | Retired | 2017-04-01 | 2021-03-31 | TOP, TO, GOP, GO, DP, BA
TOP-003-3 | Operational Reliability Data | R5.1. | A mutually agreeable format | MEDIUM | Retired | 2017-04-01 | 2021-03-31 | TOP, TO, GOP, GO, DP, BA
TOP-003-3 | Operational Reliability Data | R5.2. | A mutually agreeable process for resolving data conflicts | MEDIUM | Retired | 2017-04-01 | 2021-03-31 | TOP, TO, GOP, GO, DP, BA
TOP-003-3 | Operational Reliability Data | R5.2. | A mutually agreeable process for resolving data conflicts | MEDIUM | Retired | 2017-04-01 | 2021-03-31 | TOP, TO, GOP, GO, DP, BA
TOP-003-3 | Operational Reliability Data | R5.3. | A mutually agreeable security protocol | MEDIUM | Retired | 2017-04-01 | 2021-03-31 | TOP, TO, GOP, GO, DP, BA
TOP-003-3 | Operational Reliability Data | R5.3. | A mutually agreeable security protocol | MEDIUM | Retired | 2017-04-01 | 2021-03-31 | TOP, TO, GOP, GO, DP, BA
TOP-003-4 | Operational Reliability Data | R1. | Each Transmission Operator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The data specification shall include, but not be limited to: [Violation Risk Factor: Low] [Time Horizon: Operations Planning] | LOWER | Retired | 2021-04-01 | 2023-09-30 | DP, GOP, GO, BA, TOP, TO
TOP-003-4 | Operational Reliability Data | R1. | Each Transmission Operator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The data specification shall include, but not be limited to: [Violation Risk Factor: Low] [Time Horizon: Operations Planning] | LOWER | Retired | 2021-04-01 | 2023-09-30 | DP, GOP, GO, BA, TOP, TO
TOP-003-4 | Operational Reliability Data | R1.1. | A list of data and information needed by the Transmission Operator to support its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments including non-BES data and external network data as deemed necessary by the Transmission Operator. | LOWER | Retired | 2021-04-01 | 2023-09-30 | DP, GOP, GO, BA, TOP, TO
TOP-003-4 | Operational Reliability Data | R1.1. | A list of data and information needed by the Transmission Operator to support its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments including non-BES data and external network data as deemed necessary by the Transmission Operator. | LOWER | Retired | 2021-04-01 | 2023-09-30 | DP, GOP, GO, BA, TOP, TO
TOP-003-4 | Operational Reliability Data | R1.2. | Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability. | LOWER | Retired | 2021-04-01 | 2023-09-30 | DP, GOP, GO, BA, TOP, TO
TOP-003-4 | Operational Reliability Data | R1.2. | Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability. | LOWER | Retired | 2021-04-01 | 2023-09-30 | DP, GOP, GO, BA, TOP, TO
TOP-003-4 | Operational Reliability Data | R1.3. | A periodicity for providing data. | LOWER | Retired | 2021-04-01 | 2023-09-30 | DP, GOP, GO, BA, TOP, TO
TOP-003-4 | Operational Reliability Data | R1.3. | A periodicity for providing data. | LOWER | Retired | 2021-04-01 | 2023-09-30 | DP, GOP, GO, BA, TOP, TO
TOP-003-4 | Operational Reliability Data | R1.4. | The deadline by which the respondent is to provide the indicated data. | LOWER | Retired | 2021-04-01 | 2023-09-30 | DP, GOP, GO, BA, TOP, TO
TOP-003-4 | Operational Reliability Data | R1.4. | The deadline by which the respondent is to provide the indicated data. | LOWER | Retired | 2021-04-01 | 2023-09-30 | DP, GOP, GO, BA, TOP, TO
TOP-003-4 | Operational Reliability Data | R2. | Each Balancing Authority shall maintain a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. The data specification shall include, but not be limited to: [Violation Risk Factor: Low] [Time Horizon: Operations Planning] | LOWER | Retired | 2021-04-01 | 2023-09-30 | DP, GOP, GO, BA, TOP, TO
TOP-003-4 | Operational Reliability Data | R2. | Each Balancing Authority shall maintain a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. The data specification shall include, but not be limited to: [Violation Risk Factor: Low] [Time Horizon: Operations Planning] | LOWER | Retired | 2021-04-01 | 2023-09-30 | DP, GOP, GO, BA, TOP, TO
TOP-003-4 | Operational Reliability Data | R2.1. | A list of data and information needed by the Balancing Authority to support its analysis functions and Real-time monitoring. | LOWER | Retired | 2021-04-01 | 2023-09-30 | DP, GOP, GO, BA, TOP, TO
TOP-003-4 | Operational Reliability Data | R2.1. | A list of data and information needed by the Balancing Authority to support its analysis functions and Real-time monitoring. | LOWER | Retired | 2021-04-01 | 2023-09-30 | DP, GOP, GO, BA, TOP, TO
TOP-003-4 | Operational Reliability Data | R2.2. | Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability. | LOWER | Retired | 2021-04-01 | 2023-09-30 | DP, GOP, GO, BA, TOP, TO
TOP-003-4 | Operational Reliability Data | R2.2. | Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability. | LOWER | Retired | 2021-04-01 | 2023-09-30 | DP, GOP, GO, BA, TOP, TO
TOP-003-4 | Operational Reliability Data | R2.3. | A periodicity for providing data. | LOWER | Retired | 2021-04-01 | 2023-09-30 | DP, GOP, GO, BA, TOP, TO
TOP-003-4 | Operational Reliability Data | R2.3. | A periodicity for providing data. | LOWER | Retired | 2021-04-01 | 2023-09-30 | DP, GOP, GO, BA, TOP, TO
TOP-003-4 | Operational Reliability Data | R2.4. | The deadline by which the respondent is to provide the indicated data. | LOWER | Retired | 2021-04-01 | 2023-09-30 | DP, GOP, GO, BA, TOP, TO
TOP-003-4 | Operational Reliability Data | R2.4. | The deadline by which the respondent is to provide the indicated data. | LOWER | Retired | 2021-04-01 | 2023-09-30 | DP, GOP, GO, BA, TOP, TO
TOP-003-4 | Operational Reliability Data | R3. | Each Transmission Operator shall distribute its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessment. [Violation Risk Factor: Low] [Time Horizon: Operations Planning] | LOWER | Retired | 2021-04-01 | 2023-09-30 | DP, GOP, GO, BA, TOP, TO
TOP-003-4 | Operational Reliability Data | R3. | Each Transmission Operator shall distribute its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessment. [Violation Risk Factor: Low] [Time Horizon: Operations Planning] | LOWER | Retired | 2021-04-01 | 2023-09-30 | DP, GOP, GO, BA, TOP, TO
TOP-003-4 | Operational Reliability Data | R4. | Each Balancing Authority shall distribute its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. [Violation Risk Factor: Low] [Time Horizon: Operations Planning] | LOWER | Retired | 2021-04-01 | 2023-09-30 | DP, GOP, GO, BA, TOP, TO
TOP-003-4 | Operational Reliability Data | R4. | Each Balancing Authority shall distribute its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. [Violation Risk Factor: Low] [Time Horizon: Operations Planning] | LOWER | Retired | 2021-04-01 | 2023-09-30 | DP, GOP, GO, BA, TOP, TO
TOP-003-4 | Operational Reliability Data | R5. | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall satisfy the obligations of the documented specifications using: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning, Same-Day Operations, Real-time Operations] | MEDIUM | Retired | 2021-04-01 | 2023-09-30 | DP, GOP, GO, BA, TOP, TO
TOP-003-4 | Operational Reliability Data | R5. | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall satisfy the obligations of the documented specifications using: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning, Same-Day Operations, Real-time Operations] | MEDIUM | Retired | 2021-04-01 | 2023-09-30 | DP, GOP, GO, BA, TOP, TO
TOP-003-4 | Operational Reliability Data | R5.1. | A mutually agreeable format | MEDIUM | Retired | 2021-04-01 | 2023-09-30 | DP, GOP, GO, BA, TOP, TO
TOP-003-4 | Operational Reliability Data | R5.1. | A mutually agreeable format | MEDIUM | Retired | 2021-04-01 | 2023-09-30 | DP, GOP, GO, BA, TOP, TO
TOP-003-4 | Operational Reliability Data | R5.2. | A mutually agreeable process for resolving data conflicts | MEDIUM | Retired | 2021-04-01 | 2023-09-30 | DP, GOP, GO, BA, TOP, TO
TOP-003-4 | Operational Reliability Data | R5.2. | A mutually agreeable process for resolving data conflicts | MEDIUM | Retired | 2021-04-01 | 2023-09-30 | DP, GOP, GO, BA, TOP, TO
TOP-003-4 | Operational Reliability Data | R5.3. | A mutually agreeable process for resolving data conflicts | MEDIUM | Retired | 2021-04-01 | 2023-09-30 | DP, GOP, GO, BA, TOP, TO
TOP-003-4 | Operational Reliability Data | R5.3. | A mutually agreeable process for resolving data conflicts | MEDIUM | Retired | 2021-04-01 | 2023-09-30 | DP, GOP, GO, BA, TOP, TO
TOP-003-5 | Operational Reliability Data | R1. | Each Transmission Operator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The data specification shall include, but not be limited to: [Violation Risk Factor: Low] [Time Horizon: Operations Planning] | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R1. | Each Transmission Operator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The data specification shall include, but not be limited to: [Violation Risk Factor: Low] [Time Horizon: Operations Planning] | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R1.1. | A list of data and information needed by the Transmission Operator to support its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments including non-BES data and external network data as deemed necessary by the Transmission Operator. | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R1.1. | A list of data and information needed by the Transmission Operator to support its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments including non-BES data and external network data as deemed necessary by the Transmission Operator. | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R1.2. | Provisions for notification of current Protection System and Remedial Action Scheme (RAS) status or degradation that impacts System reliability. | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R1.2. | Provisions for notification of current Protection System and Remedial Action Scheme (RAS) status or degradation that impacts System reliability. | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R1.3. | A periodicity for providing data. | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R1.3. | Provisions for notification of BES generating unit(s)during local forecasted cold weather to include | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R1.3. | Provisions for notification of BES generating unit(s)during local forecasted cold weather to include | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R1.3.1. | Operating limitations based on: | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R1.3.1. | Operating limitations based on: | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R1.3.1.1. | capability and availability; | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R1.3.1.1. | capability and availability; | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R1.3.1.2. | fuel supply and inventory concerns; | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R1.3.1.3. | fuel switching capabilities; and | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R1.3.1.3. | fuel switching capabilities; and | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R1.3.1.4. | environmental constraints | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R1.4. | The deadline by which the respondent is to provide the indicated data. | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R1.4. | The deadline by which the respondent is to provide the indicated data. | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R2. | Each Balancing Authority shall maintain a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. The data specification shall include, but not be limited to: [Violation Risk Factor: Low] [Time Horizon: Operations Planning] | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R2. | Each Balancing Authority shall maintain a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. The data specification shall include, but not be limited to: [Violation Risk Factor: Low] [Time Horizon: Operations Planning] | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R2.1. | A list of data and information needed by the Balancing Authority to support its analysis functions and Real-time monitoring. | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R2.1. | A list of data and information needed by the Balancing Authority to support its analysis functions and Real-time monitoring. | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R2.2. | Provisions for notification of current Protection System and Remedial Action Scheme status or degradation that impacts System reliability. | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R2.2. | Provisions for notification of current Protection System and Remedial Action Scheme status or degradation that impacts System reliability. | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R2.3. | Provisions for notification of BES generating unit(s) status during local forecasted cold weather to include: | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R2.3. | Provisions for notification of BES generating unit(s) status during local forecasted cold weather to include: | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R2.3.1. | Operating limitations based on: | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R2.3.1. | Operating limitations based on: | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R2.3.1.1. | capability and availability; | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R2.3.1.1. | capability and availability; | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R2.3.1.2. | fuel supply and inventory concerns; | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R2.3.1.2. | fuel supply and inventory concerns; | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R2.3.1.3. | fuel switching capabilities; and | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R2.3.1.3. | fuel switching capabilities; and | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R2.3.1.4. | environmental constraints. | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R2.3.1.4. | environmental constraints. | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R2.3.2.1. | design temperature; or | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R2.3.2.1. | design temperature; or | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R2.3.2.2. | historical operating temperature; or | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R2.3.2.2. | historical operating temperature; or | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R2.3.2.3. | current cold weather performance temperature determined by an engineering analysis. | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R2.3.2.3. | current cold weather performance temperature determined by an engineering analysis. | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R2.4. | A periodicity for providing data. | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R2.4. | A periodicity for providing data. | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R2.5. | The deadline by which the respondent is to provide the indicated data. | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R2.5. | The deadline by which the respondent is to provide the indicated data. | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R3. | Each Transmission Operator shall distribute its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessment. [Violation Risk Factor: Low] [Time Horizon: Operations Planning] | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R3. | Each Transmission Operator shall distribute its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessment. [Violation Risk Factor: Low] [Time Horizon: Operations Planning] | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R4. | Each Balancing Authority shall distribute its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. [Violation Risk Factor: Low] [Time Horizon: Operations Planning] | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R4. | Each Balancing Authority shall distribute its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. [Violation Risk Factor: Low] [Time Horizon: Operations Planning] | LOWER | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R5. | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall satisfy the obligations of the documented specifications using: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning, Same-Day Operations, Real-time Operations] | MEDIUM | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R5. | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall satisfy the obligations of the documented specifications using: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning, Same-Day Operations, Real-time Operations] | MEDIUM | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R5.1. | A mutually agreeable format | MEDIUM | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R5.1. | A mutually agreeable format | MEDIUM | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R5.2. | A mutually agreeable process for resolving data conflicts | MEDIUM | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R5.2. | A mutually agreeable process for resolving data conflicts | MEDIUM | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R5.3. | A mutually agreeable process for resolving data conflicts | MEDIUM | Effective | 2023-10-01
TOP-003-5 | Operational Reliability Data | R5.3. | A mutually agreeable process for resolving data conflicts | MEDIUM | Effective | 2023-10-01
TOP-003-6.1 | Transmission Operator and Balancing Authority Data and Information Specification and Collection | R1. | Each Transmission Operator shall maintain documented specification(s) for the data and information necessary for it to perform its Operational Planning Analyses, Realtime monitoring, and Real-time Assessments. The specification shall include, but not be limited to: [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Future Effective | 2025-10-01 |  | TOP
TOP-003-6.1 | Transmission Operator and Balancing Authority Data and Information Specification and Collection | R1.1. | A list of data and information needed by the Transmission Operator to support its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments including non-BES data and information, external network data and information, and identification of the entities responsible for responding to the specification as deemed necessary by the Transmission Operator. | LOWER | Future Effective | 2025-10-01 |  | TOP
TOP-003-6.1 | Transmission Operator and Balancing Authority Data and Information Specification and Collection | R1.2. | Provisions for notification of current Protection System and Remedial Action Scheme (RAS) status or degradation that impacts System reliability. | LOWER | Future Effective | 2025-10-01 |  | TOP
TOP-003-6.1 | Transmission Operator and Balancing Authority Data and Information Specification and Collection | R1.3. | Provisions for notification of BES generating unit(s) during local forecasted cold weather to include: | LOWER | Future Effective | 2025-10-01 |  | TOP
TOP-003-6.1 | Transmission Operator and Balancing Authority Data and Information Specification and Collection | R1.3.1. | Operating limitations based on: | LOWER | Future Effective | 2025-10-01 |  | TOP
TOP-003-6.1 | Transmission Operator and Balancing Authority Data and Information Specification and Collection | R1.3.1.1. | capability and availability; | LOWER | Future Effective | 2025-10-01 |  | TOP
TOP-003-6.1 | Transmission Operator and Balancing Authority Data and Information Specification and Collection | R1.3.1.2. | fuel supply and inventory concerns; | LOWER | Future Effective | 2025-10-01 |  | TOP
TOP-003-6.1 | Transmission Operator and Balancing Authority Data and Information Specification and Collection | R1.3.1.3. | fuel switching capabilities; and | LOWER | Future Effective | 2025-10-01 |  | TOP
TOP-003-6.1 | Transmission Operator and Balancing Authority Data and Information Specification and Collection | R1.3.1.4. | environmental constraints | LOWER | Future Effective | 2025-10-01 |  | TOP
TOP-003-6.1 | Transmission Operator and Balancing Authority Data and Information Specification and Collection | R1.3.2. | Generating unit(s) minimum: | LOWER | Future Effective | 2025-10-01 |  | TOP
TOP-003-6.1 | Transmission Operator and Balancing Authority Data and Information Specification and Collection | R1.3.2.1. | design temperature; or | LOWER | Future Effective | 2025-10-01 |  | TOP
TOP-003-6.1 | Transmission Operator and Balancing Authority Data and Information Specification and Collection | R1.3.2.2. | historical operating temperature; or | LOWER | Future Effective | 2025-10-01 |  | TOP
TOP-003-6.1 | Transmission Operator and Balancing Authority Data and Information Specification and Collection | R1.3.2.3. | current cold weather performance temperature determined by an engineering analysis. | LOWER | Future Effective | 2025-10-01 |  | TOP
TOP-003-6.1 | Transmission Operator and Balancing Authority Data and Information Specification and Collection | R1.4. | Identification of a mutually agreeable process for resolving conflicts. | LOWER | Future Effective | 2025-10-01 |  | TOP
TOP-003-6.1 | Transmission Operator and Balancing Authority Data and Information Specification and Collection | R1.5. | Method(s) for the entity identified in Part 1.1 to provide the data and information that includes at a minimum the following. | LOWER | Future Effective | 2025-10-01 |  | TOP
TOP-003-6.1 | Transmission Operator and Balancing Authority Data and Information Specification and Collection | R1.5.1. | Specified deadlines or periodicity which data and information is to be provided; | LOWER | Future Effective | 2025-10-01 |  | TOP
TOP-003-6.1 | Transmission Operator and Balancing Authority Data and Information Specification and Collection | R1.5.2. | Performance criteria for the availability and accuracy of data and information as applicable; | LOWER | Future Effective | 2025-10-01 |  | TOP
TOP-003-6.1 | Transmission Operator and Balancing Authority Data and Information Specification and Collection | R1.5.3. | Provisions to update or correct data and information, as applicable or necessary; | LOWER | Future Effective | 2025-10-01 |  | TOP
TOP-003-6.1 | Transmission Operator and Balancing Authority Data and Information Specification and Collection | R1.5.4. | A mutually agreeable format; | LOWER | Future Effective | 2025-10-01 |  | TOP
TOP-003-6.1 | Transmission Operator and Balancing Authority Data and Information Specification and Collection | R1.5.5. | Mutually agreeable method(s) for securely transferring data and information. | LOWER | Future Effective | 2025-10-01 |  | TOP
TOP-003-6.1 | Transmission Operator and Balancing Authority Data and Information Specification and Collection | R2. | Each Balancing Authority shall maintain documented specification(s) for the data and information necessary for it to perform its analysis functions and Real-time monitoring. The data specification shall include, but not be limited to: [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Future Effective | 2025-10-01 |  | BA
TOP-003-6.1 | Transmission Operator and Balancing Authority Data and Information Specification and Collection | R2.1. | A list of data and information needed by the Balancing Authority to support its analysis functions and Real-time monitoring including non-Bulk Electric System data and information, and external network data and information, as deemed necessary by the Balancing Authority, and identification of the entity responsible for responding to the specification. | LOWER | Future Effective | 2025-10-01 |  | BA
TOP-003-6.1 | Transmission Operator and Balancing Authority Data and Information Specification and Collection | R2.2. | Provisions for notification of current Protection System and Remedial Action Scheme status or degradation that impacts System reliability. | LOWER | Future Effective | 2025-10-01 |  | BA
TOP-003-6.1 | Transmission Operator and Balancing Authority Data and Information Specification and Collection | R2.3. | Provisions for notification of BES generating unit(s) status during local forecasted cold weather to include: | LOWER | Future Effective | 2025-10-01 |  | BA
TOP-003-6.1 | Transmission Operator and Balancing Authority Data and Information Specification and Collection | R2.3.1. | Operating limitations based on: | LOWER | Future Effective | 2025-10-01 |  | BA
TOP-003-6.1 | Transmission Operator and Balancing Authority Data and Information Specification and Collection | R2.3.1.1. | capability and availability; | LOWER | Future Effective | 2025-10-01 |  | BA
TOP-003-6.1 | Transmission Operator and Balancing Authority Data and Information Specification and Collection | R2.3.1.2. | fuel supply and inventory concerns; | LOWER | Future Effective | 2025-10-01 |  | BA
TOP-003-6.1 | Transmission Operator and Balancing Authority Data and Information Specification and Collection | R2.3.1.3. | fuel switching capabilities; and | LOWER | Future Effective | 2025-10-01 |  | BA
TOP-003-6.1 | Transmission Operator and Balancing Authority Data and Information Specification and Collection | R2.3.1.4. | environmental constraints. | LOWER | Future Effective | 2025-10-01 |  | BA
TOP-003-6.1 | Transmission Operator and Balancing Authority Data and Information Specification and Collection | R2.3.2. | Generating unit(s) minimum: | LOWER | Future Effective | 2025-10-01 |  | BA
TOP-003-6.1 | Transmission Operator and Balancing Authority Data and Information Specification and Collection | R2.3.2.1. | design temperature; or | LOWER | Future Effective | 2025-10-01 |  | BA
TOP-003-6.1 | Transmission Operator and Balancing Authority Data and Information Specification and Collection | R2.3.2.2. | historical operating temperature; or | LOWER | Future Effective | 2025-10-01 |  | BA
TOP-003-6.1 | Transmission Operator and Balancing Authority Data and Information Specification and Collection | R2.3.2.3. | current cold weather performance temperature determined by an engineering analysis. | LOWER | Future Effective | 2025-10-01 |  | BA
TOP-003-6.1 | Transmission Operator and Balancing Authority Data and Information Specification and Collection | R2.4. | Identification of a mutually agreeable process in resolving conflicts | LOWER | Future Effective | 2025-10-01 |  | BA
TOP-003-6.1 | Transmission Operator and Balancing Authority Data and Information Specification and Collection | R2.5. | Methods for the entity identified in Part 2.1 to provide data and information that includes at a minimum the following. | LOWER | Future Effective | 2025-10-01 |  | BA
TOP-003-6.1 | Transmission Operator and Balancing Authority Data and Information Specification and Collection | R2.5.1. | Specific deadlines or periodicity in which data and information is to be provided; | LOWER | Future Effective | 2025-10-01 |  | BA
TOP-003-6.1 | Transmission Operator and Balancing Authority Data and Information Specification and Collection | R2.5.2. | Performance criteria for the availability and accuracy of data and information, as applicable; | LOWER | Future Effective | 2025-10-01 |  | BA
TOP-003-6.1 | Transmission Operator and Balancing Authority Data and Information Specification and Collection | R2.5.3. | Provisions to update or correct data and information, as applicable or necessary. | LOWER | Future Effective | 2025-10-01 |  | BA
TOP-003-6.1 | Transmission Operator and Balancing Authority Data and Information Specification and Collection | R2.5.4. | A mutually agreeable format. | LOWER | Future Effective | 2025-10-01 |  | BA
TOP-003-6.1 | Transmission Operator and Balancing Authority Data and Information Specification and Collection | R2.5.5. | A mutually agreeable method(s) for securely transferring data and information. | LOWER | Future Effective | 2025-10-01 |  | BA
TOP-003-6.1 | Transmission Operator and Balancing Authority Data and Information Specification and Collection | R3. | Each Transmission Operator shall distribute its data and information specification(s) to entities that have data and information required by the Transmission Operator’s Operational Planning Analyses, Real- time monitoring, and Real-time Assessments. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Future Effective | 2025-10-01 |  | TOP
TOP-003-6.1 | Transmission Operator and Balancing Authority Data and Information Specification and Collection | R4. | Each Balancing Authority shall distribute its data and information specification(s) to entities that have data and information required by the Balancing Authority’s analysis functions and Real-time monitoring. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | LOWER | Future Effective | 2025-10-01 |  | BA
TOP-003-6.1 | Transmission Operator and Balancing Authority Data and Information Specification and Collection | R5. | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data and information specification(s) in Requirement R3 or R4 shall satisfy the obligations of thedocumented specifications. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning, Same-Day Operations, Real-time Operations] | MEDIUM | Future Effective | 2025-10-01 |  | TOP, TO, GOP, GO, DP, BA
TOP-004-2 | Transmission Operations | R1. | Each Transmission Operator shall operate within the Interconnection Reliability Operating Limits (IROLs) and System Operating Limits (SOLs). | HIGH | Retired | 2009-06-25 | 2017-03-31 | TOP
TOP-004-2 | Transmission Operations | R2. | Each Transmission Operator shall operate so that instability, uncontrolled separation, or cascading outages will not occur as a result of the most severe single contingency. | HIGH | Retired | 2009-06-25 | 2017-03-31 | TOP
TOP-004-2 | Transmission Operations | R3. | Each Transmission Operator shall operate to protect against instability, uncontrolled separation, or cascading outages resulting from multiple outages, as specified by its Reliability Coordinator. | HIGH | Retired | 2009-06-25 | 2017-03-31 | TOP
TOP-004-2 | Transmission Operations | R4. | If a Transmission Operator enters an unknown operating state (i.e. any state for which valid operating limits have not been determined), it will be considered to be in an emergency and shall restore operations to respect proven reliable power system limits within 30 minutes. | HIGH | Retired | 2009-06-25 | 2017-03-31 | TOP
TOP-004-2 | Transmission Operations | R5. | Each Transmission Operator shall make every effort to remain connected to the Interconnection. If the Transmission Operator determines that by remaining interconnected, it is in imminent danger of violating an IROL or SOL, the Transmission Operator may take such actions, as it deems necessary, to protect its area. | HIGH | Retired | 2009-06-25 | 2017-03-31 | TOP
TOP-004-2 | Transmission Operations | R6. | Transmission Operators, individually and jointly with other Transmission Operators, shall develop, maintain, and implement formal policies and procedures to provide for transmission reliability. These policies and procedures shall address the execution and coordination of activities that impact inter- and intra-Regional reliability, including: | MEDIUM | Retired | 2009-06-25 | 2017-03-31 | TOP
TOP-004-2 | Transmission Operations | R6.1. | Monitoring and controlling voltage levels and real and reactive power flows. | MEDIUM | Retired | 2009-06-25 | 2017-03-31 | TOP
TOP-004-2 | Transmission Operations | R6.2. | Switching transmission elements. | MEDIUM | Retired | 2009-06-25 | 2017-03-31 | TOP
TOP-004-2 | Transmission Operations | R6.3. | Planned outages of transmission elements. | MEDIUM | Retired | 2009-06-25 | 2017-03-31 | TOP
TOP-004-2 | Transmission Operations | R6.4. | Responding to IROL and SOL violations. | MEDIUM | Retired | 2009-06-25 | 2017-03-31 | TOP
TOP-005-2a | Operational Reliability Information | R1. | As a condition of receiving data from the Interregional Security Network (ISN), each ISN data recipient shall sign the NERC Confidentiality Agreement for “Electric System Reliability Data.” | N/A | Retired | 2011-10-01 | 2017-03-31
TOP-005-2a | Operational Reliability Information | R2. | Upon request, each Balancing Authority and Transmission Operator shall provide to other Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability, the operating data that are necessary to allow these Balancing Authorities and Transmission Operators to perform operational reliability assessments and to coordinate reliable operations. Balancing Authorities and Transmission Operators shall provide the types of data as listed in Attachment 1-TOP-005 “Electric System Reliability Data,” unless otherwise agreed to by the Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability. | N/A | Retired | 2011-10-01 | 2017-03-31 | TOP, BA
TOP-005-2a | Operational Reliability Information | R3. | Each Purchasing-Selling Entity shall provide information as requested by its Host Balancing Authorities and Transmission Operators to enable them to conduct operational reliability assessments and coordinate reliable operations. | N/A | Retired | 2011-10-01 | 2017-03-31
TOP-005-3a | Operational Reliability Information | R1. | As a condition of receiving data from the Interregional Security Network (ISN), each ISN data recipient shall sign the NERC Confidentiality Agreement for “Electric System Reliability Data.” | N/A | Never Came Into Effect in Ontario
TOP-005-3a | Operational Reliability Information | R2. | Upon request, each Balancing Authority and Transmission Operator shall provide to other Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability, the operating data that are necessary to allow these Balancing Authorities and Transmission Operators to perform operational reliability assessments and to coordinate reliable operations. Balancing Authorities and Transmission Operators shall provide the types of data as listed in Attachment 1-TOP-005 “Electric System Reliability Data,” unless otherwise agreed to by the Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability. | N/A | Never Came Into Effect in Ontario |  |  | TOP, BA
TOP-005-3a | Operational Reliability Information | R3. | Each Purchasing-Selling Entity shall provide information as requested by its Host Balancing Authorities and Transmission Operators to enable them to conduct operational reliability assessments and coordinate reliable operations. | N/A | Never Came Into Effect in Ontario
TOP-006-2 | Monitoring System Conditions | R1. | Each Transmission Operator and Balancing Authority shall know the status of all generation and transmission resources available for use. | MEDIUM | Retired | 2011-10-01 | 2017-03-31 | TOP, BA
TOP-006-2 | Monitoring System Conditions | R1.1. | Each Generator Operator shall inform its Host Balancing Authority and the Transmission Operator of all generation resources available for use. | MEDIUM | Retired | 2011-10-01 | 2017-03-31 | GOP
TOP-006-2 | Monitoring System Conditions | R1.2. | Each Transmission Operator and Balancing Authority shall inform the Reliability Coordinator and other affected Balancing Authorities and Transmission Operators of all generation and transmission resources available for use. | MEDIUM | Retired | 2011-10-01 | 2017-03-31 | TOP, BA
TOP-006-2 | Monitoring System Conditions | R2. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall monitor applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. | HIGH | Retired | 2011-10-01 | 2017-03-31 | TOP, RC, BA
TOP-006-2 | Monitoring System Conditions | R3. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall provide appropriate technical information concerning protective relays to their operating personnel. | MEDIUM | Retired | 2011-10-01 | 2017-03-31 | TOP, RC, BA
TOP-006-2 | Monitoring System Conditions | R4. | Each Transmission Operator, and Balancing Authority shall have information, including weather forecasts and past load patterns, available to predict the system’s near-term load pattern. | MEDIUM | Retired | 2011-10-01 | 2017-03-31 | TOP, BA
TOP-006-2 | Monitoring System Conditions | R5. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall use monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions and to indicate, if appropriate, the need for corrective action. | MEDIUM | Retired | 2011-10-01 | 2017-03-31 | TOP, RC, BA
TOP-006-2 | Monitoring System Conditions | R6. | Each Balancing Authority and Transmission Operator shall use sufficient metering of suitable range, accuracy and sampling rate (if applicable) to ensure accurate and timely monitoring of operating conditions under both normal and emergency situations. | HIGH | Retired | 2011-10-01 | 2017-03-31 | TOP, BA
TOP-006-2 | Monitoring System Conditions | R7. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall monitor system frequency. | HIGH | Retired | 2011-10-01 | 2017-03-31 | TOP, RC, BA
TOP-006-3 | Monitoring System Conditions | R1. | Each Transmission Operator and Balancing Authority shall know the status of all generation and transmission resources available for use. [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | MEDIUM | Never Came Into Effect in Ontario |  |  | TOP, BA
TOP-006-3 | Monitoring System Conditions | R1.1. | Each Generator Operator shall inform its Host Balancing Authority and the Transmission Operator of all generation resources available for use. [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | MEDIUM | Never Came Into Effect in Ontario |  |  | GOP
TOP-006-3 | Monitoring System Conditions | R1.2. | Each Transmission Operator shall inform the Reliability Coordinator and other affected Transmission Operators of all transmission resources available for use. [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | MEDIUM | Never Came Into Effect in Ontario |  |  | TOP
TOP-006-3 | Monitoring System Conditions | R1.3. | Each Balancing Authority shall inform its Reliability Coordinator of all generation resources available for use. [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | MEDIUM | Never Came Into Effect in Ontario |  |  | BA
TOP-006-3 | Monitoring System Conditions | R2. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall monitor applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. [Violation Risk Factor: High] [Time Horizon: Real-time Operations] | HIGH | Never Came Into Effect in Ontario |  |  | TOP, RC, BA
TOP-006-3 | Monitoring System Conditions | R3. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall provide its operating personnel with appropriate technical information concerning protective relays within the Reliability Coordinator Area, the Transmission Operator Area, and the Balancing Authority Area, respectively. [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | HIGH | Never Came Into Effect in Ontario |  |  | TOP, RC, BA
TOP-006-3 | Monitoring System Conditions | R4. | Each Transmission Operator, and Balancing Authority shall have information, including weather forecasts and past load patterns, available to predict the system’s near-term load pattern. [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | MEDIUM | Never Came Into Effect in Ontario |  |  | TOP, BA
TOP-006-3 | Monitoring System Conditions | R5. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall use monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions and to indicate, if appropriate, the need for corrective action. [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | MEDIUM | Never Came Into Effect in Ontario |  |  | TOP, RC, BA
TOP-006-3 | Monitoring System Conditions | R6. | Each Balancing Authority and Transmission Operator shall use sufficient metering of suitable range, accuracy and sampling rate (if applicable) to ensure accurate and timely monitoring of operating conditions under both normal and emergency situations. [Violation Risk Factor: High] [Time Horizon: Real-time Operations] | HIGH | Never Came Into Effect in Ontario |  |  | TOP, BA
TOP-006-3 | Monitoring System Conditions | R7. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall monitor system frequency. [Violation Risk Factor: High] [Time Horizon: Real-time Operations] | HIGH | Never Came Into Effect in Ontario |  |  | TOP, RC, BA
TOP-007-0 | Reporting System Operating Limit (SOL) and Interconnection Reliability Operating Limit (IROL) Violations | R1. | A Transmission Operator shall inform its Reliability Coordinator when an IROL or SOL has been exceeded and the actions being taken to return the system to within limits. | HIGH | Retired | 2005-02-08 | 2017-03-31 | TOP
TOP-007-0 | Reporting System Operating Limit (SOL) and Interconnection Reliability Operating Limit (IROL) Violations | R2. | Following a Contingency or other event that results in an IROL violation, the Transmission Operator shall return its transmission system to within IROL as soon as possible, but not longer than 30 minutes. | HIGH | Retired | 2005-02-08 | 2017-03-31 | TOP
TOP-007-0 | Reporting System Operating Limit (SOL) and Interconnection Reliability Operating Limit (IROL) Violations | R3. | A Transmission Operator shall take all appropriate actions up to and including shedding firm load, or directing the shedding of firm load, in order to comply with Requirement R 2. | HIGH | Retired | 2005-02-08 | 2017-03-31 | TOP
TOP-007-0 | Reporting System Operating Limit (SOL) and Interconnection Reliability Operating Limit (IROL) Violations | R4. | The Reliability Coordinator shall evaluate actions taken to address an IROL or SOL violation and, if the actions taken are not appropriate or sufficient, direct actions required to return the system to within limits. | HIGH | Retired | 2005-02-08 | 2017-03-31 | RC
TOP-008-1 | Response to Transmission Limit Violations | R1. | The Transmission Operator experiencing or contributing to an IROL or SOL violation shall take immediate steps to relieve the condition, which may include shedding firm load. | HIGH | Retired | 2006-11-01 | 2017-03-31 | TOP
TOP-008-1 | Response to Transmission Limit Violations | R2. | Each Transmission Operator shall operate to prevent the likelihood that a disturbance, action, or inaction will result in an IROL or SOL violation in its area or another area of the Interconnection. In instances where there is a difference in derived operating limits, the Transmission Operator shall always operate the Bulk Electric System to the most limiting parameter. | HIGH | Retired | 2006-11-01 | 2017-03-31 | TOP
TOP-008-1 | Response to Transmission Limit Violations | R3. | The Transmission Operator shall disconnect the affected facility if the overload on a transmission facility or abnormal voltage or reactive condition persists and equipment is endangered. In doing so, the Transmission Operator shall notify its Reliability Coordinator and all neighboring Transmission Operators impacted by the disconnection prior to switching, if time permits, otherwise, immediately thereafter. | HIGH | Retired | 2006-11-01 | 2017-03-31 | TOP
TOP-008-1 | Response to Transmission Limit Violations | R4. | The Transmission Operator shall have sufficient information and analysis tools to determine the cause(s) of SOL violations. This analysis shall be conducted in all operating timeframes. The Transmission Operator shall use the results of these analyses to immediately mitigate the SOL violation. | MEDIUM | Retired | 2006-11-01 | 2017-03-31 | TOP
TOP-010-1 | Real-time Reliability Monitoring and Analysis Capabilities | R1. | Each Transmission Operator shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. The Operating Process or Operating Procedure shall include: | HIGH | Retired | 2018-04-01 | 2018-03-31 | TOP
TOP-010-1 | Real-time Reliability Monitoring and Analysis Capabilities | R1.1. | Criteria for evaluating the quality of Real-time data; | HIGH | Retired | 2018-04-01 | 2018-03-31 | TOP
TOP-010-1 | Real-time Reliability Monitoring and Analysis Capabilities | R1.2. | Provisions to indicate the quality of Real-time data to the System Operator; and | HIGH | Retired | 2018-04-01 | 2018-03-31 | TOP
TOP-010-1 | Real-time Reliability Monitoring and Analysis Capabilities | R1.3. | Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects Real-time Assessments. | HIGH | Retired | 2018-04-01 | 2018-03-31 | TOP
TOP-010-1 | Real-time Reliability Monitoring and Analysis Capabilities | R2. | Each Balancing Authority shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. The Operating Process or Operating Procedure shall include: | HIGH | Retired | 2018-04-01 | 2018-03-31 | BA
TOP-010-1 | Real-time Reliability Monitoring and Analysis Capabilities | R2.1. | Criteria for evaluating the quality of Real-time data; | HIGH | Retired | 2018-04-01 | 2018-03-31 | BA
TOP-010-1 | Real-time Reliability Monitoring and Analysis Capabilities | R2.2. | Provisions to indicate the quality of Real-time data to the System Operator; and | HIGH | Retired | 2018-04-01 | 2018-03-31 | BA
TOP-010-1 | Real-time Reliability Monitoring and Analysis Capabilities | R2.3. | Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects its analysis functions. | HIGH | Retired | 2018-04-01 | 2018-03-31 | BA
TOP-010-1 | Real-time Reliability Monitoring and Analysis Capabilities | R3. | Each Transmission Operator shall implement an Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments. The Operating Process or Operating Procedure shall include: | MEDIUM | Retired | 2018-04-01 | 2018-03-31 | TOP
TOP-010-1 | Real-time Reliability Monitoring and Analysis Capabilities | R3.1. | Criteria for evaluating the quality of analysis used in its Real-time Assessments; | MEDIUM | Retired | 2018-04-01 | 2018-03-31 | TOP
TOP-010-1 | Real-time Reliability Monitoring and Analysis Capabilities | R3.2. | Provisions to indicate the quality of analysis used in its Real-time Assessments; and | MEDIUM | Retired | 2018-04-01 | 2018-03-31 | TOP
TOP-010-1 | Real-time Reliability Monitoring and Analysis Capabilities | R3.3. | Actions to address analysis quality issues affecting its Real-time Assessments. | MEDIUM | Retired | 2018-04-01 | 2018-03-31 | TOP
TOP-010-1 | Real-time Reliability Monitoring and Analysis Capabilities | R4. | Each Transmission Operator and Balancing Authority shall have an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. | MEDIUM | Retired | 2018-04-01 | 2018-03-31 | TOP, BA
TOP-010-1(i) | Real-time Reliability Monitoring and Analysis Capabilities | R1. | Each Transmission Operator shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. The Operating Process or Operating Procedure shall include: [Violation Risk Factor: High] [Time Horizon: Real-time Operations] | HIGH | Effective | 2018-04-01 |  | TOP
TOP-010-1(i) | Real-time Reliability Monitoring and Analysis Capabilities | R1.1. | Criteria for evaluating the quality of Real-time data; | HIGH | Effective | 2018-04-01 |  | TOP
TOP-010-1(i) | Real-time Reliability Monitoring and Analysis Capabilities | R1.2. | Provisions to indicate the quality of Real-time data to the System Operator; and | HIGH | Effective | 2018-04-01 |  | TOP
TOP-010-1(i) | Real-time Reliability Monitoring and Analysis Capabilities | R1.3. | Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects Real-time Assessments. | HIGH | Effective | 2018-04-01 |  | TOP
TOP-010-1(i) | Real-time Reliability Monitoring and Analysis Capabilities | R2. | Each Balancing Authority shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. The Operating Process or Operating Procedure shall include: [Violation Risk Factor: High] [Time Horizon: Real-time Operations] | HIGH | Effective | 2018-04-01 |  | BA
TOP-010-1(i) | Real-time Reliability Monitoring and Analysis Capabilities | R2.1. | Criteria for evaluating the quality of Real-time data; | HIGH | Effective | 2018-04-01 |  | BA
TOP-010-1(i) | Real-time Reliability Monitoring and Analysis Capabilities | R2.2. | Provisions to indicate the quality of Real-time data to the System Operator; and | HIGH | Effective | 2018-04-01 |  | BA
TOP-010-1(i) | Real-time Reliability Monitoring and Analysis Capabilities | R2.3. | Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects its analysis functions. | HIGH | Effective | 2018-04-01 |  | BA
TOP-010-1(i) | Real-time Reliability Monitoring and Analysis Capabilities | R3. | Each Transmission Operator shall implement an Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments. The Operating Process or Operating Procedure shall include: [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | MEDIUM | Effective | 2018-04-01 |  | TOP
TOP-010-1(i) | Real-time Reliability Monitoring and Analysis Capabilities | R3.1. | Criteria for evaluating the quality of analysis used in its Real-time Assessments; | MEDIUM | Effective | 2018-04-01 |  | TOP
TOP-010-1(i) | Real-time Reliability Monitoring and Analysis Capabilities | R3.2. | Provisions to indicate the quality of analysis used in its Real-time Assessments; and | MEDIUM | Effective | 2018-04-01 |  | TOP
TOP-010-1(i) | Real-time Reliability Monitoring and Analysis Capabilities | R3.3. | Actions to address analysis quality issues affecting its Real-time Assessments. | MEDIUM | Effective | 2018-04-01 |  | TOP
TOP-010-1(i) | Real-time Reliability Monitoring and Analysis Capabilities | R4. | Each Transmission Operator and Balancing Authority shall have an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | MEDIUM | Effective | 2018-04-01 |  | TOP, BA
TPL-001-0.1(i) | System Performance Under Normal (No Contingency) Conditions (Category A) | R1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that, with all transmission facilities in service and with normal (pre-contingency) operating procedures in effect, the Network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services at all Demand levels over the range of forecast system demands, under the conditions defined in Category A of Table I. To be considered valid, the Planning Authority and Transmission Planner assessments shall: | HIGH | Retired |  |  | TP, PA
TPL-001-0.1(i) | System Performance Under Normal (No Contingency) Conditions (Category A) | R1.1. | Be made annually. | MEDIUM | Retired |  |  | TP, PA
TPL-001-0.1(i) | System Performance Under Normal (No Contingency) Conditions (Category A) | R1.2. | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. | MEDIUM | Retired |  |  | TP, PA
TPL-001-0.1(i) | System Performance Under Normal (No Contingency) Conditions (Category A) | R1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category A of Table 1 (no contingencies). The specific elements selected (from each of the following categories) shall be acceptable to the associated Regional Reliability Organization(s). | MEDIUM | Retired |  |  | TP, PA
TPL-001-0.1(i) | System Performance Under Normal (No Contingency) Conditions (Category A) | R1.3.1. | Cover critical system conditions and study years as deemed appropriate by the entity performing the study. | MEDIUM | Retired |  |  | TP, PA
TPL-001-0.1(i) | System Performance Under Normal (No Contingency) Conditions (Category A) | R1.3.2. | Be conducted annually unless changes to system conditions do not warrant such analyses. | MEDIUM | Retired |  |  | TP, PA
TPL-001-0.1(i) | System Performance Under Normal (No Contingency) Conditions (Category A) | R1.3.3. | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. | MEDIUM | Retired |  |  | TP, PA
TPL-001-0.1(i) | System Performance Under Normal (No Contingency) Conditions (Category A) | R1.3.4. | Have established normal (pre-contingency) operating procedures in place. | MEDIUM | Retired |  |  | TP, PA
TPL-001-0.1(i) | System Performance Under Normal (No Contingency) Conditions (Category A) | R1.3.5. | Have all projected firm transfers modeled. | MEDIUM | Retired |  |  | TP, PA
TPL-001-0.1(i) | System Performance Under Normal (No Contingency) Conditions (Category A) | R1.3.6. | Be performed for selected demand levels over the range of forecast system demands. | MEDIUM | Retired |  |  | TP, PA
TPL-001-0.1(i) | System Performance Under Normal (No Contingency) Conditions (Category A) | R1.3.7. | Demonstrate that system performance meets Table 1 for Category A (no contingencies). | MEDIUM | Retired |  |  | TP, PA
TPL-001-0.1(i) | System Performance Under Normal (No Contingency) Conditions (Category A) | R1.3.8. | Include existing and planned facilities. | MEDIUM | Retired |  |  | TP, PA
TPL-001-0.1(i) | System Performance Under Normal (No Contingency) Conditions (Category A) | R1.3.9. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. | MEDIUM | Retired |  |  | TP, PA
TPL-001-0.1(i) | System Performance Under Normal (No Contingency) Conditions (Category A) | R1.4. | Address any planned upgrades needed to meet the performance requirements of Category A. | MEDIUM | Retired |  |  | TP, PA
TPL-001-0.1(i) | System Performance Under Normal (No Contingency) Conditions (Category A) | R2. | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-001-0.1(i)_R1, the Planning Authority and Transmission Planner shall each: | MEDIUM | Retired |  |  | TP, PA
TPL-001-0.1(i) | System Performance Under Normal (No Contingency) Conditions (Category A) | R2.1. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon. | MEDIUM | Retired |  |  | TP, PA
TPL-001-0.1(i) | System Performance Under Normal (No Contingency) Conditions (Category A) | R2.1.1. | Including a schedule for implementation. | MEDIUM | Retired |  |  | TP, PA
TPL-001-0.1(i) | System Performance Under Normal (No Contingency) Conditions (Category A) | R2.1.2. | Including a discussion of expected required in-service dates of facilities. | MEDIUM | Retired |  |  | TP, PA
TPL-001-0.1(i) | System Performance Under Normal (No Contingency) Conditions (Category A) | R2.1.3. | Consider lead times necessary to implement plans. | MEDIUM | Retired |  |  | TP, PA
TPL-001-0.1(i) | System Performance Under Normal (No Contingency) Conditions (Category A) | R2.2. | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. | LOWER | Retired |  |  | TP, PA
TPL-001-0.1(i) | System Performance Under Normal (No Contingency) Conditions (Category A) | R3. | The Planning Authority and Transmission Planner shall each document the results of these reliability assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. | LOWER | Retired |  |  | TP, PA
TPL-001-1 | System Performance Under Normal (No Contingency) Conditions (Category A) | R1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that, with all transmission facilities in service and with normal (pre-contingency) operating procedures in effect, the Network can be operated to supply projected customer demands and projected Firm (non- recallable reserved) Transmission Services at all Demand levels over the range of forecast system demands, under the conditions defined in Category A of Table I. To be considered valid, the Planning Authority and Transmission Planner assessments shall: | HIGH | Retired |  |  | TP, PA
TPL-001-1 | System Performance Under Normal (No Contingency) Conditions (Category A) | R1.1. | Be made annually. | MEDIUM | Retired |  |  | TP, PA
TPL-001-1 | System Performance Under Normal (No Contingency) Conditions (Category A) | R1.2. | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. | MEDIUM | Retired |  |  | TP, PA
TPL-001-1 | System Performance Under Normal (No Contingency) Conditions (Category A) | R1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category A of Table 1 (no contingencies). The specific elements selected (from each of the following categories) shall be acceptable to the associated Regional Reliability Organization(s). | MEDIUM | Retired |  |  | TP, PA
TPL-001-1 | System Performance Under Normal (No Contingency) Conditions (Category A) | R1.3.1. | Cover critical system conditions and study years as deemed appropriate by the entity performing the study. | MEDIUM | Retired |  |  | TP, PA
TPL-001-1 | System Performance Under Normal (No Contingency) Conditions (Category A) | R1.3.2. | Be conducted annually unless changes to system conditions do not warrant such analyses. | MEDIUM | Retired |  |  | TP, PA
TPL-001-1 | System Performance Under Normal (No Contingency) Conditions (Category A) | R1.3.3. | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. | MEDIUM | Retired |  |  | TP, PA
TPL-001-1 | System Performance Under Normal (No Contingency) Conditions (Category A) | R1.3.4. | Have established normal (pre-contingency) operating procedures in place. | MEDIUM | Retired |  |  | TP, PA
TPL-001-1 | System Performance Under Normal (No Contingency) Conditions (Category A) | R1.3.5. | Have all projected firm transfers modeled. | MEDIUM | Retired |  |  | TP, PA
TPL-001-1 | System Performance Under Normal (No Contingency) Conditions (Category A) | R1.3.6. | Be performed for selected demand levels over the range of forecast system demands. | MEDIUM | Retired |  |  | TP, PA
TPL-001-1 | System Performance Under Normal (No Contingency) Conditions (Category A) | R1.3.7. | Demonstrate that system performance meets Table 1 for Category A (no contingencies). | MEDIUM | Retired |  |  | TP, PA
TPL-001-1 | System Performance Under Normal (No Contingency) Conditions (Category A) | R1.3.8. | Include existing and planned facilities. | MEDIUM | Retired |  |  | TP, PA
TPL-001-1 | System Performance Under Normal (No Contingency) Conditions (Category A) | R1.3.9. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. | MEDIUM | Retired |  |  | TP, PA
TPL-001-1 | System Performance Under Normal (No Contingency) Conditions (Category A) | R1.4. | Address any planned upgrades needed to meet the performance requirements of Category A. | MEDIUM | Retired |  |  | TP, PA
TPL-001-1 | System Performance Under Normal (No Contingency) Conditions (Category A) | R2. | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-001-1_R1, the Planning Authority and Transmission Planner shall each: | MEDIUM | Retired |  |  | TP, PA
TPL-001-1 | System Performance Under Normal (No Contingency) Conditions (Category A) | R2.1. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon. | MEDIUM | Retired |  |  | TP, PA
TPL-001-1 | System Performance Under Normal (No Contingency) Conditions (Category A) | R2.1.1. | Including a schedule for implementation. | MEDIUM | Retired |  |  | TP, PA
TPL-001-1 | System Performance Under Normal (No Contingency) Conditions (Category A) | R2.1.2. | Including a discussion of expected required in-service dates of facilities. | MEDIUM | Retired |  |  | TP, PA
TPL-001-1 | System Performance Under Normal (No Contingency) Conditions (Category A) | R2.1.3. | Consider lead times necessary to implement plans. | MEDIUM | Retired |  |  | TP, PA
TPL-001-1 | System Performance Under Normal (No Contingency) Conditions (Category A) | R2.2. | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. | LOWER | Retired |  |  | TP, PA
TPL-001-1 | System Performance Under Normal (No Contingency) Conditions (Category A) | R3. | The Planning Authority and Transmission Planner shall each document the results of these reliability assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. | LOWER | Retired |  |  | TP, PA
TPL-001-2 | Transmission System Planning Performance Requirements | R1. | Each Transmission Planner and Planning Coordinator shall maintain System models within its respective area for performing the studies needed to complete its Planning Assessment. The models shall use data consistent with that provided in accordance with the MOD-010 and MOD-012 standards, supplemented by other sources as needed, including items represented in the Corrective Action Plan, and shall represent projected System conditions. This establishes Category P0 as the normal System condition in Table 1. | MEDIUM | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R1.1. | System models shall represent: | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R1.1.1. | Existing Facilities | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R1.1.2. | Known outage(s) of generation or Transmission Facility(ies) with a duration of at least six months. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R1.1.3. | New planned Facilities and changes to existing Facilities | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R1.1.4. | Real and reactive Load forecasts | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R1.1.5. | Known commitments for Firm Transmission Service and Interchange | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R1.1.6. | Resources (supply or demand side) required for Load | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R2. | Each Transmission Planner and Planning Coordinator shall prepare an annual Planning Assessment of its portion of the BES. This Planning Assessment shall use current or qualified past studies (as indicated in Requirement R2, Part 2.6), document assumptions, and document summarized results of the steady state analyses, short circuit analyses, and Stability analyses. | HIGH | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R2.1. | For the Planning Assessment, the Near-Term Transmission Planning Horizon portion of the steady state analysis shall be assessed annually and be supported by current annual studies or qualified past studies as indicated in Requirement R2, Part 2.6. Qualifying studies need to include the following conditions: | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R2.1.1. | System peak Load for either Year One or year two, and for year five. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R2.1.2. | System Off-Peak Load for one of the five years. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R2.1.3. | P1 events in Table 1, with known outages modeled as in Requirement R1, Part 1.1.2, under those System peak or Off-Peak conditions when known outages are scheduled. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R2.1.4. | For each of the studies described in Requirement R2, Parts 2.1.1 and 2.1.2, sensitivity case(s) shall be utilized to demonstrate the impact of changes to the basic assumptions used in the model. To accomplish this, the sensitivity analysis in the Planning Assessment must vary one or more of the following conditions by a sufficient amount to stress the System within a range of credible conditions that demonstrate a measurable change in System response : • Real and reactive forecasted Load. • Expected transfers. • Expected in service dates of new or modified Transmission Facilities. • Reactive resource capability. • Generation additions, retirements, or other dispatch scenarios. • Controllable Loads and Demand Side Management. • Duration or timing of known Transmission outages. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R2.1.5. | When an entity’s spare equipment strategy could result in the unavailability of major Transmission equipment that has a lead time of one year or more (such as a transformer), the impact of this possible unavailability on System performance shall be studied. The studies shall be performed for the P0, P1, and P2 categories identified in Table 1 with the conditions that the System is expected to experience during the possible unavailability of the long lead time equipment. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R2.2. | For the Planning Assessment, the Long-Term Transmission Planning Horizon portion of the steady state analysis shall be assessed annually and be supported by the following annual current study, supplemented with qualified past studies as indicated in Requirement R2, Part 2.6: | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R2.2.1. | A current study assessing expected System peak Load conditions for one of the years in the Long-Term Transmission Planning Horizon and the rationale for why that year was selected. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R2.3. | The short circuit analysis portion of the Planning Assessment shall be conducted annually addressing the Near-Term Transmission Planning Horizon and can be supported by current or past studies as qualified in Requirement R2, Part 2.6. The analysis shall be used to determine whether circuit breakers have interrupting capability for Faults that they will be expected to interrupt using the System short circuit model with any planned generation and Transmission Facilities in service which could impact the study area. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R2.4. | For the Planning Assessment, the Near-Term Transmission Planning Horizon portion of the Stability analysis shall be assessed annually and be supported by current or past studies as qualified in Requirement R2, Part2.6. The following studies are required: | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R2.4.1. | System peak Load for one of the five years. System peak Load levels shall include a Load model which represents the expected dynamic behavior of Loads that could impact the study area, considering the behavior of induction motor Loads. An aggregate System Load model which represents the overall dynamic behavior of the Load is acceptable. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R2.4.2. | System Off-Peak Load for one of the five years. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R2.4.3. | For each of the studies described in Requirement R2, Parts 2.4.1 and 2.4.2, sensitivity case(s) shall be utilized to demonstrate the impact of changes to the basic assumptions used in the model. To accomplish this, the sensitivity analysis in the Planning Assessment must vary one or more of the following conditions by a sufficient amount to stress the System within a range of credible conditions that demonstrate a measurable change in performance: • Load level, Load forecast, or dynamic Load model assumptions. • Expected transfers. • Expected in service dates of new or modified Transmission Facilities. • Reactive resource capability. • Generation additions, retirements, or other dispatch scenarios. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R2.5. | For the Planning Assessment, the Long-Term Transmission Planning Horizon portion of the Stability analysis shall be assessed to address the impact of proposed material generation additions or changes in that timeframe and be supported by current or past studies as qualified in Requirement R2, Part2.6 and shall include documentation to support the technical rationale for determining material changes. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R2.6. | Past studies may be used to support the Planning Assessment if they meet the following requirements: | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R2.6.1. | For steady state, short circuit, or Stability analysis: the study shall be five calendar years old or less, unless a technical rationale can be provided to demonstrate that the results of an older study are still valid. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R2.6.2. | For steady state, short circuit, or Stability analysis: no material changes have occurred to the System represented in the study. Documentation to support the technical rationale for determining material changes shall be included. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R2.7. | For planning events shown in Table 1, when the analysis indicates an inability of the System to meet the performance requirements in Table 1, the Planning Assessment shall include Corrective Action Plan(s) addressing how the performance requirements will be met. Revisions to the Corrective Action Plan(s) are allowed in subsequent Planning Assessments but the planned System shall continue to meet the performance requirements in Table 1. Corrective Action Plan(s) do not need to be developed solely to meet the performance requirements for a single sensitivity case analyzed in accordance with Requirements R2, Parts 2.1.4 and 2.4.3. The Corrective Action Plan(s) shall: | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R2.7.1. | List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include: • Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment. • Installation, modification, or removal of Protection Systems or Special Protection Systems • Installation or modification of automatic generation tripping as a response to a single or multiple Contingency to mitigate Stability performance violations. • Installation or modification of manual and automatic generation runback/tripping as a response to a single or multiple Contingency to mitigate steady state performance violations. • Use of Operating Procedures specifying how long they will be needed as part of the Corrective Action Plan. • Use of rate applications, DSM, new technologies, or other initiatives. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R2.7.2. | Include actions to resolve performance deficiencies identified in multiple sensitivity studies or provide a rationale for why actions were not necessary. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R2.7.3. | If situations arise that are beyond the control of the Transmission Planner or Planning Coordinator that prevent the implementation of a Corrective Action Plan in the required timeframe, then the Transmission Planner or Planning Coordinator is permitted to utilize Non-Consequential Load Loss and curtailment of Firm Transmission Service to correct the situation that would normally not be permitted in Table 1, provided that the Transmission Planner or Planning Coordinator documents that they are taking actions to resolve the situation. The Transmission Planner or Planning Coordinator shall document the situation causing the problem, alternatives evaluated, and the use of Non-Consequential Load Loss or curtailment of Firm Transmission Service. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R2.7.4. | Be reviewed in subsequent annual Planning Assessments for continued validity and implementation status of identified System Facilities and Operating Procedures. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R2.8. | For short circuit analysis, if the short circuit current interrupting duty on circuit breakers determined in Requirement R2, Part 2.3 exceeds their Equipment Rating, the Planning Assessment shall include a Corrective Action Plan to address the Equipment Rating violations. The Corrective Action Plan shall: | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R2.8.1. | List System deficiencies and the associated actions needed to achieve required System performance. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R2.8.2. | Be reviewed in subsequent annual Planning Assessments for continued validity and implementation status of identified System Facilities and Operating Procedures. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R3. | For the steady state portion of the Planning Assessment, each Transmission Planner and Planning Coordinator shall perform studies for the Near-Term and Long-Term Transmission Planning Horizons in Requirement R2, Parts 2.1, and 2.2. The studies shall be based on computer simulation models using data provided in Requirement R1. | MEDIUM | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R3.1. | Studies shall be performed for planning events to determine whether the BES meets the performance requirements in Table 1 based on the Contingency list created in Requirement R3, Part 3.4. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R3.2. | Studies shall be performed to assess the impact of the extreme events which are identified by the list created in Requirement R3, Part 3.5. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R3.3. | Contingency analyses for Requirement R3, Parts 3.1 & 3.2 shall: | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R3.3.1. | Simulate the removal of all elements that the Protection System and other automatic controls are expected to disconnect for each Contingency without operator intervention. The analyses shall include the impact of subsequent: | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R3.3.1.1. | Tripping of generators where simulations show generator bus voltages or high side of the generation step up (GSU) voltages are less than known or assumed minimum generator steady state or ride through voltage limitations. Include in the assessment any assumptions made. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R3.3.1.2. | Tripping of Transmission elements where relay loadability limits are exceeded. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R3.3.2. | Simulate the expected automatic operation of existing and planned devices designed to provide steady state control of electrical system quantities when such devices impact the study area. These devices may include equipment such as phase-shifting transformers, load tap changing transformers, and switched capacitors and inductors. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R3.4. | Those planning events in Table 1, that are expected to produce more severe System impacts on its portion of the BES, shall be identified and a list of those Contingencies to be evaluated for System performance in Requirement R3, Part 3.1 created. The rationale for those Contingencies selected for evaluation shall be available as supporting information. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R3.4.1. | The Planning Coordinator and Transmission Planner shall coordinate with adjacent Planning Coordinators and Transmission Planners to ensure that Contingencies on adjacent Systems which may impact their Systems are included in the Contingency list. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R3.5. | Those extreme events in Table 1 that are expected to produce more severe System impacts shall be identified and a list created of those events to be evaluated in Requirement R3, Part 3.2. The rationale for those Contingencies selected for evaluation shall be available as supporting information. If the analysis concludes there is Cascading caused by the occurrence of extreme events, an evaluation of possible actions designed to reduce the likelihood or mitigate the consequences and adverse impacts of the event(s) shall be conducted. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R4. | For the Stability portion of the Planning Assessment, as described in Requirement R2, Parts 2.4 and 2.5, each Transmission Planner and Planning Coordinator shall perform the Contingency analyses listed in Table 1. The studies shall be based on computer simulation models using data provided in Requirement R1. | MEDIUM | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R4.1. | Studies shall be performed for planning events to determine whether the BES meets the performance requirements in Table 1 based on the Contingency list created in Requirement R4, Part 4.4. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R4.1.1. | For planning event P1: No generating unit shall pull out of synchronism. A generator being disconnected from the System by fault clearing action or by a Special Protection System is not considered pulling out of synchronism. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R4.1.2. | For planning events P2 through P7: When a generator pulls out of synchronism in the simulations, the resulting apparent impedance swings shall not result in the tripping of any Transmission system elements other than the generating unit and its directly connected Facilities. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R4.1.3. | For planning events P1 through P7: Power oscillations shall exhibit acceptable damping as established by the Planning Coordinator and Transmission Planner. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R4.2. | Studies shall be performed to assess the impact of the extreme events which are identified by the list created in Requirement R4, Part 4.5. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R4.3. | Contingency analyses for Requirement R4, Parts 4.1 and 4.2 shall : | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R4.3.1. | Simulate the removal of all elements that the Protection System and other automatic controls are expected to disconnect for each Contingency without operator intervention. The analyses shall include the impact of subsequent: | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R4.3.1.1. | Successful high speed (less than one second) reclosing and unsuccessful high speed reclosing into a Fault where high speed reclosing is utilized. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R4.3.1.2. | Tripping of generators where simulations show generator bus voltages or high side of the GSU voltages are less than known or assumed generator low voltage ride through capability. Include in the assessment any assumptions made. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R4.3.1.3. | Tripping of Transmission lines and transformers where transient swings cause Protection System operation based on generic or actual relay models. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R4.3.2. | Simulate the expected automatic operation of existing and planned devices designed to provide dynamic control of electrical system quantities when such devices impact the study area. These devices may include equipment such as generation exciter control and power system stabilizers, static var compensators, power flow controllers, and DC Transmission controllers. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R4.4. | Those planning events in Table 1 that are expected to produce more severe System impacts on its portion of the BES, shall be identified, and a list created of those Contingencies to be evaluated in Requirement R4, Part 4.1. The rationale for those Contingencies selected for evaluation shall be available as supporting information. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R4.4.1. | Each Planning Coordinator and Transmission Planner shall coordinate with adjacent Planning Coordinators and Transmission Planners to ensure that Contingencies on adjacent Systems which may impact their Systems are included in the Contingency list. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R4.5. | Those extreme events in Table 1 that are expected to produce more severe System impacts shall be identified and a list created of those events to be evaluated in Requirement R4, Part 4.2. The rationale for those Contingencies selected for evaluation shall be available as supporting information. If the analysis concludes there is Cascading caused by the occurrence of extreme events, an evaluation of possible actions designed to reduce the likelihood or mitigate the consequences of the event(s) shall be conducted. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R5. | Each Transmission Planner and Planning Coordinator shall have criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, and the transient voltage response for its System. For transient voltage response, the criteria shall at a minimum, specify a low voltage level and a maximum length of time that transient voltages may remain below that level. | MEDIUM | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R6. | Each Transmission Planner and Planning Coordinator shall define and document, within their Planning Assessment, the criteria or methodology used in the analysis to identify System instability for conditions such as Cascading, voltage instability, or uncontrolled islanding. | LOWER | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R7. | Each Planning Coordinator, in conjunction with each of its Transmission Planners, shall determine and identify each entity’s individual and joint responsibilities for performing the required studies for the Planning Assessment. | LOWER | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R8. | Each Planning Coordinator and Transmission Planner shall distribute its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners within 90 calendar days of completing its Planning Assessment, and to any functional entity that has a reliability related need and submits a written request for the information within 30 days of such a request. | MEDIUM | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-2 | Transmission System Planning Performance Requirements | R8.1. | If a recipient of the Planning Assessment results provides documented comments on the results, the respective Planning Coordinator or Transmission Planner shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | No Individual VRF Assigned | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-001-3 | System Performance Under Normal (No Contingency) Conditions (Category A) | R1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that, with all transmission facilities in service and with normal (pre-contingency) operating procedures in effect, the Network can be operated to supply projected customer demands and projected Firm (non- recallable reserved) Transmission Services at all Demand levels over the range of forecast system demands, under the conditions defined in Category A of Table I. To be considered valid, the Planning Authority and Transmission Planner assessments shall: |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-001-3 | System Performance Under Normal (No Contingency) Conditions (Category A) | R1.1. | Be made annually. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-001-3 | System Performance Under Normal (No Contingency) Conditions (Category A) | R1.2. | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-001-3 | System Performance Under Normal (No Contingency) Conditions (Category A) | R1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category A of Table 1 (no contingencies). The specific elements selected (from each of the following categories) shall be acceptable to the associated Regional Reliability Organization(s). |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-001-3 | System Performance Under Normal (No Contingency) Conditions (Category A) | R1.3.1. | Cover critical system conditions and study years as deemed appropriate by the entity performing the study. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-001-3 | System Performance Under Normal (No Contingency) Conditions (Category A) | R1.3.2. | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-001-3 | System Performance Under Normal (No Contingency) Conditions (Category A) | R1.3.3. | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-001-3 | System Performance Under Normal (No Contingency) Conditions (Category A) | R1.3.4. | Have established normal (pre-contingency) operating procedures in place. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-001-3 | System Performance Under Normal (No Contingency) Conditions (Category A) | R1.3.5. | Have all projected firm transfers modeled. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-001-3 | System Performance Under Normal (No Contingency) Conditions (Category A) | R1.3.6. | Be performed for selected demand levels over the range of forecast system demands. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-001-3 | System Performance Under Normal (No Contingency) Conditions (Category A) | R1.3.7. | Demonstrate that system performance meets Table 1 for Category A (no contingencies). |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-001-3 | System Performance Under Normal (No Contingency) Conditions (Category A) | R1.3.8. | Include existing and planned facilities. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-001-3 | System Performance Under Normal (No Contingency) Conditions (Category A) | R1.3.9. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-001-3 | System Performance Under Normal (No Contingency) Conditions (Category A) | R1.4. | Address any planned upgrades needed to meet the performance requirements of Category A. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-001-3 | System Performance Under Normal (No Contingency) Conditions (Category A) | R2. | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-001-3_R1, the Planning Authority and Transmission Planner shall each: |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-001-3 | System Performance Under Normal (No Contingency) Conditions (Category A) | R2.1. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-001-3 | System Performance Under Normal (No Contingency) Conditions (Category A) | R2.1.1. | Including a schedule for implementation. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-001-3 | System Performance Under Normal (No Contingency) Conditions (Category A) | R2.1.2. | Including a discussion of expected required in-service dates of facilities. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-001-3 | System Performance Under Normal (No Contingency) Conditions (Category A) | R2.1.3. | Consider lead times necessary to implement plans. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-001-3 | System Performance Under Normal (No Contingency) Conditions (Category A) | R2.2. | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-001-3 | System Performance Under Normal (No Contingency) Conditions (Category A) | R3. | The Planning Authority and Transmission Planner shall each document the results of these reliability assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R1. | Each Transmission Planner and Planning Coordinator shall maintain System models within its respective area for performing the studies needed to complete its Planning Assessment. The models shall use data consistent with that provided in accordance with the MOD-010 and MOD-012 standards, supplemented by other sources as needed, including items represented in the Corrective Action Plan, and shall represent projected System conditions. This establishes Category P0 as the normal System condition in Table 1. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | HIGH | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R1.1. | System models shall represent: | HIGH | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R1.1.1. | Existing Facilities | HIGH | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R1.1.2. | Known outage(s) of generation or Transmission Facility(ies) with a duration of at least six months. | HIGH | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R1.1.3. | New planned Facilities and changes to existing Facilities | HIGH | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R1.1.4. | Real and reactive Load forecasts | HIGH | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R1.1.5. | Known commitments for Firm Transmission Service and Interchange | HIGH | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R1.1.6. | Resources (supply or demand side) required for Load | HIGH | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R2. | Each Transmission Planner and Planning Coordinator shall prepare an annual Planning Assessment of its portion of the BES. This Planning Assessment shall use current or qualified past studies (as indicated in Requirement R2, Part 2.6), document assumptions, and document summarized results of the steady state analyses, short circuit analyses, and Stability analyses. [Violation Risk Factor: High] [Time Horizon: Long-term Planning] | HIGH | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R2.1. | For the Planning Assessment, the Near-Term Transmission Planning Horizon portion of the steady state analysis shall be assessed annually and be supported by current annual studies or qualified past studies as indicated in Requirement R2, Part 2.6. Qualifying studies need to include the following conditions: | HIGH | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R2.1.1. | System peak Load for either Year One or year two, and for year five. | HIGH | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R2.1.2. | System Off-Peak Load for one of the five years. | HIGH | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R2.1.3. | P1 events in Table 1, with known outages modeled as in Requirement R1, Part 1.1.2, under those System peak or Off-Peak conditions when known outages are scheduled. | HIGH | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R2.1.4. | For each of the studies described in Requirement R2, Parts 2.1.1 and 2.1.2, sensitivity case(s) shall be utilized to demonstrate the impact of changes to the basic assumptions used in the model. To accomplish this, the sensitivity analysis in the Planning Assessment must vary one or more of the following conditions by a sufficient amount to stress the System within a range of credible conditions that demonstrate a measurable change in System response :  Real and reactive forecasted Load.  Expected transfers.  Expected in service dates of new or modified Transmission Facilities.  Reactive resource capability.  Generation additions, retirements, or other dispatch scenarios. Controllable Loads and Demand Side Management.  Duration or timing of known Transmission outages | HIGH | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R2.1.5. | When an entity’s spare equipment strategy could result in the unavailability of major Transmission equipment that has a lead time of one year or more (such as a transformer), the impact of this possible unavailability on System performance shall be studied. The studies shall be performed for the P0, P1, and P2 categories identified in Table 1 with the conditions that the System is expected to experience during the possible unavailability of the long lead time equipment. | HIGH | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R2.2. | For the Planning Assessment, the Long-Term Transmission Planning Horizon portion of the steady state analysis shall be assessed annually and be supported by the following annual current study, supplemented with qualified past studies as indicated in Requirement R2, Part 2.6: | HIGH | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R2.2.1. | A current study assessing expected System peak Load conditions for one of the years in the Long-Term Transmission Planning Horizon and the rationale for why that year was selected. | HIGH | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R2.3. | The short circuit analysis portion of the Planning Assessment shall be conducted annually addressing the Near-Term Transmission Planning Horizon and can be supported by current or past studies as qualified in Requirement R2, Part 2.6. The analysis shall be used to determine whether circuit breakers have interrupting capability for Faults that they will be expected to interrupt using the System short circuit model with any planned generation and Transmission Facilities in service which could impact the study area. | HIGH | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R2.4. | For the Planning Assessment, the Near-Term Transmission Planning Horizon portion of the Stability analysis shall be assessed annually and be supported by current or past studies as qualified in Requirement R2, Part2.6. The following studies are required: | HIGH | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R2.4.1. | System peak Load for one of the five years. System peak Load levels shall include a Load model which represents the expected dynamic behavior of Loads that could impact the study area, considering the behavior of induction motor Loads. An aggregate System Load model which represents the overall dynamic behavior of the Load is acceptable. | HIGH | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R2.4.2. | System Off-Peak Load for one of the five years. | HIGH | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R2.4.3. | For each of the studies described in Requirement R2, Parts 2.4.1 and 2.4.2, sensitivity case(s) shall be utilized to demonstrate the impact of changes to the basic assumptions used in the model. To accomplish this, the sensitivity analysis in the Planning Assessment must vary one or more of the following conditions by a sufficient amount to stress the System within a range of credible conditions that demonstrate a measurable change in performance:  Load level, Load forecast, or dynamic Load model assumptions.  Expected transfers.  Expected in service dates of new or modified Transmission Facilities.  Reactive resource capability.  Generation additions, retirements, or other dispatch scenarios. | HIGH | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R2.5. | For the Planning Assessment, the Long-Term Transmission Planning Horizon portion of the Stability analysis shall be assessed to address the impact of proposed material generation additions or changes in that timeframe and be supported by current or past studies as qualified in Requirement R2, Part2.6 and shall include documentation to support the technical rationale for determining material changes. | HIGH | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R2.6. | Past studies may be used to support the Planning Assessment if they meet the following requirements: | HIGH | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R2.6.1. | For steady state, short circuit, or Stability analysis: the study shall be five calendar years old or less, unless a technical rationale can be provided to demonstrate that the results of an older study are still valid. | HIGH | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R2.6.2. | For steady state, short circuit, or Stability analysis: no material changes have occurred to the System represented in the study. Documentation to support the technical rationale for determining material changes shall be included. | HIGH | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R2.7. | For planning events shown in Table 1, when the analysis indicates an inability of the System to meet the performance requirements in Table 1, the Planning Assessment shall include Corrective Action Plan(s) addressing how the performance requirements will be met. Revisions to the Corrective Action Plan(s) are allowed in subsequent Planning Assessments but the planned System shall continue to meet the performance requirements in Table 1. Corrective Action Plan(s) do not need to be developed solely to meet the performance requirements for a single sensitivity case analyzed in accordance with Requirements R2, Parts 2.1.4 and 2.4.3. The Corrective Action Plan(s) shall: | HIGH | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R2.7.1. | List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include:  Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment.  Installation, modification, or removal of Protection Systems or Special Protection Systems  Installation or modification of automatic generation tripping as a response to a single or multiple Contingency to mitigate Stability performance violations.  Installation or modification of manual and automatic generation runback/tripping as a response to a single or multiple Contingency to mitigate steady state performance violations.  Use of Operating Procedures specifying how long they will be needed as part of the Corrective Action Plan.  Use of rate applications, DSM, new technologies, or other initiatives. | HIGH | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R2.7.2. | Include actions to resolve performance deficiencies identified in multiple sensitivity studies or provide a rationale for why actions were not necessary. | HIGH | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R2.7.3. | If situations arise that are beyond the control of the Transmission Planner or Planning Coordinator that prevent the implementation of a Corrective Action Plan in the required timeframe, then the Transmission Planner or Planning Coordinator is permitted to utilize Non-Consequential Load Loss and curtailment of Firm Transmission Service to correct the situation that would normally not be permitted in Table 1, provided that the Transmission Planner or Planning Coordinator documents that they are taking actions to resolve the situation. The Transmission Planner or Planning Coordinator shall document the situation causing the problem, alternatives evaluated, and the use of Non-Consequential Load Loss or curtailment of Firm Transmission Service. | HIGH | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R2.7.4. | Be reviewed in subsequent annual Planning Assessments for continued validity and implementation status of identified System Facilities and Operating Procedures. | HIGH | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R2.8. | For short circuit analysis, if the short circuit current interrupting duty on circuit breakers determined in Requirement R2, Part 2.3 exceeds their Equipment Rating, the Planning Assessment shall include a Corrective Action Plan to address the Equipment Rating violations. The Corrective Action Plan shall: | HIGH | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R2.8.1. | List System deficiencies and the associated actions needed to achieve required System performance. | HIGH | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R2.8.2. | Be reviewed in subsequent annual Planning Assessments for continued validity and implementation status of identified System Facilities and Operating Procedures. | HIGH | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R3. | For the steady state portion of the Planning Assessment, each Transmission Planner and Planning Coordinator shall perform studies for the Near-Term and Long-Term Transmission Planning Horizons in Requirement R2, Parts 2.1, and 2.2. The studies shall be based on computer simulation models using data provided in Requirement R1. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R3.1. | Studies shall be performed for planning events to determine whether the BES meets the performance requirements in Table 1 based on the Contingency list created in Requirement R3, Part 3.4. | MEDIUM | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R3.2. | Studies shall be performed to assess the impact of the extreme events which are identified by the list created in Requirement R3, Part 3.5. | MEDIUM | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R3.3. | Contingency analyses for Requirement R3, Parts 3.1 & 3.2 shall: | MEDIUM | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R3.3.1. | Simulate the removal of all elements that the Protection System and other automatic controls are expected to disconnect for each Contingency without operator intervention. The analyses shall include the impact of subsequent: | MEDIUM | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R3.3.1.1. | Tripping of generators where simulations show generator bus voltages or high side of the generation step up (GSU) voltages are less than known or assumed minimum generator steady state or ride through voltage limitations. Include in the assessment any assumptions made. | MEDIUM | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R3.3.1.2. | Tripping of Transmission elements where relay loadability limits are exceeded. | MEDIUM | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R3.3.2. | Simulate the expected automatic operation of existing and planned devices designed to provide steady state control of electrical system quantities when such devices impact the study area. These devices may include equipment such as phase-shifting transformers, load tap changing transformers, and switched capacitors and inductors. | MEDIUM | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R3.4. | Those planning events in Table 1, that are expected to produce more severe System impacts on its portion of the BES, shall be identified and a list of those Contingencies to be evaluated for System performance in Requirement R3, Part 3.1 created. The rationale for those Contingencies selected for evaluation shall be available as supporting information. | MEDIUM | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R3.4.1. | The Planning Coordinator and Transmission Planner shall coordinate with adjacent Planning Coordinators and Transmission Planners to ensure that Contingencies on adjacent Systems which may impact their Systems are included in the Contingency list. | MEDIUM | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R3.5. | Those extreme events in Table 1 that are expected to produce more severe System impacts shall be identified and a list created of those events to be evaluated in Requirement R3, Part 3.2. The rationale for those Contingencies selected for evaluation shall be available as supporting information. If the analysis concludes there is Cascading caused by the occurrence of extreme events, an evaluation of possible actions designed to reduce the likelihood or mitigate the consequences and adverse impacts of the event(s) shall be conducted. | MEDIUM | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R4. | For the Stability portion of the Planning Assessment, as described in Requirement R2, Parts 2.4 and 2.5, each Transmission Planner and Planning Coordinator shall perform the Contingency analyses listed in Table 1. The studies shall be based on computer simulation models using data provided in Requirement R1. [Violation Risk Factor: Medium] [Time Horizon: Longterm Planning] | MEDIUM | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R4.1. | Studies shall be performed for planning events to determine whether the BES meets the performance requirements in Table 1 based on the Contingency list created in Requirement R4, Part 4.4. | MEDIUM | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R4.1.1. | For planning event P1: No generating unit shall pull out of synchronism. A generator being disconnected from the System by fault clearing action or by a Special Protection System is not considered pulling out of synchronism. | MEDIUM | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R4.1.2. | For planning events P2 through P7: When a generator pulls out of synchronism in the simulations, the resulting apparent impedance swings shall not result in the tripping of any Transmission system elements other than the generating unit and its directly connected Facilities. | MEDIUM | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R4.1.3. | For planning events P1 through P7: Power oscillations shall exhibit acceptable damping as established by the Planning Coordinator and Transmission Planner. | MEDIUM | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R4.2. | Studies shall be performed to assess the impact of the extreme events which are identified by the list created in Requirement R4, Part 4.5. | MEDIUM | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R4.3. | Contingency analyses for Requirement R4, Parts 4.1 and 4.2 shall : | MEDIUM | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R4.3.1. | Simulate the removal of all elements that the Protection System and other automatic controls are expected to disconnect for each Contingency without operator intervention. The analyses shall include the impact of subsequent: | MEDIUM | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R4.3.1.1. | Successful high speed (less than one second) reclosing and unsuccessful high speed reclosing into a Fault where high speed reclosing is utilized. | MEDIUM | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R4.3.1.2. | Tripping of generators where simulations show generator bus voltages or high side of the GSU voltages are less than known or assumed generator low voltage ride through capability. Include in the assessment any assumptions made. | MEDIUM | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R4.3.1.3. | Tripping of Transmission lines and transformers where transient swings cause Protection System operation based on generic or actual relay models. | MEDIUM | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R4.3.2. | Simulate the expected automatic operation of existing and planned devices designed to provide dynamic control of electrical system quantities when such devices impact the study area. These devices may include equipment such as generation exciter control and power system stabilizers, static var compensators, power flow controllers, and DC Transmission controllers. | MEDIUM | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R4.4. | Those planning events in Table 1 that are expected to produce more severe System impacts on its portion of the BES, shall be identified, and a list created of those Contingencies to be evaluated in Requirement R4, Part 4.1. The rationale for those Contingencies selected for evaluation shall be available as supporting information. | MEDIUM | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R4.4.1. | Each Planning Coordinator and Transmission Planner shall coordinate with adjacent Planning Coordinators and Transmission Planners to ensure that Contingencies on adjacent Systems which may impact their Systems are included in the Contingency list. | MEDIUM | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R4.5. | Those extreme events in Table 1 that are expected to produce more severe System impacts shall be identified and a list created of those events to be evaluated in Requirement R4, Part 4.2. The rationale for those Contingencies selected for evaluation shall be available as supporting information. If the analysis concludes there is Cascading caused by the occurrence of extreme events, an evaluation of possible actions designed to reduce the likelihood or mitigate the consequences of the event(s) shall be conducted. | MEDIUM | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R5. | Each Transmission Planner and Planning Coordinator shall have criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, and the transient voltage response for its System. For transient voltage response, the criteria shall at a minimum, specify a low voltage level and a maximum length of time that transient voltages may remain below that level. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R6. | Each Transmission Planner and Planning Coordinator shall define and document, within their Planning Assessment, the criteria or methodology used in the analysis to identify System instability for conditions such as Cascading, voltage instability, or uncontrolled islanding. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R7. | Each Planning Coordinator, in conjunction with each of its Transmission Planners, shall determine and identify each entity’s individual and joint responsibilities for performing the required studies for the Planning Assessment. [Violation Risk Factor: Low] [Time Horizon: Long-term Planning] | LOWER | Effective | 2015-01-01 |  | PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R8. | Each Planning Coordinator and Transmission Planner shall distribute its Planning Assessment results to adjacent Planning coordinators and adjacent Transmission Planners within 90 calendar days of completing its Planning Assessment, and to any functional entity that has a reliability related need and submits a written request for the information within 30 days of such a request. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-4 | Transmission System Planning Performance Requirements | R8.1. | If a recipient of the Planning Assessment results provides documented comments on the results, the respective Planning Coordinator or Transmission Planner shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | MEDIUM | Effective | 2015-01-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R1. | Each Transmission Planner and Planning Coordinator shall maintain System models within its respective area for performing the studies needed to complete its Planning Assessment. The models shall use data consistent with that provided in accordance with the MOD-032 standard, supplemented by other sources as needed, including items represented in the Corrective Action Plan, and shall represent projected System conditions. This establishes Category P0 as the normal System condition in Table 1. [Violation Risk Factor: High] [Time Horizon: Long-term Planning] | HIGH | Effective | 2022-07-01 |  | PA, PC, TP
TPL-001-5 | Transmission System Planning Performance Requirements | R1.1. | System models shall represent: | HIGH | Effective | 2022-07-01 |  | PA, PC, TP
TPL-001-5 | Transmission System Planning Performance Requirements | R1.1.1. | Existing Facilities. | HIGH | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R1.1.2. | New planned Facilities and changes to existing Facilities. | HIGH | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R1.1.3. | Real and reactive Load forecasts. | HIGH | Effective | 2022-07-01 |  | PC, PA, TP
TPL-001-5 | Transmission System Planning Performance Requirements | R1.1.4. | Known commitments for Firm Transmission Service and Interchange. | HIGH | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R1.1.5. | Resources (supply or demand side) required for Load. | HIGH | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R2. | Each Transmission Planner and Planning Coordinator shall prepare an annual Planning Assessment of its portion of the BES. This Planning Assessment shall use current or qualified past studies (as indicated in Requirement R2, Part 2.6), document assumptions, and document summarized results of the steady state analyses, short circuit analyses, and Stability analyses. [Violation Risk Factor: High] [Time Horizon: Long-term Planning] | HIGH | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R2.1. | For the Planning Assessment, the Near-Term Transmission Planning Horizon portion of the steady state analysis shall be assessed annually and be supported by current annual studies or qualified past studies as indicated in Requirement R2, Part 2.6. Qualifying studies need to include the following conditions: | HIGH | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R2.1.1. | System peak Load for either Year One or year two, and for year five. | HIGH | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R2.1.2. | System Off-Peak Load for one of the five years. | HIGH | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R2.1.3. | For each of the studies described in Requirement R2, Parts 2.1.1 and 2.1.2, sensitivity case(s) shall be utilized to demonstrate the impact of changes to the basic assumptions used in the model. To accomplish this, the sensitivity analysis in the Planning Assessment must vary one or more of the following conditions by a sufficient amount to stress the System within a range of credible conditions that demonstrate a measurable change in System response : • Real and reactive forecasted Load. • Expected transfers. • Expected in service dates of new or modified Transmission Facilities. • Reactive resource capability. • Generation additions, retirements, or other dispatch scenarios. • Controllable Loads and Demand Side Management. • Duration or timing of known Transmission outages. | HIGH | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R2.1.4. | When known outage(s) of generation or Transmission Facility(ies) are planned in the Near-Term Planning Horizon, the impact of selected known outages on System performance shall be assessed. These known outage(s) shall be selected for assessment consistent with a documented outage coordination procedure or technical rationale by the Planning Coordinator or Transmission Planner. Known outage(s) shall not be excluded solely based upon outage duration. The assessment shall be performed for the P0 and P1 categories identified in Table 1 with the System peak or Off-Peak conditions that the System is expected to experience when the known outage(s) are planned. This assessment shall include, at a minimum known outages expected to produce more severe System impacts on the Planning Coordinator or Transmission Planner’s portion of the BES. Past or current studies may support the selection of known outage(s), if the study(s) has comparable post-Contingency System conditions and configuration such as those following P3 or P6 category events in Table 1. | HIGH | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R2.1.5. | When an entity’s spare equipment strategy could result in the unavailability of major Transmission equipment that has a lead time of one year or more (such as a transformer), the impact of this possible unavailability on System performance shall be assessed. Based upon this assessment, an analysis shall be performed for the P0, P1, and P2 categories identified in Table 1 with the conditions that the System is expected to experience during the possible unavailability of the long lead time equipment. | HIGH | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R2.2. | For the Planning Assessment, the Long-Term Transmission Planning Horizon portion of the steady state analysis shall be assessed annually and be supported by the following annual current study, supplemented with qualified past studies as indicated in Requirement R2, Part 2.6: | HIGH | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R2.2.1. | A current study assessing expected System peak Load conditions for one of the years in the Long-Term Transmission Planning Horizon and the rationale for why that year was selected. | HIGH | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R2.3. | The short circuit analysis portion of the Planning Assessment shall be conducted annually addressing the Near-Term Transmission Planning Horizon and can be supported by current or past studies as qualified in Requirement R2, Part 2.6. The analysis shall be used to determine whether circuit breakers have interrupting capability for Faults that they will be expected to interrupt using the System short circuit model with any planned generation and Transmission Facilities in service which could impact the study area. | HIGH | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R2.4. | For the Planning Assessment, the Near-Term Transmission Planning Horizon portion of the Stability analysis shall be assessed annually and be supported by current or past studies as qualified in Requirement R2, Part2.6. The following studies are required: | HIGH | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R2.4.1. | System peak Load for one of the five years. System peak Load levels shall include a Load model which represents the expected dynamic behavior of Loads that could impact the study area, considering the behavior of induction motor Loads. An aggregate System Load model which represents the overall dynamic behavior of the Load is acceptable. | HIGH | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R2.4.2. | System Off-Peak Load for one of the five years. | HIGH | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R2.4.3. | For each of the studies described in Requirement R2, Parts 2.4.1 and 2.4.2, sensitivity case(s) shall be utilized to demonstrate the impact of changes to the basic assumptions used in the model. To accomplish this, the sensitivity analysis in the Planning Assessment must vary one or more of the following conditions by a sufficient amount to stress the System within a range of credible conditions that demonstrate a measurable change in performance: • Load level, Load forecast, or dynamic Load model assumptions. • Expected transfers. • Expected in service dates of new or modified Transmission Facilities. • Reactive resource capability. • Generation additions, retirements, or other dispatch scenarios. | HIGH | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R2.4.4. | When known outage(s) of generation or Transmission Facility(ies) are planned in the Near-Term Planning Horizon, the impact of selected known outages on System performance shall be assessed. These known outage(s) shall be selected for assessment consistent with a documented outage coordination procedure or technical rationale by the Planning Coordinator or Transmission Planner. Known outage(s) shall not be excluded solely based upon outage duration. The assessment shall be performed for the P1 categories identified in Table 1 with the System peak or Off-Peak conditions that the System is expected to experience when the known outage(s) are planned. This assessment shall include, at a minimum, those known outages expected to produce more severe System impacts on the Planning Coordinator or Transmission Planner’s portion of the BES. Past or current studies may support the selection of known outage(s), if the study(s) has comparable post-Contingency System conditions and configuration such as those following P3 or P6 category events in Table 1. | HIGH | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R2.4.5. | unavailability of major Transmission equipment that has a lead time of one year or more (such as a transformer), the impact of this possible unavailability on System performance shall be assessed. Based upon this assessment, an analysis shall be performed for the selected P1 and P2 category events identified in Table 1 for which the unavailability is expected to produce more severe System impacts on its portion of the BES. The analysis shall simulate the conditions that the System is expected to experience during the possible unavailability of the long lead time equipment. | HIGH | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R2.5. | For the Planning Assessment, the Long-Term Transmission Planning Horizon portion of the Stability analysis shall be assessed to address the impact of proposed material generation additions or changes in that timeframe and be supported by current or past studies as qualified in Requirement R2, Part2.6 and shall include documentation to support the technical rationale for determining material changes. | HIGH | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R2.6. | Past studies may be used to support the Planning Assessment if they meet the following requirements: | HIGH | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R2.6.1. | For steady state, short circuit, or Stability analysis: the study shall be five calendar years old or less, unless a technical rationale can be provided to demonstrate that the results of an older study are still valid. | HIGH | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R2.6.2. | For steady state, short circuit, or Stability analysis: no material changes have occurred to the System represented in the study. Documentation to support the technical rationale for determining material changes shall be included. | HIGH | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R2.7. | For planning events shown in Table 1, when the analysis indicates an inability of the System to meet the performance requirements in Table 1, the Planning Assessment shall include Corrective Action Plan(s) addressing how the performance requirements will be met. Revisions to the Corrective Action Plan(s) are allowed in subsequent Planning Assessments, but the planned System shall continue to meet the performance requirements in Table 1. Corrective Action Plan(s) do not need to be developed solely to meet the performance requirements for a single sensitivity case analyzed in accordance with Requirements R2, Parts 2.1.4 and 2.4.3. The Corrective Action Plan(s) shall: | HIGH | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R2.7.1. | List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include: • Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment. • Installation, modification, or removal of Protection Systems or Remedial Action Schemes. • Installation or modification of automatic generation tripping as a response to a single or multiple Contingency to mitigate Stability performance violations. • Installation or modification of manual and automatic generation runback/tripping as a response to a single or multiple Contingency to mitigate steady state performance violations. • Use of Operating Procedures specifying how long they will be needed as part of the Corrective Action Plan. • Use of rate applications, DSM, new technologies, or other initiatives. | HIGH | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R2.7.2. | Include actions to resolve performance deficiencies identified in multiple sensitivity studies or provide a rationale for why actions were not necessary. • Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment. • Installation, modification, or removal of Protection Systems or Remedial Action Schemes. • Installation or modification of automatic generation tripping as a response to a single or multiple Contingency to mitigate Stability performance violations. • Installation or modification of manual and automatic generation runback/tripping as a response to a single or multiple Contingency to mitigate steady state performance violations. • Use of Operating Procedures specifying how long they will be needed as part of the Corrective Action Plan. • Use of rate applications, DSM, new technologies, or other initiatives. | HIGH | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R2.7.3. | If situations arise that are beyond the control of the Transmission Planner or Planning Coordinator that prevent the implementation of a Corrective Action Plan in the required timeframe, then the Transmission Planner or Planning Coordinator is permitted to utilize Non-Consequential Load Loss and curtailment of Firm Transmission Service to correct the situation that would normally not be permitted in Table 1, provided that the Transmission Planner or Planning Coordinator documents that they are taking actions to resolve the situation. The Transmission Planner or Planning Coordinator shall document the situation causing the problem, alternatives evaluated, and the use of Non-Consequential Load Loss or curtailment of Firm Transmission Service. | HIGH | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R2.7.4. | Be reviewed in subsequent annual Planning Assessments for continued validity and implementation status of identified System Facilities and Operating Procedures. | HIGH | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R2.8. | For short circuit analysis, if the short circuit current interrupting duty on circuit breakers determined in Requirement R2, Part 2.3 exceeds their Equipment Rating, the Planning Assessment shall include a Corrective Action Plan to address the Equipment Rating violations. The Corrective Action Plan shall: | HIGH | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R2.8.1. | List System deficiencies and the associated actions needed to achieve required System performance. | HIGH | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R2.8.2. | Be reviewed in subsequent annual Planning Assessments for continued validity and implementation status of identified System Facilities and Operating Procedures. | HIGH | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R3. | For the steady state portion of the Planning Assessment, each Transmission Planner and Planning Coordinator shall perform studies for the Near-Term and Long-Term Transmission Planning Horizons in Requirement R2, Parts 2.1, and 2.2. The studies shall be based on computer simulation models using data provided in Requirement R1. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R3.1. | Studies shall be performed for planning events to determine whether the BES meets the performance requirements in Table 1 based on the Contingency list created in Requirement R3, Part 3.4. | MEDIUM | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R3.2. | Studies shall be performed to assess the impact of the extreme events which are identified by the list created in Requirement R3, Part 3.5. If the analysis concludes there is Cascading caused by the occurrence of extreme events, an evaluation of possible actions designed to reduce the likelihood or mitigate the consequences and adverse impacts of the event(s) shall be conducted. | MEDIUM | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R3.3. | Contingency analyses for Requirement R3, Parts 3.1 and 3.2 shall: | MEDIUM | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R3.3.1. | Simulate the removal of all elements that the Protection System and other automatic controls are expected to disconnect for each Contingency without operator intervention. The analyses shall include the impact of subsequent: | MEDIUM | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R3.3.1.1. | Tripping of generators where simulations show generator bus voltages or high side of the generation step up (GSU) voltages are less than known or assumed minimum generator steady state or ride through voltage limitations. Include in the assessment any assumptions made. | MEDIUM | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R3.3.1.2. | Tripping of Transmission elements where relay loadability limits are exceeded. | MEDIUM | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R3.3.2. | Simulate the expected automatic operation of existing and planned devices designed to provide steady state control of electrical system quantities when such devices impact the study area. These devices may include equipment such as phase-shifting transformers, load tap changing transformers, and switched capacitors and inductors. | MEDIUM | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R3.4. | Those planning events in Table 1 that are expected to produce more severe System impacts on its portion of the BES shall be identified, and a list of those Contingencies to be evaluated for System performance in Requirement R3, Part 3.1 created. The rationale for those Contingencies selected for evaluation shall be available as supporting information. | MEDIUM | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R3.4.1. | The Planning Coordinator and Transmission Planner shall coordinate with adjacent Planning Coordinators and Transmission Planners to ensure that Contingencies on adjacent Systems which may impact their Systems are included in the Contingency list. | MEDIUM | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R3.5. | Those extreme events in Table 1 that are expected to produce more severe System impacts shall be identified and a list created of those events to be evaluated in Requirement R3, Part 3.2. The rationale for those Contingencies selected for evaluation shall be available as supporting information. | MEDIUM | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R4. | For the Stability portion of the Planning Assessment, as described in Requirement R2, Parts 2.4 and 2.5, each Transmission Planner and Planning Coordinator shall perform the Contingency analyses listed in Table 1. The studies shall be based on computer simulation models using data provided in Requirement R1. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R4.1. | Studies shall be performed for planning events to determine whether the BES meets the performance requirements in Table 1 based on the Contingency list created in Requirement R4, Part 4.4. | MEDIUM | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R4.1.1. | For planning event P1: No generating unit shall pull out of synchronism. A generator being disconnected from the System by fault clearing action or by a Remedial Action Scheme is not considered pulling out of synchronism. | MEDIUM | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R4.1.2. | For planning events P2 through P7: When a generator pulls out of synchronism in the simulations, the resulting apparent impedance swings shall not result in the tripping of any Transmission system elements other than the generating unit and its directly connected Facilities. | MEDIUM | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R4.1.3. | For planning events P1 through P7: Power oscillations shall exhibit acceptable damping as established by the Planning Coordinator and Transmission Planner. | MEDIUM | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R4.2. | Studies shall be performed to assess the impact of the extreme events which are identified by the list created in Requirement R4, Part 4.5. If the analysis concludes there is Cascading caused by the occurrence of extreme events, an evaluation of possible actions designed to reduce the likelihood or mitigate the consequences of the event (s) shall be conducted. | MEDIUM | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R4.3. | Contingency analyses for Requirement R4, Parts 4.1 and 4.2 shall : | MEDIUM | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R4.3.1. | Simulate the removal of all elements that the Protection System and other automatic controls are expected to disconnect for each Contingency without operator intervention. The analyses shall include the impact of subsequent: | MEDIUM | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R4.3.1.1. | Successful high speed (less than one second) reclosing and unsuccessful high speed reclosing into a Fault where high speed reclosing is utilized. | MEDIUM | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R4.3.1.2. | Tripping of generators where simulations show generator bus voltages or high side of the GSU voltages are less than known or assumed generator low voltage ride through capability. Include in the assessment any assumptions made. | MEDIUM | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R4.3.1.3. | Tripping of Transmission lines and transformers where transient swings cause Protection System operation based on generic or actual relay models. | MEDIUM | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R4.3.2. | Simulate the expected automatic operation of existing and planned devices designed to provide dynamic control of electrical system quantities when such devices impact the study area. These devices may include equipment such as generation exciter control and power system stabilizers, static var compensators, power flow controllers, and DC Transmission controllers. | MEDIUM | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R4.4. | Those planning events in Table 1 that are expected to produce more severe System impacts on its portion of the BES, shall be identified, and a list created of those Contingencies to be evaluated in Requirement R4, Part 4.1. The rationale for those Contingencies selected for evaluation shall be available as supporting information. | MEDIUM | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R4.4.1. | Each Planning Coordinator and Transmission Planner shall coordinate with adjacent Planning Coordinators and Transmission Planners to ensure that Contingencies on adjacent Systems which may impact their Systems are included in the Contingency list. | MEDIUM | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R4.5. | Those extreme events in Table 1 that are expected to produce more severe System impacts shall be identified and a list created of those events to be evaluated in Requirement R4, Part 4.2. The rationale for those Contingencies selected for evaluation shall be available as supporting information. | MEDIUM | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R5. | Each Transmission Planner and Planning Coordinator shall have criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, and the transient voltage response for its System. For transient voltage response, the criteria shall at a minimum, specify a low voltage level and a maximum length of time that transient voltages may remain below that level. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R6. | Each Transmission Planner and Planning Coordinator shall define and document, within their Planning Assessment, the criteria or methodology used in the analysis to identify System instability for conditions such as Cascading, voltage instability, or uncontrolled islanding. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R7. | Each Planning Coordinator, in conjunction with each of its Transmission Planners, shall determine and identify each entity’s individual and joint responsibilities for performing the required studies for the Planning Assessment. [Violation Risk Factor: Low] [Time Horizon: Long-term Planning] | LOWER | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R8. | Each Planning Coordinator and Transmission Planner shall distribute its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners within 90 calendar days of completing its Planning Assessment, and to any functional entity that has a reliability related need and submits a written request for the information within 30 days of such a request. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5 | Transmission System Planning Performance Requirements | R8.1. | If a recipient of the Planning Assessment results provides documented comments on the results, the respective Planning Coordinator or Transmission Planner shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | MEDIUM | Effective | 2022-07-01 |  | TP, PC, PA
TPL-001-5.1 | Transmission System Planning Performance Requirements | R1. | Each Transmission Planner and Planning Coordinator shall maintain System models within its respective area for performing the studies needed to complete its Planning Assessment. The models shall use data consistent with that provided in accordance with the MOD-032 standard, supplemented by other sources as needed, including items represented in the Corrective Action Plan, and shall represent projected System conditions. This establishes Category P0 as the normal System condition in Table 1.[Violation Risk Factor: High] [Time Horizon: Long-term Planning] | HIGH | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R1.1. | System models shall represent: | HIGH | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R1.1.1. | Existing Facilities. | HIGH | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R1.1.2. | New planned Facilities and changes to existing Facilities. | HIGH | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R1.1.3. | Real and reactive Load forecasts. | HIGH | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R1.1.4. | Known commitments for Firm Transmission Service and Interchange. | HIGH | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R1.1.5. | Resources (supply or demand side) required for Load. | HIGH | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R2. | Each Transmission Planner and Planning Coordinator shall prepare an annual Planning Assessment of its portion of the BES. This Planning Assessment shall use current or qualified past studies (as indicated in Requirement R2, Part 2.6), document assumptions, and document summarized results of the steady state analyses, short circuit analyses, and Stability analyses. [Violation Risk Factor: High] [Time Horizon: Long-term Planning] | HIGH | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R2.1. | For the Planning Assessment, the Near-Term Transmission Planning Horizonportion of the steady state analysis shall be assessed annually and be supported by current annual studies or qualified past studies as indicated in Requirement R2, Part 2.6. Qualifying studies need to include the following conditions: | HIGH | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R2.1.1. | System peak Load for either Year One or year two, and for year five. | HIGH | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R2.1.2. | System Off-Peak Load for one of the five years. | HIGH | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R2.1.3. | For each of the studies described in Requirement R2, Parts 2.1.1 and 2.1.2, sensitivity case(s) shall be utilized to demonstrate the impact of changes to the basic assumptions used in the model. To accomplish this, the sensitivity analysis in the Planning Assessment must vary one or more of the following conditions by a sufficient amount to stress the System within a range of credible conditions that demonstrate a measurable change in System response : • Real and reactive forecasted Load. • Expected transfers. • Expected in service dates of new or modified Transmission Facilities. • Reactive resource capability. • Generation additions, retirements, or other dispatch scenarios. • Controllable Loads and Demand Side Management. • Duration or timing of known Transmission outages. | HIGH | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R2.1.4. | When known outage(s) of generation or Transmission Facility(ies) are planned in the Near-Term Planning Horizon, the impact of selected known outages on System performance shall be assessed. These known outage(s) shall be selected for assessment consistent with a documented outage coordination procedure or technical rationale by the Planning Coordinator or Transmission Planner. Known outage(s) shall not be excluded solely based upon outage duration. The assessment shall be performed for the P0 and P1 categories identified in Table 1 with the System peak or Off-Peak conditions that the System is expected to experience when the known outage(s) are planned. This assessment shall include, at a minimum known outages expected to produce more severe System impacts on the Planning Coordinator or Transmission Planner’s portion of the BES. Past or current studies may support the selection of known outage(s), if the study(s) has comparable post-Contingency System conditions andconfiguration such as those following P3 or P6 category events in Table 1. | HIGH | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R2.1.5. | When an entity’s spare equipment strategy could result in the unavailability of major Transmission equipment that has a lead time of one year or more (such as a transformer), the impact of this possible unavailability on System performance shall be assessed. Based upon this assessment, an analysis shall be performed for the P0, P1, and P2 categories identified in Table 1 with the conditions that the System is expected to experience during the possible unavailability of the long lead time equipment. | HIGH | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R2.2. | For the Planning Assessment, the Long-Term Transmission Planning Horizon portion of the steady state analysis shall be assessed annually and be supported by the following annual current study, supplemented with qualified past studies as indicated in Requirement R2, Part 2.6: | HIGH | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R2.2.1. | A current study assessing expected System peak Load conditions for one of the years in the Long-Term Transmission Planning Horizon and the rationale for why that year was selected. | HIGH | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R2.3. | The short circuit analysis portion of the Planning Assessment shall be conducted annually addressing the Near-Term Transmission Planning Horizon and can be supported by current or past studies as qualified in Requirement R2, Part 2.6. The analysis shall be used to determine whether circuit breakers have interrupting capability for Faults that they will be expected to interrupt using the System short circuit model with any planned generation and Transmission Facilities in service which could impact the study area. | HIGH | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R2.4. | For the Planning Assessment, the Near-Term Transmission Planning Horizon portion of the Stability analysis shall be assessed annually and be supported by current or past studies as qualified in Requirement R2, Part2.6. The following studies are required: | HIGH | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R2.4.1. | System peak Load for one of the five years. System peak Load levels shall include a Load model which represents the expected dynamic behavior of Loads that could impact the study area, considering the behavior of induction motor Loads. An aggregate System Load model which represents the overall dynamic behavior of the Load is acceptable. | HIGH | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R2.4.2. | System Off-Peak Load for one of the five years. | HIGH | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R2.4.3. | For each of the studies described in Requirement R2, Parts 2.4.1 and 2.4.2, sensitivity case(s) shall be utilized to demonstrate the impact of changes to the basic assumptions used in the model. To accomplish this, the sensitivity analysis in the Planning Assessment must vary one or more of the following conditions by a sufficient amount to stressthe System within a range of credible conditions that demonstrate a measurable change in performance: • Load level, Load forecast, or dynamic Load model assumptions. • Expected transfers. • Expected in service dates of new or modified Transmission Facilities. • Reactive resource capability. • Generation additions, retirements, or other dispatch scenarios. | HIGH | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R2.4.4. | When known outage(s) of generation or Transmission Facility(ies) are planned in the Near-Term Planning Horizon, the impact of selected known outages on System performance shall be assessed. These known outage(s) shall be selected for assessment consistent with a documented outage coordination procedure or technical rationale by the Planning Coordinator or Transmission Planner. Known outage(s) shall not be excluded solely based upon outage duration. The assessment shall be performed for the P1 categories identified in Table 1 with the System peak or Off-Peak conditions that the System is expected to experience when the known outage(s) are planned. This assessment shall include, at a minimum, those known outages expected to produce more severe System impacts on the Planning Coordinator or Transmission Planner’s portion of the BES. Past or current studies may support the selection of known outage(s), if the study(s) has comparable post-Contingency System conditions and configuration such as those following P3 or P6 category events in Table 1. | HIGH | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R2.5. | For the Planning Assessment, the Long-Term Transmission Planning Horizon portion of the Stability analysis shall be assessed to address the impact of proposed material generation additions or changes in that timeframe and be supported by current or past studies as qualified in Requirement R2, Part2.6and shall include documentation to support the technical rationale for determining material changes. | HIGH | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R2.6. | Past studies may be used to support the Planning Assessment if they meet the following requirements: | HIGH | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R2.6.1. | For steady state, short circuit, or Stability analysis: the study shall be five calendar years old or less, unless a technical rationale can be provided to demonstrate that the results of an older study are still valid. | HIGH | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R2.6.2. | For steady state, short circuit, or Stability analysis: no material changes have occurred to the System represented in the study. Documentation to support the technical rationale for determining material changes shall be included. | HIGH | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R2.7. | For planning events shown in Table 1, when the analysis indicates an inability of the System to meet the performance requirements in Table 1, the Planning Assessment shall include Corrective Action Plan(s) addressing how the performance requirements will be met. Revisions to the Corrective Action Plan(s) are allowed in subsequent Planning Assessments, but the planned System shall continue to meet the performance requirements in Table 1. Corrective Action Plan(s) do not need to be developed solely to meet the performance requirements for a single sensitivity case analyzed in accordance with Requirements R2, Parts 2.1.3 and 2.4.3. The Corrective Action Plan(s) shall: | HIGH | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R2.7.1. | List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include: • Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment. • Installation, modification, or removal of Protection Systems or Remedial Action Schemes. • Installation or modification of automatic generation tripping as a response to a single or multiple Contingency to mitigate Stability performance violations. • Installation or modification of manual and automatic generation runback/tripping as a response to a single or multiple Contingency to mitigate steady state performance violations. • Use of Operating Procedures specifying how long they will be needed as part of the Corrective Action Plan. • Use of rate applications, DSM, new technologies, or other initiatives. | HIGH | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R2.7.2. | Include actions to resolve performance deficiencies identified in multiple sensitivity studies or provide a rationale for why actions were not necessary. | HIGH | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R2.7.3. | If situations arise that are beyond the control of the Transmission Planner or Planning Coordinator that prevent the implementation of a Corrective Action Plan in the required timeframe, then the Transmission Planner or Planning Coordinator is permitted to utilize Non-Consequential Load Loss and curtailment of Firm Transmission Service to correct the situation that would normally not be permitted in Table 1, provided that the Transmission Planner or Planning Coordinator documents that they are taking actions to resolve the situation. The Transmission Planner or Planning Coordinator shall document the situation causing the problem, alternatives evaluated, and the use of Non-Consequential Load Loss or curtailment of Firm Transmission Service. | HIGH | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R2.7.4. | Be reviewed in subsequent annual Planning Assessments for continued validity and implementation status of identified System Facilities and Operating Procedures. | HIGH | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R2.8. | For short circuit analysis, if the short circuit current interrupting duty on circuit breakers determined in Requirement R2, Part 2.3 exceeds their Equipment Rating, the Planning Assessment shall include a Corrective Action Plan to address the Equipment Rating violations. The Corrective Action Plan shall: | HIGH | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R2.8.1. | List System deficiencies and the associated actions needed to achieve required System performance. | HIGH | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R2.8.2. | Be reviewed in subsequent annual Planning Assessments for continued validity and implementation status of identified System Facilities and Operating Procedures. | HIGH | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R3. | For the steady state portion of the Planning Assessment, each Transmission Planner and Planning Coordinator shall perform studies for the Near-Term and Long-Term Transmission Planning Horizons in Requirement R2, Parts 2.1, and 2.2. The studies shall be based on computer simulation models using data provided in Requirement R1. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R3.1. | Studies shall be performed for planning events to determine whether the BESmeets the performance requirements in Table 1 based on the Contingency list created in Requirement R3, Part 3.4. | MEDIUM | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R3.2. | Studies shall be performed to assess the impact of the extreme events which are identified by the list created in Requirement R3, Part 3.5. If the analysis concludes there is Cascading caused by the occurrence of extreme events, anevaluation of possible actions designed to reduce the likelihood or mitigate the consequences and adverse impacts of the event(s) shall be conducted. | MEDIUM | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R3.3. | Contingency analyses for Requirement R3, Parts 3.1 and 3.2 shall: | MEDIUM | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R3.3.1. | Simulate the removal of all elements that the Protection System and other automatic controls are expected to disconnect for each Contingency without operator intervention. The analyses shall include the impact of subsequent: | MEDIUM | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R3.3.1.1. | Tripping of generators where simulations show generator bus voltages or high side of the generation step up (GSU)voltages are less than known or assumed minimum generator steady state or ride through voltage limitations. Include in the assessment any assumptions made. | MEDIUM | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R3.3.1.2. | Tripping of Transmission elements where relay loadability limits are exceeded. | MEDIUM | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R3.3.2. | Simulate the expected automatic operation of existing and planned devices designed to provide steady state control of electrical system quantities when such devices impact the study area. These devices may include equipment such as phase-shifting transformers, load tap changing transformers, and switched capacitors and inductors. | MEDIUM | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R3.4. | Those planning events in Table 1 that are expected to produce more severeSystem impacts on its portion of the BES shall be identified, and a list of those Contingencies to be evaluated for System performance in Requirement R3, Part 3.1 created. The rationale for those Contingencies selected for evaluation shall be available as supporting information. | MEDIUM | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R3.4.1. | The Planning Coordinator and Transmission Planner shall coordinate with adjacent Planning Coordinators and Transmission Planners to ensure that Contingencies on adjacent Systems which may impact their Systems are included in the Contingency list. | MEDIUM | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R3.5. | Those extreme events in Table 1 that are expected to produce more severe System impacts shall be identified and a list created of those events to be evaluated in Requirement R3, Part 3.2. The rationale for those Contingencies selected for evaluation shall be available as supporting information. | MEDIUM | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R4. | For the Stability portion of the Planning Assessment, as described in Requirement R2, Parts 2.4 and 2.5, each Transmission Planner and Planning Coordinator shall perform the Contingency analyses listed in Table 1. The studies shall be based on computer simulation models using data provided in Requirement R1. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R4.1. | Studies shall be performed for planning events to determine whether the BES meets the performance requirements in Table 1 based on the Contingency list created in Requirement R4, Part 4.4. | MEDIUM | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R4.1.1. | For planning event P1: No generating unit shall pull out of synchronism. A generator being disconnected from the System by fault clearing action or by a Remedial Action Scheme is not considered pulling out of synchronism. | MEDIUM | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R4.1.2. | For planning events P2 through P7: When a generator pulls out of synchronism in the simulations, the resulting apparent impedance swings shall not result in the tripping of any Transmission system elements other than the generating unit and its directly connected Facilities. | MEDIUM | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R4.1.3. | For planning events P1 through P7: Power oscillations shall exhibit acceptable damping as established by the Planning Coordinator and Transmission Planner. | MEDIUM | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R4.2. | Studies shall be performed to assess the impact of the extreme events which are identified by the list created in Requirement R4, Part 4.5. If the analysis concludes there is Cascading caused by the occurrence of extreme events, an evaluation of possible actions designed to reduce the likelihood or mitigate the consequences of the event (s) shall be conducted. | MEDIUM | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R4.3. | Contingency analyses for Requirement R4, Parts 4.1 and 4.2 shall : | MEDIUM | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R4.3.1. | Simulate the removal of all elements that the Protection System and other automatic controls are expected to disconnect for each Contingency without operator intervention. The analyses shall include the impact of subsequent: | MEDIUM | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R4.3.1.1. | Successful high speed (less than one second) reclosing andunsuccessful high speed reclosing into a Fault where high speed reclosing is utilized. | MEDIUM | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R4.3.1.2. | Tripping of generators where simulations show generator bus voltages or high side of the GSU voltages are less than known or assumed generator low voltage ride through capability. Include in the assessment any assumptions made. | MEDIUM | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R4.3.1.3. | Tripping of Transmission lines and transformers where transient swings cause Protection System operation based on generic or actual relay models. | MEDIUM | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R4.3.2. | Simulate the expected automatic operation of existing and planned devices designed to provide dynamic control of electrical system quantities when such devices impact the study area. These devices may include equipment such as generation exciter control and powersystem stabilizers, static var compensators, power flow controllers, and DC Transmission controllers. | MEDIUM | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R4.4. | Those planning events in Table 1 that are expected to produce more severe System impacts on its portion of the BES, shall be identified, and a list created of those Contingencies to be evaluated in Requirement R4, Part 4.1. The rationale for those Contingencies selected for evaluation shall be available as supporting information. | MEDIUM | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R4.4.1. | Each Planning Coordinator and Transmission Planner shall coordinate with adjacent Planning Coordinators and Transmission Planners to ensure that Contingencies on adjacent Systems which may impact their Systems are included in the Contingency list. | MEDIUM | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R4.5. | Those extreme events in Table 1 that are expected to produce more severe System impacts shall be identified and a list created of those events to be evaluated in Requirement R4, Part 4.2. The rationale for those Contingencies selected for evaluation shall be available as supporting information. | MEDIUM | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R5. | Each Transmission Planner and Planning Coordinator shall have criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, and the transient voltage response for its System. For transient voltage response, the criteria shall at a minimum, specify a low voltage level and a maximum length of time that transient voltages may remain below that level. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R6. | Each Transmission Planner and Planning Coordinator shall define and document, within their Planning Assessment, the criteria or methodology used in the analysis to identify System instability for conditions such as Cascading, voltage instability, or uncontrolled islanding. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R7. | Each Planning Coordinator, in conjunction with each of its Transmission Planners, shall determine and identify each entity’s individual and joint responsibilities for performing the required studies for the Planning Assessment. [Violation Risk Factor: Low] [Time Horizon: Long-term Planning] | LOW | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R8. | Each Planning Coordinator and Transmission Planner shall distribute its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners within 90 calendar days of completing its Planning Assessment, and to any functional entity that has a reliability related need and submits a written request for the information within 30 days of such a request. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2023-07-01 |  | TP, PC
TPL-001-5.1 | Transmission System Planning Performance Requirements | R8.1. | If a recipient of the Planning Assessment results provides documented comments on the results, the respective Planning Coordinator or Transmission Planner shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | MEDIUM | Effective | 2023-07-01 |  | TP, PC
TPL-002-0(i)b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that the Network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand levels over the range of forecast system demands, under the contingency conditions as defined in Category B of Table I. To be valid, the Planning Authority and Transmission Planner assessments shall: | HIGH | Retired |  |  | TP, PA
TPL-002-0(i)b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.1. | Be made annually. | MEDIUM | Retired |  |  | TP, PA
TPL-002-0(i)b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.2. | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. | MEDIUM | Retired |  |  | TP, PA
TPL-002-0(i)b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category B of Table 1 (single contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). | MEDIUM | Retired |  |  | TP, PA
TPL-002-0(i)b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.3.1. | Be performed and evaluated only for those Category B contingencies that would produce the more severe System results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. | MEDIUM | Retired |  |  | TP, PA
TPL-002-0(i)b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.3.10. | Include the effects of existing and planned protection systems, including any backup or redundant systems. | MEDIUM | Retired |  |  | TP, PA
TPL-002-0(i)b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.3.11. | Include the effects of existing and planned control devices. | MEDIUM | Retired |  |  | TP, PA
TPL-002-0(i)b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.3.12. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. | MEDIUM | Retired |  |  | TP, PA
TPL-002-0(i)b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. | MEDIUM | Retired |  |  | TP, PA
TPL-002-0(i)b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. | MEDIUM | Retired |  |  | TP, PA
TPL-002-0(i)b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.3.4. | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. | MEDIUM | Retired |  |  | TP, PA
TPL-002-0(i)b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.3.5. | Have all projected firm transfers modeled. | MEDIUM | Retired |  |  | TP, PA
TPL-002-0(i)b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.3.6. | Be performed and evaluated for selected demand levels over the range of forecast system Demands. | MEDIUM | Retired |  |  | TP, PA
TPL-002-0(i)b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.3.7. | Demonstrate that system performance meets Category B contingencies. | MEDIUM | Retired |  |  | TP, PA
TPL-002-0(i)b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.3.8. | Include existing and planned facilities. | MEDIUM | Retired |  |  | TP, PA
TPL-002-0(i)b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.3.9. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. | MEDIUM | Retired |  |  | TP, PA
TPL-002-0(i)b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.4. | Address any planned upgrades needed to meet the performance requirements of Category B of Table I. | MEDIUM | Retired |  |  | TP, PA
TPL-002-0(i)b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.5. | Consider all contingencies applicable to Category B. | MEDIUM | Retired |  |  | TP, PA
TPL-002-0(i)b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R2. | When System simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-002-0(i)b_R1, the Planning Authority and Transmission Planner shall each: | MEDIUM | Retired |  |  | TP, PA
TPL-002-0(i)b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R2.1. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: | MEDIUM | Retired |  |  | TP, PA
TPL-002-0(i)b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R2.1.1. | Including a schedule for implementation. | MEDIUM | Retired |  |  | TP, PA
TPL-002-0(i)b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R2.1.2. | Including a discussion of expected required in-service dates of facilities. | MEDIUM | Retired |  |  | TP, PA
TPL-002-0(i)b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R2.1.3. | Consider lead times necessary to implement plans. | MEDIUM | Retired |  |  | TP, PA
TPL-002-0(i)b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R2.2. | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. | MEDIUM | Retired |  |  | TP, PA
TPL-002-0(i)b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R3. | The Planning Authority and Transmission Planner shall each document the results of its Reliability Assessments and corrective plans and shall annually provide the results to its respective Regional Reliability Organization(s), as required by the Regional Reliability Organization. | LOWER | Retired |  |  | TP, PA
TPL-002-1b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that the Network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand levels over the range of forecast system demands, under the contingency conditions as defined in Category B of Table I. To be valid, the Planning Authority and Transmission Planner assessments shall: | HIGH | Retired |  |  | TP, PA
TPL-002-1b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.1. | Be made annually. | MEDIUM | Retired |  |  | TP, PA
TPL-002-1b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.2. | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. | MEDIUM | Retired |  |  | TP, PA
TPL-002-1b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category B of Table 1 (single contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). | MEDIUM | Retired |  |  | TP, PA
TPL-002-1b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.3.1. | Be performed and evaluated only for those Category B contingencies that would produce the more severe System results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. | MEDIUM | Retired |  |  | TP, PA
TPL-002-1b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.3.10. | Include the effects of existing and planned protection systems, including any backup or redundant systems. | MEDIUM | Retired |  |  | TP, PA
TPL-002-1b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.3.11. | Include the effects of existing and planned control devices. | MEDIUM | Retired |  |  | TP, PA
TPL-002-1b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.3.12. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. | MEDIUM | Retired |  |  | TP, PA
TPL-002-1b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. | MEDIUM | Retired |  |  | TP, PA
TPL-002-1b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. | MEDIUM | Retired |  |  | TP, PA
TPL-002-1b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.3.4. | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. | MEDIUM | Retired |  |  | TP, PA
TPL-002-1b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.3.5. | Have all projected firm transfers modeled. | MEDIUM | Retired |  |  | TP, PA
TPL-002-1b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.3.6. | Be performed and evaluated for selected demand levels over the range of forecast system Demands. | MEDIUM | Retired |  |  | TP, PA
TPL-002-1b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.3.7. | Demonstrate that system performance meets Category B contingencies. | MEDIUM | Retired |  |  | TP, PA
TPL-002-1b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.3.8. | Include existing and planned facilities. | MEDIUM | Retired |  |  | TP, PA
TPL-002-1b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.3.9. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. | MEDIUM | Retired |  |  | TP, PA
TPL-002-1b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.4. | Address any planned upgrades needed to meet the performance requirements of Category B of Table I. | MEDIUM | Retired |  |  | TP, PA
TPL-002-1b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.5. | Consider all contingencies applicable to Category B. | MEDIUM | Retired |  |  | TP, PA
TPL-002-1b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R2. | When System simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-002-1_R1, the Planning Authority and Transmission Planner shall each: | MEDIUM | Retired |  |  | TP, PA
TPL-002-1b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R2.1. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: | MEDIUM | Retired |  |  | TP, PA
TPL-002-1b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R2.1.1. | Including a schedule for implementation. | MEDIUM | Retired |  |  | TP, PA
TPL-002-1b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R2.1.2. | Including a discussion of expected required in-service dates of facilities. | MEDIUM | Retired |  |  | TP, PA
TPL-002-1b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R2.1.3. | Consider lead times necessary to implement plans. | MEDIUM | Retired |  |  | TP, PA
TPL-002-1b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R2.2. | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. | MEDIUM | Retired |  |  | TP, PA
TPL-002-1b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R3. | The Planning Authority and Transmission Planner shall each document the results of its Reliability Assessments and corrective plans and shall annually provide the results to its respective Regional Reliability Organization(s), as required by the Regional Reliability Organization. | LOWER | Retired |  |  | TP, PA
TPL-002-2b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that the Network can be operated to supply projected customer demands and projected Firm (nonrecallable reserved) Transmission Services, at all demand levels over the range of forecast system demands, under the contingency conditions as defined in Category B of Table I. To be valid, the Planning Authority and Transmission Planner assessments shall: |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-002-2b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.1. | Be made annually. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-002-2b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.2. | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-002-2b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category B of Table 1 (single contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-002-2b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.3.1. | Be performed and evaluated only for those Category B contingencies that would produce the more severe System results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-002-2b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.3.10. | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-002-2b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.3.11. | Include the effects of existing and planned control devices. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-002-2b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.3.12. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-002-2b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-002-2b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-002-2b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.3.4. | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-002-2b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.3.5. | Have all projected firm transfers modeled. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-002-2b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.3.6. | Be performed and evaluated for selected demand levels over the range of forecast system Demands. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-002-2b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.3.7. | Demonstrate that system performance meets Category B contingencies. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-002-2b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.3.8. | Include existing and planned facilities. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-002-2b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.3.9. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-002-2b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.4. | Address any planned upgrades needed to meet the performance requirements of Category B of Table I. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-002-2b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R1.5. | Consider all contingencies applicable to Category B. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-002-2b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R2. | When System simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-002-1_R1, the Planning Authority and Transmission Planner shall each: |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-002-2b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R2.1. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-002-2b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R2.1.1. | Including a schedule for implementation. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-002-2b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R2.1.2. | Including a discussion of expected required in-service dates of facilities. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-002-2b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R2.1.3. | Consider lead times necessary to implement plans. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-002-2b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R2.2. | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-002-2b | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | R3. | The Planning Authority and Transmission Planner shall each document the results of its Reliability Assessments and corrective plans and shall annually provide the results to its respective Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-0(i)b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission systems is planned such that the network can be operated to supply projected customer demands and projected Firm (nonrecallable reserved) Transmission Services, at all demand Levels over the range of forecast system demands, under the contingency conditions as defined in Category C of Table I (attached). The controlled interruption of customer Demand, the planned removal of generators, or the Curtailment of firm (non-recallable reserved) power transfers may be necessary to meet this standard. To be valid, the Planning Authority and Transmission Planner assessments shall: | HIGH | Retired |  |  | TP, PA
TPL-003-0(i)b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.1. | Be made annually. | MEDIUM | Retired |  |  | TP, PA
TPL-003-0(i)b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.2. | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. | MEDIUM | Retired |  |  | TP, PA
TPL-003-0(i)b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category C of Table 1 (multiple contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). | MEDIUM | Retired |  |  | TP, PA
TPL-003-0(i)b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3.1. | Be performed and evaluated only for those Category C contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. | MEDIUM | Retired |  |  | TP, PA
TPL-003-0(i)b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3.10. | Include the effects of existing and planned protection systems, including any backup or redundant systems. | MEDIUM | Retired |  |  | TP, PA
TPL-003-0(i)b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3.11. | Include the effects of existing and planned control devices. | MEDIUM | Retired |  |  | TP, PA
TPL-003-0(i)b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3.12. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those Demand levels for which planned (including maintenance) outages are performed. | MEDIUM | Retired |  |  | TP, PA
TPL-003-0(i)b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. | MEDIUM | Retired |  |  | TP, PA
TPL-003-0(i)b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. | MEDIUM | Retired |  |  | TP, PA
TPL-003-0(i)b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3.4. | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. | MEDIUM | Retired |  |  | TP, PA
TPL-003-0(i)b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3.5. | Have all projected firm transfers modeled. | MEDIUM | Retired |  |  | TP, PA
TPL-003-0(i)b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3.6. | Be performed and evaluated for selected demand levels over the range of forecast system demands. | MEDIUM | Retired |  |  | TP, PA
TPL-003-0(i)b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3.7. | Demonstrate that System performance meets Table 1 for Category C contingencies. | MEDIUM | Retired |  |  | TP, PA
TPL-003-0(i)b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3.8. | Include existing and planned facilities. | MEDIUM | Retired |  |  | TP, PA
TPL-003-0(i)b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3.9. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet System performance. | MEDIUM | Retired |  |  | TP, PA
TPL-003-0(i)b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.4. | Address any planned upgrades needed to meet the performance requirements of Category C. | MEDIUM | Retired |  |  | TP, PA
TPL-003-0(i)b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.5. | Consider all contingencies applicable to Category C. | MEDIUM | Retired |  |  | TP, PA
TPL-003-0(i)b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R2. | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-003-0(i)b_R1, the Planning Authority and Transmission Planner shall each: | MEDIUM | Retired |  |  | TP, PA
TPL-003-0(i)b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R2.1. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: | MEDIUM | Retired |  |  | TP, PA
TPL-003-0(i)b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R2.1.1. | Including a schedule for implementation. | MEDIUM | Retired |  |  | TP, PA
TPL-003-0(i)b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R2.1.2. | Including a discussion of expected required in-service dates of facilities. | MEDIUM | Retired |  |  | TP, PA
TPL-003-0(i)b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R2.1.3. | Consider lead times necessary to implement plans. | MEDIUM | Retired |  |  | TP, PA
TPL-003-0(i)b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R2.2. | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. | MEDIUM | Retired |  |  | TP, PA
TPL-003-0(i)b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R3. | The Planning Authority and Transmission Planner shall each document the results of these Reliability Assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. | LOWER | Retired |  |  | TP, PA
TPL-003-1a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission systems is planned such that the network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand Levels over the range of forecast system demands, under the contingency conditions as defined in Category C of Table I (attached). The controlled interruption of customer Demand, the planned removal of generators, or the Curtailment of firm (non-recallable reserved) power transfers may be necessary to meet this standard. To be valid, the Planning Authority and Transmission Planner assessments shall: | HIGH | Retired |  |  | TP, PA
TPL-003-1a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.1. | Be made annually. | MEDIUM | Retired |  |  | TP, PA
TPL-003-1a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.2. | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. | MEDIUM | Retired |  |  | TP, PA
TPL-003-1a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category C of Table 1 (multiple contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). | MEDIUM | Retired |  |  | TP, PA
TPL-003-1a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3.1. | Be performed and evaluated only for those Category C contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. | MEDIUM | Retired |  |  | TP, PA
TPL-003-1a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3.10. | Include the effects of existing and planned protection systems, including any backup or redundant systems. | MEDIUM | Retired |  |  | TP, PA
TPL-003-1a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3.11. | Include the effects of existing and planned control devices. | MEDIUM | Retired |  |  | TP, PA
TPL-003-1a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3.12. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those Demand levels for which planned (including maintenance) outages are performed. | MEDIUM | Retired |  |  | TP, PA
TPL-003-1a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. | MEDIUM | Retired |  |  | TP, PA
TPL-003-1a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. | MEDIUM | Retired |  |  | TP, PA
TPL-003-1a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3.4. | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. | MEDIUM | Retired |  |  | TP, PA
TPL-003-1a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3.5. | Have all projected firm transfers modeled. | MEDIUM | Retired |  |  | TP, PA
TPL-003-1a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3.6. | Be performed and evaluated for selected demand levels over the range of forecast system demands. | MEDIUM | Retired |  |  | TP, PA
TPL-003-1a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3.7. | Demonstrate that System performance meets Table 1 for Category C contingencies. | MEDIUM | Retired |  |  | TP, PA
TPL-003-1a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3.8. | Include existing and planned facilities. | MEDIUM | Retired |  |  | TP, PA
TPL-003-1a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3.9. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet System performance. | MEDIUM | Retired |  |  | TP, PA
TPL-003-1a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.4. | Address any planned upgrades needed to meet the performance requirements of Category C. | MEDIUM | Retired |  |  | TP, PA
TPL-003-1a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.5. | Consider all contingencies applicable to Category C. | MEDIUM | Retired |  |  | TP, PA
TPL-003-1a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R2. | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-003-1_R1, the Planning Authority and Transmission Planner shall each: | MEDIUM | Retired |  |  | TP, PA
TPL-003-1a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R2.1. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: | MEDIUM | Retired |  |  | TP, PA
TPL-003-1a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R2.1.1. | Including a schedule for implementation. | MEDIUM | Retired |  |  | TP, PA
TPL-003-1a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R2.1.2. | Including a discussion of expected required in-service dates of facilities. | MEDIUM | Retired |  |  | TP, PA
TPL-003-1a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R2.1.3. | Consider lead times necessary to implement plans. | MEDIUM | Retired |  |  | TP, PA
TPL-003-1a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R2.2. | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. | MEDIUM | Retired |  |  | TP, PA
TPL-003-1a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R3. | The Planning Authority and Transmission Planner shall each document the results of these Reliability Assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. | LOWER | Retired |  |  | TP, PA
TPL-003-2a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission systems is planned such that the network can be operated to supply projected customer demands and projected Firm (nonrecallable reserved) Transmission Services, at all demand Levels over the range of forecast system demands, under the contingency conditions as defined in Category C of Table I (attached). The controlled interruption of customer Demand, the planned removal of generators, or the Curtailment of firm (non-recallable reserved) power transfers may be necessary to meet this standard. To be valid, the Planning Authority and Transmission Planner assessments shall: |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.1. | Be made annually. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.2. | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category C of Table 1 (multiple contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3.1. | Be performed and evaluated only for those Category C contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3.10. | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3.11. | Include the effects of existing and planned control devices. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3.12. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those Demand levels for which planned (including maintenance) outages are performed. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3.4. | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3.5. | Have all projected firm transfers modeled. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3.6. | Be performed and evaluated for selected demand levels over the range of forecast system demands. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3.7. | Demonstrate that System performance meets Table 1 for Category C contingencies. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3.8. | Include existing and planned facilities. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3.9. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet System performance. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.4. | Address any planned upgrades needed to meet the performance requirements of Category C. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.5. | Consider all contingencies applicable to Category C. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R2. | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-003-2_R1, the Planning Authority and Transmission Planner shall each: |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R2.1. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R2.1.1. | Including a schedule for implementation. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R2.1.2. | Including a discussion of expected required in-service dates of facilities. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R2.1.3. | Consider lead times necessary to implement plans. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R2.2. | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2a | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R3. | The Planning Authority and Transmission Planner shall each document the results of these Reliability Assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission systems is planned such that the network can be operated to supply projected customer demands and projected Firm (nonrecallable reserved) Transmission Services, at all demand Levels over the range of forecast system demands, under the contingency conditions as defined in Category C of Table I (attached). The controlled interruption of customer Demand, the planned removal of generators, or the Curtailment of firm (non-recallable reserved) power transfers may be necessary to meet this standard. To be valid, the Planning Authority and Transmission Planner assessments shall: |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.1. | Be made annually. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.2. | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category C of Table 1 (multiple contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3.1. | Be performed and evaluated only for those Category C contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3.10. | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3.11. | Include the effects of existing and planned control devices. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3.12. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those Demand levels for which planned (including maintenance) outages are performed. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3.4. | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3.5. | Have all projected firm transfers modeled. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3.6. | Be performed and evaluated for selected demand levels over the range of forecast system demands. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3.7. | Demonstrate that System performance meets Table 1 for Category C contingencies. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3.8. | Include existing and planned facilities. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.3.9. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet System performance. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.4. | Address any planned upgrades needed to meet the performance requirements of Category C. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R1.5. | Consider all contingencies applicable to Category C. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R2. | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-003-2_R1, the Planning Authority and Transmission Planner shall each: |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R2.1. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R2.1.1. | Including a schedule for implementation. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R2.1.2. | Including a discussion of expected required in-service dates of facilities. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R2.1.3. | Consider lead times necessary to implement plans. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R2.2. | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-003-2b | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | R3. | The Planning Authority and Transmission Planner shall each document the results of these Reliability Assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-004-0(i)a | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is evaluated for the risks and consequences of a number of each of the extreme contingencies that are listed under Category D of Table I. To be valid, the Planning Authority’s and Transmission Planner’s assessment shall: | MEDIUM | Retired |  |  | TP, PA
TPL-004-0(i)a | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.1. | Be made annually. | MEDIUM | Retired |  |  | TP, PA
TPL-004-0(i)a | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.2. | Be conducted for near-term (years one through five). | MEDIUM | Retired |  |  | TP, PA
TPL-004-0(i)a | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category D contingencies of Table I. The specific elements selected (from within each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). | MEDIUM | Retired |  |  | TP, PA
TPL-004-0(i)a | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.3.1. | Be performed and evaluated only for those Category D contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. | MEDIUM | Retired |  |  | TP, PA
TPL-004-0(i)a | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. | MEDIUM | Retired |  |  | TP, PA
TPL-004-0(i)a | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. | MEDIUM | Retired |  |  | TP, PA
TPL-004-0(i)a | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.3.4. | Have all projected firm transfers modeled. | MEDIUM | Retired |  |  | TP, PA
TPL-004-0(i)a | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.3.5. | Include existing and planned facilities. | MEDIUM | Retired |  |  | TP, PA
TPL-004-0(i)a | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.3.6. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. | MEDIUM | Retired |  |  | TP, PA
TPL-004-0(i)a | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.3.7. | Include the effects of existing and planned protection systems, including any backup or redundant systems. | MEDIUM | Retired |  |  | TP, PA
TPL-004-0(i)a | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.3.8. | Include the effects of existing and planned control devices. | MEDIUM | Retired |  |  | TP, PA
TPL-004-0(i)a | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.3.9. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. | MEDIUM | Retired |  |  | TP, PA
TPL-004-0(i)a | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.4. | Consider all contingencies applicable to Category D. | MEDIUM | Retired |  |  | TP, PA
TPL-004-0(i)a | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R2. | The Planning Authority and Transmission Planner shall each document the results of its reliability assessments and shall annually provide the results to its entities’ respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. | LOWER | Retired |  |  | TP, PA
TPL-004-1 | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is evaluated for the risks and consequences of a number of each of the extreme contingencies that are listed under Category D of Table I. To be valid, the Planning Authority’s and Transmission Planner’s assessment shall: | MEDIUM | Retired |  |  | TP, PA
TPL-004-1 | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.1. | Be made annually. | MEDIUM | Retired |  |  | TP, PA
TPL-004-1 | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.2. | Be conducted for near-term (years one through five). | MEDIUM | Retired |  |  | TP, PA
TPL-004-1 | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category D contingencies of Table I. The specific elements selected (from within each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). | MEDIUM | Retired |  |  | TP, PA
TPL-004-1 | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.3.1. | Be performed and evaluated only for those Category D contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. | MEDIUM | Retired |  |  | TP, PA
TPL-004-1 | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. | MEDIUM | Retired |  |  | TP, PA
TPL-004-1 | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. | MEDIUM | Retired |  |  | TP, PA
TPL-004-1 | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.3.4. | Have all projected firm transfers modeled. | MEDIUM | Retired |  |  | TP, PA
TPL-004-1 | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.3.5. | Include existing and planned facilities. | MEDIUM | Retired |  |  | TP, PA
TPL-004-1 | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.3.6. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. | MEDIUM | Retired |  |  | TP, PA
TPL-004-1 | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.3.7. | Include the effects of existing and planned protection systems, including any backup or redundant systems. | MEDIUM | Retired |  |  | TP, PA
TPL-004-1 | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.3.8. | Include the effects of existing and planned control devices. | MEDIUM | Retired |  |  | TP, PA
TPL-004-1 | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.3.9. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. | MEDIUM | Retired |  |  | TP, PA
TPL-004-1 | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.4. | Consider all contingencies applicable to Category D. | MEDIUM | Retired |  |  | TP, PA
TPL-004-1 | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R2. | The Planning Authority and Transmission Planner shall each document the results of its reliability assessments and shall annually provide the results to its entities’ respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. | LOWER | Retired |  |  | TP, PA
TPL-004-2 | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is evaluated for the risks and consequences of a number of each of the extreme contingencies that are listed under Category D of Table I. To be valid, the Planning Authority’s and Transmission Planner’s assessment shall: |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-004-2 | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.1. | Be made annually. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-004-2 | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.2. | Be conducted for near-term (years one through five). |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-004-2 | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category D contingencies of Table I. The specific elements selected (from within each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-004-2 | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.3.1. | Be performed and evaluated only for those Category D contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-004-2 | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-004-2 | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-004-2 | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.3.4. | Have all projected firm transfers modeled. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-004-2 | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.3.5. | Include existing and planned facilities. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-004-2 | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.3.6. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-004-2 | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.3.7. | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-004-2 | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.3.8. | Include the effects of existing and planned control devices. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-004-2 | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.3.9. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-004-2 | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.4. | Consider all contingencies applicable to Category D. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-004-2 | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R2. | The Planning Authority and Transmission Planner shall each document the results of its reliability assessments and shall annually provide the results to its entities’ respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-004-2a | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is evaluated for the risks and consequences of a number of each of the extreme contingencies that are listed under Category D of Table I. To be valid, the Planning Authority’s and Transmission Planner’s assessment shall: |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-004-2a | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.1. | Be made annually |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-004-2a | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.2. | Be conducted for near-term (years one through five). |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-004-2a | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category D contingencies of Table I. The specific elements selected (from within each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-004-2a | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.3.1. | Be performed and evaluated only for those Category D contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-004-2a | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-004-2a | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-004-2a | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.3.4. | Have all projected firm transfers modeled. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-004-2a | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.3.5. | Include existing and planned facilities. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-004-2a | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.3.6. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-004-2a | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.3.7. | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-004-2a | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.3.8. | Include the effects of existing and planned control devices. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-004-2a | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.3.9. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-004-2a | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R1.4. | Consider all contingencies applicable to Category D. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-004-2a | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | R2. | The Planning Authority and Transmission Planner shall each document the results of its reliability assessments and shall annually provide the results to its entities’ respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | Never Came Into Effect in Ontario |  |  | TP, PC, PA
TPL-007-1 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R1. | Each Planning Coordinator, in conjunction with its Transmission Planner(s), shall identify the individual and joint responsibilities of the Planning Coordinator and Transmission Planner(s) in the Planning Coordinator’s planning area for maintaining models and performing the study or studies needed to complete GMD Vulnerability Assessment(s). [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | LOWER | Effective | 2017-07-01 |  | TP, PC
TPL-007-1 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R2. | Each responsible entity, as determined in Requirement R1, shall maintain System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete GMD Vulnerability Assessment(s). [Violation Risk Factor: High] [Time Horizon: Long-term Planning] | HIGH | Effective | 2018-07-01 |  | TP, PC
TPL-007-1 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R3. | Each responsible entity, as determined in Requirement R1, shall have criteria for acceptable System steady state voltage performance for its System during the benchmark GMD event described in Attachment 1. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2022-01-01 |  | TP, PC
TPL-007-1 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R4. | Each responsible entity, as determined in Requirement R1, shall complete a GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon once every 60 calendar months. This GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. [Violation Risk Factor: High] [Time Horizon: Long-term Planning] | HIGH | Effective | 2022-01-01 |  | TP, PC
TPL-007-1 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R4.1. | The study or studies shall include the following conditions: | HIGH | Effective | 2022-01-01 |  | TP, PC
TPL-007-1 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R4.1.1. | System On-Peak Load for at least one year within the Near-Term Transmission Planning Horizon; and | HIGH | Effective | 2022-01-01 |  | TP, PC
TPL-007-1 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R4.1.2. | System Off-Peak Load for at least one year within the Near-Term Transmission Planning Horizon. | HIGH | Effective | 2022-01-01 |  | TP, PC
TPL-007-1 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R4.2. | The study or studies shall be conducted based on the benchmark GMD event described in Attachment 1 to determine whether the System meets the performance requirements in Table 1. | HIGH | Effective | 2022-01-01 |  | TP, PC
TPL-007-1 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R4.3. | The GMD Vulnerability Assessment shall be provided within 90 calendar days of completion to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners, and to any functional entity that submits a written request and has a reliability-related need. | HIGH | Effective | 2022-01-01 |  | TP, PC
TPL-007-1 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R4.3.1. | If a recipient of the GMD Vulnerability Assessment provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | HIGH | Effective | 2022-01-01 |  | TP, PC
TPL-007-1 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R5. | Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the transformer thermal impact assessment specified in Requirement R6 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2019-01-01 |  | TP, PC
TPL-007-1 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R5.1. | The maximum effective GIC value for the worst case geoelectric field orientation for the benchmark GMD event described in Attachment 1. This value shall be provided to the Transmission Owner or Generator Owner that owns each applicable BES power transformer in the planning area. | MEDIUM | Effective | 2019-01-01 |  | TP, PC
TPL-007-1 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R5.2. | The effective GIC time series, GIC(t), calculated using the benchmark GMD event described in Attachment 1 in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. GIC(t) shall be provided within 90 calendar days of receipt of the written request and after determination of the maximum effective GIC value in Part 5.1. | MEDIUM | Effective | 2019-01-01 |  | TP, PC
TPL-007-1 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R6. | Each Transmission Owner and Generator Owner shall conduct a thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater. The thermal impact assessment shall: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Effective | 2021-01-01 |  | TO, GO
TPL-007-1 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R6.1. | Be based on the effective GIC flow information provided in Requirement R5; | MEDIUM | Effective | 2021-01-01 |  | TO, GO
TPL-007-1 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R6.2. | Document assumptions used in the analysis; | MEDIUM | Effective | 2021-01-01 |  | TO, GO
TPL-007-1 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R6.3. | Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and | MEDIUM | Effective | 2021-01-01 |  | TO, GO
TPL-007-1 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R6.4. | Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1. | MEDIUM | Effective | 2021-01-01 |  | TO, GO
TPL-007-1 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R7. | Each responsible entity, as determined in Requirement R1, that concludes, through the GMD Vulnerability Assessment conducted in Requirement R4, that their System does not meet the performance requirements of Table 1 shall develop a Corrective Action Plan addressing how the performance requirements will be met. The Corrective Action Plan shall: [Violation Risk Factor: High] [Time Horizon: Long-term Planning] | HIGH | Effective | 2022-01-01 |  | TP, PC
TPL-007-1 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R7.1. | List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include:  Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment.  Installation, modification, or removal of Protection Systems or Special Protection Systems.  Use of Operating Procedures, specifying how long they will be needed as part of the Corrective Action Plan.  Use of Demand-Side Management, new technologies, or other initiatives. | HIGH | Effective | 2022-01-01 |  | TP, PC
TPL-007-1 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R7.2. | Be reviewed in subsequent GMD Vulnerability Assessments until it is determined that the System meets the performance requirements contained in Table 1. | HIGH | Effective | 2022-01-01 |  | TP, PC
TPL-007-1 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R7.3. | Be provided within 90 calendar days of completion to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), functional entities referenced in the Corrective Action Plan, and any functional entity that submits a written request and has a reliability-related need. | HIGH | Effective | 2022-01-01 |  | TP, PC
TPL-007-1 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R7.3.1. | If a recipient of the Corrective Action Plan provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | HIGH | Effective | 2022-01-01 |  | TP, PC
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R1. | Each Planning Coordinator, in conjunction with its Transmission Planner(s), shall identify the individual and joint responsibilities of the Planning Coordinator and Transmission Planner(s) in the Planning Coordinator’s planning area for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data as specified in this standard. | LOWER | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R10. | Each Transmission Owner and Generator Owner shall conduct a supplemental thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater. The supplemental thermal impact assessment shall: | MEDIUM | Never Came Into Effect in Ontario |  |  | TO, GO
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R10.1. | Be based on the effective GIC flow information provided in Requirement R9; | MEDIUM | Never Came Into Effect in Ontario |  |  | TO, GO
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R10.2. | Document assumptions used in the analysis; | MEDIUM | Never Came Into Effect in Ontario |  |  | TO, GO
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R10.3. | Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and | MEDIUM | Never Came Into Effect in Ontario |  |  | TO, GO
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R10.4. | Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1. | MEDIUM | Never Came Into Effect in Ontario |  |  | TO, GO
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R11. | Each responsible entity, as determined in Requirement R1, shall implement a process to obtain GIC monitor data from at least one GIC monitor located in the Planning Coordinator's planning area or other part of the system included in the Planning Coordinator's GIC System model. | LOWER | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R12. | Each responsible entity, as determined in Requirement R1, shall implement a process to obtain geomagnetic field data for its Planning Coordinator’s planning area. | LOWER | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R2. | Each responsible entity, as determined in Requirement R1, shall maintain System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | HIGH | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R3. | Each responsible entity, as determined in Requirement R1, shall have criteria for acceptable System steady state voltage performance for its System during the GMD events described in Attachment 1. | MEDIUM | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R4. | Each responsible entity, as determined in Requirement R1, shall complete a benchmark GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon at least once every 60 calendar months. This benchmark GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. | HIGH | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R4.1. | The study or studies shall include the following conditions: | HIGH | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R4.1.1. | System On-Peak Load for at least one year within the Near-Term Transmission Planning Horizon; and | HIGH | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R4.1.2. | System Off-Peak Load for at least one year within the Near-Term Transmission Planning Horizon. | HIGH | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R4.2. | The study or studies shall be conducted based on the benchmark GMD event described in Attachment 1 to determine whether the System meets the performance requirements for the steady state planning benchmark GMD event contained in Table 1. | HIGH | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R4.3. | The benchmark GMD Vulnerability Assessment shall be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later. | HIGH | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R4.3.1. | If a recipient of the benchmark GMD Vulnerability Assessment provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | HIGH | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R5. | Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the benchmark thermal impact assessment of transformers specified in Requirement R6 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: | MEDIUM | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R5.1. | The maximum effective GIC value for the worst case geoelectric field orientation for the benchmark GMD event described in Attachment 1. This value shall be provided to the Transmission Owner or Generator Owner that owns each applicable BES power transformer in the planning area. | MEDIUM | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R5.2. | The effective GIC time series, GIC(t), calculated using the benchmark GMD event described in Attachment 1 in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. GIC(t) shall be provided within 90 calendar days of receipt of the written request and after determination of the maximum effective GIC value in Part 5.1. | MEDIUM | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R6. | Each Transmission Owner and Generator Owner shall conduct a benchmark thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater. The benchmark thermal impact assessment shall: | MEDIUM | Never Came Into Effect in Ontario |  |  | TO, GO
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R6.1. | Be based on the effective GIC flow information provided in Requirement R5; | MEDIUM | Never Came Into Effect in Ontario |  |  | TO, GO
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R6.2. | Document assumptions used in the analysis; | MEDIUM | Never Came Into Effect in Ontario |  |  | TO, GO
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R6.3. | Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and | MEDIUM | Never Came Into Effect in Ontario |  |  | TO, GO
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R6.4. | Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1. | MEDIUM | Never Came Into Effect in Ontario |  |  | TO, GO
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R7. | Each responsible entity, as determined in Requirement R1, that concludes through the benchmark GMD Vulnerability Assessment conducted in Requirement R4 that their System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1, shall develop a Corrective Action Plan (CAP) addressing how the performance requirements will be met. The CAP shall: | HIGH | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R7.1. | List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include: • Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment. • Installation, modification, or removal of Protection Systems or Remedial Action Schemes. • Use of Operating Procedures, specifying how long they will be needed as part of the CAP. • Use of Demand-Side Management, new technologies, or other initiatives. | HIGH | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R7.2. | Be developed within one year of completion of the benchmark GMD Vulnerability Assessment. | HIGH | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R7.3. | Include a timetable, subject to revision by the responsible entity in Part 7.4, for implementing the selected actions from Part 7.1. The timetable shall: | HIGh | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R7.3.1. | Specify implementation of non-hardware mitigation, if any, within two years of development of the CAP; and | HIGH | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R7.3.2. | Specify implementation of hardware mitigation, if any, within four years of development of the CAP. | HIGH | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R7.4. | Be revised if situations beyond the control of the responsible entity determined in Requirement R1 prevent implementation of the CAP within the timetable for implementation provided in Part 7.3. The revised CAP shall document the following, and be updated at least once every 12 calendar months until implemented: | HIGH | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R7.4.1. | Circumstances causing the delay for fully or partially implementing the selected actions in Part 7.1; | HIGH | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R7.4.2. | Description of the original CAP, and any previous changes to the CAP, with the associated timetable(s) for implementing the selected actions in Part 7.1; and | HIGH | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R7.4.3. | Revisions to the selected actions in Part 7.1, if any, including utilization of Operating Procedures if applicable, and the updated timetable for implementing the selected actions. | HIGH | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R7.5. | Be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later. | HIGH | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R7.5.1. | If a recipient of the CAP provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | HIGH | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R8. | Each responsible entity, as determined in Requirement R1, shall complete a supplemental GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon at least once every 60 calendar months. This supplemental GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. | HIGH | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R8.1. | The study or studies shall include the following conditions: | HIGH | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R8.1.1. | System On-Peak Load for at least one year within the Near-Term Transmission Planning Horizon; and | HIGH | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R8.1.2. | System Off-Peak Load for at least one year within the Near-Term Transmission Planning Horizon. | HIGH | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R8.2. | The study or studies shall be conducted based on the supplemental GMD event described in Attachment 1 to determine whether the System meets the performance requirements for the steady state planning supplemental GMD event contained in Table 1. | HIGH | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R8.3. | If the analysis concludes there is Cascading caused by the supplemental GMD event described in Attachment 1, an evaluation of possible actions designed to reduce the likelihood or mitigate the consequences and adverse impacts of the event(s) shall be conducted. | HIGH | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R8.4. | The supplemental GMD Vulnerability Assessment shall be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later. | HIGH | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R8.4.1. | If a recipient of the supplemental GMD Vulnerability Assessment provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | HIGH | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R9. | Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the supplemental thermal impact assessment of transformers specified in Requirement R10 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: | MEDIUM | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R9.1. | The maximum effective GIC value for the worst case geoelectric field orientation for the supplemental GMD event described in Attachment 1. This value shall be provided to the Transmission Owner or Generator Owner that owns each applicable BES power transformer in the planning area. | MEDIUM | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R9.2. | The effective GIC time series, GIC(t), calculated using the supplemental GMD event described in Attachment 1 in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. GIC(t) shall be provided within 90 calendar days of receipt of the written request and after determination of the maximum effective GIC value in Part 9.1. | MEDIUM | Never Came Into Effect in Ontario |  |  | TP, PC
TPL-007-3 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R1. | Each Planning Coordinator, in conjunction with its Transmission Planner(s), shall identify the individual and joint responsibilities of the Planning Coordinator and Transmission Planner(s) in the Planning Coordinator’s planning area for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data as specified in this standard. [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | LOWER | Retired | 2019-07-01 | 2020-10-01 | TP, PC
TPL-007-3 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R10. | Each Transmission Owner and Generator Owner shall conduct a supplemental thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater. The supplemental thermal impact assessment shall: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Retired | 2022-07-01 | 2020-10-01 | TP, PC
TPL-007-3 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R10.1. | . Be based on the effective GIC flow information provided in Requirement R9; | MEDIUM | Retired | 2022-07-01 | 2020-10-01 | TP, PC
TPL-007-3 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R10.2. | Document assumptions used in the analysis; | MEDIUM | Retired | 2022-07-01 | 2020-10-01 | TP, PC
TPL-007-3 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R10.3. | . Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and | MEDIUM | Retired | 2022-07-01 | 2020-10-01 | TP, PC
TPL-007-3 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R10.4. | . Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1. | MEDIUM | Retired | 2022-07-01 | 2020-10-01 | TP, PC
TPL-007-3 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R11. | Each responsible entity, as determined in Requirement R1, shall implement a process to obtain GIC monitor data from at least one GIC monitor located in the Planning Coordinator's planning area or other part of the system included in the Planning Coordinator's GIC System model. [Violation Risk Factor: Lower] [Time Horizon: Longterm Planning] | LOWER | Retired | 2021-07-01 | 2020-10-01 | TP, PC
TPL-007-3 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R12. | Each responsible entity, as determined in Requirement R1, shall implement a process to obtain geomagnetic field data for its Planning Coordinator’s planning area. [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | LOWER | Retired | 2021-07-01 | 2020-10-01 | TP, PC
TPL-007-3 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R2. | Each responsible entity, as determined in Requirement R1, shall maintain System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. [Violation Risk Factor: High] [Time Horizon: Longterm Planning] | HIGH | Retired | 2019-07-01 | 2020-10-01 | TP, PC
TPL-007-3 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R3. | . Each responsible entity, as determined in Requirement R1, shall have criteria for acceptable System steady state voltage performance for its System during the GMD events described in Attachment 1. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Retired | 2023-01-01 | 2020-10-01 | TP, PC
TPL-007-3 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R4. | Each responsible entity, as determined in Requirement R1, shall complete a benchmark GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon at least once every 60 calendar months. This benchmark GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. [Violation Risk Factor: High] [Time Horizon: Long-term Planning] | HIGH | Retired | 2023-01-01 | 2020-10-01 | TP, PC
TPL-007-3 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R4.1. | The study or studies shall include the following conditions: | HIGH | Retired | 2023-01-01 | 2020-10-01 | TP, PC
TPL-007-3 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R4.1.1. | System On-Peak Load for at least one year within the Near-Term Transmission Planning Horizon; and | HIGH | Retired | 2023-01-01 | 2020-10-01 | TP, PC
TPL-007-3 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R4.1.2. | System Off-Peak Load for at least one year within the Near-Term Transmission Planning Horizon. | HIGH | Retired | 2023-01-01 | 2020-10-01 | TP, PC
TPL-007-3 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R4.2. | The study or studies shall be conducted based on the benchmark GMD event described in Attachment 1 to determine whether the System meets the performance requirements for the steady state planning benchmark GMD event contained in Table 1. | HIGH | Retired | 2023-01-01 | 2020-10-01 | TP, PC
TPL-007-3 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R4.3. | The benchmark GMD Vulnerability Assessment shall be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later | HIGH | Retired | 2023-01-01 | 2020-10-01 | TP, PC
TPL-007-3 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R4.3.1. | If a recipient of the benchmark GMD Vulnerability Assessment provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | HIGH | Retired | 2023-01-01 | 2020-10-01 | PC, TP
TPL-007-3 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R5. | Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the benchmark thermal impact assessment of transformers specified in Requirement R6 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Retired | 2020-01-01 | 2020-10-01 | TP, PC
TPL-007-3 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R5.1. | The maximum effective GIC value for the worst case geoelectric field orientation for the benchmark GMD event described in Attachment 1. This value shall be provided to the Transmission Owner or Generator Owner that owns each applicable BES power transformer in the planning area. | MEDIUM | Retired | 2020-01-01 | 2020-10-01 | TP, PC
TPL-007-3 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R5.2. | The effective GIC time series, GIC(t), calculated using the benchmark GMD event described in Attachment 1 in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. GIC(t) shall be provided within 90 calendar days of receipt of the written request and after determination of the maximum effective GIC value in Part 5.1. | MEDIUM | Retired | 2020-01-01 | 2020-10-01 | PC, TP
TPL-007-3 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R6. | Each Transmission Owner and Generator Owner shall conduct a benchmark thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater. The benchmark thermal impact assessment shall: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Retired | 2022-07-01 | 2020-10-01 | TP, PC
TPL-007-3 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R6.1. | Be based on the effective GIC flow information provided in Requirement R5; | MEDIUM | Retired | 2022-07-01 | 2020-10-01 | TP, PC
TPL-007-3 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R6.2. | Document assumptions used in the analysis; | MEDIUM | Retired | 2022-07-01 | 2020-10-01 | TP, PC
TPL-007-3 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R6.3. | Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and | MEDIUM | Retired | 2022-07-01 | 2020-10-01 | TP, PC
TPL-007-3 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R6.4. | . Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1. | MEDIUM | Retired | 2022-07-01 | 2020-10-01 | TP, PC
TPL-007-3 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R7. | Each responsible entity, as determined in Requirement R1, that concludes through the benchmark GMD Vulnerability Assessment conducted in Requirement R4 that their System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1, shall develop a Corrective TPL-007-3 – Transmission System Planned Performance for Geomagnetic Disturbance Events Page 5 of 44 Action Plan (CAP) addressing how the performance requirements will be met. The CAP shall: [Violation Risk Factor: High] [Time Horizon: Long-term Planning] | HIGH | Retired | 2024-01-01 | 2020-10-01 | TP, PC
TPL-007-3 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R7.1. | List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include: • Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment. • Installation, modification, or removal of Protection Systems or Remedial Action Schemes. • Use of Operating Procedures, specifying how long they will be needed as part of the CAP. • Use of Demand-Side Management, new technologies, or other initiatives. | HIGH | Retired | 2024-01-01 | 2020-10-01 | TP, PC
TPL-007-3 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R7.2. | . Be developed within one year of completion of the benchmark GMD Vulnerability Assessment. | HIGH | Retired | 2024-01-01 | 2020-10-01 | TP, PC
TPL-007-3 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R7.3. | . Include a timetable, subject to revision by the responsible entity in Part 7.4, for implementing the selected actions from Part 7.1. The timetable shall: | HIGH | Retired | 2024-01-01 | 2020-10-01 | TP, PC
TPL-007-3 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R7.3.1. | Specify implementation of non-hardware mitigation, if any, within two years of development of the CAP; and | HIGH | Retired | 2024-01-01 | 2020-10-01 | TP, PC
TPL-007-3 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R7.3.2. | Specify implementation of hardware mitigation, if any, within four years of development of the CAP. | HIGH | Retired | 2024-01-01 | 2020-10-01 | TP, PC
TPL-007-3 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R7.4. | Be revised if situations beyond the control of the responsible entity determined in Requirement R1 prevent implementation of the CAP within the timetable for implementation provided in Part 7.3. The revised CAP shall document the following, and be updated at least once every 12 calendar months until implemented: | HIGH | Retired | 2024-01-01 | 2020-10-01 | TP, PC
TPL-007-3 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R7.4.1. | Circumstances causing the delay for fully or partially implementing the selected actions in Part 7.1; | HIGH | Retired | 2024-01-01 | 2020-10-01 | TP, PC
TPL-007-3 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R7.4.2. | Description of the original CAP, and any previous changes to the CAP, with the associated timetable(s) for implementing the selected actions in Part 7.1; and | HIGH | Retired | 2024-01-01 | 2020-10-01 | TP, PC
TPL-007-3 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R7.4.3. | Revisions to the selected actions in Part 7.1, if any, including utilization of Operating Procedures if applicable, and the updated timetable for implementing the selected actions. | HIGH | Retired | 2024-01-01 | 2020-10-01 | TP, PC
TPL-007-3 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R7.5. | Be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later. | HIGH | Retired | 2024-01-01 | 2020-10-01 | TP, PC
TPL-007-3 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R7.5.1. | If a recipient of the CAP provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | HIGH | Retired | 2024-01-01 | 2020-10-01 | TP, PC
TPL-007-3 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R8. | Each responsible entity, as determined in Requirement R1, shall complete a supplemental GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon at least once every 60 calendar months. This supplemental GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. [Violation Risk Factor: High] [Time Horizon: Long-term Planning] | HIGH | Retired | 2023-01-01 | 2020-10-01 | TP, PC
TPL-007-3 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R8.1. | . The study or studies shall include the following conditions: | HIGH | Retired | 2023-01-01 | 2020-10-01 | TP, PC
TPL-007-3 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R8.1.1. | System On-Peak Load for at least one year within the Near-Term Transmission Planning Horizon; and | HIGH | Retired | 2023-01-01 | 2020-10-01 | TP, PC
TPL-007-3 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R8.1.2. | System Off-Peak Load for at least one year within the Near-Term Transmission Planning Horizon. | HIGH | Retired | 2023-01-01 | 2020-10-01 | TP, PC
TPL-007-3 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R8.2. | The study or studies shall be conducted based on the supplemental GMD event described in Attachment 1 to determine whether the System meets the performance requirements for the steady state planning supplemental GMD event contained in Table 1. | HIGH | Retired | 2023-01-01 | 2020-10-01 | TP, PC
TPL-007-3 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R8.3. | If the analysis concludes there is Cascading caused by the supplemental GMD event described in Attachment 1, an evaluation of possible actions designed to reduce the likelihood or mitigate the consequences and adverse impacts of the event(s) shall be conducted. | HIGH | Retired | 2023-01-01 | 2020-10-01 | TP, PC
TPL-007-3 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R8.4. | The supplemental GMD Vulnerability Assessment shall be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later. | HIGH | Retired | 2023-01-01 | 2020-10-01 | TP, PC
TPL-007-3 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R8.4.1. | If a recipient of the supplemental GMD Vulnerability Assessment provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | HIGH | Retired | 2023-01-01 | 2020-10-01 | TP, PC
TPL-007-3 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R9. | Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the supplemental thermal impact assessment of transformers specified in Requirement R10 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | MEDIUM | Retired | 2020-01-01 | 2020-10-01 | TP, PC
TPL-007-3 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R9.1. | The maximum effective GIC value for the worst case geoelectric field orientation for the supplemental GMD event described in Attachment 1. This value shall be provided to the Transmission Owner or Generator Owner that owns each applicable BES power transformer in the planning area. | MEDIUM | Retired | 2020-01-01 | 2020-10-01 | TP, PC
TPL-007-3 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R9.2. | The effective GIC time series, GIC(t), calculated using the supplemental GMD event described in Attachment 1 in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. GIC(t) shall be provided within 90 calendar days of receipt of the written request and after determination of the maximum effective GIC value in Part 9.1. | MEDIUM | Retired | 2020-01-01 | 2020-10-01 | TP, PC
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R1. | Each Planning Coordinator, in conjunction with its Transmission Planner(s), shall identify the individual and joint responsibilities of the Planning Coordinator and Transmission Planner(s) in the Planning Coordinator’s planning area for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data as specified in this standard. [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | LOWER | Effective | 2020-10-01 |  | TP, PC
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R10. | Each Transmission Owner and Generator Owner shall conduct a supplemental thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater. The supplemental thermal impact assessment shall: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | Medium | Effective | 2022-10-01 |  | TO, GO
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R10.1. | Be based on the effective GIC flow information provided in Requirement R9; | Medium | Effective | 2022-10-01 |  | TO, GO
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R10.2. | Document assumptions used in the analysis; | Medium | Effective | 2022-10-01 |  | TO, GO
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R10.3. | Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and | Medium | Effective | 2022-10-01 |  | TO, GO
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R10.4. | Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1. | Medium | Effective | 2022-10-01 |  | TO, GO
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R11. | Each responsible entity, as determined in Requirement R1, that concludes through the supplemental GMD Vulnerability Assessment conducted in Requirement R8 that their System does not meet the performance requirements for the steady state planning supplemental GMD event contained in Table 1, shall develop a Corrective Action Plan (CAP) addressing how the performance requirements will be met. The CAP shall: [Violation Risk Factor: High] [Time Horizon: Long-term Planning] | HIGH | Effective | 2021-10-01 |  | TP, PC
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R11.1. | List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include: • Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment. • Installation, modification, or removal of Protection Systems or Remedial Action Schemes. • Use of Operating Procedures, specifying how long they will be needed as part of the CAP. • Use of Demand-Side Management, new technologies, or other initiatives. | HIGH | Effective | 2021-10-01 |  | TP, PC
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R11.2. | Be developed within one year of completion of the supplemental GMD Vulnerability Assessment. | HIGH | Effective | 2021-10-01 |  | TP, PC
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R11.3. | .Include a timetable, subject to approval for any extension sought under Part 11.4, for implementing the selected actions from Part 11.1. The timetable shall: | HIGH | Effective | 2021-10-01 |  | PC, TP
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R11.3.1. | Specify implementation of non-hardware mitigation, if any, within two years of development of the CAP; and | HIGH | Effective | 2021-10-01 |  | TP, PC
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R11.3.2. | Specify implementation of hardware mitigation, if any, within four years of development of the CAP. | HIGH | Effective | 2021-10-01 |  | TP, PC
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R11.4. | Be submitted to the CEA with a request for extension of time if the responsible entity is unable to implement the CAP within the timetable provided in Part 11.3. The submitted CAP shall document the following: | HIGH | Effective | 2021-10-01 |  | TP, PC
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R11.4.1. | Circumstances causing the delay for fully or partially implementing the selected actions in Part 11.1 and how those circumstances are beyond the control of the responsible entity; | HIGH | Effective | 2021-10-01 |  | TP, PC
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R11.4.2. | Revisions to the selected actions in Part 11.1, if any, including utilization of Operating Procedures, if applicable; and | HIGH | Effective | 2021-10-01 |  | TP, PC
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R11.4.3. | Updated timetable for implementing the selected actions in Part 11.1. | HIGH | Effective | 2021-10-01 |  | TP, PC
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R11.5. | .Be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later. | HIGH | Effective | 2021-10-01 |  | TP, PC
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R11.5.1. | If a recipient of the CAP provides documented comments on the CAP, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | HIGH | Effective | 2021-10-01 |  | TP, PC
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R12. | . Each responsible entity, as determined in Requirement R1, shall implement a process to obtain GIC monitor data from at least one GIC monitor located in the Planning Coordinator’s planning area or other part of the system included in the Planning Coordinator’s GIC System model. [Violation Risk Factor: Lower] [Time Horizon: Longterm Planning] | LOWER | Effective | 2021-10-01 |  | TP, PC
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R13. | Each responsible entity, as determined in Requirement R1, shall implement a process to obtain geomagnetic field data for its Planning Coordinator’s planning area. [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] |  | Effective |  |  | TP, PC
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R2. | Each responsible entity, as determined in Requirement R1, shall maintain System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. [Violation Risk Factor: High] [Time Horizon: Longterm Planning] | High | Effective | 2020-10-01 |  | TP, PC
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R3. | Each responsible entity, as determined in Requirement R1, shall have criteria for acceptable System steady state voltage performance for its System during the GMD events described in Attachment 1. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | Medium | Effective | 2023-04-01 |  | TP, PC
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R4. | Each responsible entity, as determined in Requirement R1, shall complete a benchmark GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon at least once every 60 calendar months. This benchmark GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. [Violation Risk Factor: High] [Time Horizon: Long-term Planning] | High | Effective | 2023-04-01 |  | PC, TP
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R4.1. | The study or studies shall include the following conditions: | High | Effective | 2023-04-01 |  | TP, PC
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R4.1.1. | System On-Peak Load for at least one year within the Near-Term Transmission Planning Horizon; and | High | Effective | 2023-04-01 |  | TP, PC
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R4.1.2. | . System Off-Peak Load for at least one year within the Near-Term Transmission Planning Horizon. | High | Effective | 2023-04-01 |  | TP, PC
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R4.2. | The study or studies shall be conducted based on the benchmark GMD event described in Attachment 1 to determine whether the System meets the performance requirements for the steady state planning benchmark GMD event contained in Table 1. | High | Effective | 2023-04-01 |  | TP, PC
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R4.3. | The benchmark GMD Vulnerability Assessment shall be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later. | High | Effective | 2023-04-01 |  | TP, PC
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R4.3.1. | If a recipient of the benchmark GMD Vulnerability Assessment provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | High | Effective | 2023-04-01 |  | TP, PC
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R5. | Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the benchmark thermal impact assessment of transformers specified in Requirement R6 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | Medium | Effective | 2021-04-01 |  | TP, PC
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R5.1. | The maximum effective GIC value for the worst case geoelectric field orientation for the benchmark GMD event described in Attachment 1. This value shall be provided to the Transmission Owner or Generator Owner that owns each applicable BES power transformer in the planning area. | Medium | Effective | 2021-04-01 |  | TP, PC
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R5.2. | The effective GIC time series, GIC(t), calculated using the benchmark GMD event described in Attachment 1 in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. GIC(t) shall be provided within 90 calendar days of receipt of the written request and after determination of the maximum effective GIC value in Part 5.1. | Medium | Effective | 2021-04-01 |  | TP, PC
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R6. | Each Transmission Owner and Generator Owner shall conduct a benchmark thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater. The benchmark thermal impact assessment shall: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | Medium | Effective | 2022-10-01 |  | TO, GO
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R7. | Each responsible entity, as determined in Requirement R1, that concludes through Action Plan (CAP) addressing how the performance requirements will be met. The CAP shall: [Violation Risk Factor: High] [Time Horizon: Long-term Planning] the benchmark GMD Vulnerability Assessment conducted in Requirement R4 that their System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1, shall develop a Corrective | High | Effective | 2024-04-01 |  | TP, PC
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R7.1. | List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include: • Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment. • Installation, modification, or removal of Protection Systems or Remedial Action Schemes. • Use of Operating Procedures, specifying how long they will be needed as part of the CAP. • Use of Demand-Side Management, new technologies, or other initiatives. | High | Effective | 2024-04-01 |  | TP, PC
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R7.2. | Be developed within one year of completion of the benchmark GMD Vulnerability Assessment. | High | Effective | 2024-04-01 |  | TP, PC
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R7.3. | Include a timetable, subject to approval for any extension sought under Part 7.4, for implementing the selected actions from Part 7.1. The timetable shall: | High | Effective | 2024-04-01 |  | TP, PC
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R7.3.1. | Specify implementation of non-hardware mitigation, if any, within two years of development of the CAP; and | High | Effective | 2024-04-01 |  | TP, PC
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R7.3.2. | Specify implementation of hardware mitigation, if any, within four years of development of the CAP. | High | Effective | 2024-04-01 |  | TP, PC
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R7.4. | Be submitted to the Compliance Enforcement Authority (CEA) with a request for extension of time if the responsible entity is unable to implement the CAP within the timetable provided in Part 7.3. The submitted CAP shall document the following: | High | Effective | 2024-04-01 |  | TP, PC
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R7.4.1. | Circumstances causing the delay for fully or partially implementing the selected actions in Part 7.1 and how those circumstances are beyond the control of the responsible entity; | High | Effective | 2024-04-01 |  | TP, PC
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R7.4.2. | Revisions to the selected actions in Part 7.1, if any, including utilization of Operating Procedures, if applicable; and | High | Effective | 2024-04-01 |  | TP, PC
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R7.4.3. | Updated timetable for implementing the selected actions in Part 7.1. | High | Effective | 2024-04-01 |  | TP, PC
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R7.5. | Be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later. | High | Effective | 2024-04-01 |  | TP, PC
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R7.5.1. | If a recipient of the CAP provides documented comments on the CAP, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments | High | Effective | 2024-04-01 |  | TP, PC
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R8. | Each responsible entity, as determined in Requirement R1, shall complete a supplemental GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon at least once every 60 calendar months. This supplemental GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. [Violation Risk Factor: High] [Time Horizon: Long-term Planning] | HIGH | Effective | 2023-04-01 |  | TP, PC
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R8.1. | System On-Peak Load for at least one year within the Near-Term Transmission Planning Horizon; and | HIGH | Effective | 2023-04-01 |  | TP, PC
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R8.1.2. | System Off-Peak Load for at least one year within the Near-Term Transmission Planning Horizon. | HIGH | Effective | 2023-04-01 |  | TP, PC
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R8.2. | The study or studies shall be conducted based on the supplemental GMD event described in Attachment 1 to determine whether the System meets the performance requirements for the steady state planning supplemental GMD event contained in Table 1. | HIGH | Effective | 2023-04-01 |  | TP, PC
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R8.3. | The supplemental GMD Vulnerability Assessment shall be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later. | HIGH | Effective | 2023-04-01 |  | TP, PC
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R8.3.1. | If a recipient of the supplemental GMD Vulnerability Assessment provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | HIGH | Effective | 2023-04-01 |  | TP, PC
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R9. | Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the supplemental thermal impact assessment of transformers specified in Requirement R10 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | Medium | Effective | 2021-04-01 |  | TP, PC
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R9.1. | The maximum effective GIC value for the worst case geoelectric field orientation for the supplemental GMD event described in Attachment 1. This value shall be provided to the Transmission Owner or Generator Owner that owns each applicable BES power transformer in the planning area. | Medium | Effective | 2021-04-01 |  | TP, PC
TPL-007-4 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R9.2. | The effective GIC time series, GIC(t), calculated using the supplemental GMD event described in Attachment 1 in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. GIC(t) shall be provided within 90 calendar days of receipt of the written request and after determination of the maximum effective GIC value in Part 9.1. | Medium | Effective | 2021-04-01 |  | TP, PC
VAR-001-4 | Voltage and Reactive Control | R1. | Each Transmission Operator shall specify a system voltage schedule (which is either a range or a target value with an associated tolerance band) as part of its plan to operate within System Operating Limits and Interconnection Reliability Operating Limits. | HIGH | Retired |  |  | TOP
VAR-001-4 | Voltage and Reactive Control | R1.1. | Each Transmission Operator shall provide a copy of the voltage schedules (which is either a range or a target value with an associated tolerance band) to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. | HIGH | Retired |  |  | TOP
VAR-001-4 | Voltage and Reactive Control | R2. | Each Transmission Operator shall schedule sufficient reactive resources to regulate voltage levels under normal and Contingency conditions. Transmission Operators can provide sufficient reactive resources through various means including, but not limited to, reactive generation scheduling, transmission line and reactive resource switching, and using controllable load. | HIGH | Retired |  |  | TOP
VAR-001-4 | Voltage and Reactive Control | R3. | Each Transmission Operator shall operate or direct the Real-time operation of devices to regulate transmission voltage and reactive flow as necessary. | HIGH | Retired |  |  | TOP
VAR-001-4 | Voltage and Reactive Control | R4. | The Transmission Operator shall specify the criteria that will exempt generators from: 1) following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any associated notifications. | LOWER | Retired |  |  | TOP
VAR-001-4 | Voltage and Reactive Control | R4.1. | If a Transmission Operator determines that a generator has satisfied the exemption criteria, it shall notify the associated Generator Operator. | LOWER | Retired |  |  | TOP
VAR-001-4 | Voltage and Reactive Control | R5. | Each Transmission Operator shall specify a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) at either the high voltage side or low voltage side of the generator step-up transformer at the Transmission Operator’s discretion. | MEDIUM | Retired |  |  | TOP
VAR-001-4 | Voltage and Reactive Control | R5.1. | The Transmission Operator shall provide the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (the AVR is in service and controlling voltage). | MEDIUM | Retired |  |  | TOP
VAR-001-4 | Voltage and Reactive Control | R5.2. | The Transmission Operator shall provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). | MEDIUM | Retired |  |  | TOP
VAR-001-4 | Voltage and Reactive Control | R5.3. | The Transmission Operator shall provide the criteria used to develop voltage schedules Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the Generator Operator within 30 days of receiving a request. | MEDIUM | Retired |  |  | TOP
VAR-001-4 | Voltage and Reactive Control | R6. | After consultation with the Generator Owner regarding necessary step-up transformer tap changes and the implementation schedule, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. | LOWER | Retired |  |  | TOP
VAR-001-4.1 | Voltage and Reactive Control | R1. | Each Transmission Operator shall specify a system voltage schedule (which is either a range or a target value with an associated tolerance band) as part of its plan to operate within System Operating Limits and Interconnection Reliability Operating Limits. | HIGH | Retired |  |  | TOP
VAR-001-4.1 | Voltage and Reactive Control | R1.1. | Each Transmission Operator shall provide a copy of the voltage schedules (which is either a range or a target value with an associated tolerance band) to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. | HIGH | Retired |  |  | TOP
VAR-001-4.1 | Voltage and Reactive Control | R2. | Each Transmission Operator shall schedule sufficient reactive resources to regulate voltage levels under normal and Contingency conditions. Transmission Operators can provide sufficient reactive resources through various means including, but not limited to, reactive generation scheduling, transmission line and reactive resource switching, and using controllable load. | HIGH | Retired |  |  | TOP
VAR-001-4.1 | Voltage and Reactive Control | R3. | Each Transmission Operator shall operate or direct the Real-time operation of devices to regulate transmission voltage and reactive flow as necessary. | HIGH | Retired |  |  | TOP
VAR-001-4.1 | Voltage and Reactive Control | R4. | The Transmission Operator shall specify the criteria that will exempt generators from: 1) following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any associated notifications. | LOWER | Retired |  |  | TOP
VAR-001-4.1 | Voltage and Reactive Control | R4.1. | If a Transmission Operator determines that a generator has satisfied the exemption criteria, it shall notify the associated Generator Operator. | LOWER | Retired |  |  | TOP
VAR-001-4.1 | Voltage and Reactive Control | R5. | Each Transmission Operator shall specify a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) at either the high voltage side or low voltage side of the generator step-up transformer at the Transmission Operator’s discretion. | MEDIUM | Retired |  |  | TOP
VAR-001-4.1 | Voltage and Reactive Control | R5.1. | The Transmission Operator shall provide the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (the AVR is in service and controlling voltage). | MEDIUM | Retired |  |  | TOP
VAR-001-4.1 | Voltage and Reactive Control | R5.2. | The Transmission Operator shall provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). | MEDIUM | Retired |  |  | TOP
VAR-001-4.1 | Voltage and Reactive Control | R5.3. | The Transmission Operator shall provide the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the Generator Operator within 30 days of receiving a request. | MEDIUM | Retired |  |  | TOP
VAR-001-4.1 | Voltage and Reactive Control | R6. | After consultation with the Generator Owner regarding necessary step-up transformer tap changes and the implementation schedule, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. | LOWER | Retired |  |  | TOP
VAR-001-4.2 | Voltage and Reactive Control | R1. | Each Transmission Operator shall specify a system voltage schedule (which is either a range or a target value with an associated tolerance band) as part of its plan to operate within System Operating Limits and Interconnection Reliability Operating Limits. | HIGH | Retired |  | 2019-03-31 | TOP
VAR-001-4.2 | Voltage and Reactive Control | R1.1. | Each Transmission Operator shall provide a copy of the voltage schedules (which is either a range or a target value with an associated tolerance band) to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. | HIGH | Retired |  | 2019-03-31 | TOP
VAR-001-4.2 | Voltage and Reactive Control | R2. | Each Transmission Operator shall schedule sufficient reactive resources to regulate voltage levels under normal and Contingency conditions. Transmission Operators can provide sufficient reactive resources through various means including, but not limited to, reactive generation scheduling, transmission line and reactive resource switching, and using controllable load. | HIGH | Retired |  | 2019-03-31 | TOP
VAR-001-4.2 | Voltage and Reactive Control | R3. | Each Transmission Operator shall operate or direct the Real-time operation of devices to regulate transmission voltage and reactive flow as necessary. | HIGH | Retired |  | 2019-03-31 | TOP
VAR-001-4.2 | Voltage and Reactive Control | R4. | Each Transmission Operator shall specify the criteria that will exempt generators: 1) from following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any associated notifications. | HIGH | Retired |  | 2019-03-31 | TOP
VAR-001-4.2 | Voltage and Reactive Control | R4.1. | If a Transmission Operator determines that a generator has satisfied the exemption criteria, it shall notify the associated Generator Operator. | HIGH | Retired |  | 2019-03-31 | TOP
VAR-001-4.2 | Voltage and Reactive Control | R5. | Each Transmission Operator shall specify a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) at either the high voltage side or low voltage side of the generator step-up transformer at the Transmission Operator’s discretion. | HIGH | Retired |  | 2019-03-31 | TOP
VAR-001-4.2 | Voltage and Reactive Control | R5.1. | The Transmission Operator shall provide the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (the AVR is in service and controlling voltage). | HIGH | Retired |  | 2019-03-31 | TOP
VAR-001-4.2 | Voltage and Reactive Control | R5.2. | The Transmission Operator shall provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). | MEDIUM | Retired |  | 2019-03-31 | TOP
VAR-001-4.2 | Voltage and Reactive Control | R5.3. | The Transmission Operator shall provide the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the Generator Operator within 30 days of receiving a request. | MEDIUM | Retired |  | 2019-03-31 | TOP
VAR-001-4.2 | Voltage and Reactive Control | R6. | After consultation with the Generator Owner regarding necessary step-up transformer tap changes and the implementation schedule, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. | HIGH | Retired |  | 2019-03-31 | TOP
VAR-001-5 | Voltage and Reactive Control | R1. | Each Transmission Operator shall specify a system voltage schedule (which is either a range or a target value with an associated tolerance band) as part of its plan to operate within System Operating Limits and Interconnection Reliability Operating Limits. [Violation Risk Factor: High] [Time Horizon: Operations Planning] | HIGH | Effective | 2019-04-01 |  | TOP
VAR-001-5 | Voltage and Reactive Control | R1. | Each Transmission Operator shall specify a system voltage schedule (which is either a range or a target value with an associated tolerance band) as part of its plan to operate within System Operating Limits and Interconnection Reliability Operating Limits. [Violation Risk Factor: High] [Time Horizon: Operations Planning] | HIGH | Effective | 2019-04-01
VAR-001-5 | Voltage and Reactive Control | R1.1. | Each Transmission Operator shall provide a copy of the voltage schedules (which is either a range or a target value with an associated tolerance band) to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. | HIGH | Effective | 2019-04-01 |  | TOP
VAR-001-5 | Voltage and Reactive Control | R1.1. | Each Transmission Operator shall provide a copy of the voltage schedules (which is either a range or a target value with an associated tolerance band) to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. | HIGH | Effective | 2019-04-01
VAR-001-5 | Voltage and Reactive Control | R2. | Each Transmission Operator shall schedule sufficient reactive resources to regulate voltage levels under normal and Contingency conditions. Transmission Operators can provide sufficient reactive resources through various means including, but not limited to, reactive generation scheduling, transmission line and reactive resource switching, and using controllable load. [Violation Risk Factor: High] [Time Horizon: Real-time Operations, Same-day Operations, and Operations Planning] | HIGH | Effective | 2019-04-01 |  | TOP
VAR-001-5 | Voltage and Reactive Control | R2. | Each Transmission Operator shall schedule sufficient reactive resources to regulate voltage levels under normal and Contingency conditions. Transmission Operators can provide sufficient reactive resources through various means including, but not limited to, reactive generation scheduling, transmission line and reactive resource switching, and using controllable load. [Violation Risk Factor: High] [Time Horizon: Real-time Operations, Same-day Operations, and Operations Planning] | HIGH | Effective | 2019-04-01
VAR-001-5 | Voltage and Reactive Control | R3. | Each Transmission Operator shall operate or direct the Real-time operation of devices to regulate transmission voltage and reactive flow as necessary. [Violation Risk Factor: High] [Time Horizon: Real-time Operations, Same-day Operations, and Operations Planning] | HIGH | Effective | 2019-04-01 |  | TOP
VAR-001-5 | Voltage and Reactive Control | R4. | Each Transmission Operator shall specify the criteria that will exempt generators: 1) from following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any associated notifications. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | HIGH | Effective | 2019-04-01 |  | TOP
VAR-001-5 | Voltage and Reactive Control | R4. | Each Transmission Operator shall specify the criteria that will exempt generators: 1) from following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any associated notifications. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | HIGH | Effective | 2019-04-01
VAR-001-5 | Voltage and Reactive Control | R4.1. | If a Transmission Operator determines that a generator has satisfied the exemption criteria, it shall notify the associated Generator Operator. | HIGH | Effective | 2019-04-01 |  | GOP, TOP
VAR-001-5 | Voltage and Reactive Control | R4.1. | If a Transmission Operator determines that a generator has satisfied the exemption criteria, it shall notify the associated Generator Operator. | HIGH | Effective | 2019-04-01
VAR-001-5 | Voltage and Reactive Control | R5. | Each Transmission Operator shall specify a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) at either the high voltage side or low voltage side of the generator step-up transformer at the Transmission Operator’s discretion. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | HIGH | Effective | 2019-04-01 |  | TOP
VAR-001-5 | Voltage and Reactive Control | R5.1. | The Transmission Operator shall provide the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (the AVR is in service and controlling voltage). | HIGH | Effective | 2019-04-01 |  | GOP, TOP
VAR-001-5 | Voltage and Reactive Control | R5.2. | The Transmission Operator shall provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). | HIGH | Effective | 2019-04-01 |  | TOP, GOP
VAR-001-5 | Voltage and Reactive Control | R5.2. | The Transmission Operator shall provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). | HIGH | Effective | 2019-04-01
VAR-001-5 | Voltage and Reactive Control | R5.3. | The Transmission Operator shall provide the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the Generator Operator within 30 days of receiving a request. | HIGH | Effective | 2019-04-01 |  | TOP, GOP
VAR-001-5 | Voltage and Reactive Control | R6. | After consultation with the Generator Owner regarding necessary step-up transformer tap changes and the implementation schedule, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | HIGH | Effective | 2019-04-01 |  | GO, TOP
VAR-002-3 | Generator Operation for Maintaining Network Voltage Schedules | R1. | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (with its automatic voltage regulator (AVR) in service and controlling voltage) or in a different control mode as instructed by the Transmission Operator unless: 1) the generator is exempted by the Transmission Operator, or 2) the Generator Operator has notified the Transmission Operator of one of the following: [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations]  That the generator is being operated in start-up,1 shutdown,2 or testing mode pursuant to a Realtime communication or a procedure that was previously provided to the Transmission Operator; or  That the generator is not being operated in automatic voltage control mode or in the control mode that was instructed by the Transmission Operator for a reason other than start-up, shutdown, or testing. | MEDIUM | Retired | 2015-01-01 | 2015-06-13 | GOP
VAR-002-3 | Generator Operation for Maintaining Network Voltage Schedules | R2. | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power schedule3 (within each generating Facility’s capabilities4) provided by the Transmission Operator, or otherwise shall meet the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator. [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | MEDIUM | Retired | 2015-01-01 | 2015-06-13 | GOP
VAR-002-3 | Generator Operation for Maintaining Network Voltage Schedules | R2.1. | When a generator’s AVR is out of service or the generator does not have an AVR, the Generator Operator shall use an alternative method to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. | MEDIUM | Retired | 2015-01-01 | 2015-06-13 | GOP
VAR-002-3 | Generator Operation for Maintaining Network Voltage Schedules | R2.2. | When instructed to modify voltage, the Generator Operator shall comply or provide an explanation of why the schedule cannot be met. | MEDIUM | Retired | 2015-01-01 | 2015-06-13 | GOP
VAR-002-3 | Generator Operation for Maintaining Network Voltage Schedules | R2.3. | Generator Operators that do not monitor the voltage at the location specified in their voltage schedule shall have a methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator. | MEDIUM | Retired | 2015-01-01 | 2015-06-13 | GOP
VAR-002-3 | Generator Operation for Maintaining Network Voltage Schedules | R3. | Each Generator Operator shall notify its associated Transmission Operator of a status change on the AVR, power system stabilizer, or alternative voltage controlling device within 30 minutes of the change. If the status has been restored within 30 minutes of such change, then the Generator Operator is not required to notify the Transmission Operator of the status change [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | MEDIUM | Retired | 2015-01-01 | 2015-06-13 | GOP
VAR-002-3 | Generator Operation for Maintaining Network Voltage Schedules | R4. | Each Generator Operator shall notify its associated Transmission Operator within 30 minutes of becoming aware of a change in reactive capability due to factors other than a status change described in Requirement R3. If the capability has been restored within 30 minutes of the Generator Operator becoming aware of such change, then the Generator Operator is not required to notify the Transmission Operator of the change in reactive capability. [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | MEDIUM | Retired | 2015-01-01 | 2015-06-13 | GOP
VAR-002-3 | Generator Operation for Maintaining Network Voltage Schedules | R5. | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. [Violation Risk Factor: Lower] [Time Horizon: Real-time Operations] | LOWER | Retired | 2015-01-01 | 2015-06-13 | GO
VAR-002-3 | Generator Operation for Maintaining Network Voltage Schedules | R5.1. | For generator step-up transformers and auxiliary transformers with primary voltages equal to or greater than the generator terminal voltage: | LOWER | Retired | 2015-01-01 | 2015-06-13 | GO
VAR-002-3 | Generator Operation for Maintaining Network Voltage Schedules | R5.1.1. | Tap settings. | LOWER | Retired | 2015-01-01 | 2015-06-13 | GO
VAR-002-3 | Generator Operation for Maintaining Network Voltage Schedules | R5.1.2. | Available fixed tap ranges. | LOWER | Retired | 2015-01-01 | 2015-06-13 | GO
VAR-002-3 | Generator Operation for Maintaining Network Voltage Schedules | R5.1.3. | Impedance data. | LOWER | Retired | 2015-01-01 | 2015-06-13 | GO
VAR-002-3 | Generator Operation for Maintaining Network Voltage Schedules | R6. | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. [Violation Risk Factor: Lower] [Time Horizon: Real-time Operations] | LOWER | Retired | 2015-01-01 | 2015-06-13 | GO
VAR-002-3 | Generator Operation for Maintaining Network Voltage Schedules | R6.1. | If the Generator Owner cannot comply with the Transmission Operator’s specifications, the Generator Owner shall notify the Transmission Operator and shall provide the technical justification. | LOWER | Retired | 2015-01-01 | 2015-06-13 | GO
VAR-002-4 | Generator Operation for Maintaining Network Voltage Schedules | R1. | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (with its automatic voltage regulator (AVR) in service and controlling voltage) or in a different control mode as instructed by the Transmission Operator unless: 1) the generator is exempted by the Transmission Operator, or 2) the Generator Operator has notified the Transmission Operator of one of the following: [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations]  That the generator is being operated in start-up,1 shutdown,2 or testing mode pursuant to a Real-time communication or a procedure that was previously provided to the Transmission Operator; or  That the generator is not being operated in automatic voltage control mode or in the control mode that was instructed by the Transmission Operator for a reason other than start-up, shutdown, or testing. | MEDIUM | Retired |  |  | GOP
VAR-002-4 | Generator Operation for Maintaining Network Voltage Schedules | R2. | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power schedule3 (within each generating Facility’s capabilities4) provided by the Transmission Operator, or otherwise shall meet the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator. [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | MEDIUM | Retired |  |  | GOP
VAR-002-4 | Generator Operation for Maintaining Network Voltage Schedules | R2.1. | When a generator’s AVR is out of service or the generator does not have an AVR, the Generator Operator shall use an alternative method to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. | MEDIUM | Retired |  |  | GOP
VAR-002-4 | Generator Operation for Maintaining Network Voltage Schedules | R2.2. | When instructed to modify voltage, the Generator Operator shall comply or provide an explanation of why the schedule cannot be met. | MEDIUM | Retired |  |  | GOP
VAR-002-4 | Generator Operation for Maintaining Network Voltage Schedules | R2.3. | Generator Operators that do not monitor the voltage at the location specified in their voltage schedule shall have a methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator. | MEDIUM | Retired |  |  | GOP
VAR-002-4 | Generator Operation for Maintaining Network Voltage Schedules | R3. | Each Generator Operator shall notify its associated Transmission Operator of a status change on the AVR, power system stabilizer, or alternative voltage controlling device within 30 minutes of the change. If the status has been restored within 30 minutes of such change, then the Generator Operator is not required to notify the Transmission Operator of the status change [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | MEDIUM | Retired |  |  | GOP
VAR-002-4 | Generator Operation for Maintaining Network Voltage Schedules | R4. | Each Generator Operator shall notify its associated Transmission Operator within 30 minutes of becoming aware of a change in reactive capability due to factors other than a status change described in Requirement R3. If the capability has been restored within 30 minutes of the Generator Operator becoming aware of such change, then the Generator Operator is not required to notify the Transmission Operator of the change in reactive capability. [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations]  Reporting of status or capability changes as stated in Requirement R4 is not applicable to the individual generating units of dispersed power producing resources identified through Inclusion I4 of the Bulk Electric System definition. | MEDIUM | Retired |  |  | GOP
VAR-002-4 | Generator Operation for Maintaining Network Voltage Schedules | R5. | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. [Violation Risk Factor: Lower] [Time Horizon: Real-time Operations] | LOWER | Retired |  |  | GO
VAR-002-4 | Generator Operation for Maintaining Network Voltage Schedules | R5.1. | For generator step-up and auxiliary transformers5 with primary voltages equal to or greater than the generator terminal voltage: | LOWER | Retired |  |  | GO
VAR-002-4 | Generator Operation for Maintaining Network Voltage Schedules | R5.1.1. | Tap settings. | LOWER | Retired |  |  | GO
VAR-002-4 | Generator Operation for Maintaining Network Voltage Schedules | R5.1.2. | Available fixed tap ranges. | LOWER | Retired |  |  | GO
VAR-002-4 | Generator Operation for Maintaining Network Voltage Schedules | R5.1.3. | Impedance data. | LOWER | Retired |  |  | GO
VAR-002-4 | Generator Operation for Maintaining Network Voltage Schedules | R6. | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. [Violation Risk Factor: Lower] [Time Horizon: Real-time Operations] | LOWER | Retired |  |  | GO
VAR-002-4 | Generator Operation for Maintaining Network Voltage Schedules | R6.1. | If the Generator Owner cannot comply with the Transmission Operator’s specifications, the Generator Owner shall notify the Transmission Operator and shall provide the technical justification. | LOWER | Retired |  |  | GO
VAR-002-4.1 | Generator Operation for Maintaining Network Voltage Schedules | R1. | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (with its automatic voltage regulator (AVR) in service and controlling voltage) or in a different control mode as instructed by the Transmission Operator unless: 1) the generator is exempted by the Transmission Operator, or 2) the Generator Operator has notified the Transmission Operator of one of the following: [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] • That the generator is being operated in start-up,1 shutdown,2 or testing mode pursuant to a Real-time communication or a procedure that was previously provided to the Transmission Operator; or • That the generator is not being operated in automatic voltage control mode or in the control mode that was instructed by the Transmission Operator for a reason other than start-up, shutdown, or testing. | MEDIUM | Effective |  |  | GO
VAR-002-4.1 | Generator Operation for Maintaining Network Voltage Schedules | R2. | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power schedule3 (within each generating Facility’s capabilities4) provided by the Transmission Operator, or otherwise shall meet the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator. [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | MEDIUM | Effective |  |  | GO
VAR-002-4.1 | Generator Operation for Maintaining Network Voltage Schedules | R2.1. | When a generator’s AVR is out of service or the generator does not have an AVR, the Generator Operator shall use an alternative method to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. | MEDIUM | Effective |  |  | GO
VAR-002-4.1 | Generator Operation for Maintaining Network Voltage Schedules | R2.2. | When instructed to modify voltage, the Generator Operator shall comply or provide an explanation of why the schedule cannot be met. | MEDIUM | Effective |  |  | GO
VAR-002-4.1 | Generator Operation for Maintaining Network Voltage Schedules | R2.3. | Generator Operators that do not monitor the voltage at the location specified in their voltage schedule shall have a methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator. | MEDIUM | Effective |  |  | GO
VAR-002-4.1 | Generator Operation for Maintaining Network Voltage Schedules | R3. | Each Generator Operator shall notify its associated Transmission Operator of a status change on the AVR, power system stabilizer, or alternative voltage controlling device within 30 minutes of the change. If the status has been restored within 30 minutes of such change, then the Generator Operator is not required to notify the Transmission Operator of the status change. [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | MEDIUM | Effective |  |  | GO
VAR-002-4.1 | Generator Operation for Maintaining Network Voltage Schedules | R4. | Each Generator Operator shall notify its associated Transmission Operator within 30 minutes of becoming aware of a change in reactive capability due to factors other than a status change described in Requirement R3. If the capability has been restored within 30 minutes of the Generator Operator becoming aware of such change, then the Generator Operator is not required to notify the Transmission Operator of the change in reactive capability. [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] • Reporting of status or capability changes as stated in Requirement R4 is not applicable to the individual generating units of dispersed power producing resources identified through Inclusion I4 of the Bulk Electric System definition. | MEDIUM | Effective |  |  | GO
VAR-002-4.1 | Generator Operation for Maintaining Network Voltage Schedules | R5. | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. [Violation Risk Factor: Lower] [Time Horizon: Real-time Operations] | LOWER | Effective |  |  | GO
VAR-002-4.1 | Generator Operation for Maintaining Network Voltage Schedules | R5.1. | For generator step-up and auxiliary transformers5 with primary voltages equal to or greater than the generator terminal voltage: | LOWER | Effective |  |  | GO
VAR-002-4.1 | Generator Operation for Maintaining Network Voltage Schedules | R5.1.1. | Tap settings. | LOWER | Effective |  |  | GO
VAR-002-4.1 | Generator Operation for Maintaining Network Voltage Schedules | R5.1.2. | Available fixed tap ranges. | LOWER | Effective |  |  | GO
VAR-002-4.1 | Generator Operation for Maintaining Network Voltage Schedules | R5.1.3. | Impedance data. | LOWER | Effective |  |  | GO
VAR-002-4.1 | Generator Operation for Maintaining Network Voltage Schedules | R6. | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. [Violation Risk Factor: Lower] [Time Horizon: Real-time Operations] | LOWER | Effective |  |  | GO
VAR-002-4.1 | Generator Operation for Maintaining Network Voltage Schedules | R6.1. | If the Generator Owner cannot comply with the Transmission Operator’s specifications, the Generator Owner shall notify the Transmission Operator and shall provide the technical justification. | LOWER | Effective |  |  | GO

## NPCC Documents List
ID | NPCC Document | Document Title | NPCC Adoption Date | OEB Start Date | OEB End Date | Review Status in Ontario | USA Approval Status | Mandatory Enforcement Date in Ontario | Inactive Date in Ontario | Status in Ontario | External Link | Functional Entities
46 | Directory # 1 V1 | Design and Operation of the Bulk Power System | 2012-04-20 | 2013-12-03 | 2014-04-02 | Not Initiated | Approved | 2014-04-03 | 2016-10-12 | Retired | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/directory-01-design-and-operation-of-the-bulk-power-system.pdf | RC, TOP, BA, PC, TP, RP, GO, TO
47 | Directory # 1 V2 | Design and Operation of the Bulk Power System | 2015-09-30 | 2016-06-15 | 2016-10-13 | Not Initiated | Approved | 2016-10-13 | 2020-03-04 | Retired | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/directory-01-design-and-operation-of-the-bulk-power-system.pdf | RC, TOP, BA, PC, TP, RP, GO, TO
51 | Directory # 2 V3 | Emergency Operations | 2011-06-01 | 2013-12-03 | 2014-04-02 | Not Initiated | Approved | 2014-04-02 | 2014-12-08 | Retired | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/directory-2-emergency-operations-20180703.pdf | RC, BA, TOP
52 | Directory # 2 V5 | Emergency Operations | 2015-03-30 | 2016-06-15 | 2016-10-13 | Not Initiated | Approved | 2016-10-13 | 2018-06-28 | Retired | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/directory-2-emergency-operations-20180703.pdfC:\Users\lagans\AppData\Local\Microsoft\Windows\INetCache\Content.Outlook\IDWC0DRY\Updated NPCC Links.xlsxSheet1!D3 | RC, BA, TOP
55 | Directory # 4 | Bulk Power System Protection Criteria | 2009-12-01 | 2010-03-15 | 2010-07-13 | Not Initiated | Approved | 2010-07-13 | 2015-03-30 | Retired | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/directory-4-tfsp-rev-20200130.pdf | DP, GO, TO
56 | Directory # 4 V2 | Bulk Power System Protection Criteria | 2015-09-30 | 2016-06-15 | 2016-10-13 | Not Initiated | Approved | 2016-10-13 | 2020-05-28 | Retired | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/directory-4-tfsp-rev-20200130.pdf | DP, GO, TO
58 | Directory # 5 V2 | Reserve | 2012-10-11 | 2013-12-03 | 2014-04-02 | Not Initiated | Approved | 2014-04-02 | 2019-09-26 | Retired | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/directory-5-reserve-20200426.pdf | RC, BA, GOP, DP
59 | Directory # 5 V3 | Reserve | 2019-09-27 |  |  | Not Initiated | Approved | 2019-09-27 | 2020-01-15 | Pending Regulatory Filing | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/directory-5-reserve-20200426.pdf | RC, BA, GOP, DP
60 | Directory # 6 | Reserve Sharing Groups | 2012-04-06 | 2012-04-10 | 2012-08-08 | Not Initiated | Approved | 2012-08-08 | 2016-10-12 | Retired | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/directory-6-reserve-sharing-groups-20190930.pdf | BA, RSG
61 | Directory # 6 V1 | Reserve Sharing Groups | 2015-03-30 | 2016-06-15 | 2016-10-13 | Not Initiated | Approved | 2016-10-13 | 2019-09-26 | Retired | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/directory-6-reserve-sharing-groups-20190930.pdf | RSG, BA
63 | Directory # 7 | Remedial Action Schemes | 2007-12-27 |  |  | Not Initiated | Approved | 2007-12-27 | 2007-09-12 | Pending Regulatory Filing | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/directory-7-ras-review-form-20231004-clean.pdf | RC, PC, TO, GO, DP
64 | Directory # 7 V1 | Remedial Action Schemes | 2007-09-13 |  |  | Not Initiated | Approved | 2007-09-13 | 2020-12-21 | Pending Regulatory Filing | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/directory-7-ras-review-form-20231004-clean.pdf | DP, GO, RC, PC, TO
66 | Directory # 8 | System Restoration | 2008-10-22 |  |  | Not Initiated | Approved | 2008-10-22 | 2014-04-01 | Pending Regulatory Filing | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/directory-08.pdf | RC, TOP, BA, TO, GO, GOP, PC
67 | Directory # 8 V3 | System Restoration | 2018-02-16 |  |  | Not Initiated | Approved | 2018-02-16 | 2019-01-22 | Pending Regulatory Filing | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/directory-08.pdf | RC, TOP, BA, TO, GO, GOP, PC
70 | Directory # 9 V | Verification of Generator Gross and Net Real Power Capability | 2008-12-22 |  |  | Not Initiated | Approved | 2008-12-22 | 2009-07-06 | Pending Regulatory Filing | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/retired-directories/directory-09-verification-of-real-power-capability | GO, TOP
71 | Directory # 9 V3 | Verification of Generator Gross and Net Real Power Capability | 2015-03-31 | 2016-06-15 | 2016-10-13 | Not Initiated | Approved | 2016-10-13 | 2019-07-01 | Retired | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/retired-directories/directory-09-verification-of-real-power-capability | GO, TOP
74 | Directory # 10 V1 | Verification of Generator Gross and Net Reactive Power Capability | 2009-07-07 |  |  | Not Initiated | Approved | 2009-07-07 | 2012-10-25 | Pending Regulatory Filing | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/retired-directories/directory-10-verification-of-reactive-power-capability | GO, TOP
75 | Directory # 10 V3 | Verification of Generator Gross and Net Reactive Power Capability | 2015-03-31 | 2016-06-15 | 2016-10-13 | Not Initiated | Approved | 2016-10-13 | 2019-07-01 | Retired | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/retired-directories/directory-10-verification-of-reactive-power-capability | GO, TOP
76 | Directory # 11 | Disturbance Monitoring Equipment Criteria | 2016-10-24 | 2016-07-28 | 2016-11-25 | Not Initiated | Approved | 2016-11-25 | 2020-11-07 | Retired | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/d11-20220214.pdf | TO, GO
79 | Directory # 12 V2 | Under frequency Load Shedding Program Requirements | 2011-01-06 |  |  | Not Initiated | Approved | 2011-01-06 | 2013-11-25 | Pending Regulatory Filing | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/retired-directories/d12-retired-20211024.pdf | BA, GO, TOP
80 | Directory # 12 V3 | Under frequency Load Shedding Program Requirements | 2013-07-09 | 2013-07-29 | 2013-11-26 | Not Initiated | Approved | 2013-11-26 | 2016-10-12 | Retired | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/retired-directories/d12-retired-20211024.pdf | BA, GO, TOP
81 | Directory # 12 V4 | Under frequency Load Shedding Program Requirements | 2015-03-30 | 2016-06-15 | 2016-10-13 | Not Initiated | Approved | 2016-10-13 |  | Effective | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/retired-directories/d12-retired-20211024.pdf | BA, GO, TOP
84 | Criterion A-01 V1 | Criteria for Review and Approval of Documents | 2005-03-01 |  |  | Not Initiated | Approved | 2005-03-01 | 2017-04-20 | Pending Regulatory Filing | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/development/regional-criteria/criteria-for-review-and-approval-of-documents/a-01-retirement-ballot-20180910 | BA, RC, PC, TO, TOP
86 | Criterion A-10 V1 | Classification of Bulk Power System Elements | 2009-12-01 | 2009-12-01 | 2010-03-31 | Not Initiated | Approved | 2010-03-31 | 2020-03-26 | Retired | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/criteria/a-10-20200508.pdf | BA, DP, GO, PC, RC, RP, TO, TOP, TP
87 | Criterion A-15 | Disturbance Monitoring Equipment Criteria | 2007-08-23 | 2007-08-23 | 2007-12-21 | Not Initiated | Approved | 2007-12-21 | 2016-10-23 | Retired
93 | Directory # 2 V6 | Emergency Operations | 2018-06-29 |  |  | Not Initiated | Approved | 2018-06-29 |  | Pending Regulatory Filing | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/directory-2-emergency-operations-20180703.pdf | RC, BA, TOP
94 | Directory # 5 V4 | Reserve | 2020-01-16 |  |  | Not Initiated | Approved | 2020-01-16 | 2020-04-25 | Pending Regulatory Filing | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/directory-5-reserve-20200426.pdf | RC, BA, GOP, DP
96 | Directory # 6 V2 | Reserve Sharing Groups | 2019-09-27 |  |  | Not Initiated | Approved | 2019-09-27 |  | Effective | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/directory-6-reserve-sharing-groups-20190930.pdf | BA, RSG
97 | Directory # 8 V4 | System Restoration | 2018-09-25 | 2018-09-25 | 2019-01-23 | Not Initiated | Approved | 2019-01-23 | 2023-07-17 | Retired | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/directory-08.pdf | RC, TOP, BA, TO, GO, GOP, PC
99 | Directory # 1 V3 | Design and Operation of the Bulk Power System | 2020-03-05 |  |  | Not Initiated | Approved | 2020-03-05 | 2020-09-08 | Retired | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/directory-01-design-and-operation-of-the-bulk-power-system.pdf | RC, TOP, BA, PC, TP, RP, GO, TO
101 | Directory # 12 V1 | Under frequency Load Shedding Program Requirements | 2010-03-03 | 2010-03-15 | 2010-07-13 | Not Initiated | Approved | 2010-07-13 | 2011-01-05 | Retired | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/retired-directories/d12-retired-20211024.pdf | GO, BA, TOP
105 | Directory # 1 | Design and Operation of the Bulk Power System | 2009-12-01 | 2010-03-15 | 2010-07-13 | Not Initiated | Approved | 2010-07-13 | 2014-04-02 | Retired | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/directory-01-design-and-operation-of-the-bulk-power-system.pdf | BA, GO, PC, RC, RP, TO, TOP, TP
106 | Directory # 1 V4 | Design and Operation of the Bulk Power System | 2020-09-09 | 2020-03-31 | 2020-07-29 | Not Initiated | Approved | 2020-09-09 | 2022-12-05 | Retired | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/directory-01-design-and-operation-of-the-bulk-power-system.pdf | BA, GO, PC, RC, RP, TO, TOP, TP
107 | Directory # 1 V5 | Design and Operation of the Bulk Power System | 2022-12-06 |  |  | Not Initiated | Approved | 2022-12-06 |  | Effective | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/directory-01-design-and-operation-of-the-bulk-power-system.pdf | BA, GO, PC, RC, RP, TO, TOP, TP
108 | Directory # 2 | Emergency Operations | 2008-10-21 |  |  | Not Initiated | Approved | 2008-10-21 | 2009-06-25 | Retired | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/directory-2-emergency-operations-20180703.pdf | BA, RC, TOP
110 | Directory # 2 V1 | Emergency Operations | 2009-06-26 |  |  | Not Initiated | Approved | 2009-06-26 | 2010-07-12 | Retired | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/directory-2-emergency-operations-20180703.pdf | BA, RC, TOP
111 | Directory # 2 V2 | Emergency Operations | 2009-08-19 | 2010-03-15 | 2010-07-13 | Not Initiated | Approved | 2010-07-13 | 2014-04-01 | Retired | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/directory-2-emergency-operations-20180703.pdf | BA, RC, TOP
112 | Directory # 2 V4 | Emergency Operations | 2014-12-09 |  |  | Not Initiated | Approved | 2014-12-09 | 2016-10-12 | Retired | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/directory-2-emergency-operations-20180703.pdf | BA, RC, TOP
113 | Directory # 3 | Maintenance Criteria for Bulk Power System Protection | 2007-11-08 |  |  | Not Initiated | Approved | 2007-11-08 | 2010-07-12 | Retired | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/retired-directories/directory-03-maintenance-criteria-for-bulk-power-system-protection | TO, GO, DP
114 | Directory # 3 V1 | Maintenance Criteria for Bulk Power System Protection | 2009-06-30 | 2010-03-15 | 2010-07-13 | Not Initiated | Approved | 2010-07-13 | 2015-04-01 | Retired | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/retired-directories/directory-03-maintenance-criteria-for-bulk-power-system-protection | DP, GO, TO
115 | Directory # 4 V1 | Bulk Power System Protection Criteria | 2015-03-31 |  |  | Not Initiated | Approved | 2015-03-31 | 2016-10-12 | Retired | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/directory-4-tfsp-rev-20200130.pdf | DP, GO, TO
118 | Directory # 4 V4 | Bulk Power System Protection Criteria | 2020-11-08 | 2020-02-06 | 2020-06-05 | Not Initiated | Approved | 2020-11-08 |  | Effective | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/directory-4-tfsp-rev-20200130.pdf | DP, GO, TO
119 | Directory # 4 V3 | Bulk Power System Protection Criteria | 2020-01-30 | 2020-01-30 | 2020-05-29 | Not Initiated | Approved | 2020-05-29 | 2020-11-07 | Retired | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/directory-4-tfsp-rev-20200130.pdf | DP, GO, TO
120 | Directory # 5 V1 | Reserve | 2010-12-02 |  |  | Not Initiated | Approved | 2010-12-02 | 2014-04-01 | Retired | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/directory-5-reserve-20200426.pdf | BA, RC, DP, GOP
121 | Directory # 5 V5 | Reserve | 2020-04-26 |  |  | Not Initiated | Approved | 2020-04-26 |  | Effective | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/directory-5-reserve-20200426.pdf | BA, RC, DP, GOP
122 | Directory # 7 V2 | Remedial Action Schemes | 2020-12-22 |  |  | Not Initiated | Approved | 2020-12-22 | 2021-01-18 | Retired | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/directory-7-ras-review-form-20231004-clean.pdf | DP, GO, PC, RC, TO
124 | Directory # 7 V3 | Remedial Action Schemes | 2021-01-19 |  |  | Not Initiated | Approved | 2021-01-19 | 2023-10-03 | Retired | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/directory-7-ras-review-form-20231004-clean.pdf | DP, GO, PC, RC, TO
125 | Directory # 7 V4 | Remedial Action Schemes | 2023-10-04 |  |  | Not Initiated | Approved | 2023-10-04 |  | Effective | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/directory-7-ras-review-form-20231004-clean.pdf | DP, GO, TO, PC, RC
126 | Directory # 8 V1 | System Restoration | 2010-10-22 | 2013-12-03 | 2014-04-02 | Not Initiated | Approved | 2014-04-02 | 2017-10-05 | Retired | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/directory-08.pdf | RC, BA, PC, TO, TOP, GO, GOP
127 | Directory # 8 V2 | System Restoration | 2017-10-06 |  |  | Not Initiated | Approved | 2017-10-06 | 2018-02-15 | Retired | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/directory-08.pdf | BA, RC, PC, TO, TOP, GO, GOP
128 | Directory # 8 V5 | System Restoration | 2023-02-02 | 2023-03-20 | 2023-07-18 | Not Initiated | Approved | 2023-07-18 |  | Effective | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/directory-08.pdf | BA, RC, PC, TOP, TO, GO, GOP
130 | Directory # 10 | Verification of Generator Gross and Net Reactive Power Capability | 2008-12-22 |  |  | Not Initiated | Approved | 2008-12-22 | 2009-07-06 | Retired | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/retired-directories/directory-10-verification-of-reactive-power-capability | GO, TOP
131 | Directory # 9 V1 | Verification of Generator Gross and Net Real Power Capability | 2009-07-07 |  |  | Not Initiated | Approved | 2009-07-07 | 2012-10-25 | Retired | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/retired-directories/directory-09-verification-of-real-power-capability | GO, TOP
132 | Directory # 9 V2 | Verification of Generator Gross and Net Real Power Capability | 2011-12-28 | 2012-06-28 | 2012-10-26 | Not Initiated | Approved | 2012-10-26 | 2016-10-12 | Retired | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/retired-directories/directory-09-verification-of-real-power-capability | GO, TOP
133 | Directory # 10 V2 | Verification of Generator Gross and Net Reactive Power Capability | 2011-12-28 | 2012-06-28 | 2012-10-26 | Not Initiated | Approved | 2012-10-26 | 2016-10-12 | Retired | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/retired-directories/directory-10-verification-of-reactive-power-capability | GO, TOP
135 | Directory # 11 V1 | Disturbance Monitoring Equipment Criteria | 2020-11-08 |  |  | Not Initiated | Approved | 2020-11-08 | 2022-11-01 | Retired | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/d11-20220214.pdf | GO, TO
136 | Directory # 11 V2 | Disturbance Monitoring Equipment Criteria | 2022-11-02 |  |  | Not Initiated | Approved | 2022-11-02 |  | Effective | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/d11-20220214.pdf | GO, TO
137 | Directory # 12 | Under frequency Load Shedding Program Requirements | 2009-06-26 |  |  | Not Initiated | Approved | 2009-06-26 | 2010-07-12 | Retired | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/directories/retired-directories/d12-retired-20211024.pdf | BA, TOP, GO
138 | Criterion A-01 | Criteria for Review and Approval of Documents | 1997-03-01 |  |  | Not Initiated | Approved | 1997-03-01 | 2005-02-28 | Retired | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/development/regional-criteria/criteria-for-review-and-approval-of-documents/a-01-retirement-ballot-20180910 | RC, PC, TO, BA, TOP
139 | Criterion A-01 V2 | Criteria for Review and Approval of Documents | 2017-04-21 |  |  | Not Initiated | Approved | 2017-04-21 | 2018-09-26 | Retired | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/development/regional-criteria/criteria-for-review-and-approval-of-documents/a-01-retirement-ballot-20180910 | BA, RC, PC, TO, TOP
140 | Criterion A-10 | Classification of Bulk Power System Elements | 2007-04-28 |  |  | Not Initiated | Approved | 2007-04-28 | 2009-11-30 | Retired | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/criteria/a-10-20200508.pdf | BA, DP, GO, PC, RC, RP, TO, TP, TOP
141 | Criterion A-10 V2 | Classification of Bulk Power System Elements | 2020-03-27 |  |  | Not Initiated | Approved | 2020-03-27 | 2020-05-05 | Retired | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/criteria/a-10-20200508.pdf | BA, DP, GO, PC, RC, RP, TO, TOP, TP
142 | Criterion A-10 V3 | Classification of Bulk Power System Elements | 2020-05-06 |  |  | Not Initiated | Approved | 2020-05-06 |  | Effective | https://www.npcc.org/content/docs/public/program-areas/standards-and-criteria/regional-criteria/criteria/a-10-20200508.pdf | BA, DP, GO, PC, RC, RP, TO, TOP, TP
Total Number of Documents: 63

## NPCC Requirements
ID | NPCC Directory | NPCC Criteria Name | Req't . | Text of Requirement | Status In Ontario | Requirement Enforcement Date | Requirement Inactive Date | Functional Entities
315 | Directory # 1 | Design and Operation of the Bulk Power System | R1. | Each Functional Entity that owns equipment shall submit verified information representing the physical or control characteristics of its equipment for system modelling and reliability analysis of the bulk power system in accordance with Requirement R2. | Retired | 2010-07-13 | 2017-01-20
339 | Directory # 1 | Design and Operation of the Bulk Power System | R10. | Each Transmission Planner and Planning Coordinator shall have procedures and implement a system design that ensures equipment capabilities are adequate for fault current levels with all transmission and generation facilities in service for all operating conditions which are not prohibited by a procedure and coordinate these procedures with materially affected Transmission Planner and Planning Coordinator Areas. | Retired | 2010-07-13 | 2014-04-02
340 | Directory # 1 | Design and Operation of the Bulk Power System | R11. | Each Planning Coordinator shall conduct and obtain Reliability Coordinating Committee (RCC) approval for its Transmission Review. Appendix B provides guidance for Transmission Reviews. | Retired | 2010-07-13 | 2014-04-02
341 | Directory # 1 | Design and Operation of the Bulk Power System | R11.1. | A Comprehensive Transmission Review is required at least once every five years or if major or pervasive system changes have occurred. If changes in the planned facilities or forecasted system conditions warrant, the Task Force on System Studies (TFSS) may require a Comprehensive Transmission Review in less than five years. | Retired | 2010-07-13 | 2014-04-02
342 | Directory # 1 | Design and Operation of the Bulk Power System | R11.2. | The proposal for the type of annual Transmission Review shall be presented to TFSS by March of the year during which the review is conducted. Approval for the type of Transmission Review shall be obtained from the TFSS. The annual Transmission Review shall be presented to the TFSS by April of the following year. | Retired | 2010-07-13 | 2014-04-02
343 | Directory # 1 | Design and Operation of the Bulk Power System | R11.3. | If the results of the Transmission Review indicate that the planned bulk power system will not be in conformance with NPCC Directory #1, the Transmission Review shall incorporate a corrective action plan to achieve conformance. | Retired | 2010-07-13 | 2014-04-02
344 | Directory # 1 | Design and Operation of the Bulk Power System | R12. | Each Functional Entity that proposes a new or modified SPS shall consider the complexity of the scheme and the consequences of correct or incorrect operation as well as its benefits. | Retired | 2010-07-13 | 2014-04-02
345 | Directory # 1 | Design and Operation of the Bulk Power System | R12.1. | Provide a rationale and justification to the TFCP including factors such as project delays, temporary construction configurations, unusual combinations of system conditions, equipment outages and infrequent contingencies. | Retired | 2010-07-13 | 2014-04-02
346 | Directory # 1 | Design and Operation of the Bulk Power System | R13. | Each Reliability Coordinator and Transmission Operator shall establish normal transfer capabilities and emergency transfer capabilities, for its portion of the bulk power system to meet the respective performance requirements for the contingencies as specified in Table 3. | Retired | 2010-07-13 | 2014-04-02
349 | Directory # 1 | Design and Operation of the Bulk Power System | R14. | Each Reliability Coordinator and Transmission Operator shall operate to normal transfer capabilities unless an emergency, in accordance with NPCC Directory# 2, is identified. | Retired | 2010-07-13 | 2014-04-02
352 | Directory # 1 | Design and Operation of the Bulk Power System | R15. | Each Reliability Coordinator and Transmission Operator shall make system adjustments once an emergency has been identified, including the pre-contingency disconnection of firm load, to avoid exceeding emergency transfer capabilities. | Retired | 2010-07-13 | 2014-04-02
354 | Directory # 1 | Design and Operation of the Bulk Power System | R16. | Each Reliability Coordinator and Transmission Operator shall assess the status of the bulk power system immediately after the occurrence of any contingency and prepare for the next contingency as specified in Table 3. | Retired | 2010-07-13 | 2014-04-02
356 | Directory # 1 | Design and Operation of the Bulk Power System | R16.1. | Voltage reduction and shedding of firm load shall be deployed to return the system to a secure state, if other system adjustments are not adequate. Voltage reduction need not be initiated and firm load need not be shed to observe a post contingency loading requirement until the contingency occurs, provided that adequate response time for this action is available. | Retired | 2010-07-13 | 2014-04-02
358 | Directory # 1 | Design and Operation of the Bulk Power System | R16.2. | System adjustments shall be completed as quickly as possible following any contingency, but within 30 minutes after the occurrence of any contingency specified in Table 3. | Retired | 2010-07-13 | 2014-04-02
360 | Directory # 1 | Design and Operation of the Bulk Power System | R17. | Each Reliability Coordinator shall notify the applicable Reliability Coordinators of forced outages of any facility as per the NPCC Transmission Facilities Notification List and of any other condition which may impact inter-Area reliability. | Retired | 2010-07-13 | 2014-04-02
362 | Directory # 1 | Design and Operation of the Bulk Power System | R18. | Each Reliability Coordinator shall coordinate scheduled outages of facilities that are on the NPCC Transmission Facilities Notification List sufficiently in advance of the outage to permit the affected Reliability Coordinators to maintain reliability. Appendix F provides guidance for Operational Planning Coordination. | Retired | 2010-07-13 | 2014-04-02
364 | Directory # 1 | Design and Operation of the Bulk Power System | R18.1. | Review and update its Facilities Notification List and submit the list to the NPCC Task Force on Coordination of Operation (TFCO) annually. | Retired | 2010-07-13 | 2014-04-02
366 | Directory # 1 | Design and Operation of the Bulk Power System | R19. | Each Reliability Coordinator shall coordinate voltage control between Transmission Operator Areas. Appendix G provides guidance for Inter- Reliability Coordinator Area Voltage Control. | Retired | 2010-07-13 | 2014-04-02
367 | Directory # 1 | Design and Operation of the Bulk Power System | R19.1. | Metering for reactive power resources and voltage controller status shall be consistent between adjacent Transmission Operators. | Retired | 2010-07-13 | 2014-04-02
368 | Directory # 1 | Design and Operation of the Bulk Power System | R19.2. | Upon request from the TFCO, perform an Inter-Area Voltage Control Assessment. | Retired | 2010-07-13 | 2014-04-02
316 | Directory # 1 | Design and Operation of the Bulk Power System | R2. | Each Planning Coordinator and Reliability Coordinator shall collect and maintain information needed for system modelling and reliability analysis of the bulk power system. | Retired | 2010-07-13 | 2017-01-20
321 | Directory # 1 | Design and Operation of the Bulk Power System | R2.1. | System modelling information shall be submitted to an NPCC Task Force upon request. | Retired | 2010-07-13 | 2017-01-20
322 | Directory # 1 | Design and Operation of the Bulk Power System | R3. | Each Reliability Coordinator shall share and coordinate forecast system information and real-time information to enable and enhance the analysis and modeling of the interconnected bulk power system by security application software on energy management systems. | Retired | 2010-07-13 | 2017-01-20
325 | Directory # 1 | Design and Operation of the Bulk Power System | R4. | Each Planning Coordinator or Resource Planner shall probabilistically evaluate resource adequacy of its Planning Coordinator Area portion of the bulk power system to demonstrate that the loss of load expectation (LOLE) of disconnecting firm load due to resource deficiencies is, on average, no more than 0.1 days per year. | Retired | 2010-07-13 | 2014-04-02
326 | Directory # 1 | Design and Operation of the Bulk Power System | R4.1. | Make due allowances for demand uncertainty, scheduled outages and deratings, forced outages and deratings, assistance over interconnections with neighboring Planning Coordinator Areas, transmission transfer capabilities, and capacity and/or load relief from available operating procedures. | Retired | 2010-07-13 | 2014-04-02
327 | Directory # 1 | Design and Operation of the Bulk Power System | R5. | Each Planning Coordinator shall report and obtain Reliability Coordinating Committee (RCC) approval for its Review of Resource Adequacy. Appendix D provides guidance for the Area Review of Resource Adequacy. | Retired | 2010-07-13 | 2014-04-02
328 | Directory # 1 | Design and Operation of the Bulk Power System | R5.1. | The Review of Resource Adequacy will be presented to the NPCC Task Force on Coordination of Planning (TFCP). Comprehensive and Interim reviews shall be presented to the TFCP before the beginning of the first time period covered by the assessment. | Retired | 2010-07-13 | 2014-04-02
329 | Directory # 1 | Design and Operation of the Bulk Power System | R5.2. | A Comprehensive Review of Resource Adequacy is required every three years and will cover a time period of five years. If changes in planned facilities or forecasted system conditions warrant, TFCP may require a Comprehensive Review of Resource Adequacy in less than 3 years. | Retired | 2010-07-13 | 2014-04-02
330 | Directory # 1 | Design and Operation of the Bulk Power System | R5.3. | In subsequent years, each Planning Coordinator shall conduct an Annual Interim Review of Resource Adequacy that will cover, at a minimum, the remaining years studied in the Comprehensive Review of Resource Adequacy. | Retired | 2010-07-13 | 2014-04-02
331 | Directory # 1 | Design and Operation of the Bulk Power System | R6. | Each Reliability Coordinator shall coordinate outages and deratings of resources to verify adequate resources will be available to meet the forecasted demand and reserve requirements. Appendix F provides guidance for Operational Planning Coordination. | Retired | 2010-07-13 | 2014-04-02
333 | Directory # 1 | Design and Operation of the Bulk Power System | R6.1. | A Summer and Winter Reliability Assessment will be presented to the NPCC Task Force on Coordination of Operation (TFCO) every year. | Retired | 2010-07-13 | 2014-04-02
335 | Directory # 1 | Design and Operation of the Bulk Power System | R7. | Each Transmission Planner and Planning Coordinator shall plan its bulk power system to have sufficient transmission capability to meet the respective requirements as specified in Table 1 while serving forecasted demand. | Retired | 2010-07-13 | 2014-04-02
336 | Directory # 1 | Design and Operation of the Bulk Power System | R7.1. | Credible combinations of system conditions which stress the system shall be modelled including, load forecast, inter-Area and intra-Area transfers, transmission configuration, active and reactive resources, generation availability and other dispatch scenarios. All reclosing facilities shall be assumed in service unless it is known that such facilities will be rendered inoperative. | Retired | 2010-07-13 | 2014-04-02
337 | Directory # 1 | Design and Operation of the Bulk Power System | R8. | Each Transmission Planner and Planning Coordinator shall assess the impact of the extreme contingencies listed in Table 2. Appendix C provides guidance for testing and analyzing extreme contingencies. | Retired | 2010-07-13 | 2014-04-02
338 | Directory # 1 | Design and Operation of the Bulk Power System | R9. | Each Transmission Planner and Planning Coordinator shall assess the impact of extreme system conditions, one condition at a time, subject to contingencies as listed in the “Extreme System Conditions” category of Table 2. | Retired | 2010-07-13 | 2014-04-02
731 | Directory # 1 V1 | Design and Operation of the Bulk Power System | R1. | Each Functional Entity that owns equipment shall submit verified information representing the physical or control characteristics of its equipment for system modelling and reliability analysis of the bulk power system in accordance with Requirement R2. | Retired | 2014-04-03 | 2016-10-12
747 | Directory # 1 V1 | Design and Operation of the Bulk Power System | R10. | Each Transmission Planner and Planning Coordinator shall have procedures and implement a system design that ensures equipment capabilities are adequate for fault current levels with all transmission and generation facilities in service for all operating conditions which are not prohibited by a procedure and coordinate these procedures with materially affected Transmission Planner and Planning Coordinator Areas. | Retired | 2014-04-03 | 2016-10-12
748 | Directory # 1 V1 | Design and Operation of the Bulk Power System | R11. | Each Planning Coordinator shall conduct and obtain Reliability Coordinating Committee (RCC) approval for its Transmission Review. Appendix B provides guidance for Transmission Reviews. | Retired | 2014-04-03 | 2016-10-12
749 | Directory # 1 V1 | Design and Operation of the Bulk Power System | R11.1. | A Comprehensive Transmission Review is required at least once every five years or if major or pervasive system changes have occurred. If changes in the planned facilities or forecasted system conditions warrant, the Task Force on System Studies (TFSS) may require a Comprehensive Transmission Review in less than five years. | Retired | 2014-04-03 | 2016-10-12
750 | Directory # 1 V1 | Design and Operation of the Bulk Power System | R11.2. | The proposal for the type of annual Transmission Review shall be presented to TFSS by March of the year during which the review is conducted. Approval for the type of Transmission Review shall be obtained from the TFSS. The annual Transmission Review shall be presented to the TFSS by April of the following year. | Retired | 2014-04-03 | 2016-10-12
751 | Directory # 1 V1 | Design and Operation of the Bulk Power System | R11.3. | If the results of the Transmission Review indicate that the planned bulk power system will not be in conformance with NPCC Directory #1, the Transmission Review shall incorporate a corrective action plan to achieve conformance. | Retired | 2014-04-03 | 2016-10-12
752 | Directory # 1 V1 | Design and Operation of the Bulk Power System | R12. | Each Functional Entity that proposes a new or modified SPS shall consider the complexity of the scheme and the consequences of correct or incorrect operation as well as its benefits. | Retired | 2014-04-03 | 2016-10-12
753 | Directory # 1 V1 | Design and Operation of the Bulk Power System | R12.1. | Provide a rationale and justification to the TFCP including factors such as project delays, temporary construction configurations, unusual combinations of system conditions, equipment outages and infrequent contingencies. | Retired | 2014-04-03 | 2016-10-12
754 | Directory # 1 V1 | Design and Operation of the Bulk Power System | R13. | Each Reliability Coordinator and Transmission Operator shall establish normal transfer capabilities and emergency transfer capabilities, for its portion of the bulk power system to meet the respective performance requirements for the contingencies as specified in Table 3. | Retired | 2014-04-03 | 2016-10-12
755 | Directory # 1 V1 | Design and Operation of the Bulk Power System | R14. | Each Reliability Coordinator and Transmission Operator shall operate to normal transfer capabilities unless an emergency, in accordance with NPCC Directory# 2, is identified. | Retired | 2014-04-03 | 2016-10-12
756 | Directory # 1 V1 | Design and Operation of the Bulk Power System | R15. | Each Reliability Coordinator and Transmission Operator shall make system adjustments once an emergency has been identified, including the pre-contingency disconnection of firm load, to avoid exceeding emergency transfer capabilities. | Retired | 2014-04-03 | 2016-10-12
757 | Directory # 1 V1 | Design and Operation of the Bulk Power System | R16. | Each Reliability Coordinator and Transmission Operator shall assess the status of the bulk power system immediately after the occurrence of any contingency and prepare for the next contingency as specified in Table 3. | Retired | 2014-04-03 | 2016-10-12
758 | Directory # 1 V1 | Design and Operation of the Bulk Power System | R16.1. | Voltage reduction and shedding of firm load shall be deployed to return the system to a secure state, if other system adjustments are not adequate. Voltage reduction need not be initiated and firm load need not be shed to observe a post contingency loading requirement until the contingency occurs, provided that adequate response time for this action is available. | Retired | 2014-04-03 | 2016-10-12
759 | Directory # 1 V1 | Design and Operation of the Bulk Power System | R16.2. | System adjustments shall be completed as quickly as possible following any contingency, but within 30 minutes after the occurrence of any contingency specified in Table 3. | Retired | 2014-04-03 | 2016-10-12
760 | Directory # 1 V1 | Design and Operation of the Bulk Power System | R17. | Each Reliability Coordinator shall notify the applicable Reliability Coordinators of forced outages of any facility as per the NPCC Transmission Facilities Notification List and of any other condition which may impact inter-Area reliability. | Retired | 2014-04-03 | 2016-10-12
761 | Directory # 1 V1 | Design and Operation of the Bulk Power System | R18. | Each Reliability Coordinator shall coordinate scheduled outages of facilities that are on the NPCC Transmission Facilities Notification List sufficiently in advance of the outage to permit the affected Reliability Coordinators to maintain reliability. Appendix F provides guidance for Operational Planning Coordination. | Retired | 2014-04-03 | 2016-10-12
762 | Directory # 1 V1 | Design and Operation of the Bulk Power System | R18.1. | Review and update its Facilities Notification List and submit the list to the NPCC Task Force on Coordination of Operation (TFCO) annually. | Retired | 2014-04-03 | 2016-10-12
763 | Directory # 1 V1 | Design and Operation of the Bulk Power System | R19. | Each Reliability Coordinator shall coordinate voltage control between Transmission Operator Areas. Appendix G provides guidance for Inter- Reliability Coordinator Area Voltage Control. | Retired | 2014-04-03 | 2016-10-12
764 | Directory # 1 V1 | Design and Operation of the Bulk Power System | R19.1. | Metering for reactive power resources and voltage controller status shall be consistent between adjacent Transmission Operators. | Retired | 2014-04-03 | 2016-10-12
765 | Directory # 1 V1 | Design and Operation of the Bulk Power System | R19.2. | Upon request from the TFCO, perform an Inter-Area Voltage Control Assessment. | Retired | 2014-04-03 | 2016-10-12
732 | Directory # 1 V1 | Design and Operation of the Bulk Power System | R2. | Each Planning Coordinator and Reliability Coordinator shall collect and maintain information needed for system modelling and reliability analysis of the bulk power system. | Retired | 2014-04-03 | 2016-10-12
733 | Directory # 1 V1 | Design and Operation of the Bulk Power System | R2.1. | System modelling information shall be submitted to an NPCC Task Force upon request. | Retired | 2014-04-03 | 2016-10-12
734 | Directory # 1 V1 | Design and Operation of the Bulk Power System | R3. | Each Reliability Coordinator shall share and coordinate forecast system information and real-time information to enable and enhance the analysis and modeling of the interconnected bulk power system by security application software on energy management systems. | Retired | 2014-04-03 | 2016-10-12
735 | Directory # 1 V1 | Design and Operation of the Bulk Power System | R4. | Each Planning Coordinator or Resource Planner shall probabilistically evaluate resource adequacy of its Planning Coordinator Area portion of the bulk power system to demonstrate that the loss of load expectation (LOLE) of disconnecting firm load due to resource deficiencies is, on average, no more than 0.1 days per year. | Retired | 2014-04-03 | 2016-10-12
736 | Directory # 1 V1 | Design and Operation of the Bulk Power System | R4.1. | Make due allowances for demand uncertainty, scheduled outages and deratings, forced outages and deratings, assistance over interconnections with neighboring Planning Coordinator Areas, transmission transfer capabilities, and capacity and/or load relief from available operating procedures. | Retired | 2014-04-03 | 2016-10-12
737 | Directory # 1 V1 | Design and Operation of the Bulk Power System | R5. | Each Planning Coordinator shall report and obtain Reliability Coordinating Committee (RCC) approval for its Review of Resource Adequacy. Appendix D provides guidance for the Area Review of Resource Adequacy. | Retired | 2014-04-03 | 2016-10-12
738 | Directory # 1 V1 | Design and Operation of the Bulk Power System | R5.1. | The Review of Resource Adequacy will be presented to the NPCC Task Force on Coordination of Planning (TFCP). Comprehensive and Interim reviews shall be presented to the TFCP before the beginning of the first time period covered by the assessment. | Retired | 2014-04-03 | 2016-10-12
739 | Directory # 1 V1 | Design and Operation of the Bulk Power System | R5.2. | A Comprehensive Review of Resource Adequacy is required every three years and will cover a time period of five years. If changes in planned facilities or forecasted system conditions warrant, TFCP may require a Comprehensive Review of Resource Adequacy in less than 3 years. | Retired | 2014-04-03 | 2016-10-12
740 | Directory # 1 V1 | Design and Operation of the Bulk Power System | R5.3. | In subsequent years, each Planning Coordinator shall conduct an Annual Interim Review of Resource Adequacy that will cover, at a minimum, the remaining years studied in the Comprehensive Review of Resource Adequacy. | Retired | 2014-04-03 | 2016-10-12
741 | Directory # 1 V1 | Design and Operation of the Bulk Power System | R6. | Each Reliability Coordinator shall coordinate outages and deratings of resources to verify adequate resources will be available to meet the forecasted demand and reserve requirements. Appendix F provides guidance for Operational Planning Coordination. | Retired | 2014-04-03 | 2016-10-12
742 | Directory # 1 V1 | Design and Operation of the Bulk Power System | R6.1. | A Summer and Winter Reliability Assessment will be presented to the NPCC Task Force on Coordination of Operation (TFCO) every year. | Retired | 2014-04-03 | 2016-10-12
743 | Directory # 1 V1 | Design and Operation of the Bulk Power System | R7. | Each Transmission Planner and Planning Coordinator shall plan its bulk power system to have sufficient transmission capability to meet the respective requirements as specified in Table 1 while serving forecasted demand. | Retired | 2014-04-03 | 2016-10-12
744 | Directory # 1 V1 | Design and Operation of the Bulk Power System | R7.1. | Credible combinations of system conditions which stress the system shall be modelled including, load forecast, inter-Area and intra-Area transfers, transmission configuration, active and reactive resources, generation availability and other dispatch scenarios. All reclosing facilities shall be assumed in service unless it is known that such facilities will be rendered inoperative. | Retired | 2014-04-03 | 2016-10-12
745 | Directory # 1 V1 | Design and Operation of the Bulk Power System | R8. | Each Transmission Planner and Planning Coordinator shall assess the impact of the extreme contingencies listed in Table 2. Appendix C provides guidance for testing and analyzing extreme contingencies. | Retired | 2014-04-03 | 2016-10-12
746 | Directory # 1 V1 | Design and Operation of the Bulk Power System | R9. | Each Transmission Planner and Planning Coordinator shall assess the impact of extreme system conditions, one condition at a time, subject to contingencies as listed in the “Extreme System Conditions” category of Table 2. | Retired | 2014-04-03 | 2016-10-12
1 | Directory # 1 V2 | Design and Operation of the Bulk Power System | R1. | Each Functional Entity that owns equipment shall submit verified information representing the physical or control characteristics of its equipment for system modelling and reliability analysis of the bulk power system in accordance with Requirement R2. | Retired | 2016-10-13 | 2020-03-04 | RP, TP, PC, BA, TOP, RC, TO, GO
2 | Directory # 1 V2 | Design and Operation of the Bulk Power System | R10. | Each Transmission Planner and Planning Coordinator shall have procedures and implement a system design that ensures equipment capabilities are adequate for fault current levels with all transmission and generation facilities in service for all operating conditions which are not prohibited by a procedure and coordinate these procedures with materially affected Transmission Planner and Planning Coordinator Areas. | Retired | 2016-10-13 | 2020-03-04 | TO, GO, RP, BA, TOP, RC, TP, PC
3 | Directory # 1 V2 | Design and Operation of the Bulk Power System | R11. | Each Planning Coordinator shall conduct and obtain Reliability Coordinating Committee (RCC) approval for its Transmission Review. Appendix B provides guidance for Transmission Reviews. | Retired | 2016-10-13 | 2020-03-04 | TO, GO, RP, TP, BA, TOP, RC, PC
4 | Directory # 1 V2 | Design and Operation of the Bulk Power System | R11.1 | A Comprehensive Transmission Review is required at least once every five years or if major or pervasive system changes have occurred. If changes in the planned facilities or forecasted system conditions warrant, the Task Force on System Studies (TFSS) may require a Comprehensive Transmission Review in less than five years. | Retired | 2016-10-13 | 2020-03-04 | TO, GO, RP, TP, PC, BA, TOP, RC
5 | Directory # 1 V2 | Design and Operation of the Bulk Power System | R11.2 | The proposal for the type of annual Transmission Review shall be presented to TFSS by March of the year during which the review is conducted. Approval for the type of Transmission Review shall be obtained from the TFSS. The annual Transmission Review shall be presented to the TFSS by April of the following year. | Retired | 2016-10-13 | 2020-03-04 | TO, GO, RP, TP, PC, BA, TOP, RC
6 | Directory # 1 V2 | Design and Operation of the Bulk Power System | R11.3 | If the results of the Transmission Review indicate that the planned bulk power system will not be in conformance with NPCC Directory #1, the Transmission Review shall incorporate a corrective action plan to achieve conformance. | Retired | 2016-10-13 | 2020-03-04 | TO, GO, RP, TP, PC, BA, TOP, RC
7 | Directory # 1 V2 | Design and Operation of the Bulk Power System | R12. | Each Functional Entity that proposes a new or modified SPS shall consider the complexity of the scheme and the consequences of correct or incorrect operation as well as its benefits. | Retired | 2016-10-13 | 2020-03-04 | RP, TP, PC, BA, TOP, RC, TO, GO
8 | Directory # 1 V2 | Design and Operation of the Bulk Power System | R12.1 | Provide a rationale and justification to the TFCP including factors such as project delays, temporary construction configurations, unusual combinations of system conditions, equipment outages and infrequent contingencies. | Retired | 2016-10-13 | 2020-03-04 | TO, GO, RP, TP, PC, BA, TOP, RC, TO, GO
9 | Directory # 1 V2 | Design and Operation of the Bulk Power System | R13. | Each Reliability Coordinator and Transmission Operator shall establish normal transfer capabilities and emergency transfer capabilities, for its portion of the bulk power system to meet the respective performance requirements for the contingencies as specified in Table 3. | Retired | 2016-10-13 | 2020-03-04 | TO, GO, RP, TP, PC, BA, TOP, RC
12 | Directory # 1 V2 | Design and Operation of the Bulk Power System | R14. | Each Reliability Coordinator and Transmission Operator shall operate to normal transfer capabilities unless an emergency, in accordance with NPCC Directory# 2, is identified. | Retired | 2016-10-13 | 2020-03-04 | TO, GO, RP, TP, PC, BA, TOP, RC
15 | Directory # 1 V2 | Design and Operation of the Bulk Power System | R15. | Each Reliability Coordinator and Transmission Operator shall make system adjustments once an emergency has been identified, including the pre-contingency disconnection of firm load, to avoid exceeding emergency transfer capabilities. | Retired | 2016-10-13 | 2020-03-04 | TO, GO, RP, TP, PC, BA, TOP, RC
17 | Directory # 1 V2 | Design and Operation of the Bulk Power System | R16. | Each Reliability Coordinator and Transmission Operator shall assess the status of the bulk power system immediately after the occurrence of any contingency and prepare for the next contingency as specified in Table 3. | Retired | 2016-10-13 | 2020-03-04 | TO, GO, RP, TP, PC, BA, TOP, RC
19 | Directory # 1 V2 | Design and Operation of the Bulk Power System | R16.1 | Voltage reduction and shedding of firm load shall be deployed to return the system to a secure state, if other system adjustments are not adequate. Voltage reduction need not be initiated and firm load need not be shed to observe a post contingency loading requirement until the contingency occurs, provided that adequate response time for this action is available. | Retired | 2016-10-13 | 2020-03-04 | TO, GO, RP, TP, PC, BA, TOP, RC
21 | Directory # 1 V2 | Design and Operation of the Bulk Power System | R16.2 | System adjustments shall be completed as quickly as possible following any contingency, but within 30 minutes after the occurrence of any contingency specified in Table 3. | Retired | 2016-10-13 | 2020-03-04 | TO, GO, RP, TP, PC, BA, TOP, RC
22 | Directory # 1 V2 | Design and Operation of the Bulk Power System | R16.2 | System adjustments shall be completed as quickly as possible following any contingency, but within 30 minutes after the occurrence of any contingency specified in Table 3. | Retired | 2016-10-13 | 2020-03-04 | TO, GO, RP, TP, PC, BA, TOP, RC
23 | Directory # 1 V2 | Design and Operation of the Bulk Power System | R17. | Each Reliability Coordinator shall notify the applicable Reliability Coordinators of forced outages of any facility as per the NPCC Transmission Facilities Notification List and of any other condition which may impact inter-Area reliability. | Retired | 2016-10-13 | 2020-03-04 | TO, GO, RP, TP, PC, BA, TOP, RC
25 | Directory # 1 V2 | Design and Operation of the Bulk Power System | R18. | Each Reliability Coordinator shall coordinate scheduled outages of facilities that are on the NPCC Transmission Facilities Notification List sufficiently in advance of the outage to permit the affected Reliability Coordinators to maintain reliability. Appendix F provides guidance for Operational Planning Coordination. | Retired | 2016-10-13 | 2020-03-04 | TO, GO, RP, TP, PC, BA, TOP, RC
27 | Directory # 1 V2 | Design and Operation of the Bulk Power System | R18.1. | Review and update its Facilities Notification List and submit the list to the NPCC Task Force on Coordination of Operation (TFCO) annually. | Retired | 2016-10-13 | 2020-03-04 | TO, GO, RP, TP, PC, BA, TOP, RC
29 | Directory # 1 V2 | Design and Operation of the Bulk Power System | R19. | Each Reliability Coordinator shall coordinate voltage control between Transmission Operator Areas. Appendix G provides guidance for Inter- Reliability Coordinator Area Voltage Control. | Retired | 2016-10-13 | 2020-03-04 | TO, GO, RP, TP, PC, BA, TOP, RC
30 | Directory # 1 V2 | Design and Operation of the Bulk Power System | R19.1. | Metering for reactive power resources and voltage controller status shall be consistent between adjacent Transmission Operators. | Retired | 2016-10-13 | 2020-03-04 | TO, GO, RP, TP, PC, BA, TOP, RC
31 | Directory # 1 V2 | Design and Operation of the Bulk Power System | R19.2. | Upon request from the TFCO, perform an Inter-Area Voltage Control Assessment. | Retired | 2016-10-13 | 2020-03-04 | TO, GO, RP, TP, PC, BA, TOP, RC
32 | Directory # 1 V2 | Design and Operation of the Bulk Power System | R2. | Each Planning Coordinator and Reliability Coordinator shall collect and maintain information needed for system modelling and reliability analysis of the bulk power system. | Retired | 2016-10-13 | 2020-03-04 | TO, GO, RP, TP, BA, TOP, RC, PC
35 | Directory # 1 V2 | Design and Operation of the Bulk Power System | R2.1. | System modelling information shall be submitted to an NPCC Task Force upon request. | Retired | 2016-10-13 | 2020-03-04 | TO, GO, RP, TP, BA, TOP, RC, PC
38 | Directory # 1 V2 | Design and Operation of the Bulk Power System | R3. | Each Reliability Coordinator shall share and coordinate forecast system information and real-time information to enable and enhance the analysis and modeling of the interconnected bulk power system by security application software on energy management systems. | Retired | 2016-10-13 | 2020-03-04 | TO, GO, RP, TP, PC, BA, TOP, RC
41 | Directory # 1 V2 | Design and Operation of the Bulk Power System | R4. | Each Planning Coordinator or Resource Planner shall probabilistically evaluate resource adequacy of its Planning Coordinator Area portion of the bulk power system to demonstrate that the loss of load expectation (LOLE) of disconnecting firm load due to resource deficiencies is, on average, no more than 0.1 days per year. | Retired | 2016-10-13 | 2020-03-04 | TP, GO, TO, BA, TOP, RC, RP, PC
42 | Directory # 1 V2 | Design and Operation of the Bulk Power System | R4.1. | Make due allowances for demand uncertainty, scheduled outages and deratings, forced outages and deratings, assistance over interconnections with neighboring Planning Coordinator Areas, transmission transfer capabilities, and capacity and/or load relief from available operating procedures. | Retired | 2016-10-13 | 2020-03-04 | TO, GO, TP, BA, TOP, RC, RP, PC
43 | Directory # 1 V2 | Design and Operation of the Bulk Power System | R5. | Each Planning Coordinator shall report and obtain Reliability Coordinating Committee (RCC) approval for its Review of Resource Adequacy. Appendix D provides guidance for the Area Review of Resource Adequacy. | Retired | 2016-10-13 | 2020-03-04 | TO, GO, TP, RP, PC, BA, TOP, PC
44 | Directory # 1 V2 | Design and Operation of the Bulk Power System | R5.1 | The Review of Resource Adequacy will be presented to the NPCC Task Force on Coordination of Planning (TFCP). Comprehensive and Interim reviews shall be presented to the TFCP before the beginning of the first time period covered by the assessment. | Retired | 2016-10-13 | 2020-03-04 | TO, GO, RP, TP, BA, TOP, RC, PC
45 | Directory # 1 V2 | Design and Operation of the Bulk Power System | R5.2. | A Comprehensive Review of Resource Adequacy is required every three years and will cover a time period of five years. If changes in planned facilities or forecasted system conditions warrant, TFCP may require a Comprehensive Review of Resource Adequacy in less than 3 years. | Retired | 2016-10-13 | 2020-03-04 | PC, TO, GO, RP, TP, PC, BA, TOP, RC, PC
46 | Directory # 1 V2 | Design and Operation of the Bulk Power System | R5.3. | In subsequent years, each Planning Coordinator shall conduct an Annual Interim Review of Resource Adequacy that will cover, at a minimum, the remaining years studied in the Comprehensive Review of Resource Adequacy. | Retired | 2016-10-13 | 2020-03-04 | TO, GO, RP, TP, BA, TOP, RC, PC
47 | Directory # 1 V2 | Design and Operation of the Bulk Power System | R6. | Each Reliability Coordinator shall coordinate outages and deratings of resources to verify adequate resources will be available to meet the forecasted demand and reserve requirements. Appendix F provides guidance for Operational Planning Coordination. | Retired | 2016-10-13 | 2020-03-04 | TO, GO, RP, PC, TP, BA, TOP, RC
49 | Directory # 1 V2 | Design and Operation of the Bulk Power System | R6.1 | A Summer and Winter Reliability Assessment will be presented to the NPCC Task Force on Coordination of Operation (TFCO) every year. | Retired | 2016-10-13 | 2020-03-04 | TO, GO, RP, TP, PC, BA, TOP, RC
51 | Directory # 1 V2 | Design and Operation of the Bulk Power System | R7. | Each Transmission Planner and Planning Coordinator shall plan its bulk power system to have sufficient transmission capability to meet the respective requirements as specified in Table 1 while serving forecasted demand. | Retired | 2016-10-13 | 2020-03-04 | TO, GO, RP, BA, TOP, RC, TP, PC
52 | Directory # 1 V2 | Design and Operation of the Bulk Power System | R7.1. | Credible combinations of system conditions which stress the system shall be modelled including, load forecast, inter-Area and intra-Area transfers, transmission configuration, active and reactive resources, generation availability and other dispatch scenarios. All reclosing facilities shall be assumed in service unless it is known that such facilities will be rendered inoperative. | Retired | 2016-10-13 | 2020-03-04 | TO, GO, RP, BA, TOP, RC, TP, PC
53 | Directory # 1 V2 | Design and Operation of the Bulk Power System | R8. | Each Transmission Planner and Planning Coordinator shall assess the impact of the extreme contingencies listed in Table 2. Appendix C provides guidance for testing and analyzing extreme contingencies. | Retired | 2016-10-13 | 2020-03-04 | TO, GO, RP, BA, TOP, RC, TP, PC
54 | Directory # 1 V2 | Design and Operation of the Bulk Power System | R9. | Each Transmission Planner and Planning Coordinator shall assess the impact of extreme system conditions, one condition at a time, subject to contingencies as listed in the “Extreme System Conditions” category of Table 2. | Retired | 2016-10-13 | 2020-03-04 | TO, GO, RP, BA, TOP, RC, TP, PC
698 | Directory # 1 V3 | Design and Operation of the Bulk Power System | R.10. | Each Transmission Planner and Planning Coordinator shall have procedures and implement a system design that ensures equipment capabilities are adequate for fault current levels with all transmission and generation facilities in service for all operating conditions which are not prohibited by a procedure and coordinate these procedures with materially affected Transmission Planner and Planning Coordinator Areas. | Retired | 2020-03-05 | 2020-09-08 | TO, GO, TP, RP, PC, BA, TOP, RC
600 | Directory # 1 V3 | Design and Operation of the Bulk Power System | R1. | Each Functional Entity that owns equipment shall submit verified information representing the physical or control characteristics of its equipment for system modelling and reliability analysis of the bulk power system in accordance with Requirement R2. | Retired | 2020-03-05 | 2020-09-08 | TO, GO, TP, RP, PC, BA, TOP, RC
699 | Directory # 1 V3 | Design and Operation of the Bulk Power System | R11. | Each Planning Coordinator shall conduct and obtain Reliability Coordinating Committee (RCC) approval for its Transmission Review. Appendix B provides guidance for Transmission Reviews. | Retired | 2020-03-05 | 2020-09-08 | TO, GO, TP, RP, PC, BA, TOP, RC
700 | Directory # 1 V3 | Design and Operation of the Bulk Power System | R11.1. | A Comprehensive Transmission Review is required at least once every five years or if major or pervasive system changes have occurred. If changes in the planned facilities or forecasted system conditions warrant, the Task Force on System Studies (TFSS) may require a Comprehensive Transmission Review in less than five years. | Retired | 2020-03-05 | 2020-09-08 | TO, GO, TP, RP, PC, BA, TOP, RC
701 | Directory # 1 V3 | Design and Operation of the Bulk Power System | R11.2. | The proposal for the type of annual Transmission Review shall be presented to TFSS by March of the year during which the review is conducted. Approval for the type of Transmission Review shall be obtained from the TFSS. The annual Transmission Review shall be presented to the TFSS by April of the following year. | Retired | 2020-03-05 | 2020-09-08 | TO, GO, TP, RP, PC, BA, TOP, RC
702 | Directory # 1 V3 | Design and Operation of the Bulk Power System | R11.3. | If the results of the Transmission Review indicate that the planned bulk power system will not be in conformance with NPCC Directory #1, the Transmission Review shall incorporate a corrective action plan to achieve conformance. | Retired | 2020-03-05 | 2020-09-08 | TO, GO, TP, RP, PC, BA, TOP, RC
703 | Directory # 1 V3 | Design and Operation of the Bulk Power System | R12. | Each Functional Entity that proposes a new or modified SPS shall consider the complexity of the scheme and the consequences of correct or incorrect operation as well as its benefits. | Retired | 2020-03-05 | 2020-09-08 | TO, GO, TP, RP, PC, BA, TOP, RC
704 | Directory # 1 V3 | Design and Operation of the Bulk Power System | R12.1. | Provide a rationale and justification to the TFCP including factors such as project delays, temporary construction configurations, unusual combinations of system conditions, equipment outages and infrequent contingencies. | Retired | 2020-03-05 | 2020-09-08 | TO, GO, TP, RP, PC, BA, TOP, RC
705 | Directory # 1 V3 | Design and Operation of the Bulk Power System | R13. | Each Reliability Coordinator and Transmission Operator shall establish normal transfer capabilities and emergency transfer capabilities, for its portion of the bulk power system to meet the respective performance requirements for the contingencies as specified in Table 3. | Retired | 2020-03-05 | 2020-09-08 | TO, GO, TP, RP, PC, BA, TOP, RC
708 | Directory # 1 V3 | Design and Operation of the Bulk Power System | R14. | Each Reliability Coordinator and Transmission Operator shall operate to normal transfer capabilities unless an emergency, in accordance with NPCC Directory# 2, is identified. | Retired | 2020-03-05 | 2020-09-08 | TO, GO, TP, RP, PC, BA, TOP, RC
711 | Directory # 1 V3 | Design and Operation of the Bulk Power System | R15. | Each Reliability Coordinator and Transmission Operator shall make system adjustments once an emergency has been identified, including the pre-contingency disconnection of firm load, to avoid exceeding emergency transfer capabilities. | Retired | 2020-03-05 | 2020-09-08 | TO, GO, TP, RP, PC, BA, TOP, RC
713 | Directory # 1 V3 | Design and Operation of the Bulk Power System | R16. | Each Reliability Coordinator and Transmission Operator shall assess the status of the bulk power system immediately after the occurrence of any contingency and prepare for the next contingency as specified in Table 3. | Retired | 2020-03-05 | 2020-09-08 | TO, GO, TP, RP, PC, BA, TOP, RC
715 | Directory # 1 V3 | Design and Operation of the Bulk Power System | R16.1 | Voltage reduction and shedding of firm load shall be deployed to return the system to a secure state, if other system adjustments are not adequate. Voltage reduction need not be initiated and firm load need not be shed to observe a post contingency loading requirement until the contingency occurs, provided that adequate response time for this action is available. | Retired | 2020-03-05 | 2020-09-08 | TO, GO, TP, RP, PC, BA, TOP, RC
718 | Directory # 1 V3 | Design and Operation of the Bulk Power System | R16.2. | System adjustments shall be completed as quickly as possible following any contingency, but within 30 minutes after the occurrence of any contingency specified in Table 3. | Retired | 2020-03-05 | 2020-09-08 | TO, GO, TP, RP, PC, BA, TOP, RC
719 | Directory # 1 V3 | Design and Operation of the Bulk Power System | R17. | Each Reliability Coordinator shall notify the applicable Reliability Coordinators of forced outages of any facility as per the NPCC Transmission Facilities Notification List and of any other condition which may impact inter-Area reliability. | Retired | 2020-03-05 | 2020-09-08 | TO, GO, TP, RP, PC, BA, TOP, RC
721 | Directory # 1 V3 | Design and Operation of the Bulk Power System | R18. | Each Reliability Coordinator shall coordinate scheduled outages of facilities that are on the NPCC Transmission Facilities Notification List sufficiently in advance of the outage to permit the affected Reliability Coordinators to maintain reliability. Appendix F provides guidance for Operational Planning Coordination. | Retired | 2020-03-05 | 2020-09-08 | TO, GO, TP, RP, PC, BA, TOP, RC
723 | Directory # 1 V3 | Design and Operation of the Bulk Power System | R18.1. | Review and update its Facilities Notification List and submit the list to the NPCC Task Force on Coordination of Operation (TFCO) annually. | Retired | 2020-03-05 | 2020-09-08 | TO, GO, TP, RP, PC, BA, TOP, RC
725 | Directory # 1 V3 | Design and Operation of the Bulk Power System | R19. | Each Reliability Coordinator shall coordinate voltage control between Transmission Operator Areas. Appendix G provides guidance for Inter- Reliability Coordinator Area Voltage Control. | Retired | 2020-03-05 | 2020-09-08 | TO, GO, TP, RP, PC, BA, TOP, RC
726 | Directory # 1 V3 | Design and Operation of the Bulk Power System | R19.1 | Metering for reactive power resources and voltage controller status shall be consistent between adjacent Transmission Operators. | Retired | 2020-03-05 | 2020-09-08 | TO, GO, TP, RP, PC, BA, TOP, RC
727 | Directory # 1 V3 | Design and Operation of the Bulk Power System | R19.2. | Upon request from the TFCO, perform an Inter-Area Voltage Control Assessment. | Retired | 2020-03-05 | 2020-09-08 | TO, GO, TP, RP, PC, BA, TOP, RC
610 | Directory # 1 V3 | Design and Operation of the Bulk Power System | R2. | Each Planning Coordinator and Reliability Coordinator shall collect and maintain information needed for system modelling and reliability analysis of the bulk power system. | Retired | 2020-03-05 | 2020-09-08 | TO, GO, TP, RP, PC, BA, TOP, RC
611 | Directory # 1 V3 | Design and Operation of the Bulk Power System | R2.1. | System modelling information shall be submitted to an NPCC Task Force upon request. | Retired | 2020-03-05 | 2020-09-08 | TO, GO, TP, RP, PC, BA, TOP, RC
614 | Directory # 1 V3 | Design and Operation of the Bulk Power System | R3. | Each Reliability Coordinator shall share and coordinate forecast system information and real-time information to enable and enhance the analysis and modeling of the interconnected bulk power system by security application software on energy management systems. | Retired | 2020-03-05 | 2020-09-08 | TO, GO, TP, RP, PC, BA, TOP, RC
674 | Directory # 1 V3 | Design and Operation of the Bulk Power System | R4. | Each Planning Coordinator or Resource Planner shall probabilistically evaluate resource adequacy of its Planning Coordinator Area portion of the bulk power system to demonstrate that the loss of load expectation (LOLE) of disconnecting firm load due to resource deficiencies is, on average, no more than 0.1 days per year. | Retired | 2020-03-05 | 2020-09-08 | TO, GO, TP, RP, PC, BA, TOP, RC
684 | Directory # 1 V3 | Design and Operation of the Bulk Power System | R4.1. | Make due allowances for demand uncertainty, scheduled outages and deratings, forced outages and deratings, assistance over interconnections with neighboring Planning Coordinator Areas, transmission transfer capabilities, and capacity and/or load relief from available operating procedures. | Retired | 2020-03-05 | 2020-09-08 | TO, GO, TP, RP, PC, BA, TOP, RC
686 | Directory # 1 V3 | Design and Operation of the Bulk Power System | R5. | Each Planning Coordinator shall report and obtain Reliability Coordinating Committee (RCC) approval for its Review of Resource Adequacy. Appendix D provides guidance for the Area Review of Resource Adequacy. | Retired | 2020-03-05 | 2020-09-08 | TO, GO, TP, RP, PC, BA, TOP, RC
687 | Directory # 1 V3 | Design and Operation of the Bulk Power System | R5.1. | The Review of Resource Adequacy will be presented to the NPCC Task Force on Coordination of Planning (TFCP). Comprehensive and Interim reviews shall be presented to the TFCP before the beginning of the first time period covered by the assessment. | Retired | 2020-03-05 | 2020-09-08 | TO, GO, TP, RP, PC, BA, TOP, RC
688 | Directory # 1 V3 | Design and Operation of the Bulk Power System | R5.2. | A Comprehensive Review of Resource Adequacy is required every three years and will cover a time period of five years. If changes in planned facilities or forecasted system conditions warrant, TFCP may require a Comprehensive Review of Resource Adequacy in less than 3 years. | Retired | 2020-03-05 | 2020-09-08 | TO, GO, TP, RP, PC, BA, TOP, RC
689 | Directory # 1 V3 | Design and Operation of the Bulk Power System | R5.3 | In subsequent years, each Planning Coordinator shall conduct an Annual Interim Review of Resource Adequacy that will cover, at a minimum, the remaining years studied in the Comprehensive Review of Resource Adequacy. | Retired | 2020-03-05 | 2020-09-08 | TO, GO, TP, RP, PC, BA, TOP, RC
690 | Directory # 1 V3 | Design and Operation of the Bulk Power System | R6. | Each Reliability Coordinator shall coordinate outages and deratings of resources to verify adequate resources will be available to meet the forecasted demand and reserve requirements. Appendix F provides guidance for Operational Planning Coordination. | Retired | 2020-03-05 | 2020-09-08 | TO, GO, TP, RP, PC, BA, TOP, RC
692 | Directory # 1 V3 | Design and Operation of the Bulk Power System | R6.1. | A Summer and Winter Reliability Assessment will be presented to the NPCC Task Force on Coordination of Operation (TFCO) every year. | Retired | 2020-03-05 | 2020-09-08 | TO, GO, TP, RP, PC, BA, TOP, RC
694 | Directory # 1 V3 | Design and Operation of the Bulk Power System | R7. | Each Transmission Planner and Planning Coordinator shall plan its bulk power system to have sufficient transmission capability to meet the respective requirements as specified in Table 1 while serving forecasted demand. | Retired | 2020-03-05 | 2020-09-08 | TO, GO, TP, RP, PC, BA, TOP, RC
695 | Directory # 1 V3 | Design and Operation of the Bulk Power System | R7.1. | Credible combinations of system conditions which stress the system shall be modelled including, load forecast, inter-Area and intra-Area transfers, transmission configuration, active and reactive resources, generation availability and other dispatch scenarios. All reclosing facilities shall be assumed in service unless it is known that such facilities will be rendered inoperative. | Retired | 2020-03-05 | 2020-09-08 | TO, GO, TP, RP, PC, BA, TOP, RC
696 | Directory # 1 V3 | Design and Operation of the Bulk Power System | R8. | Each Transmission Planner and Planning Coordinator shall assess the impact of the extreme contingencies listed in Table 2. Appendix C provides guidance for testing and analyzing extreme contingencies. | Retired | 2020-03-05 | 2020-09-08 | TO, GO, TP, RP, PC, BA, TOP, RC
697 | Directory # 1 V3 | Design and Operation of the Bulk Power System | R9. | Each Transmission Planner and Planning Coordinator shall assess the impact of extreme system conditions, one condition at a time, subject to contingencies as listed in the “Extreme System Conditions” category of Table 2. | Retired | 2020-03-05 | 2020-09-08 | TO, GO, TP, RP, PC, BA, TOP, RC
782 | Directory # 1 V4 | Design and Operation of the Bulk Power System | R.10. | Each Transmission Planner and Planning Coordinator shall have procedures and implement a system design that ensures equipment capabilities are adequate for fault current levels with all transmission and generation facilities in service for all operating conditions which are not prohibited by a procedure and coordinate these procedures with materially affected Transmission Planner and Planning Coordinator Areas. | Retired | 2020-09-09 | 2022-12-05
766 | Directory # 1 V4 | Design and Operation of the Bulk Power System | R1. | Each Functional Entity that owns equipment shall submit verified information representing the physical or control characteristics of its equipment for system modelling and reliability analysis of the bulk power system in accordance with Requirement R2. | Retired | 2020-09-09 | 2022-12-05
783 | Directory # 1 V4 | Design and Operation of the Bulk Power System | R11. | Each Planning Coordinator shall conduct and obtain Reliability Coordinating Committee (RCC) approval for its Transmission Review. Appendix B provides guidance for Transmission Reviews. | Retired | 2020-09-09 | 2022-12-05
784 | Directory # 1 V4 | Design and Operation of the Bulk Power System | R11.1. | A Comprehensive Transmission Review is required at least once every five years or if major or pervasive system changes have occurred. If changes in the planned facilities or forecasted system conditions warrant, the Task Force on System Studies (TFSS) may require a Comprehensive Transmission Review in less than five years. | Retired | 2020-09-09 | 2022-12-05
785 | Directory # 1 V4 | Design and Operation of the Bulk Power System | R11.2. | The proposal for the type of annual Transmission Review shall be presented to TFSS by March of the year during which the review is conducted. Approval for the type of Transmission Review shall be obtained from the TFSS. The annual Transmission Review shall be presented to the TFSS by April of the following year. | Retired | 2020-09-09 | 2022-12-05
786 | Directory # 1 V4 | Design and Operation of the Bulk Power System | R11.3. | If the results of the Transmission Review indicate that the planned bulk power system will not be in conformance with NPCC Directory #1, the Transmission Review shall incorporate a corrective action plan to achieve conformance. | Retired | 2020-09-09 | 2022-12-05
787 | Directory # 1 V4 | Design and Operation of the Bulk Power System | R12. | Each Functional Entity that proposes a new or modified SPS shall consider the complexity of the scheme and the consequences of correct or incorrect operation as well as its benefits. | Retired | 2020-09-09 | 2022-12-05
788 | Directory # 1 V4 | Design and Operation of the Bulk Power System | R12.1. | Provide a rationale and justification to the TFCP including factors such as project delays, temporary construction configurations, unusual combinations of system conditions, equipment outages and infrequent contingencies. | Retired | 2020-09-09 | 2022-12-05
789 | Directory # 1 V4 | Design and Operation of the Bulk Power System | R13. | Each Reliability Coordinator and Transmission Operator shall establish normal transfer capabilities and emergency transfer capabilities, for its portion of the bulk power system to meet the respective performance requirements for the contingencies as specified in Table 3. | Retired | 2020-09-09 | 2022-12-05
790 | Directory # 1 V4 | Design and Operation of the Bulk Power System | R14. | Each Reliability Coordinator and Transmission Operator shall operate to normal transfer capabilities unless an emergency, in accordance with NPCC Directory# 2, is identified. | Retired | 2020-09-09 | 2022-12-05
791 | Directory # 1 V4 | Design and Operation of the Bulk Power System | R15. | Each Reliability Coordinator and Transmission Operator shall make system adjustments once an emergency has been identified, including the pre-contingency disconnection of firm load, to avoid exceeding emergency transfer capabilities. | Retired | 2020-09-09 | 2022-12-05
792 | Directory # 1 V4 | Design and Operation of the Bulk Power System | R16. | Each Reliability Coordinator and Transmission Operator shall assess the status of the bulk power system immediately after the occurrence of any contingency and prepare for the next contingency as specified in Table 3. | Retired | 2020-09-09 | 2022-12-05
793 | Directory # 1 V4 | Design and Operation of the Bulk Power System | R16.1 | Voltage reduction and shedding of firm load shall be deployed to return the system to a secure state, if other system adjustments are not adequate. Voltage reduction need not be initiated and firm load need not be shed to observe a post contingency loading requirement until the contingency occurs, provided that adequate response time for this action is available. | Retired | 2020-09-09 | 2022-12-05
794 | Directory # 1 V4 | Design and Operation of the Bulk Power System | R16.2. | System adjustments shall be completed as quickly as possible following any contingency, but within 30 minutes after the occurrence of any contingency specified in Table 3. | Retired | 2020-09-09 | 2022-12-05
795 | Directory # 1 V4 | Design and Operation of the Bulk Power System | R17. | Each Reliability Coordinator shall notify the applicable Reliability Coordinators of forced outages of any facility as per the NPCC Transmission Facilities Notification List and of any other condition which may impact inter-Area reliability. | Retired | 2020-09-09 | 2022-12-05
796 | Directory # 1 V4 | Design and Operation of the Bulk Power System | R18. | Each Reliability Coordinator shall coordinate scheduled outages of facilities that are on the NPCC Transmission Facilities Notification List sufficiently in advance of the outage to permit the affected Reliability Coordinators to maintain reliability. Appendix F provides guidance for Operational Planning Coordination. | Retired | 2020-09-09 | 2022-12-05
797 | Directory # 1 V4 | Design and Operation of the Bulk Power System | R18.1. | Review and update its Facilities Notification List and submit the list to the NPCC Task Force on Coordination of Operation (TFCO) annually. | Retired | 2020-09-09 | 2022-12-05
798 | Directory # 1 V4 | Design and Operation of the Bulk Power System | R19. | Each Reliability Coordinator shall coordinate voltage control between Transmission Operator Areas. Appendix G provides guidance for Inter- Reliability Coordinator Area Voltage Control. | Retired | 2020-09-09 | 2022-12-05
799 | Directory # 1 V4 | Design and Operation of the Bulk Power System | R19.1 | Metering for reactive power resources and voltage controller status shall be consistent between adjacent Transmission Operators. | Retired | 2020-09-09 | 2022-12-05
800 | Directory # 1 V4 | Design and Operation of the Bulk Power System | R19.2. | Upon request from the TFCO, perform an Inter-Area Voltage Control Assessment. | Retired | 2020-09-09 | 2022-12-05
767 | Directory # 1 V4 | Design and Operation of the Bulk Power System | R2. | Each Planning Coordinator and Reliability Coordinator shall collect and maintain information needed for system modelling and reliability analysis of the bulk power system. | Retired | 2020-09-09 | 2022-12-05
768 | Directory # 1 V4 | Design and Operation of the Bulk Power System | R2.1. | System modelling information shall be submitted to an NPCC Task Force upon request. | Retired | 2020-09-09 | 2022-12-05
769 | Directory # 1 V4 | Design and Operation of the Bulk Power System | R3. | Each Reliability Coordinator shall share and coordinate forecast system information and real-time information to enable and enhance the analysis and modeling of the interconnected bulk power system by security application software on energy management systems. | Retired | 2020-09-09 | 2022-12-05
770 | Directory # 1 V4 | Design and Operation of the Bulk Power System | R4. | Each Planning Coordinator or Resource Planner shall probabilistically evaluate resource adequacy of its Planning Coordinator Area portion of the bulk power system to demonstrate that the loss of load expectation (LOLE) of disconnecting firm load due to resource deficiencies is, on average, no more than 0.1 days per year. | Retired | 2020-09-09 | 2022-12-05
771 | Directory # 1 V4 | Design and Operation of the Bulk Power System | R4.1. | Make due allowances for demand uncertainty, scheduled outages and deratings, forced outages and deratings, assistance over interconnections with neighboring Planning Coordinator Areas, transmission transfer capabilities, and capacity and/or load relief from available operating procedures. | Retired | 2020-09-09 | 2022-12-05
772 | Directory # 1 V4 | Design and Operation of the Bulk Power System | R5. | Each Planning Coordinator shall report and obtain Reliability Coordinating Committee (RCC) approval for its Review of Resource Adequacy. Appendix D provides guidance for the Area Review of Resource Adequacy. | Retired | 2020-09-09 | 2022-12-05
773 | Directory # 1 V4 | Design and Operation of the Bulk Power System | R5.1. | The Review of Resource Adequacy will be presented to the NPCC Task Force on Coordination of Planning (TFCP). Comprehensive and Interim reviews shall be presented to the TFCP before the beginning of the first time period covered by the assessment. | Retired | 2020-09-09 | 2022-12-05
774 | Directory # 1 V4 | Design and Operation of the Bulk Power System | R5.2. | A Comprehensive Review of Resource Adequacy is required every three years and will cover a time period of five years. If changes in planned facilities or forecasted system conditions warrant, TFCP may require a Comprehensive Review of Resource Adequacy in less than 3 years. | Retired | 2020-09-09 | 2022-12-05
775 | Directory # 1 V4 | Design and Operation of the Bulk Power System | R5.3 | In subsequent years, each Planning Coordinator shall conduct an Annual Interim Review of Resource Adequacy that will cover, at a minimum, the remaining years studied in the Comprehensive Review of Resource Adequacy. | Retired | 2020-09-09 | 2022-12-05
776 | Directory # 1 V4 | Design and Operation of the Bulk Power System | R6. | Each Reliability Coordinator shall coordinate outages and deratings of resources to verify adequate resources will be available to meet the forecasted demand and reserve requirements. Appendix F provides guidance for Operational Planning Coordination. | Retired | 2020-09-09 | 2022-12-05
777 | Directory # 1 V4 | Design and Operation of the Bulk Power System | R6.1. | A Summer and Winter Reliability Assessment will be presented to the NPCC Task Force on Coordination of Operation (TFCO) every year. | Retired | 2020-09-09 | 2022-12-05
778 | Directory # 1 V4 | Design and Operation of the Bulk Power System | R7. | Each Transmission Planner and Planning Coordinator shall plan its bulk power system to have sufficient transmission capability to meet the respective requirements as specified in Table 1 while serving forecasted demand. | Retired | 2020-09-09 | 2022-12-05
779 | Directory # 1 V4 | Design and Operation of the Bulk Power System | R7.1. | Credible combinations of system conditions which stress the system shall be modelled including, load forecast, inter-Area and intra-Area transfers, transmission configuration, active and reactive resources, generation availability and other dispatch scenarios. All reclosing facilities shall be assumed in service unless it is known that such facilities will be rendered inoperative. | Retired | 2020-09-09 | 2022-12-05
780 | Directory # 1 V4 | Design and Operation of the Bulk Power System | R8. | Each Transmission Planner and Planning Coordinator shall assess the impact of the extreme contingencies listed in Table 2. Appendix C provides guidance for testing and analyzing extreme contingencies. | Retired | 2020-09-09 | 2022-12-05
781 | Directory # 1 V4 | Design and Operation of the Bulk Power System | R9. | Each Transmission Planner and Planning Coordinator shall assess the impact of extreme system conditions, one condition at a time, subject to contingencies as listed in the “Extreme System Conditions” category of Table 2. | Retired | 2020-09-09 | 2022-12-05
817 | Directory # 1 V5 | Design and Operation of the Bulk Power System | R.10. | Each Transmission Planner and Planning Coordinator shall have procedures and implement a system design that ensures equipment capabilities are adequate for fault current levels with all transmission and generation facilities in service for all operating conditions which are not prohibited by a procedure and coordinate these procedures with materially affected Transmission Planner and Planning Coordinator Areas. | Effective | 2022-12-06
801 | Directory # 1 V5 | Design and Operation of the Bulk Power System | R1. | Each Functional Entity that owns equipment shall submit verified information representing the physical or control characteristics of its equipment for system modelling and reliability analysis of the bulk power system in accordance with Requirement R2. | Effective | 2022-12-06
818 | Directory # 1 V5 | Design and Operation of the Bulk Power System | R11. | Each Planning Coordinator shall conduct and obtain Reliability Coordinating Committee (RCC) approval for its Transmission Review. Appendix B provides guidance for Transmission Reviews. | Effective | 2022-12-06
819 | Directory # 1 V5 | Design and Operation of the Bulk Power System | R11.1. | A Comprehensive Transmission Review is required at least once every five years or if major or pervasive system changes have occurred. If changes in the planned facilities or forecasted system conditions warrant, the Task Force on System Studies (TFSS) may require a Comprehensive Transmission Review in less than five years. | Effective | 2022-12-06
820 | Directory # 1 V5 | Design and Operation of the Bulk Power System | R11.2. | The proposal for the type of annual Transmission Review shall be presented to TFSS by March of the year during which the review is conducted. Approval for the type of Transmission Review shall be obtained from the TFSS. The annual Transmission Review shall be presented to the TFSS by April of the following year. | Effective | 2022-12-06
821 | Directory # 1 V5 | Design and Operation of the Bulk Power System | R11.3. | If the results of the Transmission Review indicate that the planned bulk power system will not be in conformance with NPCC Directory #1, the Transmission Review shall incorporate a corrective action plan to achieve conformance. | Effective | 2022-12-06
822 | Directory # 1 V5 | Design and Operation of the Bulk Power System | R12. | Each Functional Entity that proposes a new or modified SPS shall consider the complexity of the scheme and the consequences of correct or incorrect operation as well as its benefits. | Effective | 2022-12-06
823 | Directory # 1 V5 | Design and Operation of the Bulk Power System | R12.1. | Provide a rationale and justification to the TFCP including factors such as project delays, temporary construction configurations, unusual combinations of system conditions, equipment outages and infrequent contingencies. | Effective | 2022-12-06
824 | Directory # 1 V5 | Design and Operation of the Bulk Power System | R13. | Each Reliability Coordinator and Transmission Operator shall establish normal transfer capabilities and emergency transfer capabilities, for its portion of the bulk power system to meet the respective performance requirements for the contingencies as specified in Table 3. | Effective | 2022-12-06
825 | Directory # 1 V5 | Design and Operation of the Bulk Power System | R14. | Each Reliability Coordinator and Transmission Operator shall operate to normal transfer capabilities unless an emergency, in accordance with NPCC Directory# 2, is identified. | Effective | 2022-12-06
826 | Directory # 1 V5 | Design and Operation of the Bulk Power System | R15. | Each Reliability Coordinator and Transmission Operator shall make system adjustments once an emergency has been identified, including the pre-contingency disconnection of firm load, to avoid exceeding emergency transfer capabilities. | Effective | 2022-12-06
827 | Directory # 1 V5 | Design and Operation of the Bulk Power System | R16. | Each Reliability Coordinator and Transmission Operator shall assess the status of the bulk power system immediately after the occurrence of any contingency and prepare for the next contingency as specified in Table 3. | Effective | 2022-12-06
828 | Directory # 1 V5 | Design and Operation of the Bulk Power System | R16.1 | Voltage reduction and shedding of firm load shall be deployed to return the system to a secure state, if other system adjustments are not adequate. Voltage reduction need not be initiated and firm load need not be shed to observe a post contingency loading requirement until the contingency occurs, provided that adequate response time for this action is available. | Effective | 2022-12-06
829 | Directory # 1 V5 | Design and Operation of the Bulk Power System | R16.2. | System adjustments shall be completed as quickly as possible following any contingency, but within 30 minutes after the occurrence of any contingency specified in Table 3. | Effective | 2022-12-06
830 | Directory # 1 V5 | Design and Operation of the Bulk Power System | R17. | Each Reliability Coordinator shall notify the applicable Reliability Coordinators of forced outages of any facility as per the NPCC Transmission Facilities Notification List and of any other condition which may impact inter-Area reliability. | Effective | 2022-12-06
831 | Directory # 1 V5 | Design and Operation of the Bulk Power System | R18. | Each Reliability Coordinator shall coordinate scheduled outages of facilities that are on the NPCC Transmission Facilities Notification List sufficiently in advance of the outage to permit the affected Reliability Coordinators to maintain reliability. Appendix F provides guidance for Operational Planning Coordination. | Effective | 2022-12-06
832 | Directory # 1 V5 | Design and Operation of the Bulk Power System | R18.1. | Review and update its Facilities Notification List and submit the list to the NPCC Task Force on Coordination of Operation (TFCO) annually. | Effective | 2022-12-06
833 | Directory # 1 V5 | Design and Operation of the Bulk Power System | R19. | Each Reliability Coordinator shall coordinate voltage control between Transmission Operator Areas. Appendix G provides guidance for Inter- Reliability Coordinator Area Voltage Control. | Effective | 2022-12-06
834 | Directory # 1 V5 | Design and Operation of the Bulk Power System | R19.1 | Metering for reactive power resources and voltage controller status shall be consistent between adjacent Transmission Operators. | Effective | 2022-12-06
835 | Directory # 1 V5 | Design and Operation of the Bulk Power System | R19.2. | Upon request from the TFCO, perform an Inter-Area Voltage Control Assessment. | Effective | 2022-12-06
802 | Directory # 1 V5 | Design and Operation of the Bulk Power System | R2. | Each Planning Coordinator and Reliability Coordinator shall collect and maintain information needed for system modelling and reliability analysis of the bulk power system. | Effective | 2022-12-06
803 | Directory # 1 V5 | Design and Operation of the Bulk Power System | R2.1. | System modelling information shall be submitted to an NPCC Task Force upon request. | Effective | 2022-12-06
804 | Directory # 1 V5 | Design and Operation of the Bulk Power System | R3. | Each Reliability Coordinator shall share and coordinate forecast system information and real-time information to enable and enhance the analysis and modeling of the interconnected bulk power system by security application software on energy management systems. | Effective | 2022-12-06
805 | Directory # 1 V5 | Design and Operation of the Bulk Power System | R4. | Each Planning Coordinator or Resource Planner shall probabilistically evaluate resource adequacy of its Planning Coordinator Area portion of the bulk power system to demonstrate that the loss of load expectation (LOLE) of disconnecting firm load due to resource deficiencies is, on average, no more than 0.1 days per year. | Effective | 2022-12-06
806 | Directory # 1 V5 | Design and Operation of the Bulk Power System | R4.1. | Make due allowances for demand uncertainty, scheduled outages and deratings, forced outages and deratings, assistance over interconnections with neighboring Planning Coordinator Areas, transmission transfer capabilities, and capacity and/or load relief from available operating procedures. | Effective | 2022-12-06
807 | Directory # 1 V5 | Design and Operation of the Bulk Power System | R5. | Each Planning Coordinator shall report and obtain Reliability Coordinating Committee (RCC) approval for its Review of Resource Adequacy. Appendix D provides guidance for the Area Review of Resource Adequacy. | Effective | 2022-12-06
808 | Directory # 1 V5 | Design and Operation of the Bulk Power System | R5.1. | The Review of Resource Adequacy will be presented to the NPCC Task Force on Coordination of Planning (TFCP). Comprehensive and Interim reviews shall be presented to the TFCP before the beginning of the first time period covered by the assessment. | Effective | 2022-12-06
809 | Directory # 1 V5 | Design and Operation of the Bulk Power System | R5.2. | A Comprehensive Review of Resource Adequacy is required every three years and will cover a time period of five years. If changes in planned facilities or forecasted system conditions warrant, TFCP may require a Comprehensive Review of Resource Adequacy in less than 3 years. | Effective | 2022-12-06
810 | Directory # 1 V5 | Design and Operation of the Bulk Power System | R5.3 | In subsequent years, each Planning Coordinator shall conduct an Annual Interim Review of Resource Adequacy that will cover, at a minimum, the remaining years studied in the Comprehensive Review of Resource Adequacy. | Effective | 2022-12-06
811 | Directory # 1 V5 | Design and Operation of the Bulk Power System | R6. | Each Reliability Coordinator shall coordinate outages and deratings of resources to verify adequate resources will be available to meet the forecasted demand and reserve requirements. Appendix F provides guidance for Operational Planning Coordination. | Effective | 2022-12-06
812 | Directory # 1 V5 | Design and Operation of the Bulk Power System | R6.1. | A Summer and Winter Reliability Assessment will be presented to the NPCC Task Force on Coordination of Operation (TFCO) every year. | Effective | 2022-12-06
813 | Directory # 1 V5 | Design and Operation of the Bulk Power System | R7. | Each Transmission Planner and Planning Coordinator shall plan its bulk power system to have sufficient transmission capability to meet the respective requirements as specified in Table 1 while serving forecasted demand. | Effective | 2022-12-06
814 | Directory # 1 V5 | Design and Operation of the Bulk Power System | R7.1. | Credible combinations of system conditions which stress the system shall be modelled including, load forecast, inter-Area and intra-Area transfers, transmission configuration, active and reactive resources, generation availability and other dispatch scenarios. All reclosing facilities shall be assumed in service unless it is known that such facilities will be rendered inoperative. | Effective | 2022-12-06
815 | Directory # 1 V5 | Design and Operation of the Bulk Power System | R8. | Each Transmission Planner and Planning Coordinator shall assess the impact of the extreme contingencies listed in Table 2. Appendix C provides guidance for testing and analyzing extreme contingencies. | Effective | 2022-12-06
816 | Directory # 1 V5 | Design and Operation of the Bulk Power System | R9. | Each Transmission Planner and Planning Coordinator shall assess the impact of extreme system conditions, one condition at a time, subject to contingencies as listed in the “Extreme System Conditions” category of Table 2. | Effective | 2022-12-06
158 | Directory # 10 | Verification of Generator Gross and Net Reactive Power Capability | R1. | Transmission Operators shall develop and maintain documentation of those generators or generation facilities that must verify the Gross Reactive Power Capability and Net Reactive Power Capability for the summer and winter capability seasons. The documentation maintained by the Transmission Operator shall include the following: | Retired | 2008-12-22 | 2009-07-06 | TOP
159 | Directory # 10 | Verification of Generator Gross and Net Reactive Power Capability | R1.1. | All generators or generation facilities Declared Gross Reactive Power Capability and Declared Net Reactive Power Capability and seasonal auxiliary load reactive power requirements. (Reference Appendix B). | Retired | 2008-12-22 | 2009-07-06 | TOP
160 | Directory # 10 | Verification of Generator Gross and Net Reactive Power Capability | R1.2. | All generators or generation facilities Verified Gross Reactive Power Capability and Verified Net Reactive Power Capability, verification date and method of verification. | Retired | 2008-12-22 | 2009-07-06 | TOP
161 | Directory # 10 | Verification of Generator Gross and Net Reactive Power Capability | R1.3. | Discrepancies between a Generator Owner’s declared and verified Gross Reactive Power Capability and Net Reactive Power Capability, the reason for such discrepancies and the Generator Owner’s plan to address the discrepancies. | Retired | 2008-12-22 | 2009-07-06 | TOP
162 | Directory # 10 | Verification of Generator Gross and Net Reactive Power Capability | R1.4. | Generator Owner supplied Gross Reactive Power Capability and Net Reactive Power Capability testing, manufacturer data, performance tracking or operating historical data, certification documentation, as specified by the Transmission Operator. | Retired | 2008-12-22 | 2009-07-06 | TOP
163 | Directory # 10 | Verification of Generator Gross and Net Reactive Power Capability | R1.5. | Generators or generation facilities exempted from the verification requirements and the basis for their exemption (see Section 1.5). | Retired | 2008-12-22 | 2009-07-06 | TOP
172 | Directory # 10 | Verification of Generator Gross and Net Reactive Power Capability | R10. | If a Transmission Operator determines that the difference between the Declared Gross Reactive Power Capability and the Declared Net Reactive Power Capability of a generator or generation facility is insignificant for NPCC Bulk Power System reliability analysis, then periodic verification will be required for only one numerical value. | Retired | 2008-12-22 | 2009-07-06 | TOP
173 | Directory # 10 | Verification of Generator Gross and Net Reactive Power Capability | R11. | If a Transmission Operator determines that only the lagging or leading Gross Reactive Power Capability and Net Reactive Power Capability of a generator or generation facility is required for NPCC Bulk Power System reliability analysis, then periodic verification will be required only for that specific reactive power capability value. | Retired | 2008-12-22 | 2009-07-06 | TOP
174 | Directory # 10 | Verification of Generator Gross and Net Reactive Power Capability | R12. | The Generator Owner shall provide generator or generation facility Declared Gross Reactive Power Capability and Declared Net Reactive Power Capability to the Transmission Operator. | Retired | 2008-12-22 | 2009-07-06 | GO
175 | Directory # 10 | Verification of Generator Gross and Net Reactive Power Capability | R13. | The Generator Owner shall provide evidence, upon request, to the Transmission Operator that the generator or generation facility Gross Reactive Power Capability and Net Reactive Power Capability have been verified. | Retired | 2008-12-22 | 2009-07-06 | GO
176 | Directory # 10 | Verification of Generator Gross and Net Reactive Power Capability | R14. | The Generator Owner shall report to the Transmission Operator any discrepancies between Declared and Verified Gross Reactive Power Capability and Net Reactive Power Capability within a time frame specified by the Transmission Operator and develop and implement a plan to resolve the discrepancies. | Retired | 2008-12-22 | 2009-07-06 | TOP, GO
177 | Directory # 10 | Verification of Generator Gross and Net Reactive Power Capability | R15. | The Generator Owner shall determine and report to the Transmission Operator the generator or generation facility reactive power seasonal auxiliary loads (including common station loads). | Retired | 2008-12-22 | 2009-07-06 | GO
178 | Directory # 10 | Verification of Generator Gross and Net Reactive Power Capability | R16. | The Generator Owner shall comply with Transmission Operator requests for periodic verification of Gross Reactive Power Capability and Net Reactive Power Capability of their generators or generation facilities. | Retired | 2008-12-22 | 2009-07-06 | GO
179 | Directory # 10 | Verification of Generator Gross and Net Reactive Power Capability | R17. | The Generator Owner shall verify the Gross Reactive Power Capability and Net Reactive Power Capability of their generators or generation facilities according to their types. As specified by the Transmission Operator, the verification shall include any of the following: • Testing, • Use of operating historical data, • Commissioning data (for new generators only), • Performance tracking data acquired during the same seasonal capability period. | Retired | 2008-12-22 | 2009-07-06 | GO
180 | Directory # 10 | Verification of Generator Gross and Net Reactive Power Capability | R18. | The Generator Owner shall verify the Gross Reactive Power Capability and Net Reactive Power Capability of Thermal Generators, Internal Combustion Generators, Gas Turbine Generators, Combined Cycle and Hydro Generators or generators operated as a synchronous condenser on the average leading reactive power output for at least a 15 consecutive minute period and average lagging reactive power output for at least a 60 consecutive minute period. | Retired | 2008-12-22 | 2009-07-06 | GO
181 | Directory # 10 | Verification of Generator Gross and Net Reactive Power Capability | R19. | The Generator Owner shall verify the Gross Reactive Power Capability and Net Reactive Power Capability of Intermittent power resources (wind, tidal or geo-thermal generators) on performance tracking data. Manufacturers’ data or commissioning data can be used until sufficient performance tracking data is available to verify generator or generation facilities lagging and leading reactive capabilities. | Retired | 2008-12-22 | 2009-07-06 | GO
164 | Directory # 10 | Verification of Generator Gross and Net Reactive Power Capability | R2. | The Transmission Operator shall establish and document a program to periodically verify the Gross Reactive Power Capability and Net Reactive Power Capability of all generators and generation facilities that are subject to periodic seasonal Gross Reactive Power Capability and Net Reactive Power Capability verification. | Retired | 2008-12-22 | 2009-07-06 | TOP
182 | Directory # 10 | Verification of Generator Gross and Net Reactive Power Capability | R20. | The Generator Owner shall verify the Gross Reactive Power Capability and Net Reactive Power Capability for multiple generator facilities when limited by common elements on the reactive power capability of the facility and not the sum of the capabilities of the individual generators. | Retired | 2008-12-22 | 2009-07-06 | GO
183 | Directory # 10 | Verification of Generator Gross and Net Reactive Power Capability | R21. | The Generator Owner shall identify any equipment or other factor that will limit the capability of the generator or generation facility to meet its Declared Gross Reactive Power Capability or Declared Net Reactive Power Capability. | Retired | 2008-12-22 | 2009-07-06 | GO
184 | Directory # 10 | Verification of Generator Gross and Net Reactive Power Capability | R22. | The Generator Owner shall notify the Transmission Operator and request an exemption if it cannot conduct seasonal capability testing of a generator or generation facility for any of the reasons listed below. • Adverse impact on transmission system reliability • Potential damage to transmission system or generator equipment • Environment conditions • Governmental regulatory or operating license limitations • An extended outage to the generator or generation facility | Retired | 2008-12-22 | 2009-07-06 | GO
185 | Directory # 10 | Verification of Generator Gross and Net Reactive Power Capability | R23. | The Transmission Operator shall, within 30 calendar days of receiving notification from a Generator Owner that it is requesting an exemption because it cannot perform verification for the required seasonal period, notify the Generator Owner whether its generator will be exempted from the seasonal capability testing. Where the exemption is approved, the Transmission Operator shall coordinate with the Generator Owner to reschedule the verification for the next seasonal verification period. | Retired | 2008-12-22 | 2009-07-06 | TOP
186 | Directory # 10 | Verification of Generator Gross and Net Reactive Power Capability | R24. | The Generator Owner for a generator or generation facility exempted from seasonal capability testing shall submit the following to the Transmission Operator: • For existing generators, generator operation records, manufacturer data, or performance tracking for the previous applicable seasonal verification period for this generator or generation facility. • Engineering analysis in conjunction with performance tracking data to justify any difference between a generator's or generation facility’s declared capability and previous applicable seasonal performance tracking data. • For new generators only, commissioning data. | Retired | 2008-12-22 | 2009-07-06 | GO
165 | Directory # 10 | Verification of Generator Gross and Net Reactive Power Capability | R3. | The Transmission Operator shall provide any changes to its verification process to the Generator Owners within 30 calendar days of issue. | Retired | 2008-12-22 | 2009-07-06 | TOP
166 | Directory # 10 | Verification of Generator Gross and Net Reactive Power Capability | R4. | The Transmission Operator shall establish and document requirements for a Generator Owner to notify the Transmission Operator within a specified time period when its generator or generation facility cannot achieve the Declared Gross Reactive Power Capability or Declared Net Reactive Power Capability because of equipment issues. | Retired | 2008-12-22 | 2009-07-06 | TOP
167 | Directory # 10 | Verification of Generator Gross and Net Reactive Power Capability | R5. | The Transmission Operator shall establish and document a time frame for the Generator Owner to address equipment issues that result in a generator or generation facility not achieving the Declared Gross Reactive Power Capability and Declared Net Reactive Power Capability. | Retired | 2008-12-22 | 2009-07-06 | TOP
168 | Directory # 10 | Verification of Generator Gross and Net Reactive Power Capability | R6. | The Transmission Operator shall establish and document the real power level at which the verification shall be performed, recognizing that the verification of lagging and leading reactive power capabilities should normally be performed during on-peak and off-peak hours, respectively. | Retired | 2008-12-22 | 2009-07-06 | TOP
169 | Directory # 10 | Verification of Generator Gross and Net Reactive Power Capability | R7. | The Transmission Operator shall establish and document those intermittent or small generating units whose capability may be represented by verification results of a single generating unit. | Retired | 2008-12-22 | 2009-07-06 | TOP
170 | Directory # 10 | Verification of Generator Gross and Net Reactive Power Capability | R8. | The Transmission Operator shall request Generator Owners to verify the seasonal Gross Reactive Power Capability and Net Reactive Power Capability of their generators or generation facilities that are subject to periodic seasonal Gross Reactive Power Capability and Net Reactive Power Capability verification every five (5) years or more frequently as required by the Transmission Operator. The two (2) capability seasons are defined as summer and winter as specified by the Transmission Operator. | Retired | 2008-12-22 | 2009-07-06 | TOP
171 | Directory # 10 | Verification of Generator Gross and Net Reactive Power Capability | R9. | If a Transmission Operator determines that only one seasonal generating capability value is required for NPCC Bulk Power System reliability analysis, then periodic verification will be required only for that particular season. | Retired | 2008-12-22 | 2009-07-06 | TOP
1849 | Directory # 10 V1 | Verification of Generator Gross and Net Reactive Power Capability | R1. | Transmission Operators shall develop and maintain documentation of those generators or generation facilities that must verify the Gross Reactive Power Capability and Net Reactive Power Capability for the summer and winter capability seasons. The documentation maintained by the Transmission Operator shall include the following: | Retired | 2009-07-07 | 2012-10-25
1850 | Directory # 10 V1 | Verification of Generator Gross and Net Reactive Power Capability | R1.1. | All generators or generation facilities Declared Gross Reactive Power Capability and Declared Net Reactive Power Capability and seasonal auxiliary load reactive power requirements. (Reference Appendix B). | Retired | 2009-07-07 | 2012-10-25
1851 | Directory # 10 V1 | Verification of Generator Gross and Net Reactive Power Capability | R1.2. | All generators or generation facilities Verified Gross Reactive Power Capability and Verified Net Reactive Power Capability, verification date and method of verification. | Retired | 2009-07-07 | 2012-10-25
1852 | Directory # 10 V1 | Verification of Generator Gross and Net Reactive Power Capability | R1.3. | Discrepancies between a Generator Owner’s declared and verified Gross Reactive Power Capability and Net Reactive Power Capability, the reason for such discrepancies and the Generator Owner’s plan to address the discrepancies. | Retired | 2009-07-07 | 2012-10-25
1853 | Directory # 10 V1 | Verification of Generator Gross and Net Reactive Power Capability | R1.4. | Generator Owner supplied Gross Reactive Power Capability and Net Reactive Power Capability testing, manufacturer data, performance tracking or operating historical data, certification documentation, as specified by the Transmission Operator. | Retired | 2009-07-07 | 2012-10-25
1854 | Directory # 10 V1 | Verification of Generator Gross and Net Reactive Power Capability | R1.5. | Generators or generation facilities exempted from the verification requirements and the basis for their exemption (see Section 1.5). | Retired | 2009-07-07 | 2012-10-25
1855 | Directory # 10 V1 | Verification of Generator Gross and Net Reactive Power Capability | R10. | If a Transmission Operator determines that the difference between the Declared Gross Reactive Power Capability and the Declared Net Reactive Power Capability of a generator or generation facility is insignificant for NPCC Bulk Power System reliability analysis, then periodic verification will be required for only one numerical value. | Retired | 2009-07-07 | 2012-10-25
1856 | Directory # 10 V1 | Verification of Generator Gross and Net Reactive Power Capability | R11. | If a Transmission Operator determines that only the lagging or leading Gross Reactive Power Capability and Net Reactive Power Capability of a generator or generation facility is required for NPCC Bulk Power System reliability analysis, then periodic verification will be required only for that specific reactive power capability value. | Retired | 2009-07-07 | 2012-10-25
1857 | Directory # 10 V1 | Verification of Generator Gross and Net Reactive Power Capability | R12. | The Generator Owner shall provide generator or generation facility Declared Gross Reactive Power Capability and Declared Net Reactive Power Capability to the Transmission Operator. | Retired | 2009-07-07 | 2012-10-25
1858 | Directory # 10 V1 | Verification of Generator Gross and Net Reactive Power Capability | R13. | The Generator Owner shall provide evidence, upon request, to the Transmission Operator that the generator or generation facility Gross Reactive Power Capability and Net Reactive Power Capability have been verified. | Retired | 2009-07-07 | 2012-10-25
1859 | Directory # 10 V1 | Verification of Generator Gross and Net Reactive Power Capability | R14. | The Generator Owner shall report to the Transmission Operator any discrepancies between Declared and Verified Gross Reactive Power Capability and Net Reactive Power Capability within a time frame specified by the Transmission Operator and develop and implement a plan to resolve the discrepancies. | Retired | 2009-07-07 | 2012-10-25
1860 | Directory # 10 V1 | Verification of Generator Gross and Net Reactive Power Capability | R15. | The Generator Owner shall determine and report to the Transmission Operator the generator or generation facility reactive power seasonal auxiliary loads (including common station loads). | Retired | 2009-07-07 | 2012-10-25
1861 | Directory # 10 V1 | Verification of Generator Gross and Net Reactive Power Capability | R16. | The Generator Owner shall comply with Transmission Operator requests for periodic verification of Gross Reactive Power Capability and Net Reactive Power Capability of their generators or generation facilities. | Retired | 2009-07-07 | 2012-10-25
1862 | Directory # 10 V1 | Verification of Generator Gross and Net Reactive Power Capability | R17. | The Generator Owner shall verify the Gross Reactive Power Capability and Net Reactive Power Capability of their generators or generation facilities according to their types. As specified by the Transmission Operator, the verification shall include any of the following: • Testing, • Use of operating historical data, • Commissioning data (for new generators only), • Performance tracking data acquired during the same seasonal capability period. | Retired | 2009-07-07 | 2012-10-25
1863 | Directory # 10 V1 | Verification of Generator Gross and Net Reactive Power Capability | R18. | The Generator Owner shall verify the Gross Reactive Power Capability and Net Reactive Power Capability of Thermal Generators, Internal Combustion Generators, Gas Turbine Generators, Combined Cycle and Hydro Generators or generators operated as a synchronous condenser on the average leading reactive power output for at least a 15 consecutive minute period and average lagging reactive power output for at least a 60 consecutive minute period. | Retired | 2009-07-07 | 2012-10-25
1864 | Directory # 10 V1 | Verification of Generator Gross and Net Reactive Power Capability | R19. | The Generator Owner shall verify the Gross Reactive Power Capability and Net Reactive Power Capability of Intermittent power resources (wind, tidal or geo-thermal generators) on performance tracking data. Manufacturers’ data or commissioning data can be used until sufficient performance tracking data is available to verify generator or generation facilities lagging and leading reactive capabilities. | Retired | 2009-07-07 | 2012-10-25
1865 | Directory # 10 V1 | Verification of Generator Gross and Net Reactive Power Capability | R2. | The Transmission Operator shall establish and document a program to periodically verify the Gross Reactive Power Capability and Net Reactive Power Capability of all generators and generation facilities that are subject to periodic seasonal Gross Reactive Power Capability and Net Reactive Power Capability verification. | Retired | 2009-07-07 | 2012-10-25
1866 | Directory # 10 V1 | Verification of Generator Gross and Net Reactive Power Capability | R20. | The Generator Owner shall verify the Gross Reactive Power Capability and Net Reactive Power Capability for multiple generator facilities when limited by common elements on the reactive power capability of the facility and not the sum of the capabilities of the individual generators. | Retired | 2009-07-07 | 2012-10-25
1867 | Directory # 10 V1 | Verification of Generator Gross and Net Reactive Power Capability | R21. | The Generator Owner shall identify any equipment or other factor that will limit the capability of the generator or generation facility to meet its Declared Gross Reactive Power Capability or Declared Net Reactive Power Capability. | Retired | 2009-07-07 | 2012-10-25
1868 | Directory # 10 V1 | Verification of Generator Gross and Net Reactive Power Capability | R22. | The Generator Owner shall notify the Transmission Operator and request an exemption if it cannot conduct seasonal capability testing of a generator or generation facility for any of the reasons listed below. • Adverse impact on transmission system reliability • Potential damage to transmission system or generator equipment • Environment conditions • Governmental regulatory or operating license limitations • An extended outage to the generator or generation facility | Retired | 2009-07-07 | 2012-10-25
1869 | Directory # 10 V1 | Verification of Generator Gross and Net Reactive Power Capability | R23. | The Transmission Operator shall, within 30 calendar days of receiving notification from a Generator Owner that it is requesting an exemption because it cannot perform verification for the required seasonal period, notify the Generator Owner whether its generator will be exempted from the seasonal capability testing. Where the exemption is approved, the Transmission Operator shall coordinate with the Generator Owner to reschedule the verification for the next seasonal verification period. | Retired | 2009-07-07 | 2012-10-25
1870 | Directory # 10 V1 | Verification of Generator Gross and Net Reactive Power Capability | R24. | The Generator Owner for a generator or generation facility exempted from seasonal capability testing shall submit the following to the Transmission Operator: • For existing generators, generator operation records, manufacturer data, or performance tracking for the previous applicable seasonal verification period for this generator or generation facility. • Engineering analysis in conjunction with performance tracking data to justify any difference between a generator's or generation facility’s declared capability and previous applicable seasonal performance tracking data. • For new generators only, commissioning data. | Retired | 2009-07-07 | 2012-10-25
1871 | Directory # 10 V1 | Verification of Generator Gross and Net Reactive Power Capability | R3. | The Transmission Operator shall provide any changes to its verification process to the Generator Owners within 30 calendar days of issue. | Retired | 2009-07-07 | 2012-10-25
1872 | Directory # 10 V1 | Verification of Generator Gross and Net Reactive Power Capability | R4. | The Transmission Operator shall establish and document requirements for a Generator Owner to notify the Transmission Operator within a specified time period when its generator or generation facility cannot achieve the Declared Gross Reactive Power Capability or Declared Net Reactive Power Capability because of equipment issues. | Retired | 2009-07-07 | 2012-10-25
1873 | Directory # 10 V1 | Verification of Generator Gross and Net Reactive Power Capability | R5. | The Transmission Operator shall establish and document a time frame for the Generator Owner to address equipment issues that result in a generator or generation facility not achieving the Declared Gross Reactive Power Capability and Declared Net Reactive Power Capability. | Retired | 2009-07-07 | 2012-10-25
1874 | Directory # 10 V1 | Verification of Generator Gross and Net Reactive Power Capability | R6. | The Transmission Operator shall establish and document the real power level at which the verification shall be performed, recognizing that the verification of lagging and leading reactive power capabilities should normally be performed during on-peak and off-peak hours, respectively. | Retired | 2009-07-07 | 2012-10-25
1875 | Directory # 10 V1 | Verification of Generator Gross and Net Reactive Power Capability | R7. | The Transmission Operator shall establish and document those intermittent or small generating units whose capability may be represented by verification results of a single generating unit. | Retired | 2009-07-07 | 2012-10-25
1876 | Directory # 10 V1 | Verification of Generator Gross and Net Reactive Power Capability | R8. | The Transmission Operator shall request Generator Owners to verify the seasonal Gross Reactive Power Capability and Net Reactive Power Capability of their generators or generation facilities that are subject to periodic seasonal Gross Reactive Power Capability and Net Reactive Power Capability verification every five (5) years or more frequently as required by the Transmission Operator. The two (2) capability seasons are defined as summer and winter as specified by the Transmission Operator. | Retired | 2009-07-07 | 2012-10-25
1877 | Directory # 10 V1 | Verification of Generator Gross and Net Reactive Power Capability | R9. | If a Transmission Operator determines that only one seasonal generating capability value is required for NPCC Bulk Power System reliability analysis, then periodic verification will be required only for that particular season. | Retired | 2009-07-07 | 2012-10-25
1878 | Directory # 10 V2 | Verification of Generator Gross and Net Reactive Power Capability | R1. | Transmission Operators shall develop and maintain documentation of those generators or generation facilities that must verify the Gross Reactive Power Capability and Net Reactive Power Capability for the summer and winter capability seasons. The documentation maintained by the Transmission Operator shall include the following: | Retired | 2012-10-26 | 2016-10-12
1879 | Directory # 10 V2 | Verification of Generator Gross and Net Reactive Power Capability | R1.1. | All generators or generation facilities Declared Gross Reactive Power Capability and Declared Net Reactive Power Capability and seasonal auxiliary load reactive power requirements. (Reference Appendix B). | Retired | 2012-10-26 | 2016-10-12
1880 | Directory # 10 V2 | Verification of Generator Gross and Net Reactive Power Capability | R1.2. | All generators or generation facilities Verified Gross Reactive Power Capability and Verified Net Reactive Power Capability, verification date and method of verification. | Retired | 2012-10-26 | 2016-10-12
1881 | Directory # 10 V2 | Verification of Generator Gross and Net Reactive Power Capability | R1.3. | Discrepancies between a Generator Owner’s declared and verified Gross Reactive Power Capability and Net Reactive Power Capability, the reason for such discrepancies and the Generator Owner’s plan to address the discrepancies. | Retired | 2012-10-26 | 2016-10-12
1882 | Directory # 10 V2 | Verification of Generator Gross and Net Reactive Power Capability | R1.4. | Generator Owner supplied Gross Reactive Power Capability and Net Reactive Power Capability testing, manufacturer data, performance tracking or operating historical data, certification documentation, as specified by the Transmission Operator. | Retired | 2012-10-26 | 2016-10-12
1883 | Directory # 10 V2 | Verification of Generator Gross and Net Reactive Power Capability | R1.5. | Generators or generation facilities exempted from the verification requirements and the basis for their exemption (see Section 1.5). | Retired | 2012-10-26 | 2016-10-12
1884 | Directory # 10 V2 | Verification of Generator Gross and Net Reactive Power Capability | R10. | If a Transmission Operator determines that the difference between the Declared Gross Reactive Power Capability and the Declared Net Reactive Power Capability of a generator or generation facility is insignificant for NPCC Bulk Power System reliability analysis, then periodic verification will be required for only one numerical value. | Retired | 2012-10-26 | 2016-10-12
1885 | Directory # 10 V2 | Verification of Generator Gross and Net Reactive Power Capability | R11. | If a Transmission Operator determines that only the lagging or leading Gross Reactive Power Capability and Net Reactive Power Capability of a generator or generation facility is required for NPCC Bulk Power System reliability analysis, then periodic verification will be required only for that specific reactive power capability value. | Retired | 2012-10-26 | 2016-10-12
1886 | Directory # 10 V2 | Verification of Generator Gross and Net Reactive Power Capability | R12. | The Generator Owner shall provide generator or generation facility Declared Gross Reactive Power Capability and Declared Net Reactive Power Capability to the Transmission Operator. | Retired | 2012-10-26 | 2016-10-12
1887 | Directory # 10 V2 | Verification of Generator Gross and Net Reactive Power Capability | R13. | The Generator Owner shall provide evidence, upon request, to the Transmission Operator that the generator or generation facility Gross Reactive Power Capability and Net Reactive Power Capability have been verified. | Retired | 2012-10-26 | 2016-10-12
1888 | Directory # 10 V2 | Verification of Generator Gross and Net Reactive Power Capability | R14. | The Generator Owner shall report to the Transmission Operator any discrepancies between Declared and Verified Gross Reactive Power Capability and Net Reactive Power Capability within a time frame specified by the Transmission Operator and develop and implement a plan to resolve the discrepancies. | Retired | 2012-10-26 | 2016-10-12
1889 | Directory # 10 V2 | Verification of Generator Gross and Net Reactive Power Capability | R15. | The Generator Owner shall determine and report to the Transmission Operator the generator or generation facility reactive power seasonal auxiliary loads (including common station loads). | Retired | 2012-10-26 | 2016-10-12
1890 | Directory # 10 V2 | Verification of Generator Gross and Net Reactive Power Capability | R16. | The Generator Owner shall comply with Transmission Operator requests for periodic verification of Gross Reactive Power Capability and Net Reactive Power Capability of their generators or generation facilities. | Retired | 2012-10-26 | 2016-10-12
1891 | Directory # 10 V2 | Verification of Generator Gross and Net Reactive Power Capability | R17. | The Generator Owner shall verify the Gross Reactive Power Capability and Net Reactive Power Capability of their generators or generation facilities according to their types. As specified by the Transmission Operator, the verification shall include any of the following: • Testing, • Use of operating historical data, • Commissioning data (for new generators only), • Performance tracking data acquired during the same seasonal capability period. | Retired | 2012-10-26 | 2016-10-12
1892 | Directory # 10 V2 | Verification of Generator Gross and Net Reactive Power Capability | R18. | The Generator Owner shall verify the Gross Reactive Power Capability and Net Reactive Power Capability of Thermal Generators, Internal Combustion Generators, Gas Turbine Generators, Combined Cycle and Hydro Generators or generators operated as a synchronous condenser on the average leading reactive power output for at least a 15 consecutive minute period and average lagging reactive power output for at least a 60 consecutive minute period. | Retired | 2012-10-26 | 2016-10-12
1893 | Directory # 10 V2 | Verification of Generator Gross and Net Reactive Power Capability | R19. | The Generator Owner shall verify the Gross Reactive Power Capability and Net Reactive Power Capability of Intermittent power resources (wind, tidal or geo-thermal generators) on performance tracking data. Manufacturers’ data or commissioning data can be used until sufficient performance tracking data is available to verify generator or generation facilities lagging and leading reactive capabilities. | Retired | 2012-10-26 | 2016-10-12
1894 | Directory # 10 V2 | Verification of Generator Gross and Net Reactive Power Capability | R2. | The Transmission Operator shall establish and document a program to periodically verify the Gross Reactive Power Capability and Net Reactive Power Capability of all generators and generation facilities that are subject to periodic seasonal Gross Reactive Power Capability and Net Reactive Power Capability verification. | Retired | 2012-10-26 | 2016-10-12
1895 | Directory # 10 V2 | Verification of Generator Gross and Net Reactive Power Capability | R20. | The Generator Owner shall verify the Gross Reactive Power Capability and Net Reactive Power Capability for multiple generator facilities when limited by common elements on the reactive power capability of the facility and not the sum of the capabilities of the individual generators. | Retired | 2012-10-26 | 2016-10-12
1896 | Directory # 10 V2 | Verification of Generator Gross and Net Reactive Power Capability | R21. | The Generator Owner shall identify any equipment or other factor that will limit the capability of the generator or generation facility to meet its Declared Gross Reactive Power Capability or Declared Net Reactive Power Capability. | Retired | 2012-10-26 | 2016-10-12
1897 | Directory # 10 V2 | Verification of Generator Gross and Net Reactive Power Capability | R22. | The Generator Owner shall notify the Transmission Operator and request an exemption if it cannot conduct seasonal capability testing of a generator or generation facility for any of the reasons listed below. • Adverse impact on transmission system reliability • Potential damage to transmission system or generator equipment • Environment conditions • Governmental regulatory or operating license limitations • An extended outage to the generator or generation facility | Retired | 2012-10-26 | 2016-10-12
1898 | Directory # 10 V2 | Verification of Generator Gross and Net Reactive Power Capability | R23. | The Transmission Operator shall, within 30 calendar days of receiving notification from a Generator Owner that it is requesting an exemption because it cannot perform verification for the required seasonal period, notify the Generator Owner whether its generator will be exempted from the seasonal capability testing. Where the exemption is approved, the Transmission Operator shall coordinate with the Generator Owner to reschedule the verification for the next seasonal verification period. | Retired | 2012-10-26 | 2016-10-12
1899 | Directory # 10 V2 | Verification of Generator Gross and Net Reactive Power Capability | R24. | The Generator Owner for a generator or generation facility exempted from seasonal capability testing shall submit the following to the Transmission Operator: • For existing generators, generator operation records, manufacturer data, or performance tracking for the previous applicable seasonal verification period for this generator or generation facility. • Engineering analysis in conjunction with performance tracking data to justify any difference between a generator's or generation facility’s declared capability and previous applicable seasonal performance tracking data. • For new generators only, commissioning data. | Retired | 2012-10-26 | 2016-10-12
1900 | Directory # 10 V2 | Verification of Generator Gross and Net Reactive Power Capability | R3. | The Transmission Operator shall provide any changes to its verification process to the Generator Owners within 30 calendar days of issue. | Retired | 2012-10-26 | 2016-10-12
1901 | Directory # 10 V2 | Verification of Generator Gross and Net Reactive Power Capability | R4. | The Transmission Operator shall establish and document requirements for a Generator Owner to notify the Transmission Operator within a specified time period when its generator or generation facility cannot achieve the Declared Gross Reactive Power Capability or Declared Net Reactive Power Capability because of equipment issues. | Retired | 2012-10-26 | 2016-10-12
1902 | Directory # 10 V2 | Verification of Generator Gross and Net Reactive Power Capability | R5. | The Transmission Operator shall establish and document a time frame for the Generator Owner to address equipment issues that result in a generator or generation facility not achieving the Declared Gross Reactive Power Capability and Declared Net Reactive Power Capability. | Retired | 2012-10-26 | 2016-10-12
1903 | Directory # 10 V2 | Verification of Generator Gross and Net Reactive Power Capability | R6. | The Transmission Operator shall establish and document the real power level at which the verification shall be performed, recognizing that the verification of lagging and leading reactive power capabilities should normally be performed during on-peak and off-peak hours, respectively. | Retired | 2012-10-26 | 2016-10-12
1904 | Directory # 10 V2 | Verification of Generator Gross and Net Reactive Power Capability | R7. | The Transmission Operator shall establish and document those intermittent or small generating units whose capability may be represented by verification results of a single generating unit. | Retired | 2012-10-26 | 2016-10-12
1905 | Directory # 10 V2 | Verification of Generator Gross and Net Reactive Power Capability | R8. | The Transmission Operator shall request Generator Owners to verify the seasonal Gross Reactive Power Capability and Net Reactive Power Capability of their generators or generation facilities that are subject to periodic seasonal Gross Reactive Power Capability and Net Reactive Power Capability verification every five (5) years or more frequently as required by the Transmission Operator. The two (2) capability seasons are defined as summer and winter as specified by the Transmission Operator. | Retired | 2012-10-26 | 2016-10-12
1906 | Directory # 10 V2 | Verification of Generator Gross and Net Reactive Power Capability | R9. | If a Transmission Operator determines that only one seasonal generating capability value is required for NPCC Bulk Power System reliability analysis, then periodic verification will be required only for that particular season. | Retired | 2012-10-26 | 2016-10-12
1907 | Directory # 10 V3 | Verification of Generator Gross and Net Reactive Power Capability | R1. | Transmission Operators shall develop and maintain documentation of those generators or generation facilities that must verify the Gross Reactive Power Capability and Net Reactive Power Capability for the summer and winter capability seasons. The documentation maintained by the Transmission Operator shall include the following: | Retired | 2016-10-13 | 2019-07-01
1908 | Directory # 10 V3 | Verification of Generator Gross and Net Reactive Power Capability | R1.1. | All generators or generation facilities Declared Gross Reactive Power Capability and Declared Net Reactive Power Capability and seasonal auxiliary load reactive power requirements. (Reference Appendix B). | Retired | 2016-10-13 | 2019-07-01
1909 | Directory # 10 V3 | Verification of Generator Gross and Net Reactive Power Capability | R1.2. | All generators or generation facilities Verified Gross Reactive Power Capability and Verified Net Reactive Power Capability, verification date and method of verification. | Retired | 2016-10-13 | 2019-07-01
1910 | Directory # 10 V3 | Verification of Generator Gross and Net Reactive Power Capability | R1.3. | Discrepancies between a Generator Owner’s declared and verified Gross Reactive Power Capability and Net Reactive Power Capability, the reason for such discrepancies and the Generator Owner’s plan to address the discrepancies. | Retired | 2016-10-13 | 2019-07-01
1911 | Directory # 10 V3 | Verification of Generator Gross and Net Reactive Power Capability | R1.4. | Generator Owner supplied Gross Reactive Power Capability and Net Reactive Power Capability testing, manufacturer data, performance tracking or operating historical data, certification documentation, as specified by the Transmission Operator. | Retired | 2016-10-13 | 2019-07-01
1912 | Directory # 10 V3 | Verification of Generator Gross and Net Reactive Power Capability | R1.5. | Generators or generation facilities exempted from the verification requirements and the basis for their exemption (see Section 1.5). | Retired | 2016-10-13 | 2019-07-01
1913 | Directory # 10 V3 | Verification of Generator Gross and Net Reactive Power Capability | R10. | If a Transmission Operator determines that the difference between the Declared Gross Reactive Power Capability and the Declared Net Reactive Power Capability of a generator or generation facility is insignificant for NPCC Bulk Power System reliability analysis, then periodic verification will be required for only one numerical value. | Retired | 2016-10-13 | 2019-07-01
1914 | Directory # 10 V3 | Verification of Generator Gross and Net Reactive Power Capability | R11. | If a Transmission Operator determines that only the lagging or leading Gross Reactive Power Capability and Net Reactive Power Capability of a generator or generation facility is required for NPCC Bulk Power System reliability analysis, then periodic verification will be required only for that specific reactive power capability value. | Retired | 2016-10-13 | 2019-07-01
1915 | Directory # 10 V3 | Verification of Generator Gross and Net Reactive Power Capability | R12. | The Generator Owner shall provide generator or generation facility Declared Gross Reactive Power Capability and Declared Net Reactive Power Capability to the Transmission Operator. | Retired | 2016-10-13 | 2019-07-01
1916 | Directory # 10 V3 | Verification of Generator Gross and Net Reactive Power Capability | R13. | The Generator Owner shall provide evidence, upon request, to the Transmission Operator that the generator or generation facility Gross Reactive Power Capability and Net Reactive Power Capability have been verified. | Retired | 2016-10-13 | 2019-07-01
1917 | Directory # 10 V3 | Verification of Generator Gross and Net Reactive Power Capability | R14. | The Generator Owner shall report to the Transmission Operator any discrepancies between Declared and Verified Gross Reactive Power Capability and Net Reactive Power Capability within a time frame specified by the Transmission Operator and develop and implement a plan to resolve the discrepancies. | Retired | 2016-10-13 | 2019-07-01
1918 | Directory # 10 V3 | Verification of Generator Gross and Net Reactive Power Capability | R15. | The Generator Owner shall determine and report to the Transmission Operator the generator or generation facility reactive power seasonal auxiliary loads (including common station loads). | Retired | 2016-10-13 | 2019-07-01
1919 | Directory # 10 V3 | Verification of Generator Gross and Net Reactive Power Capability | R16. | The Generator Owner shall comply with Transmission Operator requests for periodic verification of Gross Reactive Power Capability and Net Reactive Power Capability of their generators or generation facilities. | Retired | 2016-10-13 | 2019-07-01
1920 | Directory # 10 V3 | Verification of Generator Gross and Net Reactive Power Capability | R17. | The Generator Owner shall verify the Gross Reactive Power Capability and Net Reactive Power Capability of their generators or generation facilities according to their types. As specified by the Transmission Operator, the verification shall include any of the following: • Testing, • Use of operating historical data, • Commissioning data (for new generators only), • Performance tracking data acquired during the same seasonal capability period. | Retired | 2016-10-13 | 2019-07-01
1921 | Directory # 10 V3 | Verification of Generator Gross and Net Reactive Power Capability | R18. | The Generator Owner shall verify the Gross Reactive Power Capability and Net Reactive Power Capability of Thermal Generators, Internal Combustion Generators, Gas Turbine Generators, Combined Cycle and Hydro Generators or generators operated as a synchronous condenser on the average leading reactive power output for at least a 15 consecutive minute period and average lagging reactive power output for at least a 60 consecutive minute period. | Retired | 2016-10-13 | 2019-07-01
1922 | Directory # 10 V3 | Verification of Generator Gross and Net Reactive Power Capability | R19. | The Generator Owner shall verify the Gross Reactive Power Capability and Net Reactive Power Capability of Intermittent power resources (wind, tidal or geo-thermal generators) on performance tracking data. Manufacturers’ data or commissioning data can be used until sufficient performance tracking data is available to verify generator or generation facilities lagging and leading reactive capabilities. | Retired | 2016-10-13 | 2019-07-01
1923 | Directory # 10 V3 | Verification of Generator Gross and Net Reactive Power Capability | R2. | The Transmission Operator shall establish and document a program to periodically verify the Gross Reactive Power Capability and Net Reactive Power Capability of all generators and generation facilities that are subject to periodic seasonal Gross Reactive Power Capability and Net Reactive Power Capability verification. | Retired | 2016-10-13 | 2019-07-01
1924 | Directory # 10 V3 | Verification of Generator Gross and Net Reactive Power Capability | R20. | The Generator Owner shall verify the Gross Reactive Power Capability and Net Reactive Power Capability for multiple generator facilities when limited by common elements on the reactive power capability of the facility and not the sum of the capabilities of the individual generators. | Retired | 2016-10-13 | 2019-07-01
1925 | Directory # 10 V3 | Verification of Generator Gross and Net Reactive Power Capability | R21. | The Generator Owner shall identify any equipment or other factor that will limit the capability of the generator or generation facility to meet its Declared Gross Reactive Power Capability or Declared Net Reactive Power Capability. | Retired | 2016-10-13 | 2019-07-01
1926 | Directory # 10 V3 | Verification of Generator Gross and Net Reactive Power Capability | R22. | The Generator Owner shall notify the Transmission Operator and request an exemption if it cannot conduct seasonal capability testing of a generator or generation facility for any of the reasons listed below. • Adverse impact on transmission system reliability • Potential damage to transmission system or generator equipment • Environment conditions • Governmental regulatory or operating license limitations • An extended outage to the generator or generation facility | Retired | 2016-10-13 | 2019-07-01
1927 | Directory # 10 V3 | Verification of Generator Gross and Net Reactive Power Capability | R23. | The Transmission Operator shall, within 30 calendar days of receiving notification from a Generator Owner that it is requesting an exemption because it cannot perform verification for the required seasonal period, notify the Generator Owner whether its generator will be exempted from the seasonal capability testing. Where the exemption is approved, the Transmission Operator shall coordinate with the Generator Owner to reschedule the verification for the next seasonal verification period. | Retired | 2016-10-13 | 2019-07-01
1928 | Directory # 10 V3 | Verification of Generator Gross and Net Reactive Power Capability | R24. | The Generator Owner for a generator or generation facility exempted from seasonal capability testing shall submit the following to the Transmission Operator: • For existing generators, generator operation records, manufacturer data, or performance tracking for the previous applicable seasonal verification period for this generator or generation facility. • Engineering analysis in conjunction with performance tracking data to justify any difference between a generator's or generation facility’s declared capability and previous applicable seasonal performance tracking data. • For new generators only, commissioning data. | Retired | 2016-10-13 | 2019-07-01
1929 | Directory # 10 V3 | Verification of Generator Gross and Net Reactive Power Capability | R3. | The Transmission Operator shall provide any changes to its verification process to the Generator Owners within 30 calendar days of issue. | Retired | 2016-10-13 | 2019-07-01
1930 | Directory # 10 V3 | Verification of Generator Gross and Net Reactive Power Capability | R4. | The Transmission Operator shall establish and document requirements for a Generator Owner to notify the Transmission Operator within a specified time period when its generator or generation facility cannot achieve the Declared Gross Reactive Power Capability or Declared Net Reactive Power Capability because of equipment issues. | Retired | 2016-10-13 | 2019-07-01
1931 | Directory # 10 V3 | Verification of Generator Gross and Net Reactive Power Capability | R5. | The Transmission Operator shall establish and document a time frame for the Generator Owner to address equipment issues that result in a generator or generation facility not achieving the Declared Gross Reactive Power Capability and Declared Net Reactive Power Capability. | Retired | 2016-10-13 | 2019-07-01
1932 | Directory # 10 V3 | Verification of Generator Gross and Net Reactive Power Capability | R6. | The Transmission Operator shall establish and document the real power level at which the verification shall be performed, recognizing that the verification of lagging and leading reactive power capabilities should normally be performed during on-peak and off-peak hours, respectively. | Retired | 2016-10-13 | 2019-07-01
1933 | Directory # 10 V3 | Verification of Generator Gross and Net Reactive Power Capability | R7. | The Transmission Operator shall establish and document those intermittent or small generating units whose capability may be represented by verification results of a single generating unit. | Retired | 2016-10-13 | 2019-07-01
1934 | Directory # 10 V3 | Verification of Generator Gross and Net Reactive Power Capability | R8. | The Transmission Operator shall request Generator Owners to verify the seasonal Gross Reactive Power Capability and Net Reactive Power Capability of their generators or generation facilities that are subject to periodic seasonal Gross Reactive Power Capability and Net Reactive Power Capability verification every five (5) years or more frequently as required by the Transmission Operator. The two (2) capability seasons are defined as summer and winter as specified by the Transmission Operator. | Retired | 2016-10-13 | 2019-07-01
1935 | Directory # 10 V3 | Verification of Generator Gross and Net Reactive Power Capability | R9. | If a Transmission Operator determines that only one seasonal generating capability value is required for NPCC Bulk Power System reliability analysis, then periodic verification will be required only for that particular season. | Retired | 2016-10-13 | 2019-07-01
56 | Directory # 11 | Disturbance Monitoring Equipment Criteria | R1. | Each Transmission Owner and Generator Owner shall provide SER capability. This capability shall: | Retired | 2016-11-25 | 2020-11-07 | TO, GO
57 | Directory # 11 | Disturbance Monitoring Equipment Criteria | R1.1. | Be provided at all BPS facilities. | Retired | 2016-11-25 | 2020-11-07 | TO, GO
58 | Directory # 11 | Disturbance Monitoring Equipment Criteria | R1.2. | Be provided at generating facilities where the generator step up transformer is a BPS element. | Retired | 2016-11-25 | 2020-11-07 | TO, GO
59 | Directory # 11 | Disturbance Monitoring Equipment Criteria | R1.3. | Monitor and record status change for the following: | Retired | 2016-11-25 | 2020-11-07 | TO, GO
60 | Directory # 11 | Disturbance Monitoring Equipment Criteria | R1.3.1. | Transmission and generator circuit breaker positions | Retired | 2016-11-25 | 2020-11-07 | TO, GO
61 | Directory # 11 | Disturbance Monitoring Equipment Criteria | R1.3.2. | Protective relay tripping for all protection groups that operate to trip circuit breakers | Retired | 2016-11-25 | 2020-11-07 | TO, GO
62 | Directory # 11 | Disturbance Monitoring Equipment Criteria | R1.3.3. | Teleprotection keying and receive | Retired | 2016-11-25 | 2020-11-07 | TO, GO
63 | Directory # 11 | Disturbance Monitoring Equipment Criteria | R2. | Each Transmission Owner shall have fault recording capability that determines the current zero time for loss of BPS elements. | Retired | 2016-11-25 | 2020-11-07 | GO, TO
64 | Directory # 11 | Disturbance Monitoring Equipment Criteria | R3. | Each Transmission Owner shall be able to determine fault recording data for the following elements at facilities, where FR is required as per R2 above: | Retired | 2016-11-25 | 2020-11-07 | GO, TO
65 | Directory # 11 | Disturbance Monitoring Equipment Criteria | R3.1. | All transmission lines. | Retired | 2016-11-25 | 2020-11-07 | GO, TO
66 | Directory # 11 | Disturbance Monitoring Equipment Criteria | R3.2. | Transformers with the primary terminal and at least one secondary terminal operated at 100 kV or higher and phase shifters (phase angle regulators). | Retired | 2016-11-25 | 2020-11-07 | GO, TO
67 | Directory # 11 | Disturbance Monitoring Equipment Criteria | R3.3. | Shunt capacitors, shunt reactors. | Retired | 2016-11-25 | 2020-11-07 | GO, TO
68 | Directory # 11 | Disturbance Monitoring Equipment Criteria | R3.4. | Generator interconnection where the step-up transformer is a BPS element. This includes monitoring the high voltage or low voltage terminal of the step-up transformer. | Retired | 2016-11-25 | 2020-11-07 | GO, TO
69 | Directory # 11 | Disturbance Monitoring Equipment Criteria | R3.5. | Dynamic VAR Devices. | Retired | 2016-11-25 | 2020-11-07 | GO, TO
70 | Directory # 11 | Disturbance Monitoring Equipment Criteria | R3.6. | HVDC terminals. | Retired | 2016-11-25 | 2020-11-07 | GO, TO
71 | Directory # 11 | Disturbance Monitoring Equipment Criteria | R4. | Each Transmission Owner shall record for faults, sufficient electrical quantities for each element in R3 to determine the following: | Retired | 2016-11-25 | 2020-11-07 | GO, TO
72 | Directory # 11 | Disturbance Monitoring Equipment Criteria | R4.1. | Three phase-to-neutral voltages. (Common bus-side voltages may be used.) | Retired | 2016-11-25 | 2020-11-07 | GO, TO
73 | Directory # 11 | Disturbance Monitoring Equipment Criteria | R4.2. | Three phase currents and neutral currents. | Retired | 2016-11-25 | 2020-11-07 | GO, TO
74 | Directory # 11 | Disturbance Monitoring Equipment Criteria | R4.3. | Polarizing currents and voltages, if used. | Retired | 2016-11-25 | 2020-11-07 | GO, TO
75 | Directory # 11 | Disturbance Monitoring Equipment Criteria | R4.4. | Frequency. | Retired | 2016-11-25 | 2020-11-07 | GO, TO
76 | Directory # 11 | Disturbance Monitoring Equipment Criteria | R5. | Each Transmission Owner shall provide fault recording with the following capabilities: | Retired | 2016-11-25 | 2020-11-07 | GO, TO
77 | Directory # 11 | Disturbance Monitoring Equipment Criteria | R5.1. | Each FR record duration shall be a minimum of one (1) second with at least 2 cycles of pre-trigger data. | Retired | 2016-11-25 | 2020-11-07 | GO, TO
78 | Directory # 11 | Disturbance Monitoring Equipment Criteria | R5.2. | Each FR shall have a minimum recording rate of 16 samples per cycle. | Retired | 2016-11-25 | 2020-11-07 | GO, TO
79 | Directory # 11 | Disturbance Monitoring Equipment Criteria | R5.3. | Each FR shall be set to trigger for at least the following: | Retired | 2016-11-25 | 2020-11-07 | GO, TO
80 | Directory # 11 | Disturbance Monitoring Equipment Criteria | R5.3.1. | Monitored phase overcurrents set at 1.5 pu or less of rated CT secondary current or protective relay tripping for all protection groups. | Retired | 2016-11-25 | 2020-11-07 | GO, TO
55 | Directory # 11 | Disturbance Monitoring Equipment Criteria | R5.3.2. | Neutral (residual) overcurrent set at 0.2 pu or less of rated CT secondary current. | Retired | 2016-11-25 | 2020-11-07 | GO, TO
81 | Directory # 11 | Disturbance Monitoring Equipment Criteria | R5.3.3. | Monitored phase undervoltage set at 0.85 pu or greater. | Retired | 2016-11-25 | 2020-11-07 | GO, TO
82 | Directory # 11 | Disturbance Monitoring Equipment Criteria | R5.4. | Document additional triggers and deviations from the settings in 5.3.2 and 5.3.3 when local conditions dictate. | Retired | 2016-11-25 | 2020-11-07 | GO, TO
83 | Directory # 11 | Disturbance Monitoring Equipment Criteria | R6. | Each Transmission Owner and Generator Owner shall time synchronize all SER and FR data for BPS elements to meet the following: | Retired | 2016-11-25 | 2020-11-07 | TO, GO
84 | Directory # 11 | Disturbance Monitoring Equipment Criteria | R6.1. | Synchronization to Coordinated Universal Time (UTC) with or without a local time offset. | Retired | 2016-11-25 | 2020-11-07 | TO, GO
85 | Directory # 11 | Disturbance Monitoring Equipment Criteria | R6.2. | Synchronized device clock accuracy within ± 2 milliseconds of UTC. | Retired | 2016-11-25 | 2020-11-07 | TO, GO
86 | Directory # 11 | Disturbance Monitoring Equipment Criteria | R6.3. | Monthly verification of time synchronization shall be provided, or the loss of time synchronization shall be monitored and alarmed to a control center staffed 24 hours a day, 7 days a week (24/7). | Retired | 2016-11-25 | 2020-11-07 | TO, GO
87 | Directory # 11 | Disturbance Monitoring Equipment Criteria | R7. | FR settings in the software, as outlined in R5, shall be verified every six (6) years. | Retired | 2016-11-25 | 2020-11-07 | TO, GO
88 | Directory # 11 | Disturbance Monitoring Equipment Criteria | R8. | Each Transmission Owner and Generator Owner shall, within 90-calendar days of the discovery of a failure of the recording capability including time synchronization for the SER or FR data, either: • Restore the recording capability, or • Develop and implement a documented corrective action plan. | Retired | 2016-11-25 | 2020-11-07 | TO, GO
89 | Directory # 11 | Disturbance Monitoring Equipment Criteria | R9. | Each Transmission Owner and Generator Owner shall provide, upon request, all SER and FR data for BPS elements to the Responsible Entity, Reliability Coordinator, Planning Coordinator, Regional Entity, or NERC in accordance with the following: | Retired | 2016-11-25 | 2020-11-07 | TO, GO
90 | Directory # 11 | Disturbance Monitoring Equipment Criteria | R9.1. | FR data shall contain all monitored channels. SER records shall contain station name, date, time resolved to milliseconds, SER point name, status. | Retired | 2016-11-25 | 2020-11-07 | TO, GO
91 | Directory # 11 | Disturbance Monitoring Equipment Criteria | R9.2. | Data will be retrievable for the period of 10-calendar days, inclusive of the day the data was recorded. | Retired | 2016-11-25 | 2020-11-07 | TO, GO
92 | Directory # 11 | Disturbance Monitoring Equipment Criteria | R9.3. | Data will be provided within 30-calendar days of a request unless an extension is granted by the requestor. | Retired | 2016-11-25 | 2020-11-07 | TO, GO
93 | Directory # 11 | Disturbance Monitoring Equipment Criteria | R9.4. | SER data will be provided in ASCII Comma Separated Value (CSV) format following Attachment 2 of NERC PRC-002-2. | Retired | 2016-11-25 | 2020-11-07 | TO, GO
94 | Directory # 11 | Disturbance Monitoring Equipment Criteria | R9.5. | FR data will be provided in electronic files that are formatted in conformance with C37.111, (IEEE Standard for Common Format for Transient Data Exchange (COMTRADE), revision C37.111-1999 or later. | Retired | 2016-11-25 | 2020-11-07 | TO, GO
95 | Directory # 11 | Disturbance Monitoring Equipment Criteria | R9.6. | Data files will be named in conformance with C37.232, IEEE Standard for Common Format for Naming Time Sequence Data Files (COMNAME), revision C37.232-2011 or later. | Retired | 2016-11-25 | 2020-11-07 | TO, GO
1661 | Directory # 11 V1 | Disturbance Monitoring Equipment Criteria | R1. | Each Transmission Owner and Generator Owner shall provide SER capability. This capability shall: | Retired | 2020-11-08 | 2022-11-01
1662 | Directory # 11 V1 | Disturbance Monitoring Equipment Criteria | R1.1. | Be provided at all BPS facilities. | Retired | 2020-11-08 | 2022-11-01
1663 | Directory # 11 V1 | Disturbance Monitoring Equipment Criteria | R1.2. | Be provided at generating facilities where the generator step up transformer is a BPS element. | Retired | 2020-11-08 | 2022-11-01
1664 | Directory # 11 V1 | Disturbance Monitoring Equipment Criteria | R1.3. | Monitor and record status change for the following: | Retired | 2020-11-08 | 2022-11-01
1665 | Directory # 11 V1 | Disturbance Monitoring Equipment Criteria | R1.3.1. | Transmission and generator circuit breaker positions | Retired | 2020-11-08 | 2022-11-01
1666 | Directory # 11 V1 | Disturbance Monitoring Equipment Criteria | R1.3.2. | Protective relay tripping for all protection groups that operate to trip circuit breakers | Retired | 2020-11-08 | 2022-11-01
1667 | Directory # 11 V1 | Disturbance Monitoring Equipment Criteria | R1.3.3. | Teleprotection keying and receive | Retired | 2020-11-08 | 2022-11-01
1668 | Directory # 11 V1 | Disturbance Monitoring Equipment Criteria | R2. | Each Transmission Owner shall have fault recording capability that determines the current zero time for loss of BPS elements. | Retired | 2020-11-08 | 2022-11-01
1669 | Directory # 11 V1 | Disturbance Monitoring Equipment Criteria | R3. | Each Transmission Owner shall be able to determine fault recording data for the following elements at facilities, where FR is required as per R2 above: | Retired | 2020-11-08 | 2022-11-01
1670 | Directory # 11 V1 | Disturbance Monitoring Equipment Criteria | R3.1. | All transmission lines. | Retired | 2020-11-08 | 2022-11-01
1671 | Directory # 11 V1 | Disturbance Monitoring Equipment Criteria | R3.2. | Transformers with the primary terminal and at least one secondary terminal operated at 100 kV or higher and phase shifters (phase angle regulators). | Retired | 2020-11-08 | 2022-11-01
1672 | Directory # 11 V1 | Disturbance Monitoring Equipment Criteria | R3.3. | Shunt capacitors, shunt reactors. | Retired | 2020-11-08 | 2022-11-01
1673 | Directory # 11 V1 | Disturbance Monitoring Equipment Criteria | R3.4. | Generator interconnection where the step-up transformer is a BPS element. This includes monitoring the high voltage or low voltage terminal of the step-up transformer. | Retired | 2020-11-08 | 2022-11-01
1674 | Directory # 11 V1 | Disturbance Monitoring Equipment Criteria | R3.5. | Dynamic VAR Devices. | Retired | 2020-11-08 | 2022-11-01
1675 | Directory # 11 V1 | Disturbance Monitoring Equipment Criteria | R3.6. | HVDC terminals. | Retired | 2020-11-08 | 2022-11-01
1676 | Directory # 11 V1 | Disturbance Monitoring Equipment Criteria | R4. | Each Transmission Owner shall record for faults, sufficient electrical quantities for each element in R3 to determine the following: | Retired | 2020-11-08 | 2022-11-01
1677 | Directory # 11 V1 | Disturbance Monitoring Equipment Criteria | R4.1. | Three phase-to-neutral voltages. (Common bus-side voltages may be used.) | Retired | 2020-11-08 | 2022-11-01
1678 | Directory # 11 V1 | Disturbance Monitoring Equipment Criteria | R4.2. | Three phase currents and neutral currents. | Retired | 2020-11-08 | 2022-11-01
1679 | Directory # 11 V1 | Disturbance Monitoring Equipment Criteria | R4.3. | Polarizing currents and voltages, if used. | Retired | 2020-11-08 | 2022-11-01
1680 | Directory # 11 V1 | Disturbance Monitoring Equipment Criteria | R4.4. | Frequency. | Retired | 2020-11-08 | 2022-11-01
1681 | Directory # 11 V1 | Disturbance Monitoring Equipment Criteria | R5. | Each Transmission Owner shall provide fault recording with the following capabilities: | Retired | 2020-11-08 | 2022-11-01
1682 | Directory # 11 V1 | Disturbance Monitoring Equipment Criteria | R5.1. | Each FR record duration shall be a minimum of one (1) second with at least 2 cycles of pre-trigger data. | Retired | 2020-11-08 | 2022-11-01
1683 | Directory # 11 V1 | Disturbance Monitoring Equipment Criteria | R5.2. | Each FR shall have a minimum recording rate of 16 samples per cycle. | Retired | 2020-11-08 | 2022-11-01
1684 | Directory # 11 V1 | Disturbance Monitoring Equipment Criteria | R5.3. | Each FR shall be set to trigger for at least the following: | Retired | 2020-11-08 | 2022-11-01
1685 | Directory # 11 V1 | Disturbance Monitoring Equipment Criteria | R5.3.1. | Monitored phase overcurrents set at 1.5 pu or less of rated CT secondary current or protective relay tripping for all protection groups. | Retired | 2020-11-08 | 2022-11-01
1686 | Directory # 11 V1 | Disturbance Monitoring Equipment Criteria | R5.3.2. | Neutral (residual) overcurrent set at 0.2 pu or less of rated CT secondary current. | Retired | 2020-11-08 | 2022-11-01
1687 | Directory # 11 V1 | Disturbance Monitoring Equipment Criteria | R5.3.3. | Monitored phase undervoltage set at 0.85 pu or greater. | Retired | 2020-11-08 | 2022-11-01
1688 | Directory # 11 V1 | Disturbance Monitoring Equipment Criteria | R5.4. | Document additional triggers and deviations from the settings in 5.3.2 and 5.3.3 when local conditions dictate. | Retired | 2020-11-08 | 2022-11-01
1689 | Directory # 11 V1 | Disturbance Monitoring Equipment Criteria | R6. | Each Transmission Owner and Generator Owner shall time synchronize all SER and FR data for BPS elements to meet the following: | Retired | 2020-11-08 | 2022-11-01
1690 | Directory # 11 V1 | Disturbance Monitoring Equipment Criteria | R6.1. | Synchronization to Coordinated Universal Time (UTC) with or without a local time offset. | Retired | 2020-11-08 | 2022-11-01
1691 | Directory # 11 V1 | Disturbance Monitoring Equipment Criteria | R6.2. | Synchronized device clock accuracy within ± 2 milliseconds of UTC. | Retired | 2020-11-08 | 2022-11-01
1692 | Directory # 11 V1 | Disturbance Monitoring Equipment Criteria | R6.3. | Monthly verification of time synchronization shall be provided, or the loss of time synchronization shall be monitored and alarmed to a control center staffed 24 hours a day, 7 days a week (24/7). | Retired | 2020-11-08 | 2022-11-01
1693 | Directory # 11 V1 | Disturbance Monitoring Equipment Criteria | R7. | FR settings in the software, as outlined in R5, shall be verified every six (6) years. | Retired | 2020-11-08 | 2022-11-01
1694 | Directory # 11 V1 | Disturbance Monitoring Equipment Criteria | R8. | Each Transmission Owner and Generator Owner shall, within 90-calendar days of the discovery of a failure of the recording capability including time synchronization for the SER or FR data, either: • Restore the recording capability, or • Develop and implement a documented corrective action plan. | Retired | 2020-11-08 | 2022-11-01
1695 | Directory # 11 V1 | Disturbance Monitoring Equipment Criteria | R9. | Each Transmission Owner and Generator Owner shall provide, upon request, all SER and FR data for BPS elements to the Responsible Entity, Reliability Coordinator, Planning Coordinator, Regional Entity, or NERC in accordance with the following: | Retired | 2020-11-08 | 2022-11-01
1696 | Directory # 11 V1 | Disturbance Monitoring Equipment Criteria | R9.1. | FR data shall contain all monitored channels. SER records shall contain station name, date, time resolved to milliseconds, SER point name, status. | Retired | 2020-11-08 | 2022-11-01
1697 | Directory # 11 V1 | Disturbance Monitoring Equipment Criteria | R9.2. | Data will be retrievable for the period of 10-calendar days, inclusive of the day the data was recorded. | Retired | 2020-11-08 | 2022-11-01
1698 | Directory # 11 V1 | Disturbance Monitoring Equipment Criteria | R9.3. | Data will be provided within 30-calendar days of a request unless an extension is granted by the requestor. | Retired | 2020-11-08 | 2022-11-01
1699 | Directory # 11 V1 | Disturbance Monitoring Equipment Criteria | R9.4. | SER data will be provided in ASCII Comma Separated Value (CSV) format following Attachment 2 of NERC PRC-002-2. | Retired | 2020-11-08 | 2022-11-01
1700 | Directory # 11 V1 | Disturbance Monitoring Equipment Criteria | R9.5. | FR data will be provided in electronic files that are formatted in conformance with C37.111, (IEEE Standard for Common Format for Transient Data Exchange (COMTRADE), revision C37.111-1999 or later. | Retired | 2020-11-08 | 2022-11-01
1701 | Directory # 11 V1 | Disturbance Monitoring Equipment Criteria | R9.6. | Data files will be named in conformance with C37.232, IEEE Standard for Common Format for Naming Time Sequence Data Files (COMNAME), revision C37.232-2011 or later. | Retired | 2020-11-08 | 2022-11-01
1702 | Directory # 11 V2 | Disturbance Monitoring Equipment Criteria | R1. | Each Transmission Owner and Generator Owner shall provide SER capability. This capability shall: | Effective | 2022-11-02
1703 | Directory # 11 V2 | Disturbance Monitoring Equipment Criteria | R1.1. | Be provided at all BPS facilities. | Effective | 2022-11-02
1704 | Directory # 11 V2 | Disturbance Monitoring Equipment Criteria | R1.2. | Be provided at generating facilities where the generator step up transformer is a BPS element. | Effective | 2022-11-02
1705 | Directory # 11 V2 | Disturbance Monitoring Equipment Criteria | R1.3. | Monitor and record status change for the following: | Effective | 2022-11-02
1706 | Directory # 11 V2 | Disturbance Monitoring Equipment Criteria | R1.3.1. | Transmission and generator circuit breaker positions | Effective | 2022-11-02
1707 | Directory # 11 V2 | Disturbance Monitoring Equipment Criteria | R1.3.2. | Protective relay tripping for all protection groups that operate to trip circuit breakers | Effective | 2022-11-02
1708 | Directory # 11 V2 | Disturbance Monitoring Equipment Criteria | R1.3.3. | Teleprotection keying and receive | Effective | 2022-11-02
1709 | Directory # 11 V2 | Disturbance Monitoring Equipment Criteria | R2. | Each Transmission Owner shall have fault recording capability that determines the current zero time for loss of BPS elements. | Effective | 2022-11-02
1710 | Directory # 11 V2 | Disturbance Monitoring Equipment Criteria | R3. | Each Transmission Owner shall be able to determine fault recording data for the following elements at facilities, where FR is required as per R2 above: | Effective | 2022-11-02
1711 | Directory # 11 V2 | Disturbance Monitoring Equipment Criteria | R3.1. | All transmission lines. | Effective | 2022-11-02
1712 | Directory # 11 V2 | Disturbance Monitoring Equipment Criteria | R3.2. | Transformers with the primary terminal and at least one secondary terminal operated at 100 kV or higher and phase shifters (phase angle regulators). | Effective | 2022-11-02
1713 | Directory # 11 V2 | Disturbance Monitoring Equipment Criteria | R3.3. | Shunt capacitors, shunt reactors. | Effective | 2022-11-02
1714 | Directory # 11 V2 | Disturbance Monitoring Equipment Criteria | R3.4. | Generator interconnection where the step-up transformer is a BPS element. This includes monitoring the high voltage or low voltage terminal of the step-up transformer. | Effective | 2022-11-02
1715 | Directory # 11 V2 | Disturbance Monitoring Equipment Criteria | R3.5. | Dynamic VAR Devices. | Effective | 2022-11-02
1716 | Directory # 11 V2 | Disturbance Monitoring Equipment Criteria | R3.6. | HVDC terminals. | Effective | 2022-11-02
1717 | Directory # 11 V2 | Disturbance Monitoring Equipment Criteria | R4. | Each Transmission Owner shall record for faults, sufficient electrical quantities for each element in R3 to determine the following: | Effective | 2022-11-02
1718 | Directory # 11 V2 | Disturbance Monitoring Equipment Criteria | R4.1. | Three phase-to-neutral voltages. (Common bus-side voltages may be used.) | Effective | 2022-11-02
1719 | Directory # 11 V2 | Disturbance Monitoring Equipment Criteria | R4.2. | Three phase currents and neutral currents. | Effective | 2022-11-02
1720 | Directory # 11 V2 | Disturbance Monitoring Equipment Criteria | R4.3. | Polarizing currents and voltages, if used. | Effective | 2022-11-02
1721 | Directory # 11 V2 | Disturbance Monitoring Equipment Criteria | R4.4. | Frequency. | Effective | 2022-11-02
1722 | Directory # 11 V2 | Disturbance Monitoring Equipment Criteria | R5. | Each Transmission Owner shall provide fault recording with the following capabilities: | Effective | 2022-11-02
1723 | Directory # 11 V2 | Disturbance Monitoring Equipment Criteria | R5.1. | Each FR record duration shall be a minimum of one (1) second with at least 2 cycles of pre-trigger data. | Effective | 2022-11-02
1724 | Directory # 11 V2 | Disturbance Monitoring Equipment Criteria | R5.2. | Each FR shall have a minimum recording rate of 16 samples per cycle. | Effective | 2022-11-02
1725 | Directory # 11 V2 | Disturbance Monitoring Equipment Criteria | R5.3. | Each FR shall be set to trigger for at least the following: | Effective | 2022-11-02
1726 | Directory # 11 V2 | Disturbance Monitoring Equipment Criteria | R5.3.1. | Monitored phase overcurrents set at 1.5 pu or less of rated CT secondary current or protective relay tripping for all protection groups. | Effective | 2022-11-02
1727 | Directory # 11 V2 | Disturbance Monitoring Equipment Criteria | R5.3.2. | Neutral (residual) overcurrent set at 0.2 pu or less of rated CT secondary current. | Effective | 2022-11-02
1728 | Directory # 11 V2 | Disturbance Monitoring Equipment Criteria | R5.3.3. | Monitored phase undervoltage set at 0.85 pu or greater. | Effective | 2022-11-02
1729 | Directory # 11 V2 | Disturbance Monitoring Equipment Criteria | R5.4. | Document additional triggers and deviations from the settings in 5.3.2 and 5.3.3 when local conditions dictate. | Effective | 2022-11-02
1730 | Directory # 11 V2 | Disturbance Monitoring Equipment Criteria | R6. | Each Transmission Owner and Generator Owner shall time synchronize all SER and FR data for BPS elements to meet the following: | Effective | 2022-11-02
1731 | Directory # 11 V2 | Disturbance Monitoring Equipment Criteria | R6.1. | Synchronization to Coordinated Universal Time (UTC) with or without a local time offset. | Effective | 2022-11-02
1732 | Directory # 11 V2 | Disturbance Monitoring Equipment Criteria | R6.2. | Synchronized device clock accuracy within ± 2 milliseconds of UTC. | Effective | 2022-11-02
1733 | Directory # 11 V2 | Disturbance Monitoring Equipment Criteria | R6.3. | Monthly verification of time synchronization shall be provided, or the loss of time synchronization shall be monitored and alarmed to a control center staffed 24 hours a day, 7 days a week (24/7). | Effective | 2022-11-02
1734 | Directory # 11 V2 | Disturbance Monitoring Equipment Criteria | R7. | FR settings in the software, as outlined in R5, shall be verified every six (6) years. | Effective | 2022-11-02
1735 | Directory # 11 V2 | Disturbance Monitoring Equipment Criteria | R8. | Each Transmission Owner and Generator Owner shall, within 90-calendar days of the discovery of a failure of the recording capability including time synchronization for the SER or FR data, either: • Restore the recording capability, or • Develop and implement a documented corrective action plan. | Effective | 2022-11-02
1736 | Directory # 11 V2 | Disturbance Monitoring Equipment Criteria | R9. | Each Transmission Owner and Generator Owner shall provide, upon request, all SER and FR data for BPS elements to the Responsible Entity, Reliability Coordinator, Planning Coordinator, Regional Entity, or NERC in accordance with the following: | Effective | 2022-11-02
1737 | Directory # 11 V2 | Disturbance Monitoring Equipment Criteria | R9.1. | FR data shall contain all monitored channels. SER records shall contain station name, date, time resolved to milliseconds, SER point name, status. | Effective | 2022-11-02
1738 | Directory # 11 V2 | Disturbance Monitoring Equipment Criteria | R9.2. | Data will be retrievable for the period of 10-calendar days, inclusive of the day the data was recorded. | Effective | 2022-11-02
1739 | Directory # 11 V2 | Disturbance Monitoring Equipment Criteria | R9.3. | Data will be provided within 30-calendar days of a request unless an extension is granted by the requestor. | Effective | 2022-11-02
1740 | Directory # 11 V2 | Disturbance Monitoring Equipment Criteria | R9.4. | SER data will be provided in ASCII Comma Separated Value (CSV) format following Attachment 2 of NERC PRC-002-2. | Effective | 2022-11-02
1741 | Directory # 11 V2 | Disturbance Monitoring Equipment Criteria | R9.5. | FR data will be provided in electronic files that are formatted in conformance with C37.111, (IEEE Standard for Common Format for Transient Data Exchange (COMTRADE), revision C37.111-1999 or later. | Effective | 2022-11-02
1742 | Directory # 11 V2 | Disturbance Monitoring Equipment Criteria | R9.6. | Data files will be named in conformance with C37.232, IEEE Standard for Common Format for Naming Time Sequence Data Files (COMNAME), revision C37.232-2011 or later. | Effective | 2022-11-02
269 | Directory # 2 | Emergency Operations | R1. | The Transmission Operator, Balancing Authority and Reliability Coordinator shall observe normal transfer capabilities unless there is insufficient capacity or voltage support in a Balancing Authority or Transmission Operator area, in which case emergency transfer capabilities may be used prior to shedding firm load. Emergency transfer capabilities shall not be exceeded. | Retired | 2008-10-21 | 2009-06-25 | TOP, RC, BA
97 | Directory # 2 | Emergency Operations | R1.1. | The Transmission Operator, Balancing Authority and Reliability Coordinator shall have documented procedures to indicate the circumstances under which normal and emergency transfer capabilities limits are applied. | Retired | 2008-10-21 | 2009-06-25 | TOP, RC, BA
98 | Directory # 2 | Emergency Operations | R2. | Each Balancing Authority and Transmission Operator shall have the capability to manually shed at least fifty percent of its area load in ten minutes or less. Manual load shedding plans shall not interrupt bulk power system elements. | Retired | 2008-10-21 | 2009-06-25 | TOP, RC, BA
99 | Directory # 2 | Emergency Operations | R2.1. | The Balancing Authority and Transmission Operator shall review manual load shedding procedures at least annually to ensure that the proper amount of load can be shed within the time limits prescribed. | Retired | 2008-10-21 | 2009-06-25 | TOP, RC, BA
836 | Directory # 2 V1 | Emergency Operations | R1. | The Transmission Operator, Balancing Authority and Reliability Coordinator shall observe normal transfer capabilities unless there is insufficient capacity or voltage support in a Balancing Authority or Transmission Operator area, in which case emergency transfer capabilities may be used prior to shedding firm load. Emergency transfer capabilities shall not be exceeded. | Retired | 2009-06-26 | 2010-07-12
837 | Directory # 2 V1 | Emergency Operations | R1.1. | The Transmission Operator, Balancing Authority and Reliability Coordinator shall have documented procedures to indicate the circumstances under which normal and emergency transfer capabilities limits are applied. | Retired | 2009-06-26 | 2010-07-12
838 | Directory # 2 V1 | Emergency Operations | R2. | Each Balancing Authority and Transmission Operator shall have the capability to manually shed at least fifty percent of its area load in ten minutes or less. Manual load shedding plans shall not interrupt bulk power system elements. | Retired | 2009-06-26 | 2010-07-12
839 | Directory # 2 V1 | Emergency Operations | R2.1. | The Balancing Authority and Transmission Operator shall review manual load shedding procedures at least annually to ensure that the proper amount of load can be shed within the time limits prescribed. | Retired | 2009-06-26 | 2010-07-12
840 | Directory # 2 V2 | Emergency Operations | R1. | The Transmission Operator, Balancing Authority and Reliability Coordinator shall observe normal transfer capabilities unless there is insufficient capacity or voltage support in a Balancing Authority or Transmission Operator area, in which case emergency transfer capabilities may be used prior to shedding firm load. Emergency transfer capabilities shall not be exceeded. | Retired | 2010-07-13 | 2014-04-01
841 | Directory # 2 V2 | Emergency Operations | R1.1. | The Transmission Operator, Balancing Authority and Reliability Coordinator shall have documented procedures to indicate the circumstances under which normal and emergency transfer capabilities limits are applied. | Retired | 2010-07-13 | 2014-04-01
842 | Directory # 2 V2 | Emergency Operations | R2. | Each Balancing Authority and Transmission Operator shall have the capability to manually shed at least fifty percent of its area load in ten minutes or less. Manual load shedding plans shall not interrupt bulk power system elements. | Retired | 2010-07-13 | 2014-04-01
843 | Directory # 2 V2 | Emergency Operations | R2.1. | The Balancing Authority and Transmission Operator shall review manual load shedding procedures at least annually to ensure that the proper amount of load can be shed within the time limits prescribed. | Retired | 2010-07-13 | 2014-04-01
369 | Directory # 2 V3 | Emergency Operations | R1. | The Transmission Operator, Balancing Authority and Reliability Coordinator shall observe normal transfer capabilities unless there is insufficient capacity or voltage support in a Balancing Authority or Transmission Operator area, in which case emergency transfer capabilities may be used prior to shedding firm load. Emergency transfer capabilities shall not be exceeded. | Retired | 2014-04-02 | 2014-12-08 | TOP, BA, RC
370 | Directory # 2 V3 | Emergency Operations | R1.1. | The Transmission Operator, Balancing Authority and Reliability Coordinator shall have documented procedures to indicate the circumstances under which normal and emergency transfer capabilities limits are applied. | Retired | 2014-04-02 | 2014-12-08 | TOP, BA, RC
371 | Directory # 2 V3 | Emergency Operations | R2. | Each Balancing Authority and Transmission Operator shall have the capability to manually shed at least fifty percent of its area load in ten minutes or less. Manual load shedding plans shall not interrupt bulk power system elements. | Retired | 2014-04-02 | 2014-12-08 | TOP, BA, RC
372 | Directory # 2 V3 | Emergency Operations | R2.1. | The Balancing Authority and Transmission Operator shall review manual load shedding procedures at least annually to ensure that the proper amount of load can be shed within the time limits prescribed. | Retired | 2014-04-02 | 2014-12-08 | TOP, BA, RC
314 | Directory # 2 V4 | Emergency Operations | R1. | The Transmission Operator, Balancing Authority and Reliability Coordinator shall observe normal transfer capabilities unless there is insufficient capacity or voltage support in a Balancing Authority or Transmission Operator area, in which case emergency transfer capabilities may be used prior to shedding firm load. Emergency transfer capabilities shall not be exceeded. | Retired | 2014-12-09 | 2016-10-12 | TOP, BA, RC
311 | Directory # 2 V4 | Emergency Operations | R1.1. | The Transmission Operator, Balancing Authority and Reliability Coordinator shall have documented procedures to indicate the circumstances under which normal and emergency transfer capabilities limits are applied. | Retired | 2014-12-09 | 2016-10-12 | TOP, BA, RC
312 | Directory # 2 V4 | Emergency Operations | R2. | Each Balancing Authority and Transmission Operator shall have the capability to manually shed at least fifty percent of its area load in ten minutes or less. Manual load shedding plans shall not interrupt bulk power system elements. | Retired | 2014-12-09 | 2016-10-12 | TOP, BA, RC
313 | Directory # 2 V4 | Emergency Operations | R2.1. | The Balancing Authority and Transmission Operator shall review manual load shedding procedures at least annually to ensure that the proper amount of load can be shed within the time limits prescribed. | Retired | 2014-12-09 | 2016-10-12 | TOP, BA, RC
844 | Directory # 2 V5 | Emergency Operations | R1. | The Transmission Operator, Balancing Authority and Reliability Coordinator shall observe normal transfer capabilities unless there is insufficient capacity or voltage support in a Balancing Authority or Transmission Operator area, in which case emergency transfer capabilities may be used prior to shedding firm load. Emergency transfer capabilities shall not be exceeded. | Retired | 2016-10-13 | 2018-06-28
845 | Directory # 2 V5 | Emergency Operations | R1.1. | The Transmission Operator, Balancing Authority and Reliability Coordinator shall have documented procedures to indicate the circumstances under which normal and emergency transfer capabilities limits are applied. | Retired | 2016-10-13 | 2018-06-28
846 | Directory # 2 V5 | Emergency Operations | R2. | Each Balancing Authority and Transmission Operator shall have the capability to manually shed at least fifty percent of its area load in ten minutes or less. Manual load shedding plans shall not interrupt bulk power system elements. | Retired | 2016-10-13 | 2018-06-28
847 | Directory # 2 V5 | Emergency Operations | R2.1. | The Balancing Authority and Transmission Operator shall review manual load shedding procedures at least annually to ensure that the proper amount of load can be shed within the time limits prescribed. | Retired | 2016-10-13 | 2018-06-28
848 | Directory # 2 V6 | Emergency Operations | R1. | The Transmission Operator, Balancing Authority and Reliability Coordinator shall observe normal transfer capabilities unless there is insufficient capacity or voltage support in a Balancing Authority or Transmission Operator area, in which case emergency transfer capabilities may be used prior to shedding firm load. Emergency transfer capabilities shall not be exceeded. | Effective | 2018-06-29
849 | Directory # 2 V6 | Emergency Operations | R1.1. | The Transmission Operator, Balancing Authority and Reliability Coordinator shall have documented procedures to indicate the circumstances under which normal and emergency transfer capabilities limits are applied. | Effective | 2018-06-29
850 | Directory # 2 V6 | Emergency Operations | R2. | Each Balancing Authority and Transmission Operator shall have the capability to manually shed at least fifty percent of its area load in ten minutes or less. Manual load shedding plans shall not interrupt bulk power system elements. | Effective | 2018-06-29
851 | Directory # 2 V6 | Emergency Operations | R2.1. | The Balancing Authority and Transmission Operator shall review manual load shedding procedures at least annually to ensure that the proper amount of load can be shed within the time limits prescribed. | Effective | 2018-06-29
308 | Directory # 5 V1 | Reserve | R1. | Each Balancing Authority shall have ten-minute reserve available to it that is at least equal to its first contingency loss. NPCC ten-minute reserve meets the requirements for the Contingency Reserve requirements within the NERC standards. • If a Balancing Authority becomes deficient in ten-minute reserve or forecasts a deficiency, it shall restore its ten-minute reserve as soon as possible and within the duration specified in the appropriate NERC standard. • If a Balancing Authority cannot restore its ten-minute reserve per requirement R2, it shall minimize the magnitude and duration of the ten-minute reserve deficiency. | Retired | 2010-12-02 | 2014-04-01 | RC, BA, GOP, DP
285 | Directory # 5 V1 | Reserve | R10. | Resources allocating inter-Balancing Area reserve shall not offer the same reserve to more than one acquiring Balancing Authority for the same scheduling interval. | Retired | 2010-12-02 | 2014-04-01 | DP, GOP, BA, RC
286 | Directory # 5 V1 | Reserve | R11. | A Balancing Authority shall ensure that reserve is distributed so that it can be utilized without exceeding applicable element ratings or transfer limitations. | Retired | 2010-12-02 | 2014-04-01 | DP, GOP, BA, RC
287 | Directory # 5 V1 | Reserve | R12. | A Balancing Authority providing reserve to another Balancing Authority through direct procurement, bilateral, multi-lateral operating agreements, or through reserve sharing agreements, shall deliver an increase in energy as requested, up to the amount of reserve agreed upon. | Retired | 2010-12-02 | 2014-04-01 | DP, GOP, BA, RC
288 | Directory # 5 V1 | Reserve | R13. | A Balancing Authority shall not curtail an existing or planned non-recallable energy schedule in order to support the activation of reserve, unless agreed to by all affected Balancing Authorities. | Retired | 2010-12-02 | 2014-04-01 | DP, GOP, BA, RC
289 | Directory # 5 V1 | Reserve | R14. | A Balancing Authority providing or receiving inter-Balancing Area reserve shall meet the following requirements: | Retired | 2010-12-02 | 2014-04-01 | DP, GOP, BA, RC
290 | Directory # 5 V1 | Reserve | R14.1. | Decision-making related to the specific resources to be activated to provide inter-Balancing Area reserve shall be restricted to the affected Balancing Authorities. | Retired | 2010-12-02 | 2014-04-01 | DP, GOP, BA, RC
291 | Directory # 5 V1 | Reserve | R14.2. | The provision of inter-Balancing Area reserve shall be limited to adjacent Balancing Authorities only, unless specifically facilitated by an approved NPCC procedure or multilateral Balancing Authority/Reliability Coordinator procedure. | Retired | 2010-12-02 | 2014-04-01 | DP, GOP, BA, RC
292 | Directory # 5 V1 | Reserve | R14.3. | Shall agree on Interchange Schedule modifications when activating and terminating inter-Balancing Area reserve. | Retired | 2010-12-02 | 2014-04-01 | DP, GOP, BA, RC
293 | Directory # 5 V1 | Reserve | R14.4. | Where Dynamic Transfers are used to activate inter-Balancing Area reserve, it shall be agreed to by the affected Balancing Authorities, and approved by the TFCO. | Retired | 2010-12-02 | 2014-04-01 | DP, GOP, BA, RC
294 | Directory # 5 V1 | Reserve | R15. | A Balancing Authority shall activate inter-Balancing Area reserve within 5 minutes if utilized for a NERC DCS Balancing Contingency Event or a NPCC reportable event. | Retired | 2010-12-02 | 2014-04-01 | DP, GOP, BA, RC
295 | Directory # 5 V1 | Reserve | R16. | A Balancing Authority acquiring inter-Balancing Area reserve shall notify the host Balancing Authority and affected Reliability Coordinators when changes are made to the scheduling of inter-Balancing Area reserve. | Retired | 2010-12-02 | 2014-04-01 | DP, GOP, BA, RC
296 | Directory # 5 V1 | Reserve | R17. | A Balancing Authority providing (allocating or activating) inter- Balancing Area reserve, not as part of a Reserve Sharing Group, shall not count that reserve to meet its own reserve requirement. | Retired | 2010-12-02 | 2014-04-01 | DP, GOP, BA, RC
297 | Directory # 5 V1 | Reserve | R18. | A Balancing Authority providing recallable energy to another Balancing Authority shall advise the other Balancing Authority that the energy is recallable, and shall inform the receiving Balancing Authority of any change to the recallable status of this energy. | Retired | 2010-12-02 | 2014-04-01 | DP, GOP, BA, RC
298 | Directory # 5 V1 | Reserve | R19. | A Balancing Authority shall meet its Operating Reserve requirement using capacity available from resources internal to its Balancing Authority or by using capacity that is deliverable from another Balancing Authority. | Retired | 2010-12-02 | 2014-04-01 | DP, GOP, BA, RC
271 | Directory # 5 V1 | Reserve | R2. | Each Balancing Authority shall have thirty-minute reserve available to it that is at least equal to one-half its second contingency loss. • A Balancing Authority deficient in thirty-minute reserve for four hours, or forecasting a deficiency of any duration beyond a four-hour horizon, shall eliminate the deficiency if possible, | Retired | 2010-12-02 | 2014-04-01 | DP, GOP, BA, RC
299 | Directory # 5 V1 | Reserve | R20. | A Balancing Authority delivering recallable energy to another Balancing Authority may count that energy toward meeting their Operating Reserve requirement. | Retired | 2010-12-02 | 2014-04-01 | DP, GOP, BA, RC
300 | Directory # 5 V1 | Reserve | R21. | A Balancing Authority receiving recallable energy from another Balancing Authority must carry additional Operating Reserve at least equal to the amount of recallable energy being received. | Retired | 2010-12-02 | 2014-04-01 | DP, GOP, BA, RC
301 | Directory # 5 V1 | Reserve | R22. | Balancing Authorities participating in the “Simultaneous Activation of Ten-Minute Reserve”, (SAR) program shall conform to the procedures, as specified in Attachment B. | Retired | 2010-12-02 | 2014-04-01 | DP, GOP, BA, RC
302 | Directory # 5 V1 | Reserve | R23. | Balancing Authorities participating in the “ACE Diversity Interchange”, (ADI) program shall conform to the procedures, as specified in Attachment C. | Retired | 2010-12-02 | 2014-04-01 | DP, GOP, BA, RC
272 | Directory # 5 V1 | Reserve | R3. | A Balancing Authority’s requirement for synchronized reserve available within ten minutes shall be calculated by the twentieth day of each month, for the previous month, and shall be applied at the beginning of the next month. | Retired | 2010-12-02 | 2014-04-01 | DP, GOP, BA, RC
273 | Directory # 5 V1 | Reserve | R4. | A Balancing Authority’s requirement for synchronized reserve available within ten minutes shall be adjusted as follows: | Retired | 2010-12-02 | 2014-04-01 | DP, GOP, BA, RC
274 | Directory # 5 V1 | Reserve | R4.1 | A Balancing Authority’s maximum requirement for synchronized reserve available within ten minutes shall be 100 percent of its ten-minute reserve. A Balancing Authority’s minimum requirement for synchronized reserve available within ten minutes shall be 25 percent of its ten-minute reserve. | Retired | 2010-12-02 | 2014-04-01 | DP, GOP, BA, RC
275 | Directory # 5 V1 | Reserve | R4.2. | A Balancing Authority’s calculated requirement for synchronized reserve available within ten minutes shall increase by 20 percent of the ten-minute reserve requirement for every time it fails to return its ACE to pre-contingency values or to zero within fifteen minutes following the start of a reportable event that is less than a NERC reportable Balancing Contingency Event. Recovery of reporting ACE occurs when a Balancing Authority returns its reporting ACE to pre-contingency values (if it’s pre-contingency reporting ACE was negative) or to zero (if it’s pre-contingency reporting ACE was positive or equal to zero). | Retired | 2010-12-02 | 2014-04-01 | DP, GOP, BA, RC
276 | Directory # 5 V1 | Reserve | R4.3. | A Balancing Authority’s calculated requirement for synchronized reserve available within ten minutes may only be reduced by a maximum of 20 percent of the ten-minute reserve requirement, per month following the implementation month of any synchronized reserve requirement increase per R4.2. R5. If a Balancing Authority becomes deficient in synchronized | Retired | 2010-12-02 | 2014-04-01 | DP, GOP, BA, RC
277 | Directory # 5 V1 | Reserve | R5. | If a Balancing Authority becomes deficient in synchronized reserve available within ten minutes, it shall restore its synchronized reserve available within ten minutes in accordance with R1 for the restoration of ten-minute reserve. Refer to Attachment A for example scenarios of synchronized reserve requirement penalty adjustments. | Retired | 2010-12-02 | 2014-04-01 | DP, GOP, BA, RC
278 | Directory # 5 V1 | Reserve | R6. | A Balancing Authority’s synchronized reserve, ten-minute reserve, and thirty-minute reserve, if activated, shall be sustainable for at least one hour from the time of activation. | Retired | 2010-12-02 | 2014-04-01 | DP, GOP, BA, RC
279 | Directory # 5 V1 | Reserve | R7. | A Balancing Authority shall not count synchronized reserve, ten-minute reserve, or thirty-minute reserve from loads that are already counted in other demand response programs and would result in double counting the same capacity. | Retired | 2010-12-02 | 2014-04-01 | DP, GOP, BA, RC
280 | Directory # 5 V1 | Reserve | R8. | A Balancing Authority shall not count synchronized reserve from a load if the reduction in load is dependent on starting a generator to replace energy that is supplied from the grid. | Retired | 2010-12-02 | 2014-04-01 | DP, GOP, BA, RC
281 | Directory # 5 V1 | Reserve | R9. | The Balancing Authority shall specify the following criteria for resources to be eligible to provide synchronized reserve, ten-minute reserve, or thirty-minute reserve: | Retired | 2010-12-02 | 2014-04-01 | DP, GOP, BA, RC
282 | Directory # 5 V1 | Reserve | R9.1. | Requirements for metering and testing | Retired | 2010-12-02 | 2014-04-01 | DP, GOP, BA, RC
283 | Directory # 5 V1 | Reserve | R9.2. | Requirements for continuously meeting the dispatch instructions | Retired | 2010-12-02 | 2014-04-01 | DP, GOP, BA, RC
284 | Directory # 5 V1 | Reserve | R9.3. | Requirements for operating capabilities and response rates | Retired | 2010-12-02 | 2014-04-01 | DP, GOP, BA, RC
373 | Directory # 5 V2 | Reserve | R1. | Each Balancing Authority shall have ten-minute reserve available to it that is at least equal to its first contingency loss. NPCC ten-minute reserve meets the requirements for the Contingency Reserve requirements within the NERC standards. • If a Balancing Authority becomes deficient in ten-minute reserve or forecasts a deficiency, it shall restore its ten-minute reserve as soon as possible and within the duration specified in the appropriate NERC standard. • If a Balancing Authority cannot restore its ten-minute reserve per requirement R2, it shall minimize the magnitude and duration of the ten-minute reserve deficiency. | Retired | 2014-04-02 | 2019-09-26
388 | Directory # 5 V2 | Reserve | R10. | Resources allocating inter-Balancing Area reserve shall not offer the same reserve to more than one acquiring Balancing Authority for the same scheduling interval. | Retired | 2014-04-02 | 2019-09-26
389 | Directory # 5 V2 | Reserve | R11. | A Balancing Authority shall ensure that reserve is distributed so that it can be utilized without exceeding applicable element ratings or transfer limitations. | Retired | 2014-04-02 | 2019-09-26
390 | Directory # 5 V2 | Reserve | R12. | A Balancing Authority providing reserve to another Balancing Authority through direct procurement, bilateral, multi-lateral operating agreements, or through reserve sharing agreements, shall deliver an increase in energy as requested, up to the amount of reserve agreed upon. | Retired | 2014-04-02 | 2019-09-26
391 | Directory # 5 V2 | Reserve | R13. | A Balancing Authority shall not curtail an existing or planned non-recallable energy schedule in order to support the activation of reserve, unless agreed to by all affected Balancing Authorities. | Retired | 2014-04-02 | 2019-09-26
392 | Directory # 5 V2 | Reserve | R14. | A Balancing Authority providing or receiving inter-Balancing Area reserve shall meet the following requirements: | Retired | 2014-04-02 | 2019-09-26
393 | Directory # 5 V2 | Reserve | R14.1. | Decision-making related to the specific resources to be activated to provide inter-Balancing Area reserve shall be restricted to the affected Balancing Authorities. | Retired | 2014-04-02 | 2019-09-26
394 | Directory # 5 V2 | Reserve | R14.2. | The provision of inter-Balancing Area reserve shall be limited to adjacent Balancing Authorities only, unless specifically facilitated by an approved NPCC procedure or multilateral Balancing Authority/Reliability Coordinator procedure. | Retired | 2014-04-02 | 2019-09-26
395 | Directory # 5 V2 | Reserve | R14.3. | Shall agree on Interchange Schedule modifications when activating and terminating inter-Balancing Area reserve. | Retired | 2014-04-02 | 2019-09-26
396 | Directory # 5 V2 | Reserve | R14.4. | Where Dynamic Transfers are used to activate inter-Balancing Area reserve, it shall be agreed to by the affected Balancing Authorities, and approved by the TFCO. | Retired | 2014-04-02 | 2019-09-26
397 | Directory # 5 V2 | Reserve | R15. | A Balancing Authority shall activate inter-Balancing Area reserve within 5 minutes if utilized for a NERC DCS Balancing Contingency Event or a NPCC reportable event. | Retired | 2014-04-02 | 2019-09-26
398 | Directory # 5 V2 | Reserve | R16. | A Balancing Authority acquiring inter-Balancing Area reserve shall notify the host Balancing Authority and affected Reliability Coordinators when changes are made to the scheduling of inter-Balancing Area reserve. | Retired | 2014-04-02 | 2019-09-26
399 | Directory # 5 V2 | Reserve | R17. | A Balancing Authority providing (allocating or activating) inter- Balancing Area reserve, not as part of a Reserve Sharing Group, shall not count that reserve to meet its own reserve requirement. | Retired | 2014-04-02 | 2019-09-26
400 | Directory # 5 V2 | Reserve | R18. | A Balancing Authority providing recallable energy to another Balancing Authority shall advise the other Balancing Authority that the energy is recallable, and shall inform the receiving Balancing Authority of any change to the recallable status of this energy. | Retired | 2014-04-02 | 2019-09-26
401 | Directory # 5 V2 | Reserve | R19. | A Balancing Authority shall meet its Operating Reserve requirement using capacity available from resources internal to its Balancing Authority or by using capacity that is deliverable from another Balancing Authority. | Retired | 2014-04-02 | 2019-09-26
374 | Directory # 5 V2 | Reserve | R2. | Each Balancing Authority shall have thirty-minute reserve available to it that is at least equal to one-half its second contingency loss. A Balancing Authority deficient in thirty-minute reserve for four hours, or forecasting a deficiency of any duration beyond a four-hour horizon, shall eliminate the deficiency if possible, or minimize the magnitude and duration of the deficiency. | Retired | 2014-04-02 | 2019-09-26
402 | Directory # 5 V2 | Reserve | R20. | A Balancing Authority delivering recallable energy to another Balancing Authority may count that energy toward meeting their Operating Reserve requirement. | Retired | 2014-04-02 | 2019-09-26
403 | Directory # 5 V2 | Reserve | R21. | A Balancing Authority receiving recallable energy from another Balancing Authority must carry additional Operating Reserve at least equal to the amount of recallable energy being received. | Retired | 2014-04-02 | 2019-09-26
404 | Directory # 5 V2 | Reserve | R22. | Balancing Authorities participating in the “Simultaneous Activation of Ten-Minute Reserve”, (SAR) program shall conform to the procedures, as specified in Attachment B. | Retired | 2014-04-02 | 2019-09-26
405 | Directory # 5 V2 | Reserve | R23. | Balancing Authorities participating in the “ACE Diversity Interchange”, (ADI) program shall conform to the procedures, as specified in Attachment C. | Retired | 2014-04-02 | 2019-09-26
375 | Directory # 5 V2 | Reserve | R3. | A Balancing Authority’s requirement for synchronized reserve available within ten minutes shall be calculated by the twentieth day of each month, for the previous month, and shall be applied at the beginning of the next month. | Retired | 2014-04-02 | 2019-09-26
376 | Directory # 5 V2 | Reserve | R4. | A Balancing Authority’s requirement for synchronized reserve available within ten minutes shall be adjusted as follows: | Retired | 2014-04-02 | 2019-09-26
377 | Directory # 5 V2 | Reserve | R4.1. | A Balancing Authority’s maximum requirement for synchronized reserve available within ten minutes shall be 100 percent of its ten-minute reserve. A Balancing Authority’s minimum requirement for synchronized reserve available within ten minutes shall be 25 percent of its ten-minute reserve. | Retired | 2014-04-02 | 2019-09-26
378 | Directory # 5 V2 | Reserve | R4.2. | A Balancing Authority’s calculated requirement for synchronized reserve available within ten minutes shall increase by 20 percent of the ten-minute reserve requirement for every time it fails to return its ACE to pre-contingency values or to zero within fifteen minutes following the start of a reportable event that is less than a NERC reportable Balancing Contingency Event. Recovery of reporting ACE occurs when a Balancing Authority returns its reporting ACE to pre-contingency values (if it’s pre-contingency reporting ACE was negative) or to zero (if it’s pre-contingency reporting ACE was positive or equal to zero). | Retired | 2014-04-02 | 2019-09-26
379 | Directory # 5 V2 | Reserve | R4.3. | A Balancing Authority’s calculated requirement for synchronized reserve available within ten minutes may only be reduced by a maximum of 20 percent of the ten-minute reserve requirement, per month following the implementation month of any synchronized reserve requirement increase per R4.2. | Retired | 2014-04-02 | 2019-09-26
380 | Directory # 5 V2 | Reserve | R5. | If a Balancing Authority becomes deficient in synchronized reserve available within ten minutes, it shall restore its synchronized reserve available within ten minutes in accordance with R1 for the restoration of ten-minute reserve. Refer to Attachment A for example scenarios of synchronized reserve requirement penalty adjustments. | Retired | 2014-04-02 | 2019-09-26
381 | Directory # 5 V2 | Reserve | R6. | A Balancing Authority’s synchronized reserve, ten-minute reserve, and thirty-minute reserve, if activated, shall be sustainable for at least one hour from the time of activation. | Retired | 2014-04-02 | 2019-09-26
382 | Directory # 5 V2 | Reserve | R7. | A Balancing Authority shall not count synchronized reserve, ten-minute reserve, or thirty-minute reserve from loads that are already counted in other demand response programs and would result in double counting the same capacity. | Retired | 2014-04-02 | 2019-09-26
383 | Directory # 5 V2 | Reserve | R8. | A Balancing Authority shall not count synchronized reserve from a load if the reduction in load is dependent on starting a generator to replace energy that is supplied from the grid. | Retired | 2014-04-02 | 2019-09-26
384 | Directory # 5 V2 | Reserve | R9. | The Balancing Authority shall specify the following criteria for resources to be eligible to provide synchronized reserve, ten-minute reserve, or thirty-minute reserve: | Retired | 2014-04-02 | 2019-09-26
385 | Directory # 5 V2 | Reserve | R9.1. | Requirements for metering and testing | Retired | 2014-04-02 | 2019-09-26
386 | Directory # 5 V2 | Reserve | R9.2. | Requirements for continuously meeting the dispatch instructions | Retired | 2014-04-02 | 2019-09-26
387 | Directory # 5 V2 | Reserve | R9.3. | Requirements for operating capabilities and response rates | Retired | 2014-04-02 | 2019-09-26
270 | Directory # 5 V3 | Reserve | R1. | Each Balancing Authority shall have ten-minute reserve available to it that is at least equal to its first contingency loss. NPCC ten-minute reserve meets the requirements for the Contingency Reserve requirements within the NERC standards. • If a Balancing Authority becomes deficient in ten-minute reserve or forecasts a deficiency, it shall restore its ten-minute reserve as soon as possible and within the duration specified in the appropriate NERC standard. • If a Balancing Authority cannot restore its ten-minute reserve per requirement R2, it shall minimize the magnitude and duration | Retired | 2019-09-27 | 2020-01-15 | DP, GOP, BA, RC
420 | Directory # 5 V3 | Reserve | R10. | Resources allocating inter-Balancing Area reserve shall not offer the same reserve to more than one acquiring Balancing Authority for the same scheduling interval. | Retired | 2019-09-27 | 2020-01-15 | DP, GOP, BA, RC
421 | Directory # 5 V3 | Reserve | R11. | A Balancing Authority shall ensure that reserve is distributed so that it can be utilized without exceeding applicable element ratings or transfer limitations. | Retired | 2019-09-27 | 2020-01-15 | DP, GOP, BA, RC
422 | Directory # 5 V3 | Reserve | R12. | A Balancing Authority providing reserve to another Balancing Authority through direct procurement, bilateral, multi-lateral operating agreements, or through reserve sharing agreements, shall deliver an increase in energy as requested, up to the amount of reserve agreed upon. | Retired | 2019-09-27 | 2020-01-15 | DP, GOP, BA, RC
423 | Directory # 5 V3 | Reserve | R13. | A Balancing Authority shall not curtail an existing or planned non-recallable energy schedule in order to support the activation of reserve, unless agreed to by all affected Balancing Authorities. | Retired | 2019-09-27 | 2020-01-15 | DP, GOP, BA, RC
424 | Directory # 5 V3 | Reserve | R14. | A Balancing Authority providing or receiving inter-Balancing Area reserve shall meet the following requirements: | Retired | 2019-09-27 | 2020-01-15 | DP, GOP, BA, RC
425 | Directory # 5 V3 | Reserve | R14.1. | Decision-making related to the specific resources to be activated to provide inter-Balancing Area reserve shall be restricted to the affected Balancing Authorities. | Retired | 2019-09-27 | 2020-01-15 | DP, GOP, BA, RC
426 | Directory # 5 V3 | Reserve | R14.2. | The provision of inter-Balancing Area reserve shall be limited to adjacent Balancing Authorities only, unless specifically facilitated by an approved NPCC procedure or multilateral Balancing Authority/Reliability Coordinator procedure. | Retired | 2019-09-27 | 2020-01-15 | DP, GOP, BA, RC
427 | Directory # 5 V3 | Reserve | R14.3. | Shall agree on Interchange Schedule modifications when activating and terminating inter-Balancing Area reserve. | Retired | 2019-09-27 | 2020-01-15 | DP, GOP, BA, RC
428 | Directory # 5 V3 | Reserve | R14.4. | Where Dynamic Transfers are used to activate inter-Balancing Area reserve, it shall be agreed to by the affected Balancing Authorities, and approved by the TFCO. | Retired | 2019-09-27 | 2020-01-15 | DP, GOP, BA, RC
429 | Directory # 5 V3 | Reserve | R15. | A Balancing Authority shall activate inter-Balancing Area reserve within 5 minutes if utilized for a NERC DCS Balancing Contingency Event or a NPCC reportable event. | Retired | 2019-09-27 | 2020-01-15 | DP, GOP, BA, RC
430 | Directory # 5 V3 | Reserve | R16. | A Balancing Authority acquiring inter-Balancing Area reserve shall notify the host Balancing Authority and affected Reliability Coordinators when changes are made to the scheduling of inter-Balancing Area reserve. | Retired | 2019-09-27 | 2020-01-15 | DP, GOP, BA, RC
431 | Directory # 5 V3 | Reserve | R17. | A Balancing Authority providing (allocating or activating) inter- Balancing Area reserve, not as part of a Reserve Sharing Group, shall not count that reserve to meet its own reserve requirement. | Retired | 2019-09-27 | 2020-01-15 | DP, GOP, BA, RC
432 | Directory # 5 V3 | Reserve | R18. | A Balancing Authority providing recallable energy to another Balancing Authority shall advise the other Balancing Authority that the energy is recallable, and shall inform the receiving Balancing Authority of any change to the recallable status of this energy. | Retired | 2019-09-27 | 2020-01-15 | DP, GOP, BA, RC
433 | Directory # 5 V3 | Reserve | R19. | A Balancing Authority shall meet its Operating Reserve requirement using capacity available from resources internal to its Balancing Authority or by using capacity that is deliverable from another Balancing Authority. | Retired | 2019-09-27 | 2020-01-15 | DP, GOP, BA, RC
406 | Directory # 5 V3 | Reserve | R2. | Each Balancing Authority shall have thirty-minute reserve available to it that is at least equal to one-half its second contingency loss. • A Balancing Authority deficient in thirty-minute reserve for four hours, or forecasting a deficiency of any duration beyond a four-hour horizon, shall eliminate the deficiency if possible, or minimize the magnitude and duration of the deficiency. | Retired | 2019-09-27 | 2020-01-15 | DP, GOP, BA, RC
434 | Directory # 5 V3 | Reserve | R20. | A Balancing Authority delivering recallable energy to another Balancing Authority may count that energy toward meeting their Operating Reserve requirement. | Retired | 2019-09-27 | 2020-01-15 | DP, GOP, BA, RC
435 | Directory # 5 V3 | Reserve | R21. | A Balancing Authority receiving recallable energy from another Balancing Authority must carry additional Operating Reserve at least equal to the amount of recallable energy being received. | Retired | 2019-09-27 | 2020-01-15 | DP, GOP, BA, RC
436 | Directory # 5 V3 | Reserve | R22. | Balancing Authorities participating in the “Simultaneous Activation of Ten-Minute Reserve”, (SAR) program shall conform to the procedures, as specified in Attachment B. | Retired | 2019-09-27 | 2020-01-15 | DP, GOP, BA, RC
437 | Directory # 5 V3 | Reserve | R23. | Balancing Authorities participating in the “ACE Diversity Interchange”, (ADI) program shall conform to the procedures, as specified in Attachment C. | Retired | 2019-09-27 | 2020-01-15 | DP, GOP, BA, RC
407 | Directory # 5 V3 | Reserve | R3. | A Balancing Authority’s requirement for synchronized reserve available within ten minutes shall be calculated by the twentieth day of each month, for the previous month, and shall be applied at the beginning of the next month. | Retired | 2019-09-27 | 2020-01-15 | DP, GOP, BA, RC
408 | Directory # 5 V3 | Reserve | R4. | A Balancing Authority’s requirement for synchronized reserve available within ten minutes shall be adjusted as follows: | Retired | 2019-09-27 | 2020-01-15 | DP, GOP, BA, RC
409 | Directory # 5 V3 | Reserve | R4.1. | A Balancing Authority’s maximum requirement for synchronized reserve available within ten minutes shall be 100 percent of its ten-minute reserve. A Balancing Authority’s minimum requirement for synchronized reserve available within ten minutes shall be 25 percent of its ten-minute reserve. | Retired | 2019-09-27 | 2020-01-15 | DP, GOP, BA, RC
410 | Directory # 5 V3 | Reserve | R4.2. | A Balancing Authority’s calculated requirement for synchronized reserve available within ten minutes shall increase by 20 percent of the ten-minute reserve requirement for every time it fails to return its ACE to pre-contingency values or to zero within fifteen minutes following the start of a reportable event that is less than a NERC reportable Balancing Contingency Event. Recovery of reporting ACE occurs when a Balancing Authority returns its reporting ACE to pre-contingency values (if it’s pre-contingency reporting ACE was negative) or to zero (if it’s pre-contingency reporting ACE was positive or equal to zero). | Retired | 2019-09-27 | 2020-01-15 | DP, GOP, BA, RC
411 | Directory # 5 V3 | Reserve | R4.3. | A Balancing Authority’s calculated requirement for synchronized reserve available within ten minutes may only be reduced by a maximum of 20 percent of the ten-minute reserve requirement, per month following the implementation month of any synchronized reserve requirement increase per R4.2. | Retired | 2019-09-27 | 2020-01-15 | DP, GOP, BA, RC
412 | Directory # 5 V3 | Reserve | R5. | If a Balancing Authority becomes deficient in synchronized reserve available within ten minutes, it shall restore its synchronized reserve available within ten minutes in accordance with R1 for the restoration of ten-minute reserve. Refer to Attachment A for example scenarios of synchronized reserve requirement penalty adjustments. | Retired | 2019-09-27 | 2020-01-15 | DP, GOP, BA, RC
413 | Directory # 5 V3 | Reserve | R6. | A Balancing Authority’s synchronized reserve, ten-minute reserve, and thirty-minute reserve, if activated, shall be sustainable for at least one hour from the time of activation. | Retired | 2019-09-27 | 2020-01-15 | DP, GOP, BA, RC
414 | Directory # 5 V3 | Reserve | R7. | A Balancing Authority shall not count synchronized reserve, ten-minute reserve, or thirty-minute reserve from loads that are already counted in other demand response programs and would result in double counting the same capacity. | Retired | 2019-09-27 | 2020-01-15 | DP, GOP, BA, RC
415 | Directory # 5 V3 | Reserve | R8. | A Balancing Authority shall not count synchronized reserve from a load if the reduction in load is dependent on starting a generator to replace energy that is supplied from the grid. | Retired | 2019-09-27 | 2020-01-15 | DP, GOP, BA, RC
416 | Directory # 5 V3 | Reserve | R9. | The Balancing Authority shall specify the following criteria for resources to be eligible to provide synchronized reserve, ten-minute reserve, or thirty-minute reserve: | Retired | 2019-09-27 | 2020-01-15 | DP, GOP, BA, RC
417 | Directory # 5 V3 | Reserve | R9.1. | Requirements for metering and testing | Retired | 2019-09-27 | 2020-01-15 | DP, GOP, BA, RC
418 | Directory # 5 V3 | Reserve | R9.2. | Requirements for continuously meeting the dispatch instructions | Retired | 2019-09-27 | 2020-01-15 | DP, GOP, BA, RC
419 | Directory # 5 V3 | Reserve | R9.3. | Requirements for operating capabilities and response rates | Retired | 2019-09-27 | 2020-01-15 | DP, GOP, BA, RC
852 | Directory # 5 V4 | Reserve | R1. | Each Balancing Authority shall have ten-minute reserve available to it that is at least equal to its first contingency loss. NPCC ten-minute reserve meets the requirements for the Contingency Reserve requirements within the NERC standards. • If a Balancing Authority becomes deficient in ten-minute reserve or forecasts a deficiency, it shall restore its ten-minute reserve as soon as possible and within the duration specified in the appropriate NERC standard. • If a Balancing Authority cannot restore its ten-minute reserve per requirement R2, it shall minimize the magnitude and duration of the ten-minute reserve deficiency. | Retired | 2020-01-16 | 2020-04-25
867 | Directory # 5 V4 | Reserve | R10. | Resources allocating inter-Balancing Area reserve shall not offer the same reserve to more than one acquiring Balancing Authority for the same scheduling interval. | Retired | 2020-01-16 | 2020-04-25
868 | Directory # 5 V4 | Reserve | R11. | A Balancing Authority shall ensure that reserve is distributed so that it can be utilized without exceeding applicable element ratings or transfer limitations. | Retired | 2020-01-16 | 2020-04-25
869 | Directory # 5 V4 | Reserve | R12. | A Balancing Authority providing reserve to another Balancing Authority through direct procurement, bilateral, multi-lateral operating agreements, or through reserve sharing agreements, shall deliver an increase in energy as requested, up to the amount of reserve agreed upon. | Retired | 2020-01-16 | 2020-04-25
870 | Directory # 5 V4 | Reserve | R13. | A Balancing Authority shall not curtail an existing or planned nonrecallable energy schedule in order to support the activation of reserve, unless agreed to by all affected Balancing Authorities. | Retired | 2020-01-16 | 2020-04-25
872 | Directory # 5 V4 | Reserve | R14.1. | R14. A Balancing Authority providing or receiving inter-Balancing Area reserve shall meet the following requirements: R14.1. Decision-making related to the specific resources to be activated to provide inter-Balancing Area reserve shall be restricted to the affected Balancing Authorities. | Retired | 2020-01-16 | 2020-04-25
873 | Directory # 5 V4 | Reserve | R14.2. | R14. A Balancing Authority providing or receiving inter-Balancing Area reserve shall meet the following requirements: R14.2. The provision of inter-Balancing Area reserve shall be limited to adjacent Balancing Authorities only, unless specifically facilitated by an approved NPCC procedure or multilateral Balancing Authority/Reliability Coordinator procedure. | Retired | 2020-01-16 | 2020-04-25
874 | Directory # 5 V4 | Reserve | R14.3. | R14. A Balancing Authority providing or receiving inter-Balancing Area reserve shall meet the following requirements: R14.3. Shall agree on Interchange Schedule modifications when activating and terminating inter-Balancing Area reserve. | Retired | 2020-01-16 | 2020-04-25
875 | Directory # 5 V4 | Reserve | R14.4. | R14. A Balancing Authority providing or receiving inter-Balancing Area reserve shall meet the following requirements: R14.4. Where Dynamic Transfers are used to activate inter-Balancing Area reserve, it shall be agreed to by the affected Balancing Authorities, and approved by the TFCO. | Retired | 2020-01-16 | 2020-04-25
876 | Directory # 5 V4 | Reserve | R15. | A Balancing Authority shall activate inter-Balancing Area reserve within 5 minutes if utilized for a NERC DCS Balancing Contingency Event or a NPCC reportable event. | Retired | 2020-01-16 | 2020-04-25
877 | Directory # 5 V4 | Reserve | R16. | A Balancing Authority acquiring inter-Balancing Area reserve shall notify the host Balancing Authority and affected Reliability Coordinators when changes are made to the scheduling of inter-Balancing Area reserve. | Retired | 2020-01-16 | 2020-04-25
878 | Directory # 5 V4 | Reserve | R17. | A Balancing Authority providing (allocating or activating) inter-Balancing Area reserve, not as part of a Reserve Sharing Group, shall not count that reserve to meet its own reserve requirement. | Retired | 2020-01-16 | 2020-04-25
879 | Directory # 5 V4 | Reserve | R18. | A Balancing Authority providing recallable energy to another Balancing Authority shall advise the other Balancing Authority that the energy is recallable, and shall inform the receiving Balancing Authority of any change to the recallable status of this energy. | Retired | 2020-01-16 | 2020-04-25
880 | Directory # 5 V4 | Reserve | R19. | A Balancing Authority shall meet its Operating Reserve requirement using capacity available from resources internal to its Balancing Authority or by using capacity that is deliverable from another Balancing Authority. | Retired | 2020-01-16 | 2020-04-25
853 | Directory # 5 V4 | Reserve | R2. | Each Balancing Authority shall have thirty-minute reserve available to it that is at least equal to one-half its second contingency loss. • A Balancing Authority deficient in thirty-minute reserve for four hours, or forecasting a deficiency of any duration beyond a fourhour horizon, shall eliminate the deficiency if possible, or minimize the magnitude and duration of the deficiency. | Retired | 2020-01-16 | 2020-04-25
881 | Directory # 5 V4 | Reserve | R20. | A Balancing Authority delivering recallable energy to another Balancing Authority may count that energy toward meeting their Operating Reserve requirement. | Retired | 2020-01-16 | 2020-04-25
882 | Directory # 5 V4 | Reserve | R21. | A Balancing Authority receiving recallable energy from another Balancing Authority must carry additional Operating Reserve at least equal to the amount of recallable energy being received. | Retired | 2020-01-16 | 2020-04-25
883 | Directory # 5 V4 | Reserve | R22. | Balancing Authorities participating in the “Simultaneous Activation of TenMinute Reserve”, (SAR) program shall conform to the procedures, as specified in Attachment B. | Retired | 2020-01-16 | 2020-04-25
884 | Directory # 5 V4 | Reserve | R23. | Balancing Authorities participating in the “ACE Diversity Interchange”, (ADI) program shall conform to the procedures, as specified in Attachment C. | Retired | 2020-01-16 | 2020-04-25
854 | Directory # 5 V4 | Reserve | R3. | A Balancing Authority’s requirement for synchronized reserve available within ten minutes shall be calculated by the twentieth day of each month, for the previous month, and shall be applied at the beginning of the next month. | Retired | 2020-01-16 | 2020-04-25
856 | Directory # 5 V4 | Reserve | R4.1. | R4. A Balancing Authority’s requirement for synchronized reserve available within ten minutes shall be adjusted as follows: R4.1. A Balancing Authority’s maximum requirement for synchronized reserve available within ten minutes shall be 100 percent of its tenminute reserve. A Balancing Authority’s minimum requirement for synchronized reserve available within ten minutes shall be 25 percent of its ten-minute reserve. | Retired | 2020-01-16 | 2020-04-25
857 | Directory # 5 V4 | Reserve | R4.2. | R4. A Balancing Authority’s requirement for synchronized reserve available within ten minutes shall be adjusted as follows: R4.2. A Balancing Authority’s calculated requirement for synchronized reserve available within ten minutes shall increase by 20 percent of the ten-minute reserve requirement for every time it fails to return its ACE to pre-contingency values or to zero within fifteen minutes following the start of a reportable event that is less than a NERC reportable Balancing Contingency Event. Recovery of reporting ACE occurs when a Balancing Authority returns its reporting ACE to pre-contingency values (if it’s pre-contingency reporting ACE was negative) or to zero (if it’s pre-contingency reporting ACE was positive or equal to zero). | Retired | 2020-01-16 | 2020-04-25
858 | Directory # 5 V4 | Reserve | R4.3. | R4. A Balancing Authority’s requirement for synchronized reserve available within ten minutes shall be adjusted as follows: R4.3. A Balancing Authority’s calculated requirement for synchronized reserve available within ten minutes may only be reduced by a maximum of 20 percent of the ten-minute reserve requirement, per month following the implementation month of any synchronized reserve requirement increase per R4.2. | Retired | 2020-01-16 | 2020-04-25
859 | Directory # 5 V4 | Reserve | R5. | If a Balancing Authority becomes deficient in synchronized reserve available within ten minutes, it shall restore its synchronized reserve available within ten minutes in accordance with R1 for the restoration of ten-minute reserve. Refer to Attachment A for example scenarios of synchronized reserve requirement penalty adjustments. | Retired | 2020-01-16 | 2020-04-25
860 | Directory # 5 V4 | Reserve | R6. | A Balancing Authority’s synchronized reserve, ten-minute reserve, and thirty-minute reserve, if activated, shall be sustainable for at least one hour from the time of activation. | Retired | 2020-01-16 | 2020-04-25
861 | Directory # 5 V4 | Reserve | R7. | A Balancing Authority shall not count synchronized reserve, ten-minute reserve, or thirty-minute reserve from loads that are already counted in other demand response programs and would result in double counting the same capacity. | Retired | 2020-01-16 | 2020-04-25
862 | Directory # 5 V4 | Reserve | R8. | A Balancing Authority shall not count synchronized reserve from a load if the reduction in load is dependent on starting a generator to replace energy that is supplied from the grid. | Retired | 2020-01-16 | 2020-04-25
864 | Directory # 5 V4 | Reserve | R9.1. | R9. The Balancing Authority shall specify the following criteria for resources to be eligible to provide synchronized reserve, ten-minute reserve, or thirtyminute reserve: R9.1. Requirements for metering and testing | Retired | 2020-01-16 | 2020-04-25
865 | Directory # 5 V4 | Reserve | R9.2. | R9. The Balancing Authority shall specify the following criteria for resources to be eligible to provide synchronized reserve, ten-minute reserve, or thirtyminute reserve: R9.2. Requirements for continuously meeting the dispatch instructions | Retired | 2020-01-16 | 2020-04-25
866 | Directory # 5 V4 | Reserve | R9.3. | R9. The Balancing Authority shall specify the following criteria for resources to be eligible to provide synchronized reserve, ten-minute reserve, or thirtyminute reserve: R9.3. Requirements for operating capabilities and response rates | Retired | 2020-01-16 | 2020-04-25
885 | Directory # 5 V5 | Reserve | R1. | Each Balancing Authority shall have ten-minute reserve available to it that is at least equal to its first contingency loss. NPCC ten-minute reserve meets the requirements for the Contingency Reserve requirements within the NERC standards. • If a Balancing Authority becomes deficient in ten-minute reserve or forecasts a deficiency, it shall restore its ten-minute reserve as soon as possible and within the duration specified in the appropriate NERC standard. • If a Balancing Authority cannot restore its ten-minute reserve per requirement R2, it shall minimize the magnitude and duration of the ten-minute reserve deficiency. | Effective | 2020-04-26
898 | Directory # 5 V5 | Reserve | R10. | Resources allocating inter-Balancing Area reserve shall not offer the same reserve to more than one acquiring Balancing Authority for the same scheduling interval. | Effective | 2020-04-26
899 | Directory # 5 V5 | Reserve | R11. | A Balancing Authority shall ensure that reserve is distributed so that it can be utilized without exceeding applicable element ratings or transfer limitations. | Effective | 2020-04-26
900 | Directory # 5 V5 | Reserve | R12. | A Balancing Authority providing reserve to another Balancing Authority through direct procurement, bilateral, multi-lateral operating agreements, or through reserve sharing agreements, shall deliver an increase in energy as requested, up to the amount of reserve agreed upon. | Effective | 2020-04-26
901 | Directory # 5 V5 | Reserve | R13. | A Balancing Authority shall not curtail an existing or planned nonrecallable energy schedule in order to support the activation of reserve, unless agreed to by all affected Balancing Authorities. | Effective | 2020-04-26
902 | Directory # 5 V5 | Reserve | R14.1. | R14. A Balancing Authority providing or receiving inter-Balancing Area reserve shall meet the following requirements: R14.1. Decision-making related to the specific resources to be activated to provide inter-Balancing Area reserve shall be restricted to the affected Balancing Authorities. | Effective | 2020-04-26
903 | Directory # 5 V5 | Reserve | R14.2. | R14. A Balancing Authority providing or receiving inter-Balancing Area reserve shall meet the following requirements: R14.2. The provision of inter-Balancing Area reserve shall be limited to adjacent Balancing Authorities only, unless specifically facilitated by an approved NPCC procedure or multilateral Balancing Authority/Reliability Coordinator procedure. | Effective | 2020-04-26
904 | Directory # 5 V5 | Reserve | R14.3. | R14. A Balancing Authority providing or receiving inter-Balancing Area reserve shall meet the following requirements: R14.3. Shall agree on Interchange Schedule modifications when activating and terminating inter-Balancing Area reserve. | Effective | 2020-04-26
905 | Directory # 5 V5 | Reserve | R14.4. | R14. A Balancing Authority providing or receiving inter-Balancing Area reserve shall meet the following requirements: R14.4. Where Dynamic Transfers are used to activate inter-Balancing Area reserve, it shall be agreed to by the affected Balancing Authorities, and approved by the TFCO. | Effective | 2020-04-26
906 | Directory # 5 V5 | Reserve | R15. | A Balancing Authority shall activate inter-Balancing Area reserve within 5 minutes if utilized for a NERC DCS Balancing Contingency Event or a NPCC reportable event. | Effective | 2020-04-26
907 | Directory # 5 V5 | Reserve | R16. | A Balancing Authority acquiring inter-Balancing Area reserve shall notify the host Balancing Authority and affected Reliability Coordinators when changes are made to the scheduling of inter-Balancing Area reserve. | Effective | 2020-04-26
908 | Directory # 5 V5 | Reserve | R17. | A Balancing Authority providing (allocating or activating) inter-Balancing Area reserve, not as part of a Reserve Sharing Group, shall not count that reserve to meet its own reserve requirement. | Effective | 2020-04-26
909 | Directory # 5 V5 | Reserve | R18. | A Balancing Authority providing recallable energy to another Balancing Authority shall advise the other Balancing Authority that the energy is recallable, and shall inform the receiving Balancing Authority of any change to the recallable status of this energy. | Effective | 2020-04-26
910 | Directory # 5 V5 | Reserve | R19. | A Balancing Authority shall meet its Operating Reserve requirement using capacity available from resources internal to its Balancing Authority or by using capacity that is deliverable from another Balancing Authority. | Effective | 2020-04-26
886 | Directory # 5 V5 | Reserve | R2. | Each Balancing Authority shall have thirty-minute reserve available to it that is at least equal to one-half its second contingency loss. • A Balancing Authority deficient in thirty-minute reserve for four hours, or forecasting a deficiency of any duration beyond a fourhour horizon, shall eliminate the deficiency if possible, or minimize the magnitude and duration of the deficiency. | Effective | 2020-04-26
911 | Directory # 5 V5 | Reserve | R20. | A Balancing Authority delivering recallable energy to another Balancing Authority may count that energy toward meeting their Operating Reserve requirement. | Effective | 2020-04-26
912 | Directory # 5 V5 | Reserve | R21. | A Balancing Authority receiving recallable energy from another Balancing Authority must carry additional Operating Reserve at least equal to the amount of recallable energy being received. | Effective | 2020-04-26
913 | Directory # 5 V5 | Reserve | R22. | Balancing Authorities participating in the “Simultaneous Activation of TenMinute Reserve”, (SAR) program shall conform to the procedures, as specified in Attachment B. | Effective | 2020-04-26
914 | Directory # 5 V5 | Reserve | R23. | Balancing Authorities participating in the “ACE Diversity Interchange”, (ADI) program shall conform to the procedures, as specified in Attachment C. | Effective | 2020-04-26
887 | Directory # 5 V5 | Reserve | R3. | A Balancing Authority’s requirement for synchronized reserve available within ten minutes shall be calculated by the twentieth day of each month, for the previous month, and shall be applied at the beginning of the next month. | Effective | 2020-04-26
888 | Directory # 5 V5 | Reserve | R4.1. | R4. A Balancing Authority’s requirement for synchronized reserve available within ten minutes shall be adjusted as follows: R4.1. A Balancing Authority’s maximum requirement for synchronized reserve available within ten minutes shall be 100 percent of its tenminute reserve. A Balancing Authority’s minimum requirement for synchronized reserve available within ten minutes shall be 25 percent of its ten-minute reserve. | Effective | 2020-04-26
889 | Directory # 5 V5 | Reserve | R4.2. | R4. A Balancing Authority’s requirement for synchronized reserve available within ten minutes shall be adjusted as follows: R4.2. A Balancing Authority’s calculated requirement for synchronized reserve available within ten minutes shall increase by 20 percent of the ten-minute reserve requirement for every time it fails to return its ACE to pre-contingency values or to zero within fifteen minutes following the start of a reportable event that is less than a NERC reportable Balancing Contingency Event. Recovery of reporting ACE occurs when a Balancing Authority returns its reporting ACE to pre-contingency values (if it’s pre-contingency reporting ACE was negative) or to zero (if it’s pre-contingency reporting ACE was positive or equal to zero). | Effective | 2020-04-26
890 | Directory # 5 V5 | Reserve | R4.3. | R4. A Balancing Authority’s requirement for synchronized reserve available within ten minutes shall be adjusted as follows: R4.3. A Balancing Authority’s calculated requirement for synchronized reserve available within ten minutes may only be reduced by a maximum of 20 percent of the ten-minute reserve requirement, per month following the implementation month of any synchronized reserve requirement increase per R4.2. | Effective | 2020-04-26
891 | Directory # 5 V5 | Reserve | R5. | If a Balancing Authority becomes deficient in synchronized reserve available within ten minutes, it shall restore its synchronized reserve available within ten minutes in accordance with R1 for the restoration of ten-minute reserve. Refer to Attachment A for example scenarios of synchronized reserve requirement penalty adjustments. | Effective | 2020-04-26
892 | Directory # 5 V5 | Reserve | R6. | A Balancing Authority’s synchronized reserve, ten-minute reserve, and thirty-minute reserve, if activated, shall be sustainable for at least one hour from the time of activation. | Effective | 2020-04-26
893 | Directory # 5 V5 | Reserve | R7. | A Balancing Authority shall not count synchronized reserve, ten-minute reserve, or thirty-minute reserve from loads that are already counted in other demand response programs and would result in double counting the same capacity. | Effective | 2020-04-26
894 | Directory # 5 V5 | Reserve | R8. | A Balancing Authority shall not count synchronized reserve from a load if the reduction in load is dependent on starting a generator to replace energy that is supplied from the grid. | Effective | 2020-04-26
895 | Directory # 5 V5 | Reserve | R9.1. | R9. The Balancing Authority shall specify the following criteria for resources to be eligible to provide synchronized reserve, ten-minute reserve, or thirtyminute reserve: R9.1. Requirements for metering and testing | Effective | 2020-04-26
896 | Directory # 5 V5 | Reserve | R9.2. | R9. The Balancing Authority shall specify the following criteria for resources to be eligible to provide synchronized reserve, ten-minute reserve, or thirtyminute reserve: R9.2. Requirements for continuously meeting the dispatch instructions | Effective | 2020-04-26
897 | Directory # 5 V5 | Reserve | R9.3. | R9. The Balancing Authority shall specify the following criteria for resources to be eligible to provide synchronized reserve, ten-minute reserve, or thirtyminute reserve: R9.3. Requirements for operating capabilities and response rates | Effective | 2020-04-26
438 | Directory # 6 | Reserve Sharing Groups | R1. | The Balancing Authorities (BAs) participating in a Reserve Sharing Group (RSG) shall have a RSG Agreement that meets the requirements as specified in section 5.2. | Retired | 2012-08-08 | 2016-10-12
439 | Directory # 6 | Reserve Sharing Groups | R2. | Each RSG shall provide their RSG Agreement to the Task Force for Coordination of Operation for review before it is implemented. | Retired | 2012-08-08 | 2016-10-12
440 | Directory # 6 | Reserve Sharing Groups | R2.1. | New RSG Agreements and future changes to existing RSG Agreements shall be approved by the Reliability Coordinating Committee (RCC). | Retired | 2012-08-08 | 2016-10-12
441 | Directory # 6 | Reserve Sharing Groups | R3. | The Balancing Authorities (BAs) participating in a Reserve Sharing Group (RSG) shall be adjoining BAs unless they have a wheeling agreement with the intermediary BA or BAs. | Retired | 2012-08-08 | 2016-10-12
442 | Directory # 6 | Reserve Sharing Groups | R4. | Each RSG shall provide the Task Force on Coordination of Operation with a quantitative estimate of the change in reliability risk related to a RSG agreement for review before their RSG Agreement is implemented. There are a number of studies that could be performed to analyze the change in reliability risk such as: • Megawatt Loss Probability Method • Statistical analysis on the NPCC reportable events reports (NERC Form CR-1 reports)/Chronological event database • Other comparable methods that produce the required reliability risk estimate. | Retired | 2012-08-08 | 2016-10-12
443 | Directory # 6 | Reserve Sharing Groups | R5. | Each RSG Agreement shall specify the following: | Retired | 2012-08-08 | 2016-10-12
444 | Directory # 6 | Reserve Sharing Groups | R5.1. | The BAs participating in the RSG. | Retired | 2012-08-08 | 2016-10-12
453 | Directory # 6 | Reserve Sharing Groups | R5.10. | Details of how the activation and termination of RSGE are coordinated with simultaneous activation of ten-minute reserve (SAR) energy, other existing reserve activation agreements and other RSGs. | Retired | 2012-08-08 | 2016-10-12
454 | Directory # 6 | Reserve Sharing Groups | R5.11. | The Ramp to be utilized for Schedule changes when RSGE is activated and/or terminated. | Retired | 2012-08-08 | 2016-10-12
455 | Directory # 6 | Reserve Sharing Groups | R5.12. | The maximum duration for which the RSGE can be activated. | Retired | 2012-08-08 | 2016-10-12
456 | Directory # 6 | Reserve Sharing Groups | R5.13. | Times within which the RSG Coordinator shall: • Communicate changes in availability and deliverability of RSGE that are reported to it • Develop allocation shares, if necessary • Specify Schedule changes to activate RSGE • Adjust Schedules to terminate the delivery of RSGE. | Retired | 2012-08-08 | 2016-10-12
457 | Directory # 6 | Reserve Sharing Groups | R5.14. | The communication method(s) to be used to exchange information with the RSG Coordinator. | Retired | 2012-08-08 | 2016-10-12
458 | Directory # 6 | Reserve Sharing Groups | R5.15. | The information that must be exchanged between the RSG Coordinator and participating BAs and between the RSG Coordinator and other RSG Coordinators and the SAR Coordinator. | Retired | 2012-08-08 | 2016-10-12
459 | Directory # 6 | Reserve Sharing Groups | R5.16. | Requirements for the payback of any delivered RSGE. | Retired | 2012-08-08 | 2016-10-12
460 | Directory # 6 | Reserve Sharing Groups | R5.17. | How transmission capability is utilized for planning and ensuring the availability and deliverability of RSGE. | Retired | 2012-08-08 | 2016-10-12
461 | Directory # 6 | Reserve Sharing Groups | R5.18. | The allocation between participating BAs, of any penalties resulting from the violation of NPCC or NERC criteria or standards. | Retired | 2012-08-08 | 2016-10-12
462 | Directory # 6 | Reserve Sharing Groups | R5.19. | RSGE shall meet the sustainability requirements specified in NPCC Directory 5 Reserve. | Retired | 2012-08-08 | 2016-10-12
445 | Directory # 6 | Reserve Sharing Groups | R5.2. | The BA acting as the RSG Coordinator. | Retired | 2012-08-08 | 2016-10-12
446 | Directory # 6 | Reserve Sharing Groups | R5.3. | Intermediary BAs that have agreed to facilitate the transfer of Reserve Sharing Group Energy (RSGE) between non adjacent BAs in a RSG, through the intermediary BA Area(s)_ without utilizing the RSGE or providing reserve for other BAs. Such BAs will be designated as a wheeling only BA and are not part of the RSG. | Retired | 2012-08-08 | 2016-10-12
447 | Directory # 6 | Reserve Sharing Groups | R5.4. | The effective date of the RSG Agreement and the renewal, review and termination dates, if applicable. | Retired | 2012-08-08 | 2016-10-12
448 | Directory # 6 | Reserve Sharing Groups | R5.5. | The reserve product(s) being shared (e.g. ten-minute reserve, ten-minute synchronized reserve and/or thirty-minute reserve). | Retired | 2012-08-08 | 2016-10-12
449 | Directory # 6 | Reserve Sharing Groups | R5.6. | The minimum amount of each reserve product required by each of the participating BAs. | Retired | 2012-08-08 | 2016-10-12
450 | Directory # 6 | Reserve Sharing Groups | R5.7. | The conditions under which a participating BA will declare that they are unable to provide RSGE. | Retired | 2012-08-08 | 2016-10-12
451 | Directory # 6 | Reserve Sharing Groups | R5.8. | The method for determining RSGE share sizes for the participating BAs. | Retired | 2012-08-08 | 2016-10-12
452 | Directory # 6 | Reserve Sharing Groups | R5.9. | The conditions under which RSGE may be activated, including any time limits after a contingency occurs. | Retired | 2012-08-08 | 2016-10-12
464 | Directory # 6 V1 | Reserve Sharing Groups | R1. | The Balancing Authorities (BAs) participating in a Reserve Sharing Group (RSG) shall have a RSG Agreement that meets the requirements as specified in section 5.2. | Retired | 2016-10-13 | 2019-09-26
463 | Directory # 6 V1 | Reserve Sharing Groups | R2. | Each RSG shall provide their RSG Agreement to the Task Force for Coordination of Operation for review before it is implemented. | Retired | 2016-10-13 | 2019-09-26
465 | Directory # 6 V1 | Reserve Sharing Groups | R2.1. | New RSG Agreements and future changes to existing RSG Agreements shall be approved by the Reliability Coordinating Committee (RCC). | Retired | 2016-10-13 | 2019-09-26
466 | Directory # 6 V1 | Reserve Sharing Groups | R3. | The Balancing Authorities (BAs) participating in a Reserve Sharing Group (RSG) shall be adjoining BAs unless they have a wheeling agreement with the intermediary BA or BAs. | Retired | 2016-10-13 | 2019-09-26
467 | Directory # 6 V1 | Reserve Sharing Groups | R4. | Each RSG shall provide the Task Force on Coordination of Operation with a quantitative estimate of the change in reliability risk related to a RSG agreement for review before their RSG Agreement is implemented. There are a number of studies that could be performed to analyze the change in reliability risk such as: • Megawatt Loss Probability Method • Statistical analysis on the NPCC reportable events reports (NERC Form CR-1 reports)/Chronological event database • Other comparable methods that produce the required reliability risk estimate. | Retired | 2016-10-13 | 2019-09-26
468 | Directory # 6 V1 | Reserve Sharing Groups | R5. | Each RSG Agreement shall specify the following: | Retired | 2016-10-13 | 2019-09-26
469 | Directory # 6 V1 | Reserve Sharing Groups | R5.1. | The BAs participating in the RSG. | Retired | 2016-10-13 | 2019-09-26
478 | Directory # 6 V1 | Reserve Sharing Groups | R5.10. | Details of how the activation and termination of RSGE are coordinated with simultaneous activation of ten-minute reserve (SAR) energy, other existing reserve activation agreements and other RSGs. | Retired | 2016-10-13 | 2019-09-26
479 | Directory # 6 V1 | Reserve Sharing Groups | R5.11. | The Ramp to be utilized for Schedule changes when RSGE is activated and/or terminated. | Retired | 2016-10-13 | 2019-09-26
480 | Directory # 6 V1 | Reserve Sharing Groups | R5.12. | The maximum duration for which the RSGE can be activated. | Retired | 2016-10-13 | 2019-09-26
481 | Directory # 6 V1 | Reserve Sharing Groups | R5.13. | Times within which the RSG Coordinator shall: • Communicate changes in availability and deliverability of RSGE that are reported to it • Develop allocation shares, if necessary • Specify Schedule changes to activate RSGE • Adjust Schedules to terminate the delivery of RSGE. | Retired | 2016-10-13 | 2019-09-26
482 | Directory # 6 V1 | Reserve Sharing Groups | R5.14. | The communication method(s) to be used to exchange information with the RSG Coordinator. | Retired | 2016-10-13 | 2019-09-26
483 | Directory # 6 V1 | Reserve Sharing Groups | R5.15. | The information that must be exchanged between the RSG Coordinator and participating BAs and between the RSG Coordinator and other RSG Coordinators and the SAR Coordinator. | Retired | 2016-10-13 | 2019-09-26
484 | Directory # 6 V1 | Reserve Sharing Groups | R5.16. | Requirements for the payback of any delivered RSGE. | Retired | 2016-10-13 | 2019-09-26
485 | Directory # 6 V1 | Reserve Sharing Groups | R5.17. | How transmission capability is utilized for planning and ensuring the availability and deliverability of RSGE. | Retired | 2016-10-13 | 2019-09-26
486 | Directory # 6 V1 | Reserve Sharing Groups | R5.18. | The allocation between participating BAs, of any penalties resulting from the violation of NPCC or NERC criteria or standards. | Retired | 2016-10-13 | 2019-09-26
487 | Directory # 6 V1 | Reserve Sharing Groups | R5.19. | RSGE shall meet the sustainability requirements specified in NPCC Directory 5 Reserve. | Retired | 2016-10-13 | 2019-09-26
470 | Directory # 6 V1 | Reserve Sharing Groups | R5.2. | The BA acting as the RSG Coordinator. | Retired | 2016-10-13 | 2019-09-26
471 | Directory # 6 V1 | Reserve Sharing Groups | R5.3. | Intermediary BAs that have agreed to facilitate the transfer of Reserve Sharing Group Energy (RSGE) between non adjacent BAs in a RSG, through the intermediary BA Area(s)_ without utilizing the RSGE or providing reserve for other BAs. Such BAs will be designated as a wheeling only BA and are not part of the RSG. | Retired | 2016-10-13 | 2019-09-26
472 | Directory # 6 V1 | Reserve Sharing Groups | R5.4. | The effective date of the RSG Agreement and the renewal, review and termination dates, if applicable. | Retired | 2016-10-13 | 2019-09-26
473 | Directory # 6 V1 | Reserve Sharing Groups | R5.5. | The reserve product(s) being shared (e.g. ten-minute reserve, ten-minute synchronized reserve and/or thirty-minute reserve). | Retired | 2016-10-13 | 2019-09-26
474 | Directory # 6 V1 | Reserve Sharing Groups | R5.6. | The minimum amount of each reserve product required by each of the participating BAs. | Retired | 2016-10-13 | 2019-09-26
475 | Directory # 6 V1 | Reserve Sharing Groups | R5.7. | The conditions under which a participating BA will declare that they are unable to provide RSGE. | Retired | 2016-10-13 | 2019-09-26
476 | Directory # 6 V1 | Reserve Sharing Groups | R5.8. | The method for determining RSGE share sizes for the participating BAs. | Retired | 2016-10-13 | 2019-09-26
477 | Directory # 6 V1 | Reserve Sharing Groups | R5.9. | The conditions under which RSGE may be activated, including any time limits after a contingency occurs. | Retired | 2016-10-13 | 2019-09-26
100 | Directory # 6 V2 | Reserve Sharing Groups | R1. | Reserve Sharing Group Requirements: The Balancing Authorities (BAs) participating in a Reserve Sharing Group (RSG) shall have a RSG Agreement that meets the requirements as specified in section 5.2. | Effective | 2019-09-27 |  | RSG, BA
101 | Directory # 6 V2 | Reserve Sharing Groups | R2. | Each RSG shall provide their RSG Agreement to the Regional Entity for review before it is implemented. | Effective | 2019-09-27 |  | RSG, BA
303 | Directory # 6 V2 | Reserve Sharing Groups | R2.1. | New RSG Agreements and future changes to existing RSG Agreements shall be approved by the Reliability Coordinating Committee (RCC). | Effective | 2019-09-27 |  | RSG, BA
102 | Directory # 6 V2 | Reserve Sharing Groups | R3. | The Balancing Authorities (BAs) participating in a Reserve Sharing Group (RSG) shall be adjoining BAs unless they have a wheeling agreement with the intermediary BA or BAs. | Effective | 2019-09-27 |  | RSG, BA
103 | Directory # 6 V2 | Reserve Sharing Groups | R4. | Each RSG shall provide the Task Force on Coordination of Operation with a quantitative estimate of the change in reliability risk related to a RSG agreement for review before their RSG Agreement is implemented. There are a number of studies that could be performed to analyze the change in reliability risk such as: • Megawatt Loss Probability Method • Statistical analysis on the NPCC reportable events reports (NERC Form CR-1 reports)/Chronological event database • Other comparable methods that produce the required reliability risk estimate. | Effective | 2019-09-27 |  | RSG, BA
104 | Directory # 6 V2 | Reserve Sharing Groups | R5. | Reserve Sharing Group Agreement Requirements: Each RSG Agreement shall specify the following: | Effective | 2019-09-27 |  | RSG, BA
105 | Directory # 6 V2 | Reserve Sharing Groups | R5.1. | The BAs participating in the RSG. | Effective | 2019-09-27 |  | RSG, BA
114 | Directory # 6 V2 | Reserve Sharing Groups | R5.10. | Details of how the activation and termination of RSGE are coordinated with Simultaneous Activation of Reserve Energy, other existing reserve activation agreements and other RSGs. | Effective | 2019-09-27 |  | RSG, BA
115 | Directory # 6 V2 | Reserve Sharing Groups | R5.11. | The ramp duration to be utilized for schedule changes when RSGE is activated and/or terminated. | Effective | 2019-09-27 |  | RSG, BA
116 | Directory # 6 V2 | Reserve Sharing Groups | R5.12. | The maximum duration for which the RSGE can be activated. | Effective | 2019-09-27 |  | RSG, BA
117 | Directory # 6 V2 | Reserve Sharing Groups | R5.13. | Times within which the RSG Coordinator shall: • Communicate changes in availability and deliverability of RSGE that are reported to it • Develop allocation shares, if necessary • Specify Schedule changes to activate RSGE • Adjust Schedules to terminate the delivery of RSGE. | Effective | 2019-09-27 |  | RSG, BA
118 | Directory # 6 V2 | Reserve Sharing Groups | R5.14. | The communication method(s) to be used to exchange information with the RSG Coordinator. | Effective | 2019-09-27 |  | RSG, BA
119 | Directory # 6 V2 | Reserve Sharing Groups | R5.15. | The information that must be exchanged between the RSG Coordinator and participating BAs and between the RSG Coordinator and other RSG Coordinators and the SAR Coordinator. | Effective | 2019-09-27 |  | RSG, BA
120 | Directory # 6 V2 | Reserve Sharing Groups | R5.16. | Requirements for the payback of any delivered RSGE. | Effective | 2019-09-27 |  | RSG, BA
121 | Directory # 6 V2 | Reserve Sharing Groups | R5.17. | How transmission capability is utilized for planning and ensuring the availability and deliverability of RSGE. | Effective | 2019-09-27 |  | RSG, BA
122 | Directory # 6 V2 | Reserve Sharing Groups | R5.18. | The allocation between participating BAs, of any penalties resulting from the violation of NPCC or NERC criteria or standards. | Effective | 2019-09-27 |  | RSG, BA
123 | Directory # 6 V2 | Reserve Sharing Groups | R5.19. | RSGE shall meet the sustainability requirements specified in NPCC Directory 5 Reserve. | Effective | 2019-09-27 |  | RSG, BA
106 | Directory # 6 V2 | Reserve Sharing Groups | R5.2. | The BA acting as the Coordinator for the RSG. | Effective | 2019-09-27 |  | RSG, BA
107 | Directory # 6 V2 | Reserve Sharing Groups | R5.3. | Intermediary BAs that have agreed to facilitate the transfer of Reserve Sharing Group Energy (RSGE) between non adjacent BAs in a RSG, through their BA Area without utilizing the RSGE or providing reserve for other BAs. Such BAs will be designated as a wheeling only BA and are not part of the RSG. | Effective | 2019-09-27 |  | RSG, BA
108 | Directory # 6 V2 | Reserve Sharing Groups | R5.4. | The effective date of the RSG Agreement and the renewal, review and termination dates if applicable. | Effective | 2019-09-27 |  | RSG, BA
109 | Directory # 6 V2 | Reserve Sharing Groups | R5.5. | The reserve product(s) being shared (e.g. ten minute, ten minute synchronized and thirty minute). | Effective | 2019-09-27 |  | RSG, BA
110 | Directory # 6 V2 | Reserve Sharing Groups | R5.6. | The minimum amount of each reserve product required by each of the participating BAs. | Effective | 2019-09-27 |  | RSG, BA
111 | Directory # 6 V2 | Reserve Sharing Groups | R5.7. | The conditions under which a participating BA will declare that they are unable to provide RSGE. | Effective | 2019-09-27 |  | RSG, BA
112 | Directory # 6 V2 | Reserve Sharing Groups | R5.8. | The method for determining RSGE share sizes for the participating BAs. | Effective | 2019-09-27 |  | RSG, BA
113 | Directory # 6 V2 | Reserve Sharing Groups | R5.9. | The conditions under which RSGE may be activated, including any time limits after a contingency occurs. | Effective | 2019-09-27 |  | RSG, BA
488 | Directory # 8 | System Restoration | R1. | Each Reliability Coordinator shall develop and maintain a restoration plan for its Reliability Coordinator Area that shall: | Retired | 2008-10-22 | 2014-04-01
489 | Directory # 8 | System Restoration | R1.1. | Identify the Reliability Coordinator Area’s basic minimum power system(s). | Retired | 2008-10-22 | 2014-04-01
490 | Directory # 8 | System Restoration | R1.2. | Address the priority of restoring off-site power to nuclear plants; | Retired | 2008-10-22 | 2014-04-01
491 | Directory # 8 | System Restoration | R1.3. | Identify interconnection points with adjacent Reliability Coordinator areas; | Retired | 2008-10-22 | 2014-04-01
492 | Directory # 8 | System Restoration | R1.4. | Identify parameters to synchronize adjacent basic minimum power systems; | Retired | 2008-10-22 | 2014-04-01
493 | Directory # 8 | System Restoration | R1.5. | Address coordination of system restoration with neighboring Reliability Coordinator areas; | Retired | 2008-10-22 | 2014-04-01
494 | Directory # 8 | System Restoration | R1.6. | Provide for the re-energization of transmission systems to major generating stations, including inter-area tie points; | Retired | 2008-10-22 | 2014-04-01
495 | Directory # 8 | System Restoration | R1.7. | Address electrical island stabilization; | Retired | 2008-10-22 | 2014-04-01
496 | Directory # 8 | System Restoration | R1.8. | Identify provisions for fuel resources to support operation of any supplementary generators (e.g., a diesel generator) necessary for operating key facilities consistent with the expected requirements of the Restoration Plan. | Retired | 2008-10-22 | 2014-04-01
519 | Directory # 8 | System Restoration | R10. | Each functional entity shall test its backup power supplies identified as critical components as specified below. Where there are separate backup power arrangements at a key facility for transmission or generating station equipment and telecommunication equipment, they shall be separately identified in the critical components list and shall be inspected and tested individually. | Retired | 2008-10-22 | 2014-04-01
520 | Directory # 8 | System Restoration | R10.1. | Equipment Inspection: A battery and/or battery charger identified as a critical component shall be inspected in accordance with maintenance activities and maintenance intervals specified in PRC-005-Protection System, Automatic Reclosing, and Sudden Pressure Relaying Maintenance. (Reference: Table 1; Test KF-1) | Retired | 2008-10-22 | 2014-04-01
521 | Directory # 8 | System Restoration | R10.2. | Equipment Verification A battery and battery charger identified as critical components shall be verified in accordance with maintenance activities and maintenance intervals specified in PRC-005 Protection System, Automatic Reclosing, and Sudden Pressure Relaying Maintenance. (Reference: Table 1; Test KF-2) | Retired | 2008-10-22 | 2014-04-01
522 | Directory # 8 | System Restoration | R10.3. | Confirm that all Critical Component Loads can be Supplied The owner of batteries or battery chargers identified as critical components shall confirm that all critical component loads are connected to and can be supplied by the batteries and battery chargers. At least every sixty (60) calendar months, or when modifications are made to the key facility, the functional entity owner shall confirm through its design review or through testing that all critical component loads are connected to and can be sufficiently supplied by the batteries and battery chargers. (Reference: Table 1; Test KF-3) | Retired | 2008-10-22 | 2014-04-01
523 | Directory # 8 | System Restoration | R10.4. | Startup and Run Test The owner of a backup power generator identified as a critical component of a key facility, shall perform a monthly startup and run test on that backup power generator for a minimum run time of fifteen (15) minutes. (Reference: Table 1; Test KF-5). Note: This test also applies to supplemental generation required for blackstart capability and to a control center and telecommunication center backup power generator. | Retired | 2008-10-22 | 2014-04-01
524 | Directory # 8 | System Restoration | R10.5. | Startup, Transfer and Load Test The owner of a backup power generator identified as a critical component of a key facility shall verify that the backup power generator will pick up the critical component load following the loss of station service. Note: This test also applies to a control center and telecommunication center backup power generator. For automatically started backup power generators, a startup, transfer and run test simulating the loss of station service will be performed every twelve (12) calendar months for a duration of at least thirty (30) minutes. (Reference: Table 1; Test KF-6) For manually started backup power generators, the asset owner shall every twelve (12) calendar months start the generator and verify stable operation for thirty (30) minutes while supplying critical component loads. (Reference: Table 1; Test KF-6) Note: Power sources used to start blackstart units will be excluded from test KF-6. | Retired | 2008-10-22 | 2014-04-01
525 | Directory # 8 | System Restoration | R11. | Each functional entity identified as owning key facilities shall test its critical components in the control centers and the telecommunication centers identified as key facilities to demonstrate that the computer systems will be functional when required for system restoration, without dependencies on power sources that may be unavailable during a partial or complete system blackout. | Retired | 2008-10-22 | 2014-04-01
526 | Directory # 8 | System Restoration | R11.1. | AC Supply Interruption Test The uninterruptible power supply (UPS) systems in control centers and telecommunication centers shall be tested every twelve (12) calendar months by interrupting AC supply and verifying that all critical component loads are supplied for a time that is sufficient for backup power sources to restore the AC input to the UPS. (Reference: Table 1; Test CC-1) | Retired | 2008-10-22 | 2014-04-01
527 | Directory # 8 | System Restoration | R11.2. | Computer Redundancy (SCADA/EMS) Test Each functional entity identified as owning a key facility shall test its computer redundancy (SCADA/EMS) features every six (6) calendar months to ensure computer systems (SCADA/EMS) continue to function adequately. (Reference: Table 1; Test CC--2) | Retired | 2008-10-22 | 2014-04-01
528 | Directory # 8 | System Restoration | R12. | Each functional entity owning a generating station with blackstart capability shall verify such capability as follows: | Retired | 2008-10-22 | 2014-04-01
529 | Directory # 8 | System Restoration | R12.1. | Operations voice communications and auxiliary systems such as Supervisory Control and Data Acquisition (SCADA) that are required for blackstart shall be verified at least every twelve (12) calendar months to operate adequately without dependency on the interconnected system or other unrelated unit for any source of station service. | Retired | 2008-10-22 | 2014-04-01
530 | Directory # 8 | System Restoration | R12.2. | A generating station with blackstart capability shall be tested every twelve (12) calendar months for successful equipment startup and energize a transmission element or a generating station switchyard element if that doesn’t involve the disconnection of load that is not dedicated generating station load to conduct the test. Verify stable operation while isolated from the bulk power system for a minimum of ten minutes. (Reference: Table 1; Test BS-1). (Reference: Appendix A-Table 1; Test No. BS-1) | Retired | 2008-10-22 | 2014-04-01
531 | Directory # 8 | System Restoration | R13. | Reliability Coordinators shall determine the number of units within a generating station that are to be tested for blackstart capability as required by their respective system restoration plans, and shall notify the applicable functional entity. | Retired | 2008-10-22 | 2014-04-01
532 | Directory # 8 | System Restoration | R14. | Each Reliability Coordinator shall confirm that the functional entity owning a generating station with blackstart capability that is part of the basic minimum power system has completed a successful blackstart test consistent with the objectives of the Reliability Coordinator’s system restoration plan. | Retired | 2008-10-22 | 2014-04-01
533 | Directory # 8 | System Restoration | R15. | A functional entity that has confirmed the loss of functionality of a critical component shall report to the Transmission Operator responsible for operating that critical component of that critical component’s loss of functional availability as soon as possible but no longer than 15 minutes after becoming aware of the condition. | Retired | 2008-10-22 | 2014-04-01
534 | Directory # 8 | System Restoration | R15.1. | The Transmission Operator shall report to its Reliability Coordinator as soon as possible but no longer than 15 minutes after the functional entity has made the Transmission Operator aware of the loss of functionality of the critical component. Examples of such conditions are but not limited to: • Loss of control of remote equipment; • Complete loss of AC or DC service supply; • Loss of blackstart facilities. | Retired | 2008-10-22 | 2014-04-01
535 | Directory # 8 | System Restoration | R16. | A functional entity that has confirmed the loss of redundancy of a critical component shall report to the Transmission Operator responsible for that critical component as soon as possible but no longer than 12 hours after the functional entity’s staff has confirmed the loss of redundancy for the critical component. Examples of such conditions are: • Loss of a redundant AC or DC service supply; • Loss of redundant blackstart critical components. | Retired | 2008-10-22 | 2014-04-01
536 | Directory # 8 | System Restoration | R17. | A functional entity that has scheduled a maintenance condition of a critical component that will result in the loss of functionality of that critical component shall report that maintenance condition to the Transmission Operator responsible for the critical component at least 24 hours prior to that scheduled loss of functionality. | Retired | 2008-10-22 | 2014-04-01
537 | Directory # 8 | System Restoration | R17.1. | The functional entity shall report to the Transmission Operator responsible for the critical component as soon as possible after the loss of functionality has occurred. | Retired | 2008-10-22 | 2014-04-01
538 | Directory # 8 | System Restoration | R17.2. | If the scheduled maintenance condition causing the loss of functionality of a critical component affects the functionality of a key facility, the Transmission Operator responsible for the critical component shall report this scheduled maintenance condition to its Reliability Coordinator. | Retired | 2008-10-22 | 2014-04-01
539 | Directory # 8 | System Restoration | R18. | A functional entity shall report the actions to be taken to restore a critical component’s availability or redundancy to the Transmission Operator responsible for the critical component as soon as known. | Retired | 2008-10-22 | 2014-04-01
540 | Directory # 8 | System Restoration | R18.1. | The functional entity shall report to the Transmission Operator responsible for that critical component the anticipated time that the critical components functionality will be restored. | Retired | 2008-10-22 | 2014-04-01
541 | Directory # 8 | System Restoration | R18.2. | The functional entity shall report to the Transmission Operator responsible for maintaining redundancy for a critical component the anticipated time that the critical component’s redundancy will be restored. | Retired | 2008-10-22 | 2014-04-01
542 | Directory # 8 | System Restoration | R19. | A functional entity shall report the date and time when the functional availability of a critical component is restored to the Transmission Operator responsible for the critical component as soon as known. | Retired | 2008-10-22 | 2014-04-01
497 | Directory # 8 | System Restoration | R2. | In determining the basic minimum power system, the Reliability Coordinator shall involve all affected parties or functional entities. | Retired | 2008-10-22 | 2014-04-01
498 | Directory # 8 | System Restoration | R3. | The Reliability Coordinator shall ensure that the basic minimum power system includes the ability to: | Retired | 2008-10-22 | 2014-04-01
499 | Directory # 8 | System Restoration | R3.1. | Utilize generator blackstart capability; | Retired | 2008-10-22 | 2014-04-01
500 | Directory # 8 | System Restoration | R3.2. | Form an electrical island(s); | Retired | 2008-10-22 | 2014-04-01
501 | Directory # 8 | System Restoration | R3.3. | Synchronize electrical islands; and | Retired | 2008-10-22 | 2014-04-01
502 | Directory # 8 | System Restoration | R3.4. | Permit the continuation of the system restoration plan. | Retired | 2008-10-22 | 2014-04-01
503 | Directory # 8 | System Restoration | R4. | Each Reliability Coordinator shall identify key facilities and shall inform each functional entity of its identified key facilities. | Retired | 2008-10-22 | 2014-04-01
504 | Directory # 8 | System Restoration | R5. | Each functional entity identified as the owner of a newly identified or proposed key facility: | Retired | 2008-10-22 | 2014-04-01
505 | Directory # 8 | System Restoration | R5.1. | Shall identify the associated critical components for that key facility prior to implementation of the proposed facility as a key facility. | Retired | 2008-10-22 | 2014-04-01
506 | Directory # 8 | System Restoration | R5.2. | Shall provide a list of critical components associated with the proposed key facility upon request of the Reliability Coordinator within the timeframe requested. | Retired | 2008-10-22 | 2014-04-01
507 | Directory # 8 | System Restoration | R5.3. | Shall ensure that all applicable testing outlined in Appendix A has been successfully completed prior to implementation, or within the timeframe requested by the Reliability Coordinator, of the proposed key facility. | Retired | 2008-10-22 | 2014-04-01
508 | Directory # 8 | System Restoration | R6. | Each functional entity identified as the owner of an existing key facility: | Retired | 2008-10-22 | 2014-04-01
509 | Directory # 8 | System Restoration | R6.1. | Shall provide any updates, additions or deletions to the list of critical components for each identified key facility upon request of the Reliability Coordinator within the timeframe requested. | Retired | 2008-10-22 | 2014-04-01
510 | Directory # 8 | System Restoration | R6.2. | Shall ensure that all applicable testing outlined in Appendix A has been successfully completed for any updated or additional critical components associated with each identified key facility. | Retired | 2008-10-22 | 2014-04-01
511 | Directory # 8 | System Restoration | R7. | Following the occurrence of an event that required implementation of a system restoration plan and upon request of the Task Force on Coordination of Operation (TFCO): | Retired | 2008-10-22 | 2014-04-01
512 | Directory # 8 | System Restoration | R7.1. | The Reliability Coordinator shall report on the performance of its plan within the timeframe requested by the TFCO. | Retired | 2008-10-22 | 2014-04-01
513 | Directory # 8 | System Restoration | R7.2. | The Transmission Operator shall report on the performance of its plan within the timeframe requested by the TFCO. | Retired | 2008-10-22 | 2014-04-01
514 | Directory # 8 | System Restoration | R8. | Each functional entity which has been identified as owning a key facility shall: | Retired | 2008-10-22 | 2014-04-01
515 | Directory # 8 | System Restoration | R8.1. | Perform the tests outlined in Appendix A - Table 1 | Retired | 2008-10-22 | 2014-04-01
516 | Directory # 8 | System Restoration | R8.2. | Maintain records of the test results | Retired | 2008-10-22 | 2014-04-01
517 | Directory # 8 | System Restoration | R8.3. | Provide evidence, upon request, to the Reliability Coordinator and Transmission Operator within the timeframe requested that the tests specified in sub-Requirement R8.1 have been met. | Retired | 2008-10-22 | 2014-04-01
917 | Directory # 8 | System Restoration | R8.4.1. | R8.4 For each functional entity identified as owning Key Facilities, which is unable to perform a test outlined in Appendix A, a requested proposed alternate testing methodology may be permitted if each of the following criteria (R8.4.1-R8.4.6) are met: R8.4.1 Evidence must be provided to the Reliability Coordinator that conducting the specified Appendix A test would be detrimental to the operational functionality of the Key Facility. Note: The alternative testing methodology shall be reviewed on a periodic basis as determined by the Reliability Coordinator. Approval of the alternative testing methodology will either be renewed or revoked by the Reliability Coordinator. | Retired | 2008-10-22 | 2014-04-01
918 | Directory # 8 | System Restoration | R8.4.2. | R8.4 For each functional entity identified as owning Key Facilities, which is unable to perform a test outlined in Appendix A, a requested proposed alternate testing methodology may be permitted if each of the following criteria (R8.4.1-R8.4.6) are met: R8.4.2 The alternative testing methodology, with mitigating controls to meet the intent of the Directory Requirement, must be proposed to the Reliability Coordinator to evaluate and to accept or reject the requested proposed alternate testing methodology. Note: The alternative testing methodology shall be reviewed on a periodic basis as determined by the Reliability Coordinator. Approval of the alternative testing methodology will either be renewed or revoked by the Reliability Coordinator. | Retired | 2008-10-22 | 2014-04-01
919 | Directory # 8 | System Restoration | R8.4.3. | R8.4 For each functional entity identified as owning Key Facilities, which is unable to perform a test outlined in Appendix A, a requested proposed alternate testing methodology may be permitted if each of the following criteria (R8.4.1-R8.4.6) are met: R8.4.3 Post acceptance per R8.4.2, the alternative testing methodology must be successfully conducted. Note: The alternative testing methodology shall be reviewed on a periodic basis as determined by the Reliability Coordinator. Approval of the alternative testing methodology will either be renewed or revoked by the Reliability Coordinator. | Retired | 2008-10-22 | 2014-04-01
920 | Directory # 8 | System Restoration | R8.4.4. | R8.4 For each functional entity identified as owning Key Facilities, which is unable to perform a test outlined in Appendix A, a requested proposed alternate testing methodology may be permitted if each of the following criteria (R8.4.1-R8.4.6) are met: R8.4.4 Operation consistent with Good Utility Practice must be demonstrated and maintained throughout the alternative testing protocol. Note: The alternative testing methodology shall be reviewed on a periodic basis as determined by the Reliability Coordinator. Approval of the alternative testing methodology will either be renewed or revoked by the Reliability Coordinator. | Retired | 2008-10-22 | 2014-04-01
921 | Directory # 8 | System Restoration | R8.4.5. | R8.4 For each functional entity identified as owning Key Facilities, which is unable to perform a test outlined in Appendix A, a requested proposed alternate testing methodology may be permitted if each of the following criteria (R8.4.1-R8.4.6) are met: R8.4.5 The alternative testing methodology results must be submitted to the Reliability Coordinator. Note: The alternative testing methodology shall be reviewed on a periodic basis as determined by the Reliability Coordinator. Approval of the alternative testing methodology will either be renewed or revoked by the Reliability Coordinator. | Retired | 2008-10-22 | 2014-04-01
922 | Directory # 8 | System Restoration | R8.4.6. | R8.4 For each functional entity identified as owning Key Facilities, which is unable to perform a test outlined in Appendix A, a requested proposed alternate testing methodology may be permitted if each of the following criteria (R8.4.1-R8.4.6) are met: R8.4.6 Approval of the alternative testing methodology results must be received from the Reliability Coordinator. Note: The alternative testing methodology shall be reviewed on a periodic basis as determined by the Reliability Coordinator. Approval of the alternative testing methodology will either be renewed or revoked by the Reliability Coordinator. | Retired | 2008-10-22 | 2014-04-01
518 | Directory # 8 | System Restoration | R9. | Each functional entity that owns a cable pressurization system at a key facility shall test for satisfactory operation of both the primary pressurization system and/or the backup pressurization system (if applicable) ability(s) to maintain pressure upon loss of power to the key facility. This capability is required during a blackout to maintain the availability of cables for service and to preclude any damage to the cables as a result of the loss of dielectric strength. This test shall be conducted every six (6) calendar months by demonstrating that the required pressures can be maintained for a minimum of thirty (30) minutes. | Retired | 2008-10-22 | 2014-04-01
923 | Directory # 8 V1 | System Restoration | R1. | Each Reliability Coordinator shall develop and maintain a restoration plan for its Reliability Coordinator Area that shall: | Retired | 2014-04-02 | 2017-10-05
924 | Directory # 8 V1 | System Restoration | R1.1. | Identify the Reliability Coordinator Area’s basic minimum power system(s). | Retired | 2014-04-02 | 2017-10-05
925 | Directory # 8 V1 | System Restoration | R1.2. | Address the priority of restoring off-site power to nuclear plants; | Retired | 2014-04-02 | 2017-10-05
926 | Directory # 8 V1 | System Restoration | R1.3. | Identify interconnection points with adjacent Reliability Coordinator areas; | Retired | 2014-04-02 | 2017-10-05
927 | Directory # 8 V1 | System Restoration | R1.4. | Identify parameters to synchronize adjacent basic minimum power systems; | Retired | 2014-04-02 | 2017-10-05
928 | Directory # 8 V1 | System Restoration | R1.5. | Address coordination of system restoration with neighboring Reliability Coordinator areas; | Retired | 2014-04-02 | 2017-10-05
929 | Directory # 8 V1 | System Restoration | R1.6. | Provide for the re-energization of transmission systems to major generating stations, including inter-area tie points; | Retired | 2014-04-02 | 2017-10-05
930 | Directory # 8 V1 | System Restoration | R1.7. | Address electrical island stabilization; | Retired | 2014-04-02 | 2017-10-05
931 | Directory # 8 V1 | System Restoration | R1.8. | Identify provisions for fuel resources to support operation of any supplementary generators (e.g., a diesel generator) necessary for operating key facilities consistent with the expected requirements of the Restoration Plan. | Retired | 2014-04-02 | 2017-10-05
932 | Directory # 8 V1 | System Restoration | R10. | Each functional entity shall test its backup power supplies identified as critical components as specified below. Where there are separate backup power arrangements at a key facility for transmission or generating station equipment and telecommunication equipment, they shall be separately identified in the critical components list and shall be inspected and tested individually. | Retired | 2014-04-02 | 2017-10-05
933 | Directory # 8 V1 | System Restoration | R10.1. | Equipment Inspection: A battery and/or battery charger identified as a critical component shall be inspected in accordance with maintenance activities and maintenance intervals specified in PRC-005-Protection System, Automatic Reclosing, and Sudden Pressure Relaying Maintenance. (Reference: Table 1; Test KF-1) | Retired | 2014-04-02 | 2017-10-05
934 | Directory # 8 V1 | System Restoration | R10.2. | Equipment Verification A battery and battery charger identified as critical components shall be verified in accordance with maintenance activities and maintenance intervals specified in PRC-005 Protection System, Automatic Reclosing, and Sudden Pressure Relaying Maintenance. (Reference: Table 1; Test KF-2) | Retired | 2014-04-02 | 2017-10-05
935 | Directory # 8 V1 | System Restoration | R10.3. | Confirm that all Critical Component Loads can be Supplied The owner of batteries or battery chargers identified as critical components shall confirm that all critical component loads are connected to and can be supplied by the batteries and battery chargers. At least every sixty (60) calendar months, or when modifications are made to the key facility, the functional entity owner shall confirm through its design review or through testing that all critical component loads are connected to and can be sufficiently supplied by the batteries and battery chargers. (Reference: Table 1; Test KF-3) | Retired | 2014-04-02 | 2017-10-05
936 | Directory # 8 V1 | System Restoration | R10.4. | Startup and Run Test The owner of a backup power generator identified as a critical component of a key facility, shall perform a monthly startup and run test on that backup power generator for a minimum run time of fifteen (15) minutes. (Reference: Table 1; Test KF-5). Note: This test also applies to supplemental generation required for blackstart capability and to a control center and telecommunication center backup power generator. | Retired | 2014-04-02 | 2017-10-05
937 | Directory # 8 V1 | System Restoration | R10.5. | Startup, Transfer and Load Test The owner of a backup power generator identified as a critical component of a key facility shall verify that the backup power generator will pick up the critical component load following the loss of station service. Note: This test also applies to a control center and telecommunication center backup power generator. For automatically started backup power generators, a startup, transfer and run test simulating the loss of station service will be performed every twelve (12) calendar months for a duration of at least thirty (30) minutes. (Reference: Table 1; Test KF-6) For manually started backup power generators, the asset owner shall every twelve (12) calendar months start the generator and verify stable operation for thirty (30) minutes while supplying critical component loads. (Reference: Table 1; Test KF-6) Note: Power sources used to start blackstart units will be excluded from test KF-6. | Retired | 2014-04-02 | 2017-10-05
938 | Directory # 8 V1 | System Restoration | R11. | Each functional entity identified as owning key facilities shall test its critical components in the control centers and the telecommunication centers identified as key facilities to demonstrate that the computer systems will be functional when required for system restoration, without dependencies on power sources that may be unavailable during a partial or complete system blackout. | Retired | 2014-04-02 | 2017-10-05
939 | Directory # 8 V1 | System Restoration | R11.1. | AC Supply Interruption Test The uninterruptible power supply (UPS) systems in control centers and telecommunication centers shall be tested every twelve (12) calendar months by interrupting AC supply and verifying that all critical component loads are supplied for a time that is sufficient for backup power sources to restore the AC input to the UPS. (Reference: Table 1; Test CC-1) | Retired | 2014-04-02 | 2017-10-05
940 | Directory # 8 V1 | System Restoration | R11.2. | Computer Redundancy (SCADA/EMS) Test Each functional entity identified as owning a key facility shall test its computer redundancy (SCADA/EMS) features every six (6) calendar months to ensure computer systems (SCADA/EMS) continue to function adequately. (Reference: Table 1; Test CC--2) | Retired | 2014-04-02 | 2017-10-05
941 | Directory # 8 V1 | System Restoration | R12. | Each functional entity owning a generating station with blackstart capability shall verify such capability as follows: | Retired | 2014-04-02 | 2017-10-05
942 | Directory # 8 V1 | System Restoration | R12.1. | Operations voice communications and auxiliary systems such as Supervisory Control and Data Acquisition (SCADA) that are required for blackstart shall be verified at least every twelve (12) calendar months to operate adequately without dependency on the interconnected system or other unrelated unit for any source of station service. | Retired | 2014-04-02 | 2017-10-05
943 | Directory # 8 V1 | System Restoration | R12.2. | A generating station with blackstart capability shall be tested every twelve (12) calendar months for successful equipment startup and energize a transmission element or a generating station switchyard element if that doesn’t involve the disconnection of load that is not dedicated generating station load to conduct the test. Verify stable operation while isolated from the bulk power system for a minimum of ten minutes. (Reference: Table 1; Test BS-1). (Reference: Appendix A-Table 1; Test No. BS-1) | Retired | 2014-04-02 | 2017-10-05
944 | Directory # 8 V1 | System Restoration | R13. | Reliability Coordinators shall determine the number of units within a generating station that are to be tested for blackstart capability as required by their respective system restoration plans, and shall notify the applicable functional entity. | Retired | 2014-04-02 | 2017-10-05
945 | Directory # 8 V1 | System Restoration | R14. | Each Reliability Coordinator shall confirm that the functional entity owning a generating station with blackstart capability that is part of the basic minimum power system has completed a successful blackstart test consistent with the objectives of the Reliability Coordinator’s system restoration plan. | Retired | 2014-04-02 | 2017-10-05
946 | Directory # 8 V1 | System Restoration | R15. | A functional entity that has confirmed the loss of functionality of a critical component shall report to the Transmission Operator responsible for operating that critical component of that critical component’s loss of functional availability as soon as possible but no longer than 15 minutes after becoming aware of the condition. | Retired | 2014-04-02 | 2017-10-05
947 | Directory # 8 V1 | System Restoration | R15.1. | The Transmission Operator shall report to its Reliability Coordinator as soon as possible but no longer than 15 minutes after the functional entity has made the Transmission Operator aware of the loss of functionality of the critical component. Examples of such conditions are but not limited to: • Loss of control of remote equipment; • Complete loss of AC or DC service supply; • Loss of blackstart facilities. | Retired | 2014-04-02 | 2017-10-05
948 | Directory # 8 V1 | System Restoration | R16. | A functional entity that has confirmed the loss of redundancy of a critical component shall report to the Transmission Operator responsible for that critical component as soon as possible but no longer than 12 hours after the functional entity’s staff has confirmed the loss of redundancy for the critical component. Examples of such conditions are: • Loss of a redundant AC or DC service supply; • Loss of redundant blackstart critical components. | Retired | 2014-04-02 | 2017-10-05
949 | Directory # 8 V1 | System Restoration | R17. | A functional entity that has scheduled a maintenance condition of a critical component that will result in the loss of functionality of that critical component shall report that maintenance condition to the Transmission Operator responsible for the critical component at least 24 hours prior to that scheduled loss of functionality. | Retired | 2014-04-02 | 2017-10-05
950 | Directory # 8 V1 | System Restoration | R17.1. | The functional entity shall report to the Transmission Operator responsible for the critical component as soon as possible after the loss of functionality has occurred. | Retired | 2014-04-02 | 2017-10-05
951 | Directory # 8 V1 | System Restoration | R17.2. | If the scheduled maintenance condition causing the loss of functionality of a critical component affects the functionality of a key facility, the Transmission Operator responsible for the critical component shall report this scheduled maintenance condition to its Reliability Coordinator. | Retired | 2014-04-02 | 2017-10-05
952 | Directory # 8 V1 | System Restoration | R18. | A functional entity shall report the actions to be taken to restore a critical component’s availability or redundancy to the Transmission Operator responsible for the critical component as soon as known. | Retired | 2014-04-02 | 2017-10-05
953 | Directory # 8 V1 | System Restoration | R18.1. | The functional entity shall report to the Transmission Operator responsible for that critical component the anticipated time that the critical components functionality will be restored. | Retired | 2014-04-02 | 2017-10-05
954 | Directory # 8 V1 | System Restoration | R18.2. | The functional entity shall report to the Transmission Operator responsible for maintaining redundancy for a critical component the anticipated time that the critical component’s redundancy will be restored. | Retired | 2014-04-02 | 2017-10-05
955 | Directory # 8 V1 | System Restoration | R19. | A functional entity shall report the date and time when the functional availability of a critical component is restored to the Transmission Operator responsible for the critical component as soon as known. | Retired | 2014-04-02 | 2017-10-05
956 | Directory # 8 V1 | System Restoration | R2. | In determining the basic minimum power system, the Reliability Coordinator shall involve all affected parties or functional entities. | Retired | 2014-04-02 | 2017-10-05
957 | Directory # 8 V1 | System Restoration | R3. | The Reliability Coordinator shall ensure that the basic minimum power system includes the ability to: | Retired | 2014-04-02 | 2017-10-05
958 | Directory # 8 V1 | System Restoration | R3.1. | Utilize generator blackstart capability; | Retired | 2014-04-02 | 2017-10-05
959 | Directory # 8 V1 | System Restoration | R3.2. | Form an electrical island(s); | Retired | 2014-04-02 | 2017-10-05
960 | Directory # 8 V1 | System Restoration | R3.3. | Synchronize electrical islands; and | Retired | 2014-04-02 | 2017-10-05
961 | Directory # 8 V1 | System Restoration | R3.4. | Permit the continuation of the system restoration plan. | Retired | 2014-04-02 | 2017-10-05
962 | Directory # 8 V1 | System Restoration | R4. | Each Reliability Coordinator shall identify key facilities and shall inform each functional entity of its identified key facilities. | Retired | 2014-04-02 | 2017-10-05
963 | Directory # 8 V1 | System Restoration | R5. | Each functional entity identified as the owner of a newly identified or proposed key facility: | Retired | 2014-04-02 | 2017-10-05
964 | Directory # 8 V1 | System Restoration | R5.1. | Shall identify the associated critical components for that key facility prior to implementation of the proposed facility as a key facility. | Retired | 2014-04-02 | 2017-10-05
965 | Directory # 8 V1 | System Restoration | R5.2. | Shall provide a list of critical components associated with the proposed key facility upon request of the Reliability Coordinator within the timeframe requested. | Retired | 2014-04-02 | 2017-10-05
966 | Directory # 8 V1 | System Restoration | R5.3. | Shall ensure that all applicable testing outlined in Appendix A has been successfully completed prior to implementation, or within the timeframe requested by the Reliability Coordinator, of the proposed key facility. | Retired | 2014-04-02 | 2017-10-05
967 | Directory # 8 V1 | System Restoration | R6. | Each functional entity identified as the owner of an existing key facility: | Retired | 2014-04-02 | 2017-10-05
968 | Directory # 8 V1 | System Restoration | R6.1. | Shall provide any updates, additions or deletions to the list of critical components for each identified key facility upon request of the Reliability Coordinator within the timeframe requested. | Retired | 2014-04-02 | 2017-10-05
969 | Directory # 8 V1 | System Restoration | R6.2. | Shall ensure that all applicable testing outlined in Appendix A has been successfully completed for any updated or additional critical components associated with each identified key facility. | Retired | 2014-04-02 | 2017-10-05
970 | Directory # 8 V1 | System Restoration | R7. | Following the occurrence of an event that required implementation of a system restoration plan and upon request of the Task Force on Coordination of Operation (TFCO): | Retired | 2014-04-02 | 2017-10-05
971 | Directory # 8 V1 | System Restoration | R7.1. | The Reliability Coordinator shall report on the performance of its plan within the timeframe requested by the TFCO. | Retired | 2014-04-02 | 2017-10-05
972 | Directory # 8 V1 | System Restoration | R7.2. | The Transmission Operator shall report on the performance of its plan within the timeframe requested by the TFCO. | Retired | 2014-04-02 | 2017-10-05
973 | Directory # 8 V1 | System Restoration | R8. | Each functional entity which has been identified as owning a key facility shall: | Retired | 2014-04-02 | 2017-10-05
974 | Directory # 8 V1 | System Restoration | R8.1. | Perform the tests outlined in Appendix A - Table 1 | Retired | 2014-04-02 | 2017-10-05
975 | Directory # 8 V1 | System Restoration | R8.2. | Maintain records of the test results | Retired | 2014-04-02 | 2017-10-05
976 | Directory # 8 V1 | System Restoration | R8.3. | Provide evidence, upon request, to the Reliability Coordinator and Transmission Operator within the timeframe requested that the tests specified in sub-Requirement R8.1 have been met. | Retired | 2014-04-02 | 2017-10-05
977 | Directory # 8 V1 | System Restoration | R8.4.1. | R8.4 For each functional entity identified as owning Key Facilities, which is unable to perform a test outlined in Appendix A, a requested proposed alternate testing methodology may be permitted if each of the following criteria (R8.4.1-R8.4.6) are met: R8.4.1 Evidence must be provided to the Reliability Coordinator that conducting the specified Appendix A test would be detrimental to the operational functionality of the Key Facility. Note: The alternative testing methodology shall be reviewed on a periodic basis as determined by the Reliability Coordinator. Approval of the alternative testing methodology will either be renewed or revoked by the Reliability Coordinator. | Retired | 2014-04-02 | 2017-10-05
978 | Directory # 8 V1 | System Restoration | R8.4.2. | R8.4 For each functional entity identified as owning Key Facilities, which is unable to perform a test outlined in Appendix A, a requested proposed alternate testing methodology may be permitted if each of the following criteria (R8.4.1-R8.4.6) are met: R8.4.2 The alternative testing methodology, with mitigating controls to meet the intent of the Directory Requirement, must be proposed to the Reliability Coordinator to evaluate and to accept or reject the requested proposed alternate testing methodology. Note: The alternative testing methodology shall be reviewed on a periodic basis as determined by the Reliability Coordinator. Approval of the alternative testing methodology will either be renewed or revoked by the Reliability Coordinator. | Retired | 2014-04-02 | 2017-10-05
979 | Directory # 8 V1 | System Restoration | R8.4.3. | R8.4 For each functional entity identified as owning Key Facilities, which is unable to perform a test outlined in Appendix A, a requested proposed alternate testing methodology may be permitted if each of the following criteria (R8.4.1-R8.4.6) are met: R8.4.3 Post acceptance per R8.4.2, the alternative testing methodology must be successfully conducted. Note: The alternative testing methodology shall be reviewed on a periodic basis as determined by the Reliability Coordinator. Approval of the alternative testing methodology will either be renewed or revoked by the Reliability Coordinator. | Retired | 2014-04-02 | 2017-10-05
980 | Directory # 8 V1 | System Restoration | R8.4.4. | R8.4 For each functional entity identified as owning Key Facilities, which is unable to perform a test outlined in Appendix A, a requested proposed alternate testing methodology may be permitted if each of the following criteria (R8.4.1-R8.4.6) are met: R8.4.4 Operation consistent with Good Utility Practice must be demonstrated and maintained throughout the alternative testing protocol. Note: The alternative testing methodology shall be reviewed on a periodic basis as determined by the Reliability Coordinator. Approval of the alternative testing methodology will either be renewed or revoked by the Reliability Coordinator. | Retired | 2014-04-02 | 2017-10-05
981 | Directory # 8 V1 | System Restoration | R8.4.5. | R8.4 For each functional entity identified as owning Key Facilities, which is unable to perform a test outlined in Appendix A, a requested proposed alternate testing methodology may be permitted if each of the following criteria (R8.4.1-R8.4.6) are met: R8.4.5 The alternative testing methodology results must be submitted to the Reliability Coordinator. Note: The alternative testing methodology shall be reviewed on a periodic basis as determined by the Reliability Coordinator. Approval of the alternative testing methodology will either be renewed or revoked by the Reliability Coordinator. | Retired | 2014-04-02 | 2017-10-05
982 | Directory # 8 V1 | System Restoration | R8.4.6. | R8.4 For each functional entity identified as owning Key Facilities, which is unable to perform a test outlined in Appendix A, a requested proposed alternate testing methodology may be permitted if each of the following criteria (R8.4.1-R8.4.6) are met: R8.4.6 Approval of the alternative testing methodology results must be received from the Reliability Coordinator. Note: The alternative testing methodology shall be reviewed on a periodic basis as determined by the Reliability Coordinator. Approval of the alternative testing methodology will either be renewed or revoked by the Reliability Coordinator. | Retired | 2014-04-02 | 2017-10-05
983 | Directory # 8 V1 | System Restoration | R9. | Each functional entity that owns a cable pressurization system at a key facility shall test for satisfactory operation of both the primary pressurization system and/or the backup pressurization system (if applicable) ability(s) to maintain pressure upon loss of power to the key facility. This capability is required during a blackout to maintain the availability of cables for service and to preclude any damage to the cables as a result of the loss of dielectric strength. This test shall be conducted every six (6) calendar months by demonstrating that the required pressures can be maintained for a minimum of thirty (30) minutes. | Retired | 2014-04-02 | 2017-10-05
984 | Directory # 8 V2 | System Restoration | R1. | Each Reliability Coordinator, together with its respective Transmission Operators, shall jointly develop, maintain, verify, and implement a system restoration plan for its Reliability Coordinator Area that shall: | Retired | 2017-10-06 | 2018-02-15
985 | Directory # 8 V2 | System Restoration | R1.1. | Identify the Reliability Coordinator Area’s BMPS(s). | Retired | 2017-10-06 | 2018-02-15
986 | Directory # 8 V2 | System Restoration | R1.2. | Address the priority of providing off-site AC power to nuclear power stations. | Retired | 2017-10-06 | 2018-02-15
987 | Directory # 8 V2 | System Restoration | R1.3. | Identify Interconnection points with adjacent Reliability Coordinator Areas. | Retired | 2017-10-06 | 2018-02-15
988 | Directory # 8 V2 | System Restoration | R1.4. | Identify parameters to Synchronize adjacent BMPSs | Retired | 2017-10-06 | 2018-02-15
989 | Directory # 8 V2 | System Restoration | R1.5. | Address coordination of system restoration with neighboring Reliability Coordinator Areas. | Retired | 2017-10-06 | 2018-02-15
990 | Directory # 8 V2 | System Restoration | R1.6. | Provide for the re-energization of transmission systems to; R1.6.1 major generating stations; R1.6.2 inter-area tie points. | Retired | 2017-10-06 | 2018-02-15
991 | Directory # 8 V2 | System Restoration | R1.7. | Address electrical Island stabilization. | Retired | 2017-10-06 | 2018-02-15
992 | Directory # 8 V2 | System Restoration | R1.8. | Identify provisions for fuel resources to support operation of any supplementary generators (e.g., a diesel generator) necessary for operating Key Facilities consistent with the expected requirements of the system restoration plan. | Retired | 2017-10-06 | 2018-02-15
993 | Directory # 8 V2 | System Restoration | R10. | Each functional entity shall test its backup power supplies identified as Critical Components as specified in R10.1 through R10.5. Where there are separate backup power arrangements at Key Facilities for transmission or generating station equipment and telecommunication equipment, such equipment shall be separately identified on the list of Critical Components and shall be inspected and tested individually. | Retired | 2017-10-06 | 2018-02-15
994 | Directory # 8 V2 | System Restoration | R10.1. | Equipment Inspection Batteries and/or battery chargers identified as Critical Components shall be inspected in accordance with maintenance activities and maintenance intervals specified in PRC-005-Protection System, Automatic Reclosing, and Sudden Pressure Relaying Maintenance, giving consideration to exclusions per PRC-005 Table 1-4(f) (Reference: Appendix A; Test KF-1) | Retired | 2017-10-06 | 2018-02-15
995 | Directory # 8 V2 | System Restoration | R10.2. | Equipment Verification Batteries and/or battery chargers identified as Critical Components shall be verified in accordance with maintenance activities and maintenance intervals specified in PRC-005 Protection System, Automatic Reclosing, and Sudden Pressure Relaying Maintenance, giving consideration to exclusions per PRC-005 Table 1-4(f) (Reference: Appendix A; Test KF-2) | Retired | 2017-10-06 | 2018-02-15
996 | Directory # 8 V2 | System Restoration | R10.3. | Confirm That All Critical Components Loads Can Be Supplied Each owner of batteries and/or battery chargers identified as Critical Components shall confirm that all Critical Components Loads are connected to and can be supplied by the batteries and/or battery chargers. The functional entity owner shall confirm through its design review, when modifications are made to Key Facilities, or through testing, that all Critical Components Loads are connected to and can be sufficiently supplied by the batteries and/or battery chargers. Test basis: Frequency: when modifications are made to Key Facilities or at least once every sixty (60) Calendar Months (Reference: Appendix A; Test KF-3) | Retired | 2017-10-06 | 2018-02-15
997 | Directory # 8 V2 | System Restoration | R10.4. | Startup and Run Test Each owner of a backup power generator identified on the list of Critical Components of Key Facilities, shall perform a startup, and run test on that backup power generator. Test basis: Frequency: monthly Duration: at least fifteen (15) minutes (Reference: Appendix A; Test KF-5). Note: This test also applies to supplemental generation required for Blackstart Capability and to a control center and telecommunication center backup power generator. | Retired | 2017-10-06 | 2018-02-15
998 | Directory # 8 V2 | System Restoration | R10.5. | Startup, Transfer and Load Test Each owner of a backup power generator identified on the list of Critical Components of Key Facilities shall verify that the backup power generator will pick up the Critical Components Load following the loss of station service. Note: This test also applies to a control center and telecommunication center backup power generator. For automatically started backup power generators, a startup, transfer, and Load test simulating the loss of station service shall be performed. Test basis: Frequency: every twelve (12) Calendar Months Duration: at least thirty (30) minutes (Reference: Appendix A; Test KF-6) For manually started backup power generators, a startup, transfer, and Load test performed by starting the generator and verifying Reliable Operation while supplying Critical Components Loads, shall be performed by the asset owner. Test basis: Frequency: every twelve (12) Calendar Months Duration: at least thirty (30) minutes (Reference: Appendix A; Test KF-6) Note: Power sources used to start Resources with Blackstart Capability will be excluded from test KF-6. | Retired | 2017-10-06 | 2018-02-15
999 | Directory # 8 V2 | System Restoration | R11. | Each functional entity identified as owning Key Facilities shall test its Critical Components in the control centers and the telecommunication centers identified as Key Facilities to demonstrate that the computer systems will be functional without dependencies on power sources that may be unavailable during a partial or complete system blackout, when required for system restoration. | Retired | 2017-10-06 | 2018-02-15
1000 | Directory # 8 V2 | System Restoration | R11.1. | AC Supply Interruption Test The uninterruptible power supply (UPS) systems in control centers and telecommunication centers shall be tested by interrupting AC supply and verifying that all Critical Components Loads are supplied for a time that is sufficient for backup power sources to restore the AC input to the UPS Test basis: Frequency: every twelve (12) Calendar Months. (Reference: Appendix A; Test CC-1) | Retired | 2017-10-06 | 2018-02-15
1001 | Directory # 8 V2 | System Restoration | R11.2. | Computer Redundancy (SCADA/EMS) Test Each functional entity identified as owning Key Facilities shall test its computer redundancy (SCADA/EMS) features to ensure computer systems (SCADA/EMS) continue to function consistent with Good Utility Practice. Test basis: Frequency: every six (6) Calendar Months (Reference: Appendix A; Test CC-2) | Retired | 2017-10-06 | 2018-02-15
1002 | Directory # 8 V2 | System Restoration | R12. | Each functional entity owning a generating station with Blackstart Capability shall verify such concurrent capability as follows: | Retired | 2017-10-06 | 2018-02-15
1003 | Directory # 8 V2 | System Restoration | R12.1. | A generating station with Blackstart Capability shall be tested for successful equipment startup, sufficient to Energize a transmission Element or a generating station switchyard Element, if that does not involve the disconnection of Load that is not dedicated generating station Load to conduct the test. Verify Reliable Operation while isolated from the BPS . Test basis: Frequency: every twelve (12) Calendar Months Duration: at least ten (10) minutes of Reliable Operation (Reference: Appendix A; Test No. BS-1) | Retired | 2017-10-06 | 2018-02-15
1004 | Directory # 8 V2 | System Restoration | R12.2. | Operations voice communications and auxiliary systems such as Supervisory Control and Data Acquisition (SCADA) that are required for Blackstart Capability shall be verified to operate consistent with Good Utility Practice independent of the interconnected system or other unrelated unit for any source of station service. Test basis: Frequency: every twelve (12) Calendar Months Duration: Verification of at least ten (10) minutes of Reliable Operation concurrent with R12.1 (Reference: Appendix A; Test No. BS-1) | Retired | 2017-10-06 | 2018-02-15
1005 | Directory # 8 V2 | System Restoration | R13. | Each Reliability Coordinator shall determine, as required by its respective system restoration plan, the number of units within a generating station that are to be tested for Blackstart Capability, and shall notify the applicable functional entity/entities. | Retired | 2017-10-06 | 2018-02-15
1006 | Directory # 8 V2 | System Restoration | R14. | Each Reliability Coordinator shall confirm, consistent with the objectives of its respective system restoration plan, that the functional entity owning a generating station with Blackstart Capability that is part of the BMPS has completed a successful Blackstart Capabilitytest. | Retired | 2017-10-06 | 2018-02-15
1007 | Directory # 8 V2 | System Restoration | R15. | A functional entity that has confirmed the loss of functionality of Critical Components shall report to the Transmission Operator responsible for operating the Critical Components of the Critical Components’ loss of functionality as soon as possible but no longer than 15 minutes after confirmation of the loss of functionality. | Retired | 2017-10-06 | 2018-02-15
1008 | Directory # 8 V2 | System Restoration | R15.1. | The Transmission Operator shall report to its Reliability Coordinator, as soon as possible but no longer than 15 minutes after the functional entity has confirmed the loss of functionality of Critical Components to the Transmission Operator. Examples of such conditions are, but not limited to: • Loss of control of remote equipment. • Complete loss of AC or DC service supply. • Loss of Resources with Blackstart Capability. | Retired | 2017-10-06 | 2018-02-15
1009 | Directory # 8 V2 | System Restoration | R16. | A functional entity that has confirmed the loss of redundancy of Critical Components shall report to the Transmission Operator responsible for the Critical Components of loss of redundancy as soon as possible but no longer than 12 hours after confirmation of the loss of redundancy. Examples of such conditions are: • Loss of a redundant AC or DC service supply. • Loss of redundant Critical Components associated with Resources with Blackstart Capability. | Retired | 2017-10-06 | 2018-02-15
1010 | Directory # 8 V2 | System Restoration | R17. | A functional entity that has scheduled a maintenance activity (inservice or out-of-service) of Critical Components that will result in the loss of functionality of the Critical Components shall report that maintenance activity to the Transmission Operator responsible for the Critical Components at least 24 hours prior to that scheduled loss of functionality. | Retired | 2017-10-06 | 2018-02-15
1011 | Directory # 8 V2 | System Restoration | R17.1. | The functional entity shall report to the Transmission Operator responsible for Critical Components as soon as possible after the scheduled loss of functionality has begun. | Retired | 2017-10-06 | 2018-02-15
1012 | Directory # 8 V2 | System Restoration | R17.2. | If the scheduled maintenance condition causing the loss of functionality of Critical Components affects the functionality of Key Facilities, the Transmission Operator responsible for the Critical Components shall report this scheduled maintenance condition to its Reliability Coordinator. • Upon receipt of the scheduled maintenance report • Upon receipt of the scheduled maintenance start • Upon receipt of the scheduled maintenance end | Retired | 2017-10-06 | 2018-02-15
1013 | Directory # 8 V2 | System Restoration | R18. | A functional entity shall report the actions to be taken to restore Critical Components’ availability or redundancy to the Transmission Operator responsible for the Critical Components as soon as known. | Retired | 2017-10-06 | 2018-02-15
1014 | Directory # 8 V2 | System Restoration | R18.1. | The functional entity shall report to the Transmission Operator responsible for the Critical Components the anticipated time that the Critical Components functionality will be restored. | Retired | 2017-10-06 | 2018-02-15
1015 | Directory # 8 V2 | System Restoration | R18.2. | The functional entity shall report to the Transmission Operator responsible for maintaining redundancy for Critical Components the anticipated time that the Critical Components’ redundancy will be restored. | Retired | 2017-10-06 | 2018-02-15
1016 | Directory # 8 V2 | System Restoration | R19. | A functional entity shall report to the Transmission Operator responsible for the functionality of Critical Components, the date and time when the functionality of Critical Components is restored. | Retired | 2017-10-06 | 2018-02-15
1017 | Directory # 8 V2 | System Restoration | R2. | Each Reliability Coordinator shall, in determining the BMPS, coordinate with all impacted parties and/or functional entities. | Retired | 2017-10-06 | 2018-02-15
1018 | Directory # 8 V2 | System Restoration | R3. | Each Reliability Coordinator shall ensure that the BMPS includes the ability to: | Retired | 2017-10-06 | 2018-02-15
1019 | Directory # 8 V2 | System Restoration | R3.1. | Use generator Blackstart Capability. | Retired | 2017-10-06 | 2018-02-15
1020 | Directory # 8 V2 | System Restoration | R3.2. | Form an electrical Island(s). | Retired | 2017-10-06 | 2018-02-15
1021 | Directory # 8 V2 | System Restoration | R3.3. | Synchronize electrical Islands; and | Retired | 2017-10-06 | 2018-02-15
1022 | Directory # 8 V2 | System Restoration | R3.4. | Permit the successful performance of the system restoration plan. | Retired | 2017-10-06 | 2018-02-15
1023 | Directory # 8 V2 | System Restoration | R4. | Each Reliability Coordinator shall identify Key Facilities and shall inform each functional entity of its identified Key Facilities. | Retired | 2017-10-06 | 2018-02-15
1024 | Directory # 8 V2 | System Restoration | R5. | Each functional entity identified as the owner of newly identified or proposed Key Facilities: | Retired | 2017-10-06 | 2018-02-15
1025 | Directory # 8 V2 | System Restoration | R5.1. | Shall identify the associated Critical Components for those Key Facilities prior to the effective date of the approved system restoration plan. | Retired | 2017-10-06 | 2018-02-15
1026 | Directory # 8 V2 | System Restoration | R5.2. | Shall provide, upon request of the Reliability Coordinator, within the timeframe requested, a list of Critical Components associated with proposed Key Facilities. | Retired | 2017-10-06 | 2018-02-15
1027 | Directory # 8 V2 | System Restoration | R5.3. | Shall ensure, prior to the effective date of the approved system restoration plan, or within the timeframe requested by the Reliability Coordinator, that all applicable proposed Key Facilities testing outlined in Appendix A has been successfully completed. | Retired | 2017-10-06 | 2018-02-15
1028 | Directory # 8 V2 | System Restoration | R6. | Each functional entity identified as the owner of existing Key Facilities: | Retired | 2017-10-06 | 2018-02-15
1029 | Directory # 8 V2 | System Restoration | R6.1. | Shall provide, upon request of the Reliability Coordinator, within the timeframe requested, any updates, additions, or deletions to the list of Critical Components for identified Key Facilities. | Retired | 2017-10-06 | 2018-02-15
1030 | Directory # 8 V2 | System Restoration | R6.2. | Shall ensure, prior to the effective date of the approved system restoration plan, or within the timeframe requested by the Reliability Coordinator, that the following components associated with identified Key Facilities testing outlined in Appendix A have been successfully completed: R6.2.1 All applicable additional Critical Components R6.2.2 Any modifications to existing Critical Components that could potentially impact the functionality of those Critical Components. | Retired | 2017-10-06 | 2018-02-15
1031 | Directory # 8 V2 | System Restoration | R7. | Following the occurrence of an event that required implementation of a system restoration plan and upon request of the Task Force on Coordination of Operation (TFCO): | Retired | 2017-10-06 | 2018-02-15
1032 | Directory # 8 V2 | System Restoration | R7.1. | The Reliability Coordinator shall report, within the timeframe requested by the TFCO, on the performance of its system restoration plan. | Retired | 2017-10-06 | 2018-02-15
1033 | Directory # 8 V2 | System Restoration | R7.2. | The Transmission Operator shall report, within the timeframe requested by the TFCO, on the performance of its system restoration plan. | Retired | 2017-10-06 | 2018-02-15
1034 | Directory # 8 V2 | System Restoration | R8. | Each functional entity which has been identified as owning Key Facilities shall: | Retired | 2017-10-06 | 2018-02-15
1035 | Directory # 8 V2 | System Restoration | R8.1. | Perform the tests outlined in Appendix A. | Retired | 2017-10-06 | 2018-02-15
1036 | Directory # 8 V2 | System Restoration | R8.2. | Maintain evidence of the test results consistent with Section 4.0. | Retired | 2017-10-06 | 2018-02-15
1037 | Directory # 8 V2 | System Restoration | R8.3. | Provide evidence, upon request of the Reliability Coordinator and/or Transmission Operator, within the timeframe requested, that the tests specified in sub-Requirement R8.1 have been met. | Retired | 2017-10-06 | 2018-02-15
1472 | Directory # 8 V2 | System Restoration | R8.4.1. | R8.4 For each functional entity identified as owning Key Facilities, which is unable to perform a test outlined in Appendix A, a requested proposed alternate testing methodology may be permitted if each of the following criteria (R8.4.1-R8.4.6) are met: R8.4.1 Evidence must be provided to the Reliability Coordinator that conducting the specified Appendix A test would be detrimental to the operational functionality of the Key Facility. Note: The alternative testing methodology shall be reviewed on a periodic basis as determined by the Reliability Coordinator. Approval of the alternative testing methodology will either be renewed or revoked by the Reliability Coordinator. | Retired | 2017-10-06 | 2018-02-15
1473 | Directory # 8 V2 | System Restoration | R8.4.2. | R8.4 For each functional entity identified as owning Key Facilities, which is unable to perform a test outlined in Appendix A, a requested proposed alternate testing methodology may be permitted if each of the following criteria (R8.4.1-R8.4.6) are met: R8.4.2 The alternative testing methodology, with mitigating controls to meet the intent of the Directory Requirement, must be proposed to the Reliability Coordinator to evaluate and to accept or reject the requested proposed alternate testing methodology. Note: The alternative testing methodology shall be reviewed on a periodic basis as determined by the Reliability Coordinator. Approval of the alternative testing methodology will either be renewed or revoked by the Reliability Coordinator. | Retired | 2017-10-06 | 2018-02-15
1474 | Directory # 8 V2 | System Restoration | R8.4.3. | R8.4 For each functional entity identified as owning Key Facilities, which is unable to perform a test outlined in Appendix A, a requested proposed alternate testing methodology may be permitted if each of the following criteria (R8.4.1-R8.4.6) are met: R8.4.3 Post acceptance per R8.4.2, the alternative testing methodology must be successfully conducted. Note: The alternative testing methodology shall be reviewed on a periodic basis as determined by the Reliability Coordinator. Approval of the alternative testing methodology will either be renewed or revoked by the Reliability Coordinator. | Retired | 2017-10-06 | 2018-02-15
1475 | Directory # 8 V2 | System Restoration | R8.4.4. | R8.4 For each functional entity identified as owning Key Facilities, which is unable to perform a test outlined in Appendix A, a requested proposed alternate testing methodology may be permitted if each of the following criteria (R8.4.1-R8.4.6) are met: R8.4.4 Operation consistent with Good Utility Practice must be demonstrated and maintained throughout the alternative testing protocol. Note: The alternative testing methodology shall be reviewed on a periodic basis as determined by the Reliability Coordinator. Approval of the alternative testing methodology will either be renewed or revoked by the Reliability Coordinator. | Retired | 2017-10-06 | 2018-02-15
1476 | Directory # 8 V2 | System Restoration | R8.4.5. | R8.4 For each functional entity identified as owning Key Facilities, which is unable to perform a test outlined in Appendix A, a requested proposed alternate testing methodology may be permitted if each of the following criteria (R8.4.1-R8.4.6) are met: R8.4.5 The alternative testing methodology results must be submitted to the Reliability Coordinator. Note: The alternative testing methodology shall be reviewed on a periodic basis as determined by the Reliability Coordinator. Approval of the alternative testing methodology will either be renewed or revoked by the Reliability Coordinator. | Retired | 2017-10-06 | 2018-02-15
1477 | Directory # 8 V2 | System Restoration | R8.4.6. | R8.4 For each functional entity identified as owning Key Facilities, which is unable to perform a test outlined in Appendix A, a requested proposed alternate testing methodology may be permitted if each of the following criteria (R8.4.1-R8.4.6) are met: R8.4.6 Approval of the alternative testing methodology results must be received from the Reliability Coordinator. Note: The alternative testing methodology shall be reviewed on a periodic basis as determined by the Reliability Coordinator. Approval of the alternative testing methodology will either be renewed or revoked by the Reliability Coordinator. | Retired | 2017-10-06 | 2018-02-15
1044 | Directory # 8 V2 | System Restoration | R9. | Each functional entity that owns a Cable pressurization system at Key Facilities shall test for satisfactory operation of both the primary pressurization system and/or the backup pressurization system (if applicable) ability/abilities to maintain required pressure upon loss of power to the Key Facilities. Test basis: Frequency: every six (6) Calendar Months Duration: at least thirty (30) minutes (Reference: Appendix A; Test No. UG-1) Note: This capability is required during a blackout to maintain the availability of Cables for service and to preclude any damage to the Cables as a result of the loss of dielectric strength. | Retired | 2017-10-06 | 2018-02-15
1478 | Directory # 8 V3 | System Restoration | R1. | Each Reliability Coordinator, together with its respective Transmission Operators, shall jointly develop, maintain, verify, and implement a system restoration plan for its Reliability Coordinator Area that shall: | Retired | 2018-02-16 | 2019-01-22
1479 | Directory # 8 V3 | System Restoration | R1.1. | Identify the Reliability Coordinator Area’s BMPS(s). | Retired | 2018-02-16 | 2019-01-22
1480 | Directory # 8 V3 | System Restoration | R1.2. | Address the priority of providing off-site AC power to nuclear power stations. | Retired | 2018-02-16 | 2019-01-22
1481 | Directory # 8 V3 | System Restoration | R1.3. | Identify Interconnection points with adjacent Reliability Coordinator Areas. | Retired | 2018-02-16 | 2019-01-22
1482 | Directory # 8 V3 | System Restoration | R1.4. | Identify parameters to Synchronize adjacent BMPSs | Retired | 2018-02-16 | 2019-01-22
1483 | Directory # 8 V3 | System Restoration | R1.5. | Address coordination of system restoration with neighboring Reliability Coordinator Areas. | Retired | 2018-02-16 | 2019-01-22
1484 | Directory # 8 V3 | System Restoration | R1.6. | Provide for the re-energization of transmission systems to; R1.6.1 major generating stations; R1.6.2 inter-area tie points. | Retired | 2018-02-16 | 2019-01-22
1485 | Directory # 8 V3 | System Restoration | R1.7. | Address electrical Island stabilization. | Retired | 2018-02-16 | 2019-01-22
1486 | Directory # 8 V3 | System Restoration | R1.8. | Identify provisions for fuel resources to support operation of any supplementary generators (e.g., a diesel generator) necessary for operating Key Facilities consistent with the expected requirements of the system restoration plan. | Retired | 2018-02-16 | 2019-01-22
1487 | Directory # 8 V3 | System Restoration | R10. | Each functional entity shall test its backup power supplies identified as Critical Components as specified in R10.1 through R10.5. Where there are separate backup power arrangements at Key Facilities for transmission or generating station equipment and telecommunication equipment, such equipment shall be separately identified on the list of Critical Components and shall be inspected and tested individually. | Retired | 2018-02-16 | 2019-01-22
1488 | Directory # 8 V3 | System Restoration | R10.1. | Equipment Inspection Batteries and/or battery chargers identified as Critical Components shall be inspected in accordance with maintenance activities and maintenance intervals specified in PRC-005-Protection System, Automatic Reclosing, and Sudden Pressure Relaying Maintenance, giving consideration to exclusions per PRC-005 Table 1-4(f) (Reference: Appendix A; Test KF-1) | Retired | 2018-02-16 | 2019-01-22
1489 | Directory # 8 V3 | System Restoration | R10.2. | Equipment Verification Batteries and/or battery chargers identified as Critical Components shall be verified in accordance with maintenance activities and maintenance intervals specified in PRC-005 Protection System, Automatic Reclosing, and Sudden Pressure Relaying Maintenance, giving consideration to exclusions per PRC-005 Table 1-4(f) (Reference: Appendix A; Test KF-2) | Retired | 2018-02-16 | 2019-01-22
1490 | Directory # 8 V3 | System Restoration | R10.3. | Confirm That All Critical Components Loads Can Be Supplied Each owner of batteries and/or battery chargers identified as Critical Components shall confirm that all Critical Components Loads are connected to and can be supplied by the batteries and/or battery chargers. The functional entity owner shall confirm through its design review, when modifications are made to Key Facilities, or through testing, that all Critical Components Loads are connected to and can be sufficiently supplied by the batteries and/or battery chargers. Test basis: Frequency: when modifications are made to Key Facilities or at least once every sixty (60) Calendar Months (Reference: Appendix A; Test KF-3) | Retired | 2018-02-16 | 2019-01-22
1491 | Directory # 8 V3 | System Restoration | R10.4. | Startup and Run Test Each owner of a backup power generator identified on the list of Critical Components of Key Facilities, shall perform a startup, and run test on that backup power generator. Test basis: Frequency: monthly Duration: at least fifteen (15) minutes (Reference: Appendix A; Test KF-5). Note: This test also applies to supplemental generation required for Blackstart Capability and to a control center and telecommunication center backup power generator. | Retired | 2018-02-16 | 2019-01-22
1492 | Directory # 8 V3 | System Restoration | R10.5. | Startup, Transfer and Load Test Each owner of a backup power generator identified on the list of Critical Components of Key Facilities shall verify that the backup power generator will pick up the Critical Components Load following the loss of station service. Note: This test also applies to a control center and telecommunication center backup power generator. For automatically started backup power generators, a startup, transfer, and Load test simulating the loss of station service shall be performed. Test basis: Frequency: every twelve (12) Calendar Months Duration: at least thirty (30) minutes (Reference: Appendix A; Test KF-6) For manually started backup power generators, a startup, transfer, and Load test performed by starting the generator and verifying Reliable Operation while supplying Critical Components Loads, shall be performed by the asset owner. Test basis: Frequency: every twelve (12) Calendar Months Duration: at least thirty (30) minutes (Reference: Appendix A; Test KF-6) Note: Power sources used to start Resources with Blackstart Capability will be excluded from test KF-6. | Retired | 2018-02-16 | 2019-01-22
1493 | Directory # 8 V3 | System Restoration | R11. | Each functional entity identified as owning Key Facilities shall test its Critical Components in the control centers and the telecommunication centers identified as Key Facilities to demonstrate that the computer systems will be functional without dependencies on power sources that may be unavailable during a partial or complete system blackout, when required for system restoration. | Retired | 2018-02-16 | 2019-01-22
1494 | Directory # 8 V3 | System Restoration | R11.1. | AC Supply Interruption Test The uninterruptible power supply (UPS) systems in control centers and telecommunication centers shall be tested by interrupting AC supply and verifying that all Critical Components Loads are supplied for a time that is sufficient for backup power sources to restore the AC input to the UPS Test basis: Frequency: every twelve (12) Calendar Months. (Reference: Appendix A; Test CC-1) | Retired | 2018-02-16 | 2019-01-22
1495 | Directory # 8 V3 | System Restoration | R11.2. | Computer Redundancy (SCADA/EMS) Test Each functional entity identified as owning Key Facilities shall test its computer redundancy (SCADA/EMS) features to ensure computer systems (SCADA/EMS) continue to function consistent with Good Utility Practice. Test basis: Frequency: every six (6) Calendar Months (Reference: Appendix A; Test CC-2) | Retired | 2018-02-16 | 2019-01-22
1496 | Directory # 8 V3 | System Restoration | R12. | Each functional entity owning a generating station with Blackstart Capability shall verify such concurrent capability as follows: | Retired | 2018-02-16 | 2019-01-22
1497 | Directory # 8 V3 | System Restoration | R12.1. | A generating station with Blackstart Capability shall be tested for successful equipment startup, sufficient to Energize a transmission Element or a generating station switchyard Element, if that does not involve the disconnection of Load that is not dedicated generating station Load to conduct the test. Verify Reliable Operation while isolated from the BPS . Test basis: Frequency: every twelve (12) Calendar Months Duration: at least ten (10) minutes of Reliable Operation (Reference: Appendix A; Test No. BS-1) | Retired | 2018-02-16 | 2019-01-22
1498 | Directory # 8 V3 | System Restoration | R12.2. | Operations voice communications and auxiliary systems such as Supervisory Control and Data Acquisition (SCADA) that are required for Blackstart Capability shall be verified to operate consistent with Good Utility Practice independent of the interconnected system or other unrelated unit for any source of station service. Test basis: Frequency: every twelve (12) Calendar Months Duration: Verification of at least ten (10) minutes of Reliable Operation concurrent with R12.1 (Reference: Appendix A; Test No. BS-1) | Retired | 2018-02-16 | 2019-01-22
1499 | Directory # 8 V3 | System Restoration | R13. | Each Reliability Coordinator shall determine, as required by its respective system restoration plan, the number of units within a generating station that are to be tested for Blackstart Capability, and shall notify the applicable functional entity/entities. | Retired | 2018-02-16 | 2019-01-22
1500 | Directory # 8 V3 | System Restoration | R14. | Each Reliability Coordinator shall confirm, consistent with the objectives of its respective system restoration plan, that the functional entity owning a generating station with Blackstart Capability that is part of the BMPS has completed a successful Blackstart Capabilitytest. | Retired | 2018-02-16 | 2019-01-22
1501 | Directory # 8 V3 | System Restoration | R15. | A functional entity that has confirmed the loss of functionality of Critical Components shall report to the Transmission Operator responsible for operating the Critical Components of the Critical Components’ loss of functionality as soon as possible but no longer than 15 minutes after confirmation of the loss of functionality. | Retired | 2018-02-16 | 2019-01-22
1502 | Directory # 8 V3 | System Restoration | R15.1. | The Transmission Operator shall report to its Reliability Coordinator, as soon as possible but no longer than 15 minutes after the functional entity has confirmed the loss of functionality of Critical Components to the Transmission Operator. Examples of such conditions are, but not limited to: • Loss of control of remote equipment. • Complete loss of AC or DC service supply. • Loss of Resources with Blackstart Capability. | Retired | 2018-02-16 | 2019-01-22
1503 | Directory # 8 V3 | System Restoration | R16. | A functional entity that has confirmed the loss of redundancy of Critical Components shall report to the Transmission Operator responsible for the Critical Components of loss of redundancy as soon as possible but no longer than 12 hours after confirmation of the loss of redundancy. Examples of such conditions are: • Loss of a redundant AC or DC service supply. • Loss of redundant Critical Components associated with Resources with Blackstart Capability. | Retired | 2018-02-16 | 2019-01-22
1504 | Directory # 8 V3 | System Restoration | R17. | A functional entity that has scheduled a maintenance activity (inservice or out-of-service) of Critical Components that will result in the loss of functionality of the Critical Components shall report that maintenance activity to the Transmission Operator responsible for the Critical Components at least 24 hours prior to that scheduled loss of functionality. | Retired | 2018-02-16 | 2019-01-22
1505 | Directory # 8 V3 | System Restoration | R17.1. | The functional entity shall report to the Transmission Operator responsible for Critical Components as soon as possible after the scheduled loss of functionality has begun. | Retired | 2018-02-16 | 2019-01-22
1506 | Directory # 8 V3 | System Restoration | R17.2. | If the scheduled maintenance condition causing the loss of functionality of Critical Components affects the functionality of Key Facilities, the Transmission Operator responsible for the Critical Components shall report this scheduled maintenance condition to its Reliability Coordinator. • Upon receipt of the scheduled maintenance report • Upon receipt of the scheduled maintenance start • Upon receipt of the scheduled maintenance end | Retired | 2018-02-16 | 2019-01-22
1507 | Directory # 8 V3 | System Restoration | R18. | A functional entity shall report the actions to be taken to restore Critical Components’ availability or redundancy to the Transmission Operator responsible for the Critical Components as soon as known. | Retired | 2018-02-16 | 2019-01-22
1508 | Directory # 8 V3 | System Restoration | R18.1. | The functional entity shall report to the Transmission Operator responsible for the Critical Components the anticipated time that the Critical Components functionality will be restored. | Retired | 2018-02-16 | 2019-01-22
1509 | Directory # 8 V3 | System Restoration | R18.2. | The functional entity shall report to the Transmission Operator responsible for maintaining redundancy for Critical Components the anticipated time that the Critical Components’ redundancy will be restored. | Retired | 2018-02-16 | 2019-01-22
1510 | Directory # 8 V3 | System Restoration | R19. | A functional entity shall report to the Transmission Operator responsible for the functionality of Critical Components, the date and time when the functionality of Critical Components is restored. | Retired | 2018-02-16 | 2019-01-22
1511 | Directory # 8 V3 | System Restoration | R2. | Each Reliability Coordinator shall, in determining the BMPS, coordinate with all impacted parties and/or functional entities. | Retired | 2018-02-16 | 2019-01-22
1512 | Directory # 8 V3 | System Restoration | R3. | Each Reliability Coordinator shall ensure that the BMPS includes the ability to: | Retired | 2018-02-16 | 2019-01-22
1513 | Directory # 8 V3 | System Restoration | R3.1. | Use generator Blackstart Capability. | Retired | 2018-02-16 | 2019-01-22
1514 | Directory # 8 V3 | System Restoration | R3.2. | Form an electrical Island(s). | Retired | 2018-02-16 | 2019-01-22
1515 | Directory # 8 V3 | System Restoration | R3.3. | Synchronize electrical Islands; and | Retired | 2018-02-16 | 2019-01-22
1516 | Directory # 8 V3 | System Restoration | R3.4. | Permit the successful performance of the system restoration plan. | Retired | 2018-02-16 | 2019-01-22
1517 | Directory # 8 V3 | System Restoration | R4. | Each Reliability Coordinator shall identify Key Facilities and shall inform each functional entity of its identified Key Facilities. | Retired | 2018-02-16 | 2019-01-22
1518 | Directory # 8 V3 | System Restoration | R5. | Each functional entity identified as the owner of newly identified or proposed Key Facilities: | Retired | 2018-02-16 | 2019-01-22
1519 | Directory # 8 V3 | System Restoration | R5.1. | Shall identify the associated Critical Components for those Key Facilities prior to the effective date of the approved system restoration plan. | Retired | 2018-02-16 | 2019-01-22
1520 | Directory # 8 V3 | System Restoration | R5.2. | Shall provide, upon request of the Reliability Coordinator, within the timeframe requested, a list of Critical Components associated with proposed Key Facilities. | Retired | 2018-02-16 | 2019-01-22
1521 | Directory # 8 V3 | System Restoration | R5.3. | Shall ensure, prior to the effective date of the approved system restoration plan, or within the timeframe requested by the Reliability Coordinator, that all applicable proposed Key Facilities testing outlined in Appendix A has been successfully completed. | Retired | 2018-02-16 | 2019-01-22
1522 | Directory # 8 V3 | System Restoration | R6. | Each functional entity identified as the owner of existing Key Facilities: | Retired | 2018-02-16 | 2019-01-22
1523 | Directory # 8 V3 | System Restoration | R6.1. | Shall provide, upon request of the Reliability Coordinator, within the timeframe requested, any updates, additions, or deletions to the list of Critical Components for identified Key Facilities. | Retired | 2018-02-16 | 2019-01-22
1524 | Directory # 8 V3 | System Restoration | R6.2. | Shall ensure, prior to the effective date of the approved system restoration plan, or within the timeframe requested by the Reliability Coordinator, that the following components associated with identified Key Facilities testing outlined in Appendix A have been successfully completed: R6.2.1 All applicable additional Critical Components R6.2.2 Any modifications to existing Critical Components that could potentially impact the functionality of those Critical Components. | Retired | 2018-02-16 | 2019-01-22
1525 | Directory # 8 V3 | System Restoration | R7. | Following the occurrence of an event that required implementation of a system restoration plan and upon request of the Task Force on Coordination of Operation (TFCO): | Retired | 2018-02-16 | 2019-01-22
1526 | Directory # 8 V3 | System Restoration | R7.1. | The Reliability Coordinator shall report, within the timeframe requested by the TFCO, on the performance of its system restoration plan. | Retired | 2018-02-16 | 2019-01-22
1527 | Directory # 8 V3 | System Restoration | R7.2. | The Transmission Operator shall report, within the timeframe requested by the TFCO, on the performance of its system restoration plan. | Retired | 2018-02-16 | 2019-01-22
1528 | Directory # 8 V3 | System Restoration | R8. | Each functional entity which has been identified as owning Key Facilities shall: | Retired | 2018-02-16 | 2019-01-22
1529 | Directory # 8 V3 | System Restoration | R8.1. | Perform the tests outlined in Appendix A. | Retired | 2018-02-16 | 2019-01-22
1530 | Directory # 8 V3 | System Restoration | R8.2. | Maintain evidence of the test results consistent with Section 4.0. | Retired | 2018-02-16 | 2019-01-22
1531 | Directory # 8 V3 | System Restoration | R8.3. | Provide evidence, upon request of the Reliability Coordinator and/or Transmission Operator, within the timeframe requested, that the tests specified in sub-Requirement R8.1 have been met. | Retired | 2018-02-16 | 2019-01-22
1533 | Directory # 8 V3 | System Restoration | R8.4.1. | R8.4 For each functional entity identified as owning Key Facilities, which is unable to perform a test outlined in Appendix A, a requested proposed alternate testing methodology may be permitted if each of the following criteria (R8.4.1-R8.4.6) are met: R8.4.1 Evidence must be provided to the Reliability Coordinator that conducting the specified Appendix A test would be detrimental to the operational functionality of the Key Facility. Note: The alternative testing methodology shall be reviewed on a periodic basis as determined by the Reliability Coordinator. Approval of the alternative testing methodology will either be renewed or revoked by the Reliability Coordinator. | Retired | 2018-02-16 | 2019-01-22
1534 | Directory # 8 V3 | System Restoration | R8.4.2. | R8.4 For each functional entity identified as owning Key Facilities, which is unable to perform a test outlined in Appendix A, a requested proposed alternate testing methodology may be permitted if each of the following criteria (R8.4.1-R8.4.6) are met: R8.4.2 The alternative testing methodology, with mitigating controls to meet the intent of the Directory Requirement, must be proposed to the Reliability Coordinator to evaluate and to accept or reject the requested proposed alternate testing methodology. Note: The alternative testing methodology shall be reviewed on a periodic basis as determined by the Reliability Coordinator. Approval of the alternative testing methodology will either be renewed or revoked by the Reliability Coordinator. | Retired | 2018-02-16 | 2019-01-22
1535 | Directory # 8 V3 | System Restoration | R8.4.3. | R8.4 For each functional entity identified as owning Key Facilities, which is unable to perform a test outlined in Appendix A, a requested proposed alternate testing methodology may be permitted if each of the following criteria (R8.4.1-R8.4.6) are met: R8.4.3 Post acceptance per R8.4.2, the alternative testing methodology must be successfully conducted. Note: The alternative testing methodology shall be reviewed on a periodic basis as determined by the Reliability Coordinator. Approval of the alternative testing methodology will either be renewed or revoked by the Reliability Coordinator. | Retired | 2018-02-16 | 2019-01-22
1536 | Directory # 8 V3 | System Restoration | R8.4.4. | R8.4 For each functional entity identified as owning Key Facilities, which is unable to perform a test outlined in Appendix A, a requested proposed alternate testing methodology may be permitted if each of the following criteria (R8.4.1-R8.4.6) are met: R8.4.4 Operation consistent with Good Utility Practice must be demonstrated and maintained throughout the alternative testing protocol. Note: The alternative testing methodology shall be reviewed on a periodic basis as determined by the Reliability Coordinator. Approval of the alternative testing methodology will either be renewed or revoked by the Reliability Coordinator. | Retired | 2018-02-16 | 2019-01-22
1537 | Directory # 8 V3 | System Restoration | R8.4.5. | R8.4 For each functional entity identified as owning Key Facilities, which is unable to perform a test outlined in Appendix A, a requested proposed alternate testing methodology may be permitted if each of the following criteria (R8.4.1-R8.4.6) are met: R8.4.5 The alternative testing methodology results must be submitted to the Reliability Coordinator. Note: The alternative testing methodology shall be reviewed on a periodic basis as determined by the Reliability Coordinator. Approval of the alternative testing methodology will either be renewed or revoked by the Reliability Coordinator. | Retired | 2018-02-16 | 2019-01-22
1538 | Directory # 8 V3 | System Restoration | R8.4.6. | R8.4 For each functional entity identified as owning Key Facilities, which is unable to perform a test outlined in Appendix A, a requested proposed alternate testing methodology may be permitted if each of the following criteria (R8.4.1-R8.4.6) are met: R8.4.6 Approval of the alternative testing methodology results must be received from the Reliability Coordinator. Note: The alternative testing methodology shall be reviewed on a periodic basis as determined by the Reliability Coordinator. Approval of the alternative testing methodology will either be renewed or revoked by the Reliability Coordinator. | Retired | 2018-02-16 | 2019-01-22
1532 | Directory # 8 V3 | System Restoration | R9. | Each functional entity that owns a Cable pressurization system at Key Facilities shall test for satisfactory operation of both the primary pressurization system and/or the backup pressurization system (if applicable) ability/abilities to maintain required pressure upon loss of power to the Key Facilities. Test basis: Frequency: every six (6) Calendar Months Duration: at least thirty (30) minutes (Reference: Appendix A; Test No. UG-1) Note: This capability is required during a blackout to maintain the availability of Cables for service and to preclude any damage to the Cables as a result of the loss of dielectric strength. | Retired | 2018-02-16 | 2019-01-22
1539 | Directory # 8 V4 | System Restoration | R1. | Each Reliability Coordinator, together with its respective Transmission Operators, shall jointly develop, maintain, verify, and implement a system restoration plan for its Reliability Coordinator Area that shall: | Retired | 2019-01-23 | 2023-07-17
1540 | Directory # 8 V4 | System Restoration | R1.1. | Identify the Reliability Coordinator Area’s BMPS(s). | Retired | 2019-01-23 | 2023-07-17
1541 | Directory # 8 V4 | System Restoration | R1.2. | Address the priority of providing off-site AC power to nuclear power stations. | Retired | 2019-01-23 | 2023-07-17
1542 | Directory # 8 V4 | System Restoration | R1.3. | Identify Interconnection points with adjacent Reliability Coordinator Areas. | Retired | 2019-01-23 | 2023-07-17
1543 | Directory # 8 V4 | System Restoration | R1.4. | Identify parameters to Synchronize adjacent BMPSs | Retired | 2019-01-23 | 2023-07-17
1544 | Directory # 8 V4 | System Restoration | R1.5. | Address coordination of system restoration with neighboring Reliability Coordinator Areas. | Retired | 2019-01-23 | 2023-07-17
1545 | Directory # 8 V4 | System Restoration | R1.6. | Provide for the re-energization of transmission systems to; R1.6.1 major generating stations; R1.6.2 inter-area tie points. | Retired | 2019-01-23 | 2023-07-17
1546 | Directory # 8 V4 | System Restoration | R1.7. | Address electrical Island stabilization. | Retired | 2019-01-23 | 2023-07-17
1547 | Directory # 8 V4 | System Restoration | R1.8. | Identify provisions for fuel resources to support operation of any supplementary generators (e.g., a diesel generator) necessary for operating Key Facilities consistent with the expected requirements of the system restoration plan. | Retired | 2019-01-23 | 2023-07-17
1548 | Directory # 8 V4 | System Restoration | R10. | Each functional entity shall test its backup power supplies identified as Critical Components as specified in R10.1 through R10.5. Where there are separate backup power arrangements at Key Facilities for transmission or generating station equipment and telecommunication equipment, such equipment shall be separately identified on the list of Critical Components and shall be inspected and tested individually. | Retired | 2019-01-23 | 2023-07-17
1549 | Directory # 8 V4 | System Restoration | R10.1. | Equipment Inspection Batteries and/or battery chargers identified as Critical Components shall be inspected in accordance with maintenance activities and maintenance intervals specified in PRC-005-Protection System, Automatic Reclosing, and Sudden Pressure Relaying Maintenance, giving consideration to exclusions per PRC-005 Table 1-4(f) (Reference: Appendix A; Test KF-1) | Retired | 2019-01-23 | 2023-07-17
1550 | Directory # 8 V4 | System Restoration | R10.2. | Equipment Verification Batteries and/or battery chargers identified as Critical Components shall be verified in accordance with maintenance activities and maintenance intervals specified in PRC-005 Protection System, Automatic Reclosing, and Sudden Pressure Relaying Maintenance, giving consideration to exclusions per PRC-005 Table 1-4(f) (Reference: Appendix A; Test KF-2) | Retired | 2019-01-23 | 2023-07-17
1551 | Directory # 8 V4 | System Restoration | R10.3. | Confirm That All Critical Components Loads Can Be Supplied Each owner of batteries and/or battery chargers identified as Critical Components shall confirm that all Critical Components Loads are connected to and can be supplied by the batteries and/or battery chargers. The functional entity owner shall confirm through its design review, when modifications are made to Key Facilities, or through testing, that all Critical Components Loads are connected to and can be sufficiently supplied by the batteries and/or battery chargers. Test basis: Frequency: when modifications are made to Key Facilities or at least once every sixty (60) Calendar Months (Reference: Appendix A; Test KF-3) | Retired | 2019-01-23 | 2023-07-17
1552 | Directory # 8 V4 | System Restoration | R10.4. | Startup and Run Test Each owner of a backup power generator identified on the list of Critical Components of Key Facilities, shall perform a startup, and run test on that backup power generator. Test basis: Frequency: monthly Duration: at least fifteen (15) minutes (Reference: Appendix A; Test KF-5). Note: This test also applies to supplemental generation required for Blackstart Capability and to a control center and telecommunication center backup power generator. | Retired | 2019-01-23 | 2023-07-17
1553 | Directory # 8 V4 | System Restoration | R10.5. | Startup, Transfer and Load Test Each owner of a backup power generator identified on the list of Critical Components of Key Facilities shall verify that the backup power generator will pick up the Critical Components Load following the loss of station service. Note: This test also applies to a control center and telecommunication center backup power generator. For automatically started backup power generators, a startup, transfer, and Load test simulating the loss of station service shall be performed. Test basis: Frequency: every twelve (12) Calendar Months Duration: at least thirty (30) minutes (Reference: Appendix A; Test KF-6) For manually started backup power generators, a startup, transfer, and Load test performed by starting the generator and verifying Reliable Operation while supplying Critical Components Loads, shall be performed by the asset owner. Test basis: Frequency: every twelve (12) Calendar Months Duration: at least thirty (30) minutes (Reference: Appendix A; Test KF-6) Note: Power sources used to start Resources with Blackstart Capability will be excluded from test KF-6. | Retired | 2019-01-23 | 2023-07-17
1554 | Directory # 8 V4 | System Restoration | R11. | Each functional entity identified as owning Key Facilities shall test its Critical Components in the control centers and the telecommunication centers identified as Key Facilities to demonstrate that the computer systems will be functional without dependencies on power sources that may be unavailable during a partial or complete system blackout, when required for system restoration. | Retired | 2019-01-23 | 2023-07-17
1555 | Directory # 8 V4 | System Restoration | R11.1. | AC Supply Interruption Test The uninterruptible power supply (UPS) systems in control centers and telecommunication centers shall be tested by interrupting AC supply and verifying that all Critical Components Loads are supplied for a time that is sufficient for backup power sources to restore the AC input to the UPS Test basis: Frequency: every twelve (12) Calendar Months. (Reference: Appendix A; Test CC-1) | Retired | 2019-01-23 | 2023-07-17
1556 | Directory # 8 V4 | System Restoration | R11.2. | Computer Redundancy (SCADA/EMS) Test Each functional entity identified as owning Key Facilities shall test its computer redundancy (SCADA/EMS) features to ensure computer systems (SCADA/EMS) continue to function consistent with Good Utility Practice. Test basis: Frequency: every six (6) Calendar Months (Reference: Appendix A; Test CC-2) | Retired | 2019-01-23 | 2023-07-17
1557 | Directory # 8 V4 | System Restoration | R12. | Each functional entity owning a generating station with Blackstart Capability shall verify such concurrent capability as follows: | Retired | 2019-01-23 | 2023-07-17
1558 | Directory # 8 V4 | System Restoration | R12.1. | A generating station with Blackstart Capability shall be tested for successful equipment startup, sufficient to Energize a transmission Element or a generating station switchyard Element, if that does not involve the disconnection of Load that is not dedicated generating station Load to conduct the test. Verify Reliable Operation while isolated from the BPS . Test basis: Frequency: every twelve (12) Calendar Months Duration: at least ten (10) minutes of Reliable Operation (Reference: Appendix A; Test No. BS-1) | Retired | 2019-01-23 | 2023-07-17
1559 | Directory # 8 V4 | System Restoration | R12.2. | Operations voice communications and auxiliary systems such as Supervisory Control and Data Acquisition (SCADA) that are required for Blackstart Capability shall be verified to operate consistent with Good Utility Practice independent of the interconnected system or other unrelated unit for any source of station service. Test basis: Frequency: every twelve (12) Calendar Months Duration: Verification of at least ten (10) minutes of Reliable Operation concurrent with R12.1 (Reference: Appendix A; Test No. BS-1) | Retired | 2019-01-23 | 2023-07-17
1560 | Directory # 8 V4 | System Restoration | R13. | Each Reliability Coordinator shall determine, as required by its respective system restoration plan, the number of units within a generating station that are to be tested for Blackstart Capability, and shall notify the applicable functional entity/entities. | Retired | 2019-01-23 | 2023-07-17
1561 | Directory # 8 V4 | System Restoration | R14. | Each Reliability Coordinator shall confirm, consistent with the objectives of its respective system restoration plan, that the functional entity owning a generating station with Blackstart Capability that is part of the BMPS has completed a successful Blackstart Capabilitytest. | Retired | 2019-01-23 | 2023-07-17
1562 | Directory # 8 V4 | System Restoration | R15. | A functional entity that has confirmed the loss of functionality of Critical Components shall report to the Transmission Operator responsible for operating the Critical Components of the Critical Components’ loss of functionality as soon as possible but no longer than 15 minutes after confirmation of the loss of functionality. | Retired | 2019-01-23 | 2023-07-17
1563 | Directory # 8 V4 | System Restoration | R15.1. | The Transmission Operator shall report to its Reliability Coordinator, as soon as possible but no longer than 15 minutes after the functional entity has confirmed the loss of functionality of Critical Components to the Transmission Operator. Examples of such conditions are, but not limited to: • Loss of control of remote equipment. • Complete loss of AC or DC service supply. • Loss of Resources with Blackstart Capability. | Retired | 2019-01-23 | 2023-07-17
1564 | Directory # 8 V4 | System Restoration | R16. | A functional entity that has confirmed the loss of redundancy of Critical Components shall report to the Transmission Operator responsible for the Critical Components of loss of redundancy as soon as possible but no longer than 12 hours after confirmation of the loss of redundancy. Examples of such conditions are: • Loss of a redundant AC or DC service supply. • Loss of redundant Critical Components associated with Resources with Blackstart Capability. | Retired | 2019-01-23 | 2023-07-17
1565 | Directory # 8 V4 | System Restoration | R17. | A functional entity that has scheduled a maintenance activity (inservice or out-of-service) of Critical Components that will result in the loss of functionality of the Critical Components shall report that maintenance activity to the Transmission Operator responsible for the Critical Components at least 24 hours prior to that scheduled loss of functionality. | Retired | 2019-01-23 | 2023-07-17
1566 | Directory # 8 V4 | System Restoration | R17.1. | The functional entity shall report to the Transmission Operator responsible for Critical Components as soon as possible after the scheduled loss of functionality has begun. | Retired | 2019-01-23 | 2023-07-17
1567 | Directory # 8 V4 | System Restoration | R17.2. | If the scheduled maintenance condition causing the loss of functionality of Critical Components affects the functionality of Key Facilities, the Transmission Operator responsible for the Critical Components shall report this scheduled maintenance condition to its Reliability Coordinator. • Upon receipt of the scheduled maintenance report • Upon receipt of the scheduled maintenance start • Upon receipt of the scheduled maintenance end | Retired | 2019-01-23 | 2023-07-17
1568 | Directory # 8 V4 | System Restoration | R18. | A functional entity shall report the actions to be taken to restore Critical Components’ availability or redundancy to the Transmission Operator responsible for the Critical Components as soon as known. | Retired | 2019-01-23 | 2023-07-17
1569 | Directory # 8 V4 | System Restoration | R18.1. | The functional entity shall report to the Transmission Operator responsible for the Critical Components the anticipated time that the Critical Components functionality will be restored. | Retired | 2019-01-23 | 2023-07-17
1570 | Directory # 8 V4 | System Restoration | R18.2. | The functional entity shall report to the Transmission Operator responsible for maintaining redundancy for Critical Components the anticipated time that the Critical Components’ redundancy will be restored. | Retired | 2019-01-23 | 2023-07-17
1571 | Directory # 8 V4 | System Restoration | R19. | A functional entity shall report to the Transmission Operator responsible for the functionality of Critical Components, the date and time when the functionality of Critical Components is restored. | Retired | 2019-01-23 | 2023-07-17
1572 | Directory # 8 V4 | System Restoration | R2. | Each Reliability Coordinator shall, in determining the BMPS, coordinate with all impacted parties and/or functional entities. | Retired | 2019-01-23 | 2023-07-17
1573 | Directory # 8 V4 | System Restoration | R3. | Each Reliability Coordinator shall ensure that the BMPS includes the ability to: | Retired | 2019-01-23 | 2023-07-17
1574 | Directory # 8 V4 | System Restoration | R3.1. | Use generator Blackstart Capability. | Retired | 2019-01-23 | 2023-07-17
1575 | Directory # 8 V4 | System Restoration | R3.2. | Form an electrical Island(s). | Retired | 2019-01-23 | 2023-07-17
1576 | Directory # 8 V4 | System Restoration | R3.3. | Synchronize electrical Islands; and | Retired | 2019-01-23 | 2023-07-17
1577 | Directory # 8 V4 | System Restoration | R3.4. | Permit the successful performance of the system restoration plan. | Retired | 2019-01-23 | 2023-07-17
1578 | Directory # 8 V4 | System Restoration | R4. | Each Reliability Coordinator shall identify Key Facilities and shall inform each functional entity of its identified Key Facilities. | Retired | 2019-01-23 | 2023-07-17
1579 | Directory # 8 V4 | System Restoration | R5. | Each functional entity identified as the owner of newly identified or proposed Key Facilities: | Retired | 2019-01-23 | 2023-07-17
1580 | Directory # 8 V4 | System Restoration | R5.1. | Shall identify the associated Critical Components for those Key Facilities prior to the effective date of the approved system restoration plan. | Retired | 2019-01-23 | 2023-07-17
1581 | Directory # 8 V4 | System Restoration | R5.2. | Shall provide, upon request of the Reliability Coordinator, within the timeframe requested, a list of Critical Components associated with proposed Key Facilities. | Retired | 2019-01-23 | 2023-07-17
1582 | Directory # 8 V4 | System Restoration | R5.3. | Shall ensure, prior to the effective date of the approved system restoration plan, or within the timeframe requested by the Reliability Coordinator, that all applicable proposed Key Facilities testing outlined in Appendix A has been successfully completed. | Retired | 2019-01-23 | 2023-07-17
1583 | Directory # 8 V4 | System Restoration | R6. | Each functional entity identified as the owner of existing Key Facilities: | Retired | 2019-01-23 | 2023-07-17
1584 | Directory # 8 V4 | System Restoration | R6.1. | Shall provide, upon request of the Reliability Coordinator, within the timeframe requested, any updates, additions, or deletions to the list of Critical Components for identified Key Facilities. | Retired | 2019-01-23 | 2023-07-17
1585 | Directory # 8 V4 | System Restoration | R6.2. | Shall ensure, prior to the effective date of the approved system restoration plan, or within the timeframe requested by the Reliability Coordinator, that the following components associated with identified Key Facilities testing outlined in Appendix A have been successfully completed: R6.2.1 All applicable additional Critical Components R6.2.2 Any modifications to existing Critical Components that could potentially impact the functionality of those Critical Components. | Retired | 2019-01-23 | 2023-07-17
1586 | Directory # 8 V4 | System Restoration | R7. | Following the occurrence of an event that required implementation of a system restoration plan and upon request of the Task Force on Coordination of Operation (TFCO): | Retired | 2019-01-23 | 2023-07-17
1587 | Directory # 8 V4 | System Restoration | R7.1. | The Reliability Coordinator shall report, within the timeframe requested by the TFCO, on the performance of its system restoration plan. | Retired | 2019-01-23 | 2023-07-17
1588 | Directory # 8 V4 | System Restoration | R7.2. | The Transmission Operator shall report, within the timeframe requested by the TFCO, on the performance of its system restoration plan. | Retired | 2019-01-23 | 2023-07-17
1589 | Directory # 8 V4 | System Restoration | R8. | Each functional entity which has been identified as owning Key Facilities shall: | Retired | 2019-01-23 | 2023-07-17
1590 | Directory # 8 V4 | System Restoration | R8.1. | Perform the tests outlined in Appendix A. | Retired | 2019-01-23 | 2023-07-17
1591 | Directory # 8 V4 | System Restoration | R8.2. | Maintain evidence of the test results consistent with Section 4.0. | Retired | 2019-01-23 | 2023-07-17
1592 | Directory # 8 V4 | System Restoration | R8.3. | Provide evidence, upon request of the Reliability Coordinator and/or Transmission Operator, within the timeframe requested, that the tests specified in sub-Requirement R8.1 have been met. | Retired | 2019-01-23 | 2023-07-17
1594 | Directory # 8 V4 | System Restoration | R8.4.1. | R8.4 For each functional entity identified as owning Key Facilities, which is unable to perform a test outlined in Appendix A, a requested proposed alternate testing methodology may be permitted if each of the following criteria (R8.4.1-R8.4.6) are met: R8.4.1 Evidence must be provided to the Reliability Coordinator that conducting the specified Appendix A test would be detrimental to the operational functionality of the Key Facility. Note: The alternative testing methodology shall be reviewed on a periodic basis as determined by the Reliability Coordinator. Approval of the alternative testing methodology will either be renewed or revoked by the Reliability Coordinator. | Retired | 2019-01-23 | 2023-07-17
1595 | Directory # 8 V4 | System Restoration | R8.4.2. | R8.4 For each functional entity identified as owning Key Facilities, which is unable to perform a test outlined in Appendix A, a requested proposed alternate testing methodology may be permitted if each of the following criteria (R8.4.1-R8.4.6) are met: R8.4.2 The alternative testing methodology, with mitigating controls to meet the intent of the Directory Requirement, must be proposed to the Reliability Coordinator to evaluate and to accept or reject the requested proposed alternate testing methodology. Note: The alternative testing methodology shall be reviewed on a periodic basis as determined by the Reliability Coordinator. Approval of the alternative testing methodology will either be renewed or revoked by the Reliability Coordinator. | Retired | 2019-01-23 | 2023-07-17
1596 | Directory # 8 V4 | System Restoration | R8.4.3. | R8.4 For each functional entity identified as owning Key Facilities, which is unable to perform a test outlined in Appendix A, a requested proposed alternate testing methodology may be permitted if each of the following criteria (R8.4.1-R8.4.6) are met: R8.4.3 Post acceptance per R8.4.2, the alternative testing methodology must be successfully conducted. Note: The alternative testing methodology shall be reviewed on a periodic basis as determined by the Reliability Coordinator. Approval of the alternative testing methodology will either be renewed or revoked by the Reliability Coordinator. | Retired | 2019-01-23 | 2023-07-17
1597 | Directory # 8 V4 | System Restoration | R8.4.4. | R8.4 For each functional entity identified as owning Key Facilities, which is unable to perform a test outlined in Appendix A, a requested proposed alternate testing methodology may be permitted if each of the following criteria (R8.4.1-R8.4.6) are met: R8.4.4 Operation consistent with Good Utility Practice must be demonstrated and maintained throughout the alternative testing protocol. Note: The alternative testing methodology shall be reviewed on a periodic basis as determined by the Reliability Coordinator. Approval of the alternative testing methodology will either be renewed or revoked by the Reliability Coordinator. | Retired | 2019-01-23 | 2023-07-17
1598 | Directory # 8 V4 | System Restoration | R8.4.5. | R8.4 For each functional entity identified as owning Key Facilities, which is unable to perform a test outlined in Appendix A, a requested proposed alternate testing methodology may be permitted if each of the following criteria (R8.4.1-R8.4.6) are met: R8.4.5 The alternative testing methodology results must be submitted to the Reliability Coordinator. Note: The alternative testing methodology shall be reviewed on a periodic basis as determined by the Reliability Coordinator. Approval of the alternative testing methodology will either be renewed or revoked by the Reliability Coordinator. | Retired | 2019-01-23 | 2023-07-17
1599 | Directory # 8 V4 | System Restoration | R8.4.6. | R8.4 For each functional entity identified as owning Key Facilities, which is unable to perform a test outlined in Appendix A, a requested proposed alternate testing methodology may be permitted if each of the following criteria (R8.4.1-R8.4.6) are met: R8.4.6 Approval of the alternative testing methodology results must be received from the Reliability Coordinator. Note: The alternative testing methodology shall be reviewed on a periodic basis as determined by the Reliability Coordinator. Approval of the alternative testing methodology will either be renewed or revoked by the Reliability Coordinator. | Retired | 2019-01-23 | 2023-07-17
1593 | Directory # 8 V4 | System Restoration | R9. | Each functional entity that owns a Cable pressurization system at Key Facilities shall test for satisfactory operation of both the primary pressurization system and/or the backup pressurization system (if applicable) ability/abilities to maintain required pressure upon loss of power to the Key Facilities. Test basis: Frequency: every six (6) Calendar Months Duration: at least thirty (30) minutes (Reference: Appendix A; Test No. UG-1) Note: This capability is required during a blackout to maintain the availability of Cables for service and to preclude any damage to the Cables as a result of the loss of dielectric strength. | Retired | 2019-01-23 | 2023-07-17
1600 | Directory # 8 V5 | System Restoration | R1. | Each Reliability Coordinator, together with its respective Transmission Operators, shall jointly develop, maintain, verify, and implement a system restoration plan for its Reliability Coordinator Area that shall: | Effective | 2023-07-18
1601 | Directory # 8 V5 | System Restoration | R1.1. | Identify the Reliability Coordinator Area’s BMPS(s). | Effective | 2023-07-18
1602 | Directory # 8 V5 | System Restoration | R1.2. | Address the priority of providing off-site AC power to nuclear power stations. | Effective | 2023-07-18
1603 | Directory # 8 V5 | System Restoration | R1.3. | Identify Interconnection points with adjacent Reliability Coordinator Areas. | Effective | 2023-07-18
1604 | Directory # 8 V5 | System Restoration | R1.4. | Identify parameters to Synchronize adjacent BMPSs | Effective | 2023-07-18
1605 | Directory # 8 V5 | System Restoration | R1.5. | Address coordination of system restoration with neighboring Reliability Coordinator Areas. | Effective | 2023-07-18
1606 | Directory # 8 V5 | System Restoration | R1.6. | Provide for the re-energization of transmission systems to; R1.6.1 major generating stations; R1.6.2 inter-area tie points. | Effective | 2023-07-18
1607 | Directory # 8 V5 | System Restoration | R1.7. | Address electrical Island stabilization. | Effective | 2023-07-18
1608 | Directory # 8 V5 | System Restoration | R1.8. | Identify provisions for fuel resources to support operation of any supplementary generators (e.g., a diesel generator) necessary for operating Key Facilities consistent with the expected requirements of the system restoration plan. | Effective | 2023-07-18
1609 | Directory # 8 V5 | System Restoration | R10. | Each functional entity shall test its backup power supplies identified as Critical Components as specified in R10.1 through R10.5. Where there are separate backup power arrangements at Key Facilities for transmission or generating station equipment and telecommunication equipment, such equipment shall be separately identified on the list of Critical Components and shall be inspected and tested individually. | Effective | 2023-07-18
1610 | Directory # 8 V5 | System Restoration | R10.1. | Equipment Inspection Batteries and/or battery chargers identified as Critical Components shall be inspected in accordance with maintenance activities and maintenance intervals specified in PRC-005-Protection System, Automatic Reclosing, and Sudden Pressure Relaying Maintenance, giving consideration to exclusions per PRC-005 Table 1-4(f) (Reference: Appendix A; Test KF-1) | Effective | 2023-07-18
1611 | Directory # 8 V5 | System Restoration | R10.2. | Equipment Verification Batteries and/or battery chargers identified as Critical Components shall be verified in accordance with maintenance activities and maintenance intervals specified in PRC-005 Protection System, Automatic Reclosing, and Sudden Pressure Relaying Maintenance, giving consideration to exclusions per PRC-005 Table 1-4(f) (Reference: Appendix A; Test KF-2) | Effective | 2023-07-18
1612 | Directory # 8 V5 | System Restoration | R10.3. | Confirm That All Critical Components Loads Can Be Supplied Each owner of batteries and/or battery chargers identified as Critical Components shall confirm that all Critical Components Loads are connected to and can be supplied by the batteries and/or battery chargers. The functional entity owner shall confirm through its design review, when modifications are made to Key Facilities, or through testing, that all Critical Components Loads are connected to and can be sufficiently supplied by the batteries and/or battery chargers. Test basis: Frequency: when modifications are made to Key Facilities or at least once every sixty (60) Calendar Months (Reference: Appendix A; Test KF-3) | Effective | 2023-07-18
1613 | Directory # 8 V5 | System Restoration | R10.4. | Startup and Run Test Each owner of a backup power generator identified on the list of Critical Components of Key Facilities, shall perform a startup, and run test on that backup power generator. Test basis: Frequency: monthly Duration: at least fifteen (15) minutes (Reference: Appendix A; Test KF-5). Note: This test also applies to supplemental generation required for Blackstart Capability and to a control center and telecommunication center backup power generator. | Effective | 2023-07-18
1614 | Directory # 8 V5 | System Restoration | R10.5. | Startup, Transfer and Load Test Each owner of a backup power generator identified on the list of Critical Components of Key Facilities shall verify that the backup power generator will pick up the Critical Components Load following the loss of station service. Note: This test also applies to a control center and telecommunication center backup power generator. For automatically started backup power generators, a startup, transfer, and Load test simulating the loss of station service shall be performed. Test basis: Frequency: every twelve (12) Calendar Months Duration: at least thirty (30) minutes (Reference: Appendix A; Test KF-6) For manually started backup power generators, a startup, transfer, and Load test performed by starting the generator and verifying Reliable Operation while supplying Critical Components Loads, shall be performed by the asset owner. Test basis: Frequency: every twelve (12) Calendar Months Duration: at least thirty (30) minutes (Reference: Appendix A; Test KF-6) Note: Power sources used to start Resources with Blackstart Capability will be excluded from test KF-6. | Effective | 2023-07-18
1615 | Directory # 8 V5 | System Restoration | R11. | Each functional entity identified as owning Key Facilities shall test its Critical Components in the control centers and the telecommunication centers identified as Key Facilities to demonstrate that the computer systems will be functional without dependencies on power sources that may be unavailable during a partial or complete system blackout, when required for system restoration. | Effective | 2023-07-18
1616 | Directory # 8 V5 | System Restoration | R11.1. | AC Supply Interruption Test The uninterruptible power supply (UPS) systems in control centers and telecommunication centers shall be tested by interrupting AC supply and verifying that all Critical Components Loads are supplied for a time that is sufficient for backup power sources to restore the AC input to the UPS Test basis: Frequency: every twelve (12) Calendar Months. (Reference: Appendix A; Test CC-1) | Effective | 2023-07-18
1617 | Directory # 8 V5 | System Restoration | R11.2. | Computer Redundancy (SCADA/EMS) Test Each functional entity identified as owning Key Facilities shall test its computer redundancy (SCADA/EMS) features to ensure computer systems (SCADA/EMS) continue to function consistent with Good Utility Practice. Test basis: Frequency: every six (6) Calendar Months (Reference: Appendix A; Test CC-2) | Effective | 2023-07-18
1618 | Directory # 8 V5 | System Restoration | R12. | Each functional entity owning a generating station with Blackstart Capability shall verify such concurrent capability as follows: | Effective | 2023-07-18
1619 | Directory # 8 V5 | System Restoration | R12.1. | A generating station with Blackstart Capability shall be tested for successful equipment startup, sufficient to Energize a transmission Element or a generating station switchyard Element, if that does not involve the disconnection of Load that is not dedicated generating station Load to conduct the test. Verify Reliable Operation while isolated from the BPS . Test basis: Frequency: every twelve (12) Calendar Months Duration: at least ten (10) minutes of Reliable Operation (Reference: Appendix A; Test No. BS-1) | Effective | 2023-07-18
1620 | Directory # 8 V5 | System Restoration | R12.2. | Operations voice communications and auxiliary systems such as Supervisory Control and Data Acquisition (SCADA) that are required for Blackstart Capability shall be verified to operate consistent with Good Utility Practice independent of the interconnected system or other unrelated unit for any source of station service. Test basis: Frequency: every twelve (12) Calendar Months Duration: Verification of at least ten (10) minutes of Reliable Operation concurrent with R12.1 (Reference: Appendix A; Test No. BS-1) | Effective | 2023-07-18
1621 | Directory # 8 V5 | System Restoration | R13. | Each Reliability Coordinator shall determine, as required by its respective system restoration plan, the number of units within a generating station that are to be tested for Blackstart Capability, and shall notify the applicable functional entity/entities. | Effective | 2023-07-18
1622 | Directory # 8 V5 | System Restoration | R14. | Each Reliability Coordinator shall confirm, consistent with the objectives of its respective system restoration plan, that the functional entity owning a generating station with Blackstart Capability that is part of the BMPS has completed a successful Blackstart Capabilitytest. | Effective | 2023-07-18
1623 | Directory # 8 V5 | System Restoration | R15. | A functional entity that has confirmed the loss of functionality of Critical Components shall report to the Transmission Operator responsible for operating the Critical Components of the Critical Components’ loss of functionality as soon as possible but no longer than 15 minutes after confirmation of the loss of functionality. | Effective | 2023-07-18
1624 | Directory # 8 V5 | System Restoration | R15.1. | The Transmission Operator shall report to its Reliability Coordinator, as soon as possible but no longer than 15 minutes after the functional entity has confirmed the loss of functionality of Critical Components to the Transmission Operator. Examples of such conditions are, but not limited to: • Loss of control of remote equipment. • Complete loss of AC or DC service supply. • Loss of Resources with Blackstart Capability. | Effective | 2023-07-18
1625 | Directory # 8 V5 | System Restoration | R16. | A functional entity that has confirmed the loss of redundancy of Critical Components shall report to the Transmission Operator responsible for the Critical Components of loss of redundancy as soon as possible but no longer than 12 hours after confirmation of the loss of redundancy. Examples of such conditions are: • Loss of a redundant AC or DC service supply. • Loss of redundant Critical Components associated with Resources with Blackstart Capability. | Effective | 2023-07-18
1626 | Directory # 8 V5 | System Restoration | R17. | A functional entity that has scheduled a maintenance activity (inservice or out-of-service) of Critical Components that will result in the loss of functionality of the Critical Components shall report that maintenance activity to the Transmission Operator responsible for the Critical Components at least 24 hours prior to that scheduled loss of functionality. | Effective | 2023-07-18
1627 | Directory # 8 V5 | System Restoration | R17.1. | The functional entity shall report to the Transmission Operator responsible for Critical Components as soon as possible after the scheduled loss of functionality has begun. | Effective | 2023-07-18
1628 | Directory # 8 V5 | System Restoration | R17.2. | If the scheduled maintenance condition causing the loss of functionality of Critical Components affects the functionality of Key Facilities, the Transmission Operator responsible for the Critical Components shall report this scheduled maintenance condition to its Reliability Coordinator. • Upon receipt of the scheduled maintenance report • Upon receipt of the scheduled maintenance start • Upon receipt of the scheduled maintenance end | Effective | 2023-07-18
1629 | Directory # 8 V5 | System Restoration | R18. | A functional entity shall report the actions to be taken to restore Critical Components’ availability or redundancy to the Transmission Operator responsible for the Critical Components as soon as known. | Effective | 2023-07-18
1630 | Directory # 8 V5 | System Restoration | R18.1. | The functional entity shall report to the Transmission Operator responsible for the Critical Components the anticipated time that the Critical Components functionality will be restored. | Effective | 2023-07-18
1631 | Directory # 8 V5 | System Restoration | R18.2. | The functional entity shall report to the Transmission Operator responsible for maintaining redundancy for Critical Components the anticipated time that the Critical Components’ redundancy will be restored. | Effective | 2023-07-18
1632 | Directory # 8 V5 | System Restoration | R19. | A functional entity shall report to the Transmission Operator responsible for the functionality of Critical Components, the date and time when the functionality of Critical Components is restored. | Effective | 2023-07-18
1633 | Directory # 8 V5 | System Restoration | R2. | Each Reliability Coordinator shall, in determining the BMPS, coordinate with all impacted parties and/or functional entities. | Effective | 2023-07-18
1634 | Directory # 8 V5 | System Restoration | R3. | Each Reliability Coordinator shall ensure that the BMPS includes the ability to: | Effective | 2023-07-18
1635 | Directory # 8 V5 | System Restoration | R3.1. | Use generator Blackstart Capability. | Effective | 2023-07-18
1636 | Directory # 8 V5 | System Restoration | R3.2. | Form an electrical Island(s). | Effective | 2023-07-18
1637 | Directory # 8 V5 | System Restoration | R3.3. | Synchronize electrical Islands; and | Effective | 2023-07-18
1638 | Directory # 8 V5 | System Restoration | R3.4. | Permit the successful performance of the system restoration plan. | Effective | 2023-07-18
1639 | Directory # 8 V5 | System Restoration | R4. | Each Reliability Coordinator shall identify Key Facilities and shall inform each functional entity of its identified Key Facilities. | Effective | 2023-07-18
1640 | Directory # 8 V5 | System Restoration | R5. | Each functional entity identified as the owner of newly identified or proposed Key Facilities: | Effective | 2023-07-18
1641 | Directory # 8 V5 | System Restoration | R5.1. | Shall identify the associated Critical Components for those Key Facilities prior to the effective date of the approved system restoration plan. | Effective | 2023-07-18
1642 | Directory # 8 V5 | System Restoration | R5.2. | Shall provide, upon request of the Reliability Coordinator, within the timeframe requested, a list of Critical Components associated with proposed Key Facilities. | Effective | 2023-07-18
1643 | Directory # 8 V5 | System Restoration | R5.3. | Shall ensure, prior to the effective date of the approved system restoration plan, or within the timeframe requested by the Reliability Coordinator, that all applicable proposed Key Facilities testing outlined in Appendix A has been successfully completed. | Effective | 2023-07-18
1644 | Directory # 8 V5 | System Restoration | R6. | Each functional entity identified as the owner of existing Key Facilities: | Effective | 2023-07-18
1645 | Directory # 8 V5 | System Restoration | R6.1. | Shall provide, upon request of the Reliability Coordinator, within the timeframe requested, any updates, additions, or deletions to the list of Critical Components for identified Key Facilities. | Effective | 2023-07-18
1646 | Directory # 8 V5 | System Restoration | R6.2. | Shall ensure, prior to the effective date of the approved system restoration plan, or within the timeframe requested by the Reliability Coordinator, that the following components associated with identified Key Facilities testing outlined in Appendix A have been successfully completed: R6.2.1 All applicable additional Critical Components R6.2.2 Any modifications to existing Critical Components that could potentially impact the functionality of those Critical Components. | Effective | 2023-07-18
1647 | Directory # 8 V5 | System Restoration | R7. | Following the occurrence of an event that required implementation of a system restoration plan and upon request of the Task Force on Coordination of Operation (TFCO): | Effective | 2023-07-18
1648 | Directory # 8 V5 | System Restoration | R7.1. | The Reliability Coordinator shall report, within the timeframe requested by the TFCO, on the performance of its system restoration plan. | Effective | 2023-07-18
1649 | Directory # 8 V5 | System Restoration | R7.2. | The Transmission Operator shall report, within the timeframe requested by the TFCO, on the performance of its system restoration plan. | Effective | 2023-07-18
1650 | Directory # 8 V5 | System Restoration | R8. | Each functional entity which has been identified as owning Key Facilities shall: | Effective | 2023-07-18
1651 | Directory # 8 V5 | System Restoration | R8.1. | Perform the tests outlined in Appendix A. | Effective | 2023-07-18
1652 | Directory # 8 V5 | System Restoration | R8.2. | Maintain evidence of the test results consistent with Section 4.0. | Effective | 2023-07-18
1653 | Directory # 8 V5 | System Restoration | R8.3. | Provide evidence, upon request of the Reliability Coordinator and/or Transmission Operator, within the timeframe requested, that the tests specified in sub-Requirement R8.1 have been met. | Effective | 2023-07-18
1655 | Directory # 8 V5 | System Restoration | R8.4.1. | R8.4 For each functional entity identified as owning Key Facilities, which is unable to perform a test outlined in Appendix A, a requested proposed alternate testing methodology may be permitted if each of the following criteria (R8.4.1-R8.4.6) are met: R8.4.1 Evidence must be provided to the Reliability Coordinator that conducting the specified Appendix A test would be detrimental to the operational functionality of the Key Facility. Note: The alternative testing methodology shall be reviewed on a periodic basis as determined by the Reliability Coordinator. Approval of the alternative testing methodology will either be renewed or revoked by the Reliability Coordinator. | Effective | 2023-07-18
1656 | Directory # 8 V5 | System Restoration | R8.4.2. | R8.4 For each functional entity identified as owning Key Facilities, which is unable to perform a test outlined in Appendix A, a requested proposed alternate testing methodology may be permitted if each of the following criteria (R8.4.1-R8.4.6) are met: R8.4.2 The alternative testing methodology, with mitigating controls to meet the intent of the Directory Requirement, must be proposed to the Reliability Coordinator to evaluate and to accept or reject the requested proposed alternate testing methodology. Note: The alternative testing methodology shall be reviewed on a periodic basis as determined by the Reliability Coordinator. Approval of the alternative testing methodology will either be renewed or revoked by the Reliability Coordinator. | Effective | 2023-07-18
1657 | Directory # 8 V5 | System Restoration | R8.4.3. | R8.4 For each functional entity identified as owning Key Facilities, which is unable to perform a test outlined in Appendix A, a requested proposed alternate testing methodology may be permitted if each of the following criteria (R8.4.1-R8.4.6) are met: R8.4.3 Post acceptance per R8.4.2, the alternative testing methodology must be successfully conducted. Note: The alternative testing methodology shall be reviewed on a periodic basis as determined by the Reliability Coordinator. Approval of the alternative testing methodology will either be renewed or revoked by the Reliability Coordinator. | Effective | 2023-07-18
1658 | Directory # 8 V5 | System Restoration | R8.4.4. | R8.4 For each functional entity identified as owning Key Facilities, which is unable to perform a test outlined in Appendix A, a requested proposed alternate testing methodology may be permitted if each of the following criteria (R8.4.1-R8.4.6) are met: R8.4.4 Operation consistent with Good Utility Practice must be demonstrated and maintained throughout the alternative testing protocol. Note: The alternative testing methodology shall be reviewed on a periodic basis as determined by the Reliability Coordinator. Approval of the alternative testing methodology will either be renewed or revoked by the Reliability Coordinator. | Effective | 2023-07-18
1659 | Directory # 8 V5 | System Restoration | R8.4.5. | R8.4 For each functional entity identified as owning Key Facilities, which is unable to perform a test outlined in Appendix A, a requested proposed alternate testing methodology may be permitted if each of the following criteria (R8.4.1-R8.4.6) are met: R8.4.5 The alternative testing methodology results must be submitted to the Reliability Coordinator. Note: The alternative testing methodology shall be reviewed on a periodic basis as determined by the Reliability Coordinator. Approval of the alternative testing methodology will either be renewed or revoked by the Reliability Coordinator. | Effective | 2023-07-18
1660 | Directory # 8 V5 | System Restoration | R8.4.6. | R8.4 For each functional entity identified as owning Key Facilities, which is unable to perform a test outlined in Appendix A, a requested proposed alternate testing methodology may be permitted if each of the following criteria (R8.4.1-R8.4.6) are met: R8.4.6 Approval of the alternative testing methodology results must be received from the Reliability Coordinator. Note: The alternative testing methodology shall be reviewed on a periodic basis as determined by the Reliability Coordinator. Approval of the alternative testing methodology will either be renewed or revoked by the Reliability Coordinator. | Effective | 2023-07-18
1654 | Directory # 8 V5 | System Restoration | R9. | Each functional entity that owns a Cable pressurization system at Key Facilities shall test for satisfactory operation of both the primary pressurization system and/or the backup pressurization system (if applicable) ability/abilities to maintain required pressure upon loss of power to the Key Facilities. Test basis: Frequency: every six (6) Calendar Months Duration: at least thirty (30) minutes (Reference: Appendix A; Test No. UG-1) Note: This capability is required during a blackout to maintain the availability of Cables for service and to preclude any damage to the Cables as a result of the loss of dielectric strength. | Effective | 2023-07-18
124 | Directory # 9 | Verification of Generator Gross and Net Real Power Capability | R1. | The Transmission Operator shall develop and maintain documentation of those generators or generation facilities that must verify the Gross Real Power Capability and Net Real Power Capability for the summer and winter capability seasons. The documentation maintained by the Transmission Operator shall include the following: | Retired | 2008-12-22 | 2009-07-06
125 | Directory # 9 | Verification of Generator Gross and Net Real Power Capability | R1.1. | All generators or generation facilities Declared Gross Real Power Capability and Declared Net Real Power Capability. | Retired | 2008-12-22 | 2009-07-06 | TOP
126 | Directory # 9 | Verification of Generator Gross and Net Real Power Capability | R1.2. | All generators or generation facilities Verified Gross Real Power Capability and Verified Net Real Power Capability, verification date and method of verification. | Retired | 2008-12-22 | 2009-07-06 | TOP
127 | Directory # 9 | Verification of Generator Gross and Net Real Power Capability | R1.3. | Discrepancies between a Generator Owner’s declared and verified Gross Real Power Capability and Net Real Power Capability, the reason for such discrepancies and the Generator Owner’s plan to address the discrepancies. | Retired | 2008-12-22 | 2009-07-06 | TOP
128 | Directory # 9 | Verification of Generator Gross and Net Real Power Capability | R1.4. | Generator Owner supplied Gross Real Power Capability and Net Real Power Capability testing, manufacturer data, performance tracking or operating historical data, certification documentation, as specified by the Transmission Operator. | Retired | 2008-12-22 | 2009-07-06 | TOP
129 | Directory # 9 | Verification of Generator Gross and Net Real Power Capability | R1.5. | All generators or generation facilities exempted from the verification requirements and the basis for their exemption (see Section 1.5) | Retired | 2008-12-22 | 2009-07-06 | TOP
138 | Directory # 9 | Verification of Generator Gross and Net Real Power Capability | R10. | If a Transmission Operator determines that the difference between the Declared Gross Real Power and Declared Net Real Power Capability of a generator or generation facility is insignificant for NPCC Bulk Power System reliability analysis, then periodic verification will be required for only one numerical value. | Retired | 2008-12-22 | 2009-07-06 | TOP
139 | Directory # 9 | Verification of Generator Gross and Net Real Power Capability | R11 | The Generator Owner shall provide generator or generation facility Declared Gross Real Power Capability and Declared Net Real Power Capability to the Transmission Operator. | Retired | 2008-12-22 | 2009-07-06
140 | Directory # 9 | Verification of Generator Gross and Net Real Power Capability | R12. | The Generator Owner shall provide evidence, upon request, to the Transmission Operator that the generator or generation facility Gross Real Power Capability and Net Real Power Capability have been verified. | Retired | 2008-12-22 | 2009-07-06
141 | Directory # 9 | Verification of Generator Gross and Net Real Power Capability | R13. | The Generator Owner shall report to the Transmission Operator any discrepancies between declared and verified Gross Real Power Capability or Net Real Power Capability within a time frame specified by the Transmission Operator and develop and implement a plan to resolve the discrepancies. | Retired | 2008-12-22 | 2009-07-06 | TOP
142 | Directory # 9 | Verification of Generator Gross and Net Real Power Capability | R14. | The Generator Owner shall determine and report to the Transmission Operator the generator or generation facility real power seasonal auxiliary loads (including common station loads). | Retired | 2008-12-22 | 2009-07-06
143 | Directory # 9 | Verification of Generator Gross and Net Real Power Capability | R15. | The Generator Owner shall comply with Transmission Operator requests for periodic verification of Gross Real Power Capability and Net Real Power Capability of their generators or generation facilities. | Retired | 2008-12-22 | 2009-07-06
144 | Directory # 9 | Verification of Generator Gross and Net Real Power Capability | R16. | The Generator Owner shall verify the Gross Real Power Capability and Net Real Power Capability of thermal generators on the basis of operation for no less than one hour. | Retired | 2008-12-22 | 2009-07-06
145 | Directory # 9 | Verification of Generator Gross and Net Real Power Capability | R16.1. | The verification of thermal generator’s capability shall include any of the following: • Testing, • Use of operating historical data, • Commissioning data (for new generators only), • Performance tracking data acquired during the same seasonal capability period. | Retired | 2008-12-22 | 2009-07-06
146 | Directory # 9 | Verification of Generator Gross and Net Real Power Capability | R17. | The Generator Owner shall verify the Gross Real Power Capability and Net Real Power Capability of internal combustion generators and gas turbine generators. The verification shall correspond to operation for no less than one hour under the ambient conditions established in R6 for which the Gross Real Power Capability and Net Real Power Capability are being claimed. | Retired | 2008-12-22 | 2009-07-06
147 | Directory # 9 | Verification of Generator Gross and Net Real Power Capability | R17.1. | The verification of internal combustion and gas turbine generators capability shall include any of the following: • Testing, • Use of operating historical data, • Commissioning data (for new generators only), • Performance tracking data acquired during the same seasonal capability period. | Retired | 2008-12-22 | 2009-07-06
148 | Directory # 9 | Verification of Generator Gross and Net Real Power Capability | R18. | The Generator Owner shall verify the Gross Real Power Capability and Net Real Power Capability of hydro generators either on a generation facility or on an individual generator basis. The Gross Real Power Capability and Net Real Power Capability shall be determined on the basis of the availability of sufficient water at an adequate head to provide the output for no less than one hour. | Retired | 2008-12-22 | 2009-07-06
149 | Directory # 9 | Verification of Generator Gross and Net Real Power Capability | R18.1. | The verification of hydro generator’s capability shall include any of the following: • Testing, • Use of operating historical data, • Commissioning data (for new generators only), • Performance tracking data acquired during the same seasonal capability period. | Retired | 2008-12-22 | 2009-07-06
150 | Directory # 9 | Verification of Generator Gross and Net Real Power Capability | R19. | The Generator Owner shall verify the Gross Real Power Capability and Net Real Power Capability of combined cycle generators on a generation facility, individual generator or on a generator stage basis for no less than one hour under the ambient conditions established by the Transmission Operator in R6 for which the Gross Real Power Capability and Net Real Power Capability are being claimed. | Retired | 2008-12-22 | 2009-07-06
151 | Directory # 9 | Verification of Generator Gross and Net Real Power Capability | R19.1. | The verification of a combined cycle generator’s capability shall include any of the following: • Testing, • Use of operating historical data, • Commissioning data (for new generators only), • Performance tracking data acquired during the same seasonal capability period. | Retired | 2008-12-22 | 2009-07-06 | TOP
130 | Directory # 9 | Verification of Generator Gross and Net Real Power Capability | R2. | The Transmission Operator shall establish and document a program to periodically verify the Gross Real Power Capability and Net Real Power Capability of all generators and generation facilities that are subject to periodic seasonal Gross Real Power Capability and Net Real Power Capability verification. | Retired | 2008-12-22 | 2009-07-06 | TOP
152 | Directory # 9 | Verification of Generator Gross and Net Real Power Capability | R20. | The Generator Owner shall verify the Gross Real Power Capability and Net Real Power Capability of intermittent power resources (wind, solar, tidal geo-thermal, etc.) using any of the following: • Manufacturer’s data, • Performance tracking, • Operating historical data | Retired | 2008-12-22 | 2009-07-06
153 | Directory # 9 | Verification of Generator Gross and Net Real Power Capability | R21. | The Generator Owner shall verify the Gross Real Power Capability and Net Real Power Capability of multiple generator facilities when limited by common elements based on the real power capability of the facility and not the sum of the capabilities of the individual generators. | Retired | 2008-12-22 | 2009-07-06 | TOP
154 | Directory # 9 | Verification of Generator Gross and Net Real Power Capability | R22. | The Generator Owner shall identify any equipment or other factor that will limit the capability of the generator or generation facility to meet its Declared Gross Real Power Capability or Declared Net Real Power Capability. | Retired | 2008-12-22 | 2009-07-06 | TOP
155 | Directory # 9 | Verification of Generator Gross and Net Real Power Capability | R23. | The Generator Owner shall notify the Transmission Operator and request an exemption if it cannot conduct seasonal capability testing of a generator or generation facility for any of the reasons listed below. • Adverse impact on transmission system reliability • Potential damage to transmission system or generator equipment • Environment conditions • Governmental regulatory or operating license limitations • An extended outage to the generator or generation facility | Retired | 2008-12-22 | 2009-07-06
156 | Directory # 9 | Verification of Generator Gross and Net Real Power Capability | R24. | The Transmission Operator shall, within 30 calendar days of receiving notification from a Generator Owner that it is requesting an exemption because it cannot perform verification for the required seasonal period, notify the Generator Owner whether its generator will be exempted from the seasonal capability testing. Where the exemption is approved, the Transmission Operator shall coordinate with the Generator Owner to reschedule the verification for the next seasonal verification period. | Retired | 2008-12-22 | 2009-07-06 | TOP
157 | Directory # 9 | Verification of Generator Gross and Net Real Power Capability | R25. | The Generator Owner for a generator or generation facility exempted from seasonal capability testing shall submit the following to the Transmission Operator: • For existing generators, generator operation records, manufacturer data, or performance tracking for the previous applicable seasonal verification period for this generator or generation facility. • Engineering analysis in conjunction with performance tracking data to justify any difference between a generators or generation facilities declared capability and previous applicable seasonal performance tracking data. • For new generators only, commissioning data. | Retired | 2008-12-22 | 2009-07-06
131 | Directory # 9 | Verification of Generator Gross and Net Real Power Capability | R3. | The Transmission Operator shall provide any changes to its verification process to the Generator Owners within 30 calendar days of issue. | Retired | 2008-12-22 | 2009-07-06 | TOP
132 | Directory # 9 | Verification of Generator Gross and Net Real Power Capability | R4. | The Transmission Operator shall establish and document requirements for a Generator Owner to notify the Transmission Operator within a specified time period when its generator or generation facility cannot achieve the Declared Gross Real Power Capability or Declared Net Real Power Capability because of equipment issues. | Retired | 2008-12-22 | 2009-07-06 | TOP
133 | Directory # 9 | Verification of Generator Gross and Net Real Power Capability | R5. | The Transmission Operator shall establish and document a time frame for the Generator Owner to address equipment issues that result in a generator or generation facility not achieving the Declared Gross Real Power Capability or Declared Net Real Power Capability. | Retired | 2008-12-22 | 2009-07-06
134 | Directory # 9 | Verification of Generator Gross and Net Real Power Capability | R6. | The Transmission Operator shall establish and document the ambient conditions that correspond to the summer and winter capability seasons for which the Gross Real Power Capability and Net Real Power Capability are verified. | Retired | 2008-12-22 | 2009-07-06
135 | Directory # 9 | Verification of Generator Gross and Net Real Power Capability | R7. | The Transmission Operator shall establish and document those intermittent or small generating units whose capability may be represented by verification results of a single generating unit. | Retired | 2008-12-22 | 2009-07-06
136 | Directory # 9 | Verification of Generator Gross and Net Real Power Capability | R8. | The Transmission Operator shall request Generator Owners to verify the seasonal Gross Real Power Capability and Net Real Power Capability of their generators or generation facilities that are subject to periodic seasonal Gross Real Power Capability and Net Real Power Capability verification every three (3) years or more frequently as required by the Transmission Operator. The two (2) capability seasons are defined as summer and winter as specified by the Transmission Operator. | Retired | 2008-12-22 | 2009-07-06 | TOP
137 | Directory # 9 | Verification of Generator Gross and Net Real Power Capability | R9. | If a Transmission Operator determines that only one seasonal generating capability value is required for NPCC Bulk Power System reliability analysis, then periodic verification will be required only for that particular season. | Retired | 2008-12-22 | 2009-07-06 | TOP
1743 | Directory # 9 V1 | Verification of Generator Gross and Net Real Power Capability | R1. | The Transmission Operator shall develop and maintain documentation of those generators or generation facilities that must verify the Gross Real Power Capability and Net Real Power Capability for the summer and winter capability seasons. The documentation maintained by the Transmission Operator shall include the following: | Retired | 2009-07-07 | 2012-10-25
1744 | Directory # 9 V1 | Verification of Generator Gross and Net Real Power Capability | R1.1. | All generators or generation facilities Declared Gross Real Power Capability and Declared Net Real Power Capability. | Retired | 2009-07-07 | 2012-10-25
1745 | Directory # 9 V1 | Verification of Generator Gross and Net Real Power Capability | R1.2. | All generators or generation facilities Verified Gross Real Power Capability and Verified Net Real Power Capability, verification date and method of verification. | Retired | 2009-07-07 | 2012-10-25
1746 | Directory # 9 V1 | Verification of Generator Gross and Net Real Power Capability | R1.3. | Discrepancies between a Generator Owner’s declared and verified Gross Real Power Capability and Net Real Power Capability, the reason for such discrepancies and the Generator Owner’s plan to address the discrepancies. | Retired | 2009-07-07 | 2012-10-25
1747 | Directory # 9 V1 | Verification of Generator Gross and Net Real Power Capability | R1.4. | Generator Owner supplied Gross Real Power Capability and Net Real Power Capability testing, manufacturer data, performance tracking or operating historical data, certification documentation, as specified by the Transmission Operator. | Retired | 2009-07-07 | 2012-10-25
1748 | Directory # 9 V1 | Verification of Generator Gross and Net Real Power Capability | R1.5. | All generators or generation facilities exempted from the verification requirements and the basis for their exemption (see Section 1.5) | Retired | 2009-07-07 | 2012-10-25
1749 | Directory # 9 V1 | Verification of Generator Gross and Net Real Power Capability | R10. | If a Transmission Operator determines that the difference between the Declared Gross Real Power and Declared Net Real Power Capability of a generator or generation facility is insignificant for NPCC Bulk Power System reliability analysis, then periodic verification will be required for only one numerical value. | Retired | 2009-07-07 | 2012-10-25
1750 | Directory # 9 V1 | Verification of Generator Gross and Net Real Power Capability | R11 | The Generator Owner shall provide generator or generation facility Declared Gross Real Power Capability and Declared Net Real Power Capability to the Transmission Operator. | Retired | 2009-07-07 | 2012-10-25
1751 | Directory # 9 V1 | Verification of Generator Gross and Net Real Power Capability | R12. | The Generator Owner shall provide evidence, upon request, to the Transmission Operator that the generator or generation facility Gross Real Power Capability and Net Real Power Capability have been verified. | Retired | 2009-07-07 | 2012-10-25
1752 | Directory # 9 V1 | Verification of Generator Gross and Net Real Power Capability | R13. | The Generator Owner shall report to the Transmission Operator any discrepancies between declared and verified Gross Real Power Capability or Net Real Power Capability within a time frame specified by the Transmission Operator and develop and implement a plan to resolve the discrepancies. | Retired | 2009-07-07 | 2012-10-25
1753 | Directory # 9 V1 | Verification of Generator Gross and Net Real Power Capability | R14. | The Generator Owner shall determine and report to the Transmission Operator the generator or generation facility real power seasonal auxiliary loads (including common station loads). | Retired | 2009-07-07 | 2012-10-25
1754 | Directory # 9 V1 | Verification of Generator Gross and Net Real Power Capability | R15. | The Generator Owner shall comply with Transmission Operator requests for periodic verification of Gross Real Power Capability and Net Real Power Capability of their generators or generation facilities. | Retired | 2009-07-07 | 2012-10-25
1755 | Directory # 9 V1 | Verification of Generator Gross and Net Real Power Capability | R16. | The Generator Owner shall verify the Gross Real Power Capability and Net Real Power Capability of thermal generators on the basis of operation for no less than one hour. | Retired | 2009-07-07 | 2012-10-25
1756 | Directory # 9 V1 | Verification of Generator Gross and Net Real Power Capability | R16.1. | The verification of thermal generator’s capability shall include any of the following: • Testing, • Use of operating historical data, • Commissioning data (for new generators only), • Performance tracking data acquired during the same seasonal capability period. | Retired | 2009-07-07 | 2012-10-25
1757 | Directory # 9 V1 | Verification of Generator Gross and Net Real Power Capability | R17. | The Generator Owner shall verify the Gross Real Power Capability and Net Real Power Capability of internal combustion generators and gas turbine generators. The verification shall correspond to operation for no less than one hour under the ambient conditions established in R6 for which the Gross Real Power Capability and Net Real Power Capability are being claimed. | Retired | 2009-07-07 | 2012-10-25
1758 | Directory # 9 V1 | Verification of Generator Gross and Net Real Power Capability | R17.1. | The verification of internal combustion and gas turbine generators capability shall include any of the following: • Testing, • Use of operating historical data, • Commissioning data (for new generators only), • Performance tracking data acquired during the same seasonal capability period. | Retired | 2009-07-07 | 2012-10-25
1759 | Directory # 9 V1 | Verification of Generator Gross and Net Real Power Capability | R18. | The Generator Owner shall verify the Gross Real Power Capability and Net Real Power Capability of hydro generators either on a generation facility or on an individual generator basis. The Gross Real Power Capability and Net Real Power Capability shall be determined on the basis of the availability of sufficient water at an adequate head to provide the output for no less than one hour. | Retired | 2009-07-07 | 2012-10-25
1760 | Directory # 9 V1 | Verification of Generator Gross and Net Real Power Capability | R18.1. | The verification of hydro generator’s capability shall include any of the following: • Testing, • Use of operating historical data, • Commissioning data (for new generators only), • Performance tracking data acquired during the same seasonal capability period. | Retired | 2009-07-07 | 2012-10-25
1761 | Directory # 9 V1 | Verification of Generator Gross and Net Real Power Capability | R19. | The Generator Owner shall verify the Gross Real Power Capability and Net Real Power Capability of combined cycle generators on a generation facility, individual generator or on a generator stage basis for no less than one hour under the ambient conditions established by the Transmission Operator in R6 for which the Gross Real Power Capability and Net Real Power Capability are being claimed. | Retired | 2009-07-07 | 2012-10-25
1762 | Directory # 9 V1 | Verification of Generator Gross and Net Real Power Capability | R19.1. | The verification of a combined cycle generator’s capability shall include any of the following: • Testing, • Use of operating historical data, • Commissioning data (for new generators only), • Performance tracking data acquired during the same seasonal capability period. | Retired | 2009-07-07 | 2012-10-25
1763 | Directory # 9 V1 | Verification of Generator Gross and Net Real Power Capability | R2. | The Transmission Operator shall establish and document a program to periodically verify the Gross Real Power Capability and Net Real Power Capability of all generators and generation facilities that are subject to periodic seasonal Gross Real Power Capability and Net Real Power Capability verification. | Retired | 2009-07-07 | 2012-10-25
1764 | Directory # 9 V1 | Verification of Generator Gross and Net Real Power Capability | R20. | The Generator Owner shall verify the Gross Real Power Capability and Net Real Power Capability of intermittent power resources (wind, solar, tidal geo-thermal, etc.) using any of the following: • Manufacturer’s data, • Performance tracking, • Operating historical data | Retired | 2009-07-07 | 2012-10-25
1765 | Directory # 9 V1 | Verification of Generator Gross and Net Real Power Capability | R21. | The Generator Owner shall verify the Gross Real Power Capability and Net Real Power Capability of multiple generator facilities when limited by common elements based on the real power capability of the facility and not the sum of the capabilities of the individual generators. | Retired | 2009-07-07 | 2012-10-25
1766 | Directory # 9 V1 | Verification of Generator Gross and Net Real Power Capability | R22. | The Generator Owner shall identify any equipment or other factor that will limit the capability of the generator or generation facility to meet its Declared Gross Real Power Capability or Declared Net Real Power Capability. | Retired | 2009-07-07 | 2012-10-25
1767 | Directory # 9 V1 | Verification of Generator Gross and Net Real Power Capability | R23. | The Generator Owner shall notify the Transmission Operator and request an exemption if it cannot conduct seasonal capability testing of a generator or generation facility for any of the reasons listed below. • Adverse impact on transmission system reliability • Potential damage to transmission system or generator equipment • Environment conditions • Governmental regulatory or operating license limitations • An extended outage to the generator or generation facility | Retired | 2009-07-07 | 2012-10-25
1768 | Directory # 9 V1 | Verification of Generator Gross and Net Real Power Capability | R24. | The Transmission Operator shall, within 30 calendar days of receiving notification from a Generator Owner that it is requesting an exemption because it cannot perform verification for the required seasonal period, notify the Generator Owner whether its generator will be exempted from the seasonal capability testing. Where the exemption is approved, the Transmission Operator shall coordinate with the Generator Owner to reschedule the verification for the next seasonal verification period. | Retired | 2009-07-07 | 2012-10-25
1769 | Directory # 9 V1 | Verification of Generator Gross and Net Real Power Capability | R25. | The Generator Owner for a generator or generation facility exempted from seasonal capability testing shall submit the following to the Transmission Operator: • For existing generators, generator operation records, manufacturer data, or performance tracking for the previous applicable seasonal verification period for this generator or generation facility. • Engineering analysis in conjunction with performance tracking data to justify any difference between a generators or generation facilities declared capability and previous applicable seasonal performance tracking data. • For new generators only, commissioning data. | Retired | 2009-07-07 | 2012-10-25
1770 | Directory # 9 V1 | Verification of Generator Gross and Net Real Power Capability | R3. | The Transmission Operator shall provide any changes to its verification process to the Generator Owners within 30 calendar days of issue. | Retired | 2009-07-07 | 2012-10-25
1771 | Directory # 9 V1 | Verification of Generator Gross and Net Real Power Capability | R4. | The Transmission Operator shall establish and document requirements for a Generator Owner to notify the Transmission Operator within a specified time period when its generator or generation facility cannot achieve the Declared Gross Real Power Capability or Declared Net Real Power Capability because of equipment issues. | Retired | 2009-07-07 | 2012-10-25
1772 | Directory # 9 V1 | Verification of Generator Gross and Net Real Power Capability | R5. | The Transmission Operator shall establish and document a time frame for the Generator Owner to address equipment issues that result in a generator or generation facility not achieving the Declared Gross Real Power Capability or Declared Net Real Power Capability. | Retired | 2009-07-07 | 2012-10-25
1773 | Directory # 9 V1 | Verification of Generator Gross and Net Real Power Capability | R6. | The Transmission Operator shall establish and document the ambient conditions that correspond to the summer and winter capability seasons for which the Gross Real Power Capability and Net Real Power Capability are verified. | Retired | 2009-07-07 | 2012-10-25
1774 | Directory # 9 V1 | Verification of Generator Gross and Net Real Power Capability | R7. | The Transmission Operator shall establish and document those intermittent or small generating units whose capability may be represented by verification results of a single generating unit. | Retired | 2009-07-07 | 2012-10-25
1775 | Directory # 9 V1 | Verification of Generator Gross and Net Real Power Capability | R8. | The Transmission Operator shall request Generator Owners to verify the seasonal Gross Real Power Capability and Net Real Power Capability of their generators or generation facilities that are subject to periodic seasonal Gross Real Power Capability and Net Real Power Capability verification every three (3) years or more frequently as required by the Transmission Operator. The two (2) capability seasons are defined as summer and winter as specified by the Transmission Operator. | Retired | 2009-07-07 | 2012-10-25
1776 | Directory # 9 V1 | Verification of Generator Gross and Net Real Power Capability | R9. | If a Transmission Operator determines that only one seasonal generating capability value is required for NPCC Bulk Power System reliability analysis, then periodic verification will be required only for that particular season. | Retired | 2009-07-07 | 2012-10-25
1779 | Directory # 9 V2 | Verification of Generator Gross and Net Real Power Capability | R1. | The Transmission Operator shall develop and maintain documentation of those generators or generation facilities that must verify the Gross Real Power Capability and Net Real Power Capability for the summer and winter capability seasons. The documentation maintained by the Transmission Operator shall include the following: | Retired | 2012-10-26 | 2016-10-12
1780 | Directory # 9 V2 | Verification of Generator Gross and Net Real Power Capability | R1.1. | All generators or generation facilities Declared Gross Real Power Capability and Declared Net Real Power Capability. | Retired | 2012-10-26 | 2016-10-12
1781 | Directory # 9 V2 | Verification of Generator Gross and Net Real Power Capability | R1.2. | All generators or generation facilities Verified Gross Real Power Capability and Verified Net Real Power Capability, verification date and method of verification. | Retired | 2012-10-26 | 2016-10-12
1782 | Directory # 9 V2 | Verification of Generator Gross and Net Real Power Capability | R1.3. | Discrepancies between a Generator Owner’s declared and verified Gross Real Power Capability and Net Real Power Capability, the reason for such discrepancies and the Generator Owner’s plan to address the discrepancies. | Retired | 2012-10-26 | 2016-10-12
1783 | Directory # 9 V2 | Verification of Generator Gross and Net Real Power Capability | R1.4. | Generator Owner supplied Gross Real Power Capability and Net Real Power Capability testing, manufacturer data, performance tracking or operating historical data, certification documentation, as specified by the Transmission Operator. | Retired | 2012-10-26 | 2016-10-12
1784 | Directory # 9 V2 | Verification of Generator Gross and Net Real Power Capability | R1.5. | All generators or generation facilities exempted from the verification requirements and the basis for their exemption (see Section 1.5) | Retired | 2012-10-26 | 2016-10-12
1785 | Directory # 9 V2 | Verification of Generator Gross and Net Real Power Capability | R10. | If a Transmission Operator determines that the difference between the Declared Gross Real Power and Declared Net Real Power Capability of a generator or generation facility is insignificant for NPCC Bulk Power System reliability analysis, then periodic verification will be required for only one numerical value. | Retired | 2012-10-26 | 2016-10-12
1786 | Directory # 9 V2 | Verification of Generator Gross and Net Real Power Capability | R11 | The Generator Owner shall provide generator or generation facility Declared Gross Real Power Capability and Declared Net Real Power Capability to the Transmission Operator. | Retired | 2012-10-26 | 2016-10-12
1787 | Directory # 9 V2 | Verification of Generator Gross and Net Real Power Capability | R12. | The Generator Owner shall provide evidence, upon request, to the Transmission Operator that the generator or generation facility Gross Real Power Capability and Net Real Power Capability have been verified. | Retired | 2012-10-26 | 2016-10-12
1788 | Directory # 9 V2 | Verification of Generator Gross and Net Real Power Capability | R13. | The Generator Owner shall report to the Transmission Operator any discrepancies between declared and verified Gross Real Power Capability or Net Real Power Capability within a time frame specified by the Transmission Operator and develop and implement a plan to resolve the discrepancies. | Retired | 2012-10-26 | 2016-10-12
1789 | Directory # 9 V2 | Verification of Generator Gross and Net Real Power Capability | R14. | The Generator Owner shall determine and report to the Transmission Operator the generator or generation facility real power seasonal auxiliary loads (including common station loads). | Retired | 2012-10-26 | 2016-10-12
1790 | Directory # 9 V2 | Verification of Generator Gross and Net Real Power Capability | R15. | The Generator Owner shall comply with Transmission Operator requests for periodic verification of Gross Real Power Capability and Net Real Power Capability of their generators or generation facilities. | Retired | 2012-10-26 | 2016-10-12
1791 | Directory # 9 V2 | Verification of Generator Gross and Net Real Power Capability | R16. | The Generator Owner shall verify the Gross Real Power Capability and Net Real Power Capability of thermal generators on the basis of operation for no less than one hour. | Retired | 2012-10-26 | 2016-10-12
1792 | Directory # 9 V2 | Verification of Generator Gross and Net Real Power Capability | R16.1. | The verification of thermal generator’s capability shall include any of the following: • Testing, • Use of operating historical data, • Commissioning data (for new generators only), • Performance tracking data acquired during the same seasonal capability period. | Retired | 2012-10-26 | 2016-10-12
1793 | Directory # 9 V2 | Verification of Generator Gross and Net Real Power Capability | R17. | The Generator Owner shall verify the Gross Real Power Capability and Net Real Power Capability of internal combustion generators and gas turbine generators. The verification shall correspond to operation for no less than one hour under the ambient conditions established in R6 for which the Gross Real Power Capability and Net Real Power Capability are being claimed. | Retired | 2012-10-26 | 2016-10-12
1794 | Directory # 9 V2 | Verification of Generator Gross and Net Real Power Capability | R17.1. | The verification of internal combustion and gas turbine generators capability shall include any of the following: • Testing, • Use of operating historical data, • Commissioning data (for new generators only), • Performance tracking data acquired during the same seasonal capability period. | Retired | 2012-10-26 | 2016-10-12
1795 | Directory # 9 V2 | Verification of Generator Gross and Net Real Power Capability | R18. | The Generator Owner shall verify the Gross Real Power Capability and Net Real Power Capability of hydro generators either on a generation facility or on an individual generator basis. The Gross Real Power Capability and Net Real Power Capability shall be determined on the basis of the availability of sufficient water at an adequate head to provide the output for no less than one hour. | Retired | 2012-10-26 | 2016-10-12
1796 | Directory # 9 V2 | Verification of Generator Gross and Net Real Power Capability | R18.1. | The verification of hydro generator’s capability shall include any of the following: • Testing, • Use of operating historical data, • Commissioning data (for new generators only), • Performance tracking data acquired during the same seasonal capability period. | Retired | 2012-10-26 | 2016-10-12
1797 | Directory # 9 V2 | Verification of Generator Gross and Net Real Power Capability | R19. | The Generator Owner shall verify the Gross Real Power Capability and Net Real Power Capability of combined cycle generators on a generation facility, individual generator or on a generator stage basis for no less than one hour under the ambient conditions established by the Transmission Operator in R6 for which the Gross Real Power Capability and Net Real Power Capability are being claimed. | Retired | 2012-10-26 | 2016-10-12
1798 | Directory # 9 V2 | Verification of Generator Gross and Net Real Power Capability | R19.1. | The verification of a combined cycle generator’s capability shall include any of the following: • Testing, • Use of operating historical data, • Commissioning data (for new generators only), • Performance tracking data acquired during the same seasonal capability period. | Retired | 2012-10-26 | 2016-10-12
1799 | Directory # 9 V2 | Verification of Generator Gross and Net Real Power Capability | R2. | The Transmission Operator shall establish and document a program to periodically verify the Gross Real Power Capability and Net Real Power Capability of all generators and generation facilities that are subject to periodic seasonal Gross Real Power Capability and Net Real Power Capability verification. | Retired | 2012-10-26 | 2016-10-12
1800 | Directory # 9 V2 | Verification of Generator Gross and Net Real Power Capability | R20. | The Generator Owner shall verify the Gross Real Power Capability and Net Real Power Capability of intermittent power resources (wind, solar, tidal geo-thermal, etc.) using any of the following: • Manufacturer’s data, • Performance tracking, • Operating historical data | Retired | 2012-10-26 | 2016-10-12
1801 | Directory # 9 V2 | Verification of Generator Gross and Net Real Power Capability | R21. | The Generator Owner shall verify the Gross Real Power Capability and Net Real Power Capability of multiple generator facilities when limited by common elements based on the real power capability of the facility and not the sum of the capabilities of the individual generators. | Retired | 2012-10-26 | 2016-10-12
1802 | Directory # 9 V2 | Verification of Generator Gross and Net Real Power Capability | R22. | The Generator Owner shall identify any equipment or other factor that will limit the capability of the generator or generation facility to meet its Declared Gross Real Power Capability or Declared Net Real Power Capability. | Retired | 2012-10-26 | 2016-10-12
1803 | Directory # 9 V2 | Verification of Generator Gross and Net Real Power Capability | R23. | The Generator Owner shall notify the Transmission Operator and request an exemption if it cannot conduct seasonal capability testing of a generator or generation facility for any of the reasons listed below. • Adverse impact on transmission system reliability • Potential damage to transmission system or generator equipment • Environment conditions • Governmental regulatory or operating license limitations • An extended outage to the generator or generation facility | Retired | 2012-10-26 | 2016-10-12
1804 | Directory # 9 V2 | Verification of Generator Gross and Net Real Power Capability | R24. | The Transmission Operator shall, within 30 calendar days of receiving notification from a Generator Owner that it is requesting an exemption because it cannot perform verification for the required seasonal period, notify the Generator Owner whether its generator will be exempted from the seasonal capability testing. Where the exemption is approved, the Transmission Operator shall coordinate with the Generator Owner to reschedule the verification for the next seasonal verification period. | Retired | 2012-10-26 | 2016-10-12
1805 | Directory # 9 V2 | Verification of Generator Gross and Net Real Power Capability | R25. | The Generator Owner for a generator or generation facility exempted from seasonal capability testing shall submit the following to the Transmission Operator: • For existing generators, generator operation records, manufacturer data, or performance tracking for the previous applicable seasonal verification period for this generator or generation facility. • Engineering analysis in conjunction with performance tracking data to justify any difference between a generators or generation facilities declared capability and previous applicable seasonal performance tracking data. • For new generators only, commissioning data. | Retired | 2012-10-26 | 2016-10-12
1806 | Directory # 9 V2 | Verification of Generator Gross and Net Real Power Capability | R3. | The Transmission Operator shall provide any changes to its verification process to the Generator Owners within 30 calendar days of issue. | Retired | 2012-10-26 | 2016-10-12
1807 | Directory # 9 V2 | Verification of Generator Gross and Net Real Power Capability | R4. | The Transmission Operator shall establish and document requirements for a Generator Owner to notify the Transmission Operator within a specified time period when its generator or generation facility cannot achieve the Declared Gross Real Power Capability or Declared Net Real Power Capability because of equipment issues. | Retired | 2012-10-26 | 2016-10-12
1808 | Directory # 9 V2 | Verification of Generator Gross and Net Real Power Capability | R5. | The Transmission Operator shall establish and document a time frame for the Generator Owner to address equipment issues that result in a generator or generation facility not achieving the Declared Gross Real Power Capability or Declared Net Real Power Capability. | Retired | 2012-10-26 | 2016-10-12
1809 | Directory # 9 V2 | Verification of Generator Gross and Net Real Power Capability | R6. | The Transmission Operator shall establish and document the ambient conditions that correspond to the summer and winter capability seasons for which the Gross Real Power Capability and Net Real Power Capability are verified. | Retired | 2012-10-26 | 2016-10-12
1810 | Directory # 9 V2 | Verification of Generator Gross and Net Real Power Capability | R7. | The Transmission Operator shall establish and document those intermittent or small generating units whose capability may be represented by verification results of a single generating unit. | Retired | 2012-10-26 | 2016-10-12
1811 | Directory # 9 V2 | Verification of Generator Gross and Net Real Power Capability | R8. | The Transmission Operator shall request Generator Owners to verify the seasonal Gross Real Power Capability and Net Real Power Capability of their generators or generation facilities that are subject to periodic seasonal Gross Real Power Capability and Net Real Power Capability verification every three (3) years or more frequently as required by the Transmission Operator. The two (2) capability seasons are defined as summer and winter as specified by the Transmission Operator. | Retired | 2012-10-26 | 2016-10-12
1812 | Directory # 9 V2 | Verification of Generator Gross and Net Real Power Capability | R9. | If a Transmission Operator determines that only one seasonal generating capability value is required for NPCC Bulk Power System reliability analysis, then periodic verification will be required only for that particular season. | Retired | 2012-10-26 | 2016-10-12
1814 | Directory # 9 V3 | Verification of Generator Gross and Net Real Power Capability | R1. | The Transmission Operator shall develop and maintain documentation of those generators or generation facilities that must verify the Gross Real Power Capability and Net Real Power Capability for the summer and winter capability seasons. The documentation maintained by the Transmission Operator shall include the following: | Retired | 2016-10-13 | 2019-07-01
1815 | Directory # 9 V3 | Verification of Generator Gross and Net Real Power Capability | R1.1. | All generators or generation facilities Declared Gross Real Power Capability and Declared Net Real Power Capability. | Retired | 2016-10-13 | 2019-07-01
1816 | Directory # 9 V3 | Verification of Generator Gross and Net Real Power Capability | R1.2. | All generators or generation facilities Verified Gross Real Power Capability and Verified Net Real Power Capability, verification date and method of verification. | Retired | 2016-10-13 | 2019-07-01
1817 | Directory # 9 V3 | Verification of Generator Gross and Net Real Power Capability | R1.3. | Discrepancies between a Generator Owner’s declared and verified Gross Real Power Capability and Net Real Power Capability, the reason for such discrepancies and the Generator Owner’s plan to address the discrepancies. | Retired | 2016-10-13 | 2019-07-01
1818 | Directory # 9 V3 | Verification of Generator Gross and Net Real Power Capability | R1.4. | Generator Owner supplied Gross Real Power Capability and Net Real Power Capability testing, manufacturer data, performance tracking or operating historical data, certification documentation, as specified by the Transmission Operator. | Retired | 2016-10-13 | 2019-07-01
1819 | Directory # 9 V3 | Verification of Generator Gross and Net Real Power Capability | R1.5. | All generators or generation facilities exempted from the verification requirements and the basis for their exemption (see Section 1.5) | Retired | 2016-10-13 | 2019-07-01
1820 | Directory # 9 V3 | Verification of Generator Gross and Net Real Power Capability | R10. | If a Transmission Operator determines that the difference between the Declared Gross Real Power and Declared Net Real Power Capability of a generator or generation facility is insignificant for NPCC Bulk Power System reliability analysis, then periodic verification will be required for only one numerical value. | Retired | 2016-10-13 | 2019-07-01
1821 | Directory # 9 V3 | Verification of Generator Gross and Net Real Power Capability | R11 | The Generator Owner shall provide generator or generation facility Declared Gross Real Power Capability and Declared Net Real Power Capability to the Transmission Operator. | Retired | 2016-10-13 | 2019-07-01
1822 | Directory # 9 V3 | Verification of Generator Gross and Net Real Power Capability | R12. | The Generator Owner shall provide evidence, upon request, to the Transmission Operator that the generator or generation facility Gross Real Power Capability and Net Real Power Capability have been verified. | Retired | 2016-10-13 | 2019-07-01
1823 | Directory # 9 V3 | Verification of Generator Gross and Net Real Power Capability | R13. | The Generator Owner shall report to the Transmission Operator any discrepancies between declared and verified Gross Real Power Capability or Net Real Power Capability within a time frame specified by the Transmission Operator and develop and implement a plan to resolve the discrepancies. | Retired | 2016-10-13 | 2019-07-01
1824 | Directory # 9 V3 | Verification of Generator Gross and Net Real Power Capability | R14. | The Generator Owner shall determine and report to the Transmission Operator the generator or generation facility real power seasonal auxiliary loads (including common station loads). | Retired | 2016-10-13 | 2019-07-01
1825 | Directory # 9 V3 | Verification of Generator Gross and Net Real Power Capability | R15. | The Generator Owner shall comply with Transmission Operator requests for periodic verification of Gross Real Power Capability and Net Real Power Capability of their generators or generation facilities. | Retired | 2016-10-13 | 2019-07-01
1826 | Directory # 9 V3 | Verification of Generator Gross and Net Real Power Capability | R16. | The Generator Owner shall verify the Gross Real Power Capability and Net Real Power Capability of thermal generators on the basis of operation for no less than one hour. | Retired | 2016-10-13 | 2019-07-01
1827 | Directory # 9 V3 | Verification of Generator Gross and Net Real Power Capability | R16.1. | The verification of thermal generator’s capability shall include any of the following: • Testing, • Use of operating historical data, • Commissioning data (for new generators only), • Performance tracking data acquired during the same seasonal capability period. | Retired | 2016-10-13 | 2019-07-01
1828 | Directory # 9 V3 | Verification of Generator Gross and Net Real Power Capability | R17. | The Generator Owner shall verify the Gross Real Power Capability and Net Real Power Capability of internal combustion generators and gas turbine generators. The verification shall correspond to operation for no less than one hour under the ambient conditions established in R6 for which the Gross Real Power Capability and Net Real Power Capability are being claimed. | Retired | 2016-10-13 | 2019-07-01
1829 | Directory # 9 V3 | Verification of Generator Gross and Net Real Power Capability | R17.1. | The verification of internal combustion and gas turbine generators capability shall include any of the following: • Testing, • Use of operating historical data, • Commissioning data (for new generators only), • Performance tracking data acquired during the same seasonal capability period. | Retired | 2016-10-13 | 2019-07-01
1830 | Directory # 9 V3 | Verification of Generator Gross and Net Real Power Capability | R18. | The Generator Owner shall verify the Gross Real Power Capability and Net Real Power Capability of hydro generators either on a generation facility or on an individual generator basis. The Gross Real Power Capability and Net Real Power Capability shall be determined on the basis of the availability of sufficient water at an adequate head to provide the output for no less than one hour. | Retired | 2016-10-13 | 2019-07-01
1831 | Directory # 9 V3 | Verification of Generator Gross and Net Real Power Capability | R18.1. | The verification of hydro generator’s capability shall include any of the following: • Testing, • Use of operating historical data, • Commissioning data (for new generators only), • Performance tracking data acquired during the same seasonal capability period. | Retired | 2016-10-13 | 2019-07-01
1832 | Directory # 9 V3 | Verification of Generator Gross and Net Real Power Capability | R19. | The Generator Owner shall verify the Gross Real Power Capability and Net Real Power Capability of combined cycle generators on a generation facility, individual generator or on a generator stage basis for no less than one hour under the ambient conditions established by the Transmission Operator in R6 for which the Gross Real Power Capability and Net Real Power Capability are being claimed. | Retired | 2016-10-13 | 2019-07-01
1833 | Directory # 9 V3 | Verification of Generator Gross and Net Real Power Capability | R19.1. | The verification of a combined cycle generator’s capability shall include any of the following: • Testing, • Use of operating historical data, • Commissioning data (for new generators only), • Performance tracking data acquired during the same seasonal capability period. | Retired | 2016-10-13 | 2019-07-01
1834 | Directory # 9 V3 | Verification of Generator Gross and Net Real Power Capability | R2. | The Transmission Operator shall establish and document a program to periodically verify the Gross Real Power Capability and Net Real Power Capability of all generators and generation facilities that are subject to periodic seasonal Gross Real Power Capability and Net Real Power Capability verification. | Retired | 2016-10-13 | 2019-07-01
1835 | Directory # 9 V3 | Verification of Generator Gross and Net Real Power Capability | R20. | The Generator Owner shall verify the Gross Real Power Capability and Net Real Power Capability of intermittent power resources (wind, solar, tidal geo-thermal, etc.) using any of the following: • Manufacturer’s data, • Performance tracking, • Operating historical data | Retired | 2016-10-13 | 2019-07-01
1836 | Directory # 9 V3 | Verification of Generator Gross and Net Real Power Capability | R21. | The Generator Owner shall verify the Gross Real Power Capability and Net Real Power Capability of multiple generator facilities when limited by common elements based on the real power capability of the facility and not the sum of the capabilities of the individual generators. | Retired | 2016-10-13 | 2019-07-01
1837 | Directory # 9 V3 | Verification of Generator Gross and Net Real Power Capability | R22. | The Generator Owner shall identify any equipment or other factor that will limit the capability of the generator or generation facility to meet its Declared Gross Real Power Capability or Declared Net Real Power Capability. | Retired | 2016-10-13 | 2019-07-01
1838 | Directory # 9 V3 | Verification of Generator Gross and Net Real Power Capability | R23. | The Generator Owner shall notify the Transmission Operator and request an exemption if it cannot conduct seasonal capability testing of a generator or generation facility for any of the reasons listed below. • Adverse impact on transmission system reliability • Potential damage to transmission system or generator equipment • Environment conditions • Governmental regulatory or operating license limitations • An extended outage to the generator or generation facility | Retired | 2016-10-13 | 2019-07-01
1839 | Directory # 9 V3 | Verification of Generator Gross and Net Real Power Capability | R24. | The Transmission Operator shall, within 30 calendar days of receiving notification from a Generator Owner that it is requesting an exemption because it cannot perform verification for the required seasonal period, notify the Generator Owner whether its generator will be exempted from the seasonal capability testing. Where the exemption is approved, the Transmission Operator shall coordinate with the Generator Owner to reschedule the verification for the next seasonal verification period. | Retired | 2016-10-13 | 2019-07-01
1840 | Directory # 9 V3 | Verification of Generator Gross and Net Real Power Capability | R25. | The Generator Owner for a generator or generation facility exempted from seasonal capability testing shall submit the following to the Transmission Operator: • For existing generators, generator operation records, manufacturer data, or performance tracking for the previous applicable seasonal verification period for this generator or generation facility. • Engineering analysis in conjunction with performance tracking data to justify any difference between a generators or generation facilities declared capability and previous applicable seasonal performance tracking data. • For new generators only, commissioning data. | Retired | 2016-10-13 | 2019-07-01
1841 | Directory # 9 V3 | Verification of Generator Gross and Net Real Power Capability | R3. | The Transmission Operator shall provide any changes to its verification process to the Generator Owners within 30 calendar days of issue. | Retired | 2016-10-13 | 2019-07-01
1842 | Directory # 9 V3 | Verification of Generator Gross and Net Real Power Capability | R4. | The Transmission Operator shall establish and document requirements for a Generator Owner to notify the Transmission Operator within a specified time period when its generator or generation facility cannot achieve the Declared Gross Real Power Capability or Declared Net Real Power Capability because of equipment issues. | Retired | 2016-10-13 | 2019-07-01
1843 | Directory # 9 V3 | Verification of Generator Gross and Net Real Power Capability | R5. | The Transmission Operator shall establish and document a time frame for the Generator Owner to address equipment issues that result in a generator or generation facility not achieving the Declared Gross Real Power Capability or Declared Net Real Power Capability. | Retired | 2016-10-13 | 2019-07-01
1844 | Directory # 9 V3 | Verification of Generator Gross and Net Real Power Capability | R6. | The Transmission Operator shall establish and document the ambient conditions that correspond to the summer and winter capability seasons for which the Gross Real Power Capability and Net Real Power Capability are verified. | Retired | 2016-10-13 | 2019-07-01
1845 | Directory # 9 V3 | Verification of Generator Gross and Net Real Power Capability | R7. | The Transmission Operator shall establish and document those intermittent or small generating units whose capability may be represented by verification results of a single generating unit. | Retired | 2016-10-13 | 2019-07-01
1846 | Directory # 9 V3 | Verification of Generator Gross and Net Real Power Capability | R8. | The Transmission Operator shall request Generator Owners to verify the seasonal Gross Real Power Capability and Net Real Power Capability of their generators or generation facilities that are subject to periodic seasonal Gross Real Power Capability and Net Real Power Capability verification every three (3) years or more frequently as required by the Transmission Operator. The two (2) capability seasons are defined as summer and winter as specified by the Transmission Operator. | Retired | 2016-10-13 | 2019-07-01
1847 | Directory # 9 V3 | Verification of Generator Gross and Net Real Power Capability | R9. | If a Transmission Operator determines that only one seasonal generating capability value is required for NPCC Bulk Power System reliability analysis, then periodic verification will be required only for that particular season. | Retired | 2016-10-13 | 2019-07-01