PROCEDURE

PUBLIC

Market Manual 7: System Operations

# Part 7.2: Near-Term Assessments and Reports

Issue 3.1

December 2, 2026

MAN-122

This procedure describes the process by which the IESO undertakes short-term weekly and daily forecasts and assessments of expected system conditions on the IESO-controlled grid.

Document Change History

| Issue | Reason for Issue | Date |
| --- | --- | --- |
| Refer to Issue 50.0 (MDP_PRO_0033) for changes prior to Market Transition. |  |  |
| 1.0 | Market Transition | November 11, 2024 |
| 2.0 | Issued for baseline 54.1 | December 3, 2025 |
| 3.0 | Issued for baseline 56.0 | September 9, 2026 |
| 3.1 | Issued for baseline 56.1 | December 2, 2026 |

Related Documents

| Document ID | Document Title |
| --- | --- |
| MAN-123 | Market Manual 7.3: Outage Management |

Table of Contents

Table of Contents	ii

List of Tables	iv

Table of Changes	v

Market Manuals	vi

Market Manual Conventions	vi

1	Introduction	1

1.1	Purpose	1

1.2	Scope	1

1.3	Contact Information	2

2	Market Participant Data Submission Instructions	3

3	Adequacy, Demand Forecast, and Transmission Limits Reports	4

3.1	Adequacy Reports	4

3.1.1	Adequacy Report for Day 0 to Day 1	4

3.1.2	Adequacy Report for Day 2 to 34	5

3.2	Transmission Facility All-in-Service Limits Report	5

3.3	Transmission Facility Outage Limits Reports	5

4	Advisory Notices	6

5	Surplus Baseload Generation	8

5.1	Baseload Generation	8

5.2	Surplus Baseload Generation Reports	8

5.3	Minimum Generation Alerts and Events	9

Appendix A:	Method to Prepare Demand Forecasts	11

A.1	Input Drivers for Demand Forecasting	11

Appendix B:	Method to Assess Generation and Transmission Adequacy	13

Appendix C:	Terms Used in Adequacy Reports	15

C.1	Forecast Supply	15

C.2	Forecast Demand	18

C.3	Total Supply and Total Requirement	19

C.4	Energy and Capacity Excess (Shortfall)	20

C.5	Over-Generation and Under-Generation	21

Appendix D:	Transmission Interfaces	22

Appendix E:	Generation Reserve Holdback Requirements	30

List of Acronyms	33

References	34

List of Tables

Table 5-1: Minimum Generation Status	10

Table D-1: Operating Security Limits – Internal Interfaces	22

Table D-2: Operating Security Limits – External Interfaces	26

Table E-1: Generation Reserve Holdback Requirements	30

Table of Changes

| Reference | Description of Change |
| --- | --- |
| Appendix C.1 | Clarified that the IESO may require and publish regulation service requirements above the minimum requirement to support operability needs. |
| Appendix D, Table D-1 | Added CHIP (Chatham inflow), BBO (Bruce B Output), and FABCW+NBLIP interfaces and updated descriptions and notes for existing interfaces to align with current operating security limit requirements. |

Market Manuals

Market manuals set out procedural and administrative details with respect to market rule requirements. Where there is a conflict between the requirements described in a market manual or appended document, and those within the market rules, the market rules shall prevail.

Market Manual Conventions

This market manual uses the following conventions:

the word 'shall' denotes a mandatory requirement;

references to market rule sections and sub-sections may be appreviated in accordance with the following representative format: ‘MR Ch.1 ss.1.1-1.2’  (i.e. market rules, Chapter 1, sections 1.1 to 1.2);

references to market manual sections and sub-sections may be appreviated in accordance with the following representative format: ‘MM 1.5 ss.1.1-1.2’  (i.e. market manual 1.5, sections 1.1 to 1.2);

internal references to sections and sub-sections within this manual take the representative format: ‘sections 1.1 – 1.2’;

terms and acronyms used in this market manual in its appended documents that are italicized have the meanings ascribed thereto in MR Ch.11;

all user interface labels and options that appear on the IESO gateway and tools are formatted with the bold font style;

data fields are identified in all capitals; and

references to “Day 0” mean the current day, references to “Day 1” mean the day immediately after the current day, references to “Day 2” mean the day two days after the current day, and so on.

– End of Section –

## Introduction

### Purpose

This market manual describes how the IESO prepares and publishes the reports it uses to inform market participants of expected conditions on the IESO-controlled grid and in the IESO-administered markets in the near-term through the following reports and advisories:

Adequacy Reports (Day 0 to Day 34);

Ontario Near-Term Demand Forecast Report (Day 0 to 10) for the Northeast, Northwest, Southeast and Southwest demand forecast areas;

Ontario Mid-Term Demand Forecast Report (Day 11 to 34) for the legacy East and West demand zones;

Transmission Facility All-in-Service Limits Report;

Transmission Facility Outage Limits Report (Day 0 to 2);

Transmission Facility Outage Limits Report (Day 3 to 34);

Advisory notices, published as required; and

Surplus Baseload Generation (SBG) Report (Day 1 to Day 10).

The procedures for preparing and publishing long-term (18-month) forecasts and assessments are described in MM 2.8 and MM 2.11.

### Scope

This market manual supplements the following market rules:

MR Ch.5 s.4.4.2

MR Ch.5 s.7.1: Forecasts Prepared by the IESO

MR Ch.5 s.7.3.1.4

MR Ch.5 s.7.4: Purpose of Assessments

MR Ch.5 s.7.5: Information Requirements

MR Ch.7 s.12.1: IESO System Status Reports and Advisory Notices

MR Ch.7 s.12.2: Over-Generation and Under-Generation Advisories

### Contact Information

Changes to this market manual are managed via the IESO Change Management process. Stakeholders are encouraged to participate in the evolution of this market manual via this process.

To contact the IESO, market participants can email IESO Customer Relations at customer.relations@IESO.ca or use telephone or mail. Telephone numbers and the mailing address can be found on the IESO website. IESO Customer Relations staff will respond as soon as possible.

– End of Section –

## Market Participant Data Submission Instructions

(MR Ch.5 s.7.5.1)

Pre-schedules – Each Tuesday by 17:00 EST, market participants that operate energy limited resources must, in accordance with MR Ch.5 s.7.5.1, provide the IESO with a pre-schedule of these resources for the period beginning on Day 1 and going out to Day 34. The pre-schedule defines the total hourly and daily energy content of all aggregated energy limited resources. Market participants must update the energy limited resource pre-schedule if there are any changes to information previously provided.

Energy limited resources – Market participants who operate energy limited resources must submit these pre-schedules via Online IESO:

a forecast of the daily aggregated energy production of all resources for the days of week 4 (i.e. from Day 28 to Day 34); and

an updated forecast of the daily aggregated energy production for all other days of the period.

– End of Section –

## Adequacy, Demand Forecast, and Transmission Limits Reports

(MR Ch.7 s.12.1.1)

Near-term reports – In accordance with MR Ch.7 s.12.1.1, the IESO regularly produces and publishes the following near-term reports relating to the security and adequacy of the IESO-controlled grid. These reports are listed in section 1.1 of this market manual.

### Adequacy Reports

(MR Ch.7 s.12.1.1.6)

Content and granularity – Adequacy Reports cover Day 0 to 34 and have hourly granularity.

#### 3.1.1	Adequacy Report for Day 0 to Day 1

(MR Ch.7 s.12.1.1.6)

Publication schedule – In accordance with MR Ch.7 s.12.1.1.6, the IESO prepares and publishes Adequacy Reports daily for Day 0 and Day 1, according to the following schedule:

two times per hour, for [each of the remaining hours in] Day 0;

by 05:30 EPT [of Day 0], for Day 1;

by 09:00 EPT [of Day 0], for Day 1;

after successful completion of the day-ahead market calculation engine on Day 0, for Day 1; and

hourly after 20:00 EST [of Day 0], for Day 1.

Updates – These reports are updated according to the publication schedule to provide market participants with any new information since the previous scheduled publication. This may include changes in demand, generation capacity, electricity storage capacity and variable generation forecast.

Offers, bids and schedules – Reports published on Day 0 and published for Day 1 after successful completion of the day-ahead schedule will include aggregated values of the capacity offered and bid for the dispatch day and the aggregated day-ahead market or pre-dispatch schedules.

#### 3.1.2	Adequacy Report for Day 2 to 34

(MR Ch.5 s.7.3.1.4)

Publication schedule – In accordance with MR Ch.5 s.7.3.1.4, the IESO prepares and publishes Adequacy Reports for Days 2 to 34. Reports are published twice daily at approximately 8:45 EST and 15:00 EST.

Updates – These reports are updated twice daily to provide market participants with any new information since the previous scheduled publication. This may include changes in demand, generation capacity, electricity storage capacity and variable generation forecast.

### Transmission Facility All-in-Service Limits Report

(MR Ch.7 s.12.1.1.7)

- Publication schedule – Each day by 17:00 EST, the IESO prepares and publishes the Transmission Facility All-in-Service Limits Report to provide market participants with information on available transfer capabilities on major interfaces, assuming all critical elements are in-service.

### Transmission Facility Outage Limits Reports

(MR Ch.7 s.12.1.1.8)

- Reports – Each day the IESO prepares and publishes the Transmission Facility Outage Limits Report (Day 0 to 2) and the Transmission Facility Outage Limits Report (Day 3 to 34),  which provide market participants with information on available transfer capabilities for internal interfaces and interties, considering anticipated outage conditions.

Publication schedule and updates – The IESO publishes the Transmission Facility Outage Limits Report (Day 0 to 2) will be published by approximately 15 minutes and 45 minutes past the top of the hour, and the Transmission Facility Outage Limits Report (Day 3 to 34) day will be published by approximately 8:45 EST; and published by approximately 17:07 EST, to provide market participants with updates on available transfer capability since the previous report.

– End of Section –

## Advisory Notices

- (MR Ch.7 s.12.1.3)

Purpose – Advisory notices provide information to market participants that is not captured in the regularly scheduled Adequacy Report and the Transmission Limits Reports. Advisory notices are dependent on circumstances and are published as needed in accordance with MR Ch.7 s.12.1.3.

IESO assessment – The IESO will perform an assessment of occurring or expected system events and conditions to determine if an advisory notice is required. IESO will issue the advisory notices as required as soon as practicable.

Example – For example, the IESO will publish an advisory notice if it needs to identify that an external jurisdiction has made a reliability declaration calling upon Ontario capacity for firm energy exports, or to communicate the disabling or re-enabling of the five-minute variable generation forecasting tool.

Three levels – In accordance with MR Ch.7 s.12.1.2, the IESO may publish three levels of advisory notices for the benefit of market participants and/or neighbouring jurisdictions:

an Alert Notice to notify of changes or expected changes in system or market conditions to allow time for advanced preparations.

a Warning Notice to notify that the IESO is likely to take or direct future actions in the near term if the IESO-administered market does not or cannot respond sufficiently to eliminate a problem associated with either a system or market condition.

an Action Notice to notify that the IESO is, or market participants as directed by the IESO are, taking actions to eliminate an identified or potential problem associated with either a system or market condition.

Content – Any advisory notice will clearly indicate the level of the notice, Alert Notice, Warning Notice, or Action Notice.

Sequence – Typically, the IESO will publish advisory notices in the following sequence: first an Alert Notice, next a Warning Notice, and then an Action Notice. The IESO has the discretion to publish one level of advisory notice without issuing the preceding level.

– End of Section –

## Surplus Baseload Generation

- (MR Ch.7 ss.12.1.1, 12.1.3 and 12.2.1)

Definition – Surplus baseload generation (SBG) is a condition that occurs when baseload generation is expected to exceed Ontario demand. During SBG, the system is balanced via market mechanisms that may include intertie scheduling, dispatching hydroelectric generation, dispatching variable generation, and nuclear manoeuvring or shutdown.

### 5.1	Baseload Generation

Definition – Baseload generation is typically considered to be the sum of the expected generation of all available:

nuclear generation resources;

must-run hydroelectric generation resources;

self-scheduling generation resources (including commissioning units), and self-scheduling electricity storage facilities;

intermittent generation resources;

variable generation resources (including wind and solar generators); and

other resources that typically offer their output at a value lower than the highest offer for nuclear generation.

### 5.2	Surplus Baseload Generation Reports

Purpose – The SBG Report identifies times when the output of Ontario's baseload generation resources is expected to be greater than the forecast Ontario demand.

Publication schedule and content – Each day, the IESO prepares and publishes the SBG Report on the IESO website by 17:00 EST

The report spans the period from Day 1 to 10.

SBG is calculated by subtracting the forecast Ontario demand from the forecast baseload generation. Exports are not factored in the calculation.

The SBG Report will include the amount of exports we reasonably estimate will be scheduled during the highest SBG period for the day.

The IESO uses the forecast Ontario demand based on forecast weather and the embedded variable generation forecast for resources ≥ 5 MW.

The IESO uses the centralized variable generation forecast for Ontario’s variable generators for Day 1 to 7.

Minimum Generation Alerts are issued as per the conditions set out in section 5.3.

### 5.3	Minimum Generation Alerts and Events

Context and purpose of advanced notice – Some Ontario nuclear generators have the ability to reduce their output. Typically, this is accomplished by having some steam bypass the turbine, reducing the electrical output of the generator while keeping reactor power constant. However, due to the characteristics of nuclear station design and operation, the reduction often must be accomplished in a single block and held at that level for some amount of time before being reloaded in a single block.

Given the unique operating characteristics of nuclear generation, the IESO provides advance notice where possible of potential reductions of the output of nuclear generators for surplus baseload generation management – both for the benefit of the nuclear resource operators and for other market participants.

Conditions justifying publication – The IESO publishes advisory notices for Minimum Generation Alerts and Events under the following conditions:

If the IESO forecasts a nuclear manoeuvre of at least 50 MW for four or more contiguous hours in Day 3 or Day 4, the IESO will publish an advisory notice with a Minimum Generation Alert for each impacted day. The alert will identify the potential for a nuclear manoeuvre and will include a forecast of expected export quantities during the SBG event. The IESO may issue these System Advisory notices beyond Day 4 for holiday weekends or as necessary.

If the IESO forecasts a nuclear manoeuvre of at least 50 MW for two or more contiguous hours for Day 1 or Day 2, they will publish an advisory notice with a Minimum Generation Alert for each impacted day.

If pre-dispatch shows a nuclear maneuver of 50 MW or more, the IESO will publish an advisory notice indicating a Minimum Generation Alert.

In real-time, if a nuclear manoeuvre is imminent or in progress, the IESO will publish an advisory notice indicating a Minimum Generation Event.

Conditions relevant to SBG events – Conditions that may exacerbate or lessen forecast SBG events include:

demand is different (lighter or heavier) than forecast;

forced outages with forced or urgent Priority Code of dispatched generation resources, dispatched electricity storage resources, or transmission facilities;

short notice changes of hourly export transactions (increase or decrease); and/or

intermittent generators, self-scheduling generation resources, self-scheduling electricity storage resources, and variable generators producing more or less than anticipated.

The IESO will publish an advisory notice canceling a Minimum Generation Alert if conditions change such that the IESO no longer expects nuclear manoeuvres. Table 5-1 provides a summary of the Minimum Generation conditions.

Table 5-1: Minimum Generation Status

| Time Frame | Forecast Condition | Minimum Generation Status |
| --- | --- | --- |
| Day 3 or Day 4 | A nuclear manoeuvre of at least 50 MW is forecasted for four or more contiguous hours. | Alert |
| Day 1 or Day 2 | A nuclear manoeuvre of at least 50 MW is forecasted for two or more contiguous hours. | Alert |
| Pre-dispatch | Pre-dispatch shows a nuclear manoeuvre of 50 MW or more. | Alert |
| Real-Time | A nuclear generation manoeuvre is imminent or in progress | Event |

– End of Section –

## Method to Prepare Demand Forecasts

(MR Ch.5 s.7.1.3)

This appendix describes the method used to prepare the hourly average and peak demand forecasts in each demand forecast area. These demand forecasts are used as an input to the near-term adequacy assessments and presented in the:

Adequacy Report;

Ontario Near-Term Demand Forecast Report (Day 0 to 11); and

Ontario Mid-Term Demand Forecast Report (Day 11 to 34).

The IESO uses a load forecast tool to prepare near-term hourly Ontario demand forecasts from Day 0, including pre-dispatch, to Day 34. The tool uses models consisting of linear regressions and/or neural network analysis to produce the forecasts.

### A.1	Input Drivers for Demand Forecasting

The following items are used as input drivers by the demand forecasting tool:

- Weather parameters

  - Dry-Bulb Temperature

  - Wet-Bulb Temperature

  - Dew-Point Temperature

  - Wind Speed

  - Wind Direction

  - Illumination

  - GHI (Global Horizontal Irradiance in W/m2)

  - Cloud Cover

- Historical Demand Data

- Embedded Variable Generation Data

  - Historical

  - Forecast

– End of Appendix –

## Method to Assess Generation and Transmission Adequacy

(MR Ch.7 s.12.1.1)

The IESO compares forecasted demand to available resource capacity and energy, including available generation external to Ontario when assessing generation adequacy. The IESO uses the following adequacy criteria for normal operating states:

For the dispatch day and two days following the dispatch day, an acceptable level of adequacy is achieved if:

available resources, based on installed capacity, estimated imports and outage information, exceed forecasted Ontario demand by at least the operating reserve requirement; and

available resources, based on energy production of energy limited resources, installed capacity of non-energy limited resources, energy forecast from centralized forecasting of renewable resources, estimated imports and outage information, exceed forecasted Ontario demand in MWh.

The IESO takes necessary actions if there are inadequate resources in the short-term, including but not limited to:

publishing information necessary to allow the market to react to adequacy concerns;

including incremental import transactions in pre-dispatch beyond the standard T+2 timeline.

activating reliability must-run contracts to address local area adequacy only (i.e. not permitted to address lack of overall system generation adequacy);

rejecting, revoking, and recalling outages; and

issuing system advisory notices with the expected actions to be taken (e.g., voltage reductions, public appeals, load shedding).

For the balance of daily and weekly assessment out to the end of week 4 following the dispatch week, an acceptable level of adequacy is achieved if:

available resources, based on installed capacity, estimated imports, and outage information exceed forecasted Ontario demand by at least the Generation Reserve Holdback; and

available resources, based on energy production of energy limited resources, installed capacity of non-energy-limited resources, energy forecast of renewable resources, estimated imports and outage information, exceed forecasted Ontario demand in MWh.

For reliability assessments, an acceptable level of adequacy is achieved if forecast available resources exceed forecasted demand by an amount such that the loss of load expectation is less than 0.1 days per year, consistent with NPCC requirements.

The IESO compares forecast transmission flows with the applicable system operating limits under a range of load conditions and generation resource, electricity storage resource and transmission facility availability conditions when assessing transmission adequacy. An acceptable level of adequacy is achieved if forecast loads can be supplied without exceeding applicable system operating limits and acceptable system voltages can be maintained.

– End of Appendix –

## Terms Used in Adequacy Reports

(MR Ch.5 s.7.1.3)

This appendix describes the terms used and presented in Adequacy Reports. In addition to the terms in this appendix, all reports published on Day 0 and reports published on Day 1 will include aggregated values of the capacity offered and bid by market participants and the aggregated day-ahead market or pre-dispatch schedules for the dispatch day.

### C.1	Forecast Supply

The IESO forecasts the following elements of supply:

Energy (MWh) – the amount of energy available from generation and storage sources in Ontario plus imports from other control areas. This quantity is calculated from the relationship:

[generating and storage capacity in-service (MW)] * 1 hr

- [capacity unavailable due to outages (MW)] * 1 hr

- [capacity of energy limited resources (MW)] * 1 hr

- [capacity of variable generation resources (MW)] * 1 hr

+ energy (forecast) of variable generation resources (MWh)

+ energy-limited resource energy for the hour (MWh)

+ [imports from other control areas (MW)] * 1 hr

The Adequacy Report includes energy quantities for each hour.

Capacity (MW) – the net amount of generation capacity, storage capacity in-service in Ontario, including capacity generation and capacity storage resources from the capacity auction, subdivided by fuel type. Storage resources are included in the Other fuel type. This number may be revised lower if a material quantity of capacity is bottled. The Adequacy Report includes capacity quantities for each hour.

Intermittent generation resource schedules (MWh/hr) – market participants provide dispatch data for intermittent generation resources that represent the forecast energy output for these resources. For the days of the Adequacy Report in which intermittent generation resource schedules are not available, the IESO will use an estimate of these schedules in the adequacy assessment.

Self-scheduling generation and storage resource schedules (MWh/hr) – market participants provide dispatch data for self-scheduling generation resources and self-scheduling electricity storage resources that represent the forecast energy output for these resources. For the days of the Adequacy Report in which self-schedules are not available, the IESO will use an estimate of these schedules in the adequacy assessment.

Energy-limited energy (MWh) – the IESO publishes the aggregate forecast amount of energy available from energy-limited resources. An energy-limited resource is a generation resource or an electricity storage resource that is unable to supply energy equal to the capacity for each of the hours of the day (e.g. a hydro-electric resource with limited water in the forebay that does not allow it to produce energy at its rated output for each of 24 hours in the day). Market participants use Online IESO to provide the IESO with an energy-limited forecast of hourly granularity (i.e. the total forecast daily quantity of energy available) for all relevant resources. The IESO publishes the aggregate hourly energy profile of market participant forecasts for each day of the Adequacy Report.

Energy-limited capacity (MW) – the IESO publishes the nominal capacity of those resources that are energy-limited. On any day, the list of resources that may be energy-limited may change. To place the energy-limited energy quantity in context, the nominal capacity of these resources are provided to the IESO by the market participants, and the IESO publishes these quantities in the assessment reports. The Adequacy Report includes energy-limited capacity quantities for each hour.

Variable generation energy (MWh) – the IESO publishes the aggregate variable generation forecast amount of energy available from variable generation whose owners/operators are registered market participants. Variable generation means all wind and solar photovoltaic resources with an installed capacity of ≥ 5 MW, or all wind and solar photovoltaic resources that are directly connected to the IESO-controlled grid. For Days 0 and 1 of the Adequacy Report, the IESO uses and publishes the aggregated hourly quantities of forecast wind and solar generation produced by a forecasting entity. For Days 2 to 7, the IESO publishes the lesser of the forecast provided by the forecasting entity and a forecast produced by the IESO using a set of seasonal capacity factors. For Days 8 to 34, the IESO publishes a forecast of wind and solar generation, using seasonal capacity factors.

Variable generation capacity (MW) – the IESO publishes the nominal capacity of variable generation whose owners/operators are registered market participants. On any day, the list of variable generation may change. The Adequacy Report includes the aggregated quantities of wind generation capacity and solar generation capacity, for each hour.

Estimated imports (MW) – the IESO will include an amount in its adequacy assessments to account for potential imports from other control areas, as follows:

For Days 0 and 1, a value of zero will be used,

For Days 2 to 10, an estimate of up to 700 MW of imports will be used, along with the forecasted Ontario demand for this period,

Beyond Day 10, an estimate of up to 2,000 MW of imports will be used, along with the forecasted extreme weather Ontario demand firm scenario.

These estimated import MW amounts are based on IESO experience with interchange transactions and are the MW amounts reasonably assumed to be available from the interconnections. More conservative numbers will be used where available interconnection information indicates that less than 700 or 2,000 MW imports would be available. The total amount attributed to potential interchange assistance will be reviewed on a periodic basis. This quantity will be provided for each hour of each day of the Adequacy Report period.

For outages planned for Days 2 to 10, the IESO may increase imports above 700 MW to reflect outage replacement energy imports. The amount in excess of 700 MW may be an aggregate of generators arranging for replacement energy.

Capacity imports (MW) – the IESO publishes the quantity of capacity imports (including system-backed capacity import resources and generator-backed capacity import resources from the capacity auction) that can be relied upon from other control areas. This quantity is included in capacity excess (shortfall) calculations for all days in the near-term assessment period.

Outages (MW) – the IESO publishes the quantity of generation resource and electricity storage resource MWs, by fuel type, that are unavailable due to outage or derating. These quantities will be provided for each hour of each day of the Adequacy Report. Electricity storage resources are included in the ‘other’ fuel type category.

Bottled capacity (MW) – the IESO will include, in its adequacy assessments, an amount to account for the estimated quantity of bottled generation capacity. This amount will be the sum of all regional generation capacity in excess of regional demand that cannot be transferred to other internal areas as a result of transmission limitations.

Regulation – the market rules require the IESO to determine the quantity of regulation capacity needed for each hour of the following day. As a minimum the requirements shall be  100 MW, with a ramp rate of 50 MW/minute (MR Ch.5 s.4.4.2). However, due to operability needs the IESO may determine there is a need to schedule more than the minimum regulation requirement. If the IESO needs to schedule more than this minimum, it will be identified and published in the relevant adequacy assessment for Days 0 and 1 and Days 2-34. Regulation will be scheduled in the day-ahead timeframe.

Adjusted capacity in the Adequacy Reports – For all days of the Adequacy Report, an adjustment is made to the available dispatchable capacity i.e. the “Total Outages” value is increased by 2% of available dispatchable generation resources and dispatchable electricity storage resources. This adjustment is applied to compensate for the outage reporting deadband of the greater of 2% or 10 MW, and to better represent available capacity and reduce discrepancies between the forecast in the Adequacy Report and pre-dispatch. The adjustment factor of 2% may be varied by the IESO from time-to-time if considered appropriate for the above purposes.

### C.2	Forecast Demand

The IESO will forecast the following components of demand in the Adequacy Report:

Ontario demand (MW) – the IESO will forecast the Ontario demand (non-dispatchable load + dispatchable load + losses) and provide the total of these three quantities for each hour of each day of the Adequacy Report. The dispatchable load component of Ontario demand is the dispatchable load that is expected to be supplied. The “Forecast Ontario Demand” quantity in the Adequacy Report for Day 0 (current day) and Day 1 (tomorrow) represents the forecast used in pre-dispatch scheduling, and is the average demand forecast in all hours, with the exception of the IESO Ramp Hours, in which it is the peak demand forecast.

Dispatchable load (MW) – the IESO will forecast the amount of dispatchable load that is expected to be available to be dispatched off. This information is presented for each hour of the Adequacy Reports for Days 2 to 34, and the Adequacy Reports for Day 1 published prior to the day-ahead market process. Dispatchable load forecasts are included in capacity excess (shortfall) calculations.

Hourly demand response (MW) – the IESO will forecast the amount of Hourly Demand Response that is expected to be available to be curtailed off. This information is presented for each hour of the Adequacy Reports for Days 2 to 34, and the Adequacy Reports for Day 1 published prior to the day-ahead market process. Hourly Demand Response forecasts are included in capacity excess (shortfall) calculations.

Capacity exports (MW) – the IESO publishes the quantity of capacity exports that the IESO is obligated to provide to other control areas. This quantity is included in capacity excess (shortfall) calculations for all days in the near-term assessment period.

Generation reserve holdback (MW) – the IESO will forecast the Generation Reserve Holdback Requirements - operating reserve, load forecast uncertainty (LFU) and additional contingency allowance (ACA) - in accordance with the principles listed in Appendix E: Generation Reserve Holdback Requirements.

Minimum 10-minute operating reserve requirement (MW) – the IESO will forecast its 10-minute operating reserve in accordance with NPCC Directory 5: Reserve. This information is presented for each hour of each day of the Adequacy Report. Minimum 10-minute operating reserve requirements are not included in excess (shortfall) calculations.

Minimum 10-minute spinning operating reserve requirement (MW) – the IESO will forecast its 10-minute spinning operating reserve in accordance with NERC Reliability Standard BAL-002 (Disturbance Control Standard) and NPCC Directory 5: Reserve. This information is presented for each hour of each day of the Adequacy Report. Minimum 10-minute spinning operating reserve requirements are not included in excess (shortfall) calculations.

### C.3	Total Supply and Total Requirement

The IESO will include in the Adequacy Reports:

Total supply, quantified by calculating and presenting the total forecasted amount of available resources, and

Total requirement, quantified by calculating and presenting the total forecasted amount of demand.

The Total Supply (MW) for each hour is calculated from the following formulation:

generating capacity in-service (MW)– capacity unavailable due to outages (MW) – bottled capacity (MW) + estimated imports (MW) + capacity imports (MW)

The Total Requirement (MW) for each hour is calculated from the following formulation:

total hourly Ontario demand forecast (MW) + generation reserve holdback (MW) + capacity exports (MW) – dispatchable load (MW)

### C.4	Energy and Capacity Excess (Shortfall)

The IESO will include in the Adequacy Reports:

Energy adequacy, quantified by calculating and presenting the energy excess (or shortfall when there is insufficient energy); and

Capacity adequacy, quantified by calculating and presenting the capacity excess (or shortfall when there is insufficient capacity).

The Energy Excess (MWh) for each hour is calculated from the following formulation:

[generating capacity in-service (MW) + estimated imports (MW) + capacity imports (MW) +dispatchable load] * 1 hr

- [total hourly Ontario demand forecast (MW) + capacity unavailable due to outages (MW) + capacity of energy-limited resources (MW) + capacity of variable generation resources (MW)] * 1 hr

+ energy-limited resource energy for the hour (MWh)

+ energy (forecast) of variable generation resources (MWh)

IF (energy excess < 0), then there is a shortfall of energy.

The Capacity Excess (MW) for each hour is calculated from the following formulation:

[generating capacity in-service (MW) + estimated imports (MW) + capacity imports (MW) + dispatchable load]

- [total hourly Ontario demand forecast (MW) + capacity unavailable due to outages (MW) + generation reserve holdback (MW) + capacity exports (MW)]

IF (capacity excess < 0), then there is a shortfall of capacity.

The Adequacy Reports for Day 0, and Day 1 reports published after successful completion of the day-ahead market process, also include offered capacity excess (or shortfall when there is insufficient offered capacity). The Offered Capacity Excess (MW) for each hour is calculated from the following formulation:

[total internal generation offered/forecasted (MW/MWh) + total offered imports (MW) – linked wheels + dispatchable load bid]

- [total peak hourly Ontario demand forecast (MW) + generation reserve holdback (MW)]

IF (offered capacity excess < 0), then there is a shortfall of offered capacity.

### C.5	Over-Generation and Under-Generation

Over-Generation – An over-generation situation is deemed to occur when the amount of dispatched generation exceeds the Ontario demand and net interchange schedule. This would likely occur in real-time operation in low demand periods when one or more generators are dispatched to their minimum amounts and are unable to respond to the IESO’s subsequent dispatch instructions for immediate corrective actions.

Minimum Generation Alert – In the event of an actual, imminent or expected over-generation situation, the IESO will issue a Minimum Generation Alert/Event via an advisory notice, including the remedial actions that the IESO intends to take. The subsequent publication of the Adequacy Report will indicate the amounts of over-generation.

Under-Generation – An under-generation situation is expected to occur when a potential energy and capacity shortfall (see Appendix C.4) is identified in the adequacy assessment process for the Day 2 to 34 period. In the event of an expected under-generation situation, the IESO will issue an advisory notice, including the remedial actions that the IESO intends to take. The expected amounts of under-generation will be included in the Adequacy Reports.

Maximum Generation – If the IESO determines that there will be potential difficulty meeting energy and/or operating reserve requirements due to lack of market participant offers, the IESO will issue an advisory notice, requesting market participants to consider placing additional offers into the electricity market.

– End of Appendix –

## Transmission Interfaces

The Transmission All-in-Service Limits Report provides deviations in transmission limits for major internal interfaces and all intertie interfaces (MR Ch.5 s.7.4.4). These are the interfaces on which flows must be restricted below the limit specified to ensure reliable operation of the IESO-controlled grid.

Table D-1 and Table D-2 contain lists of internal interfaces and external interfaces for which the IESO will publish limits for all elements in-service and outage conditions (MR Ch.5 ss.7.4.4.1.2 and 7.4.4.1.3). These interfaces are consistent with those included in long-term forecast publications (MR Ch.5 s.7.4.2). The Maximum Interface Limits posted are representative of available transfer capability values. At any time, the actual maximum interface limits may deviate from these values.

Table D-1 and Table D-2 provide the basis for interface reporting; additional interfaces may be included in the actual reports.

Note 1: Interface Limit may be lower than the maximum limit indicated due to dependencies on other interface flows or factors such as the number of generating units and injecting electricity storage units online, amount of generation rejection armed, amount of load rejection armed, voltage levels, etc.

Note 2: Limits based on thermal restrictions for pre-contingency flow or post-contingency flow are monitored online and are not included in the above list. Thermal limitations indicated above for external interfaces are estimated values based on specified assumptions.

Table D-1: Operating Security Limits – Internal Interfaces

| Interface | Description of Interface | Notes |
| --- | --- | --- |
| TEK | Transfer East of Kenora | Voltage violation |
| TWK | Transfer West into Kenora | Voltage violation |
| MMW | Mackenzie Moose Lake Flow West | No limit under normal conditions; voltage violation under outage or high risk conditions |
| DAI | Dryden Area Inflow | No limit under normal conditions; voltage decline at the Dryden bus during outage conditions |
| FAI | Fort Frances Area Inflow | No limit under normal conditions; voltage decline at the Dryden bus during outage conditions |
| LFE | Lakehead Flow East | No limit under normal conditions; voltage violation under outage or high risk conditions |
| EWTE | East-West Transfer East | Voltage violation |
| EWTW | East-West Transfer West | Voltage violation |
| TEM | Transfer East of Mackenzie | Voltage violation |
| TWM | Transfer West into Mackenzie | No limit under normal conditions; voltage violation/transient limit under outage or high risk conditions |
| WMFE-230-115 | Wawa-MacKay Flow East on the 230 kV and 115 kV system | Voltage stability limit |
| WMFE-230 | Wawa-MacKay Flow East on the 230 kV system | Voltage violation |
| MissE | Transfer East of Mississaugi | Voltage violation |
| MissW | Transfer West into Mississaugi | Voltage violation |
| D501P+H9K (South) | Flow South on Circuits D501P plus H9K | No limit with G/R available, limit reduced to zero with D501P out of service |
| D501P+H9K (North) | Flow North on Circuits D501P plus H9K | No limit with L/R available, limit reduced to zero with D501P out of service |
| P502X+D3K (South) | Flow South on Circuits P502X plus D3K | No limit with G/R available, limit reduced to zero with P502X out of service |
| P502X+A8K+A9K (North) | Flow North on Circuits P502X plus A8K & A9K | No limit with L/R available, limit reduced to zero with P502X out of service or for high risk conditions over P502X |
| FS | Flow South (on Circuits X503E, X504E and D5H) | Stability limit and Boundary for Southern Ontario Limits |
| FN | Flow North (on Circuits X503E, X504E and D5H) | Voltage decline limit |
| P502X (South) | Flow South on Circuit P502X | Stability limit |
| Canyon 115kV Output | Canyon 115kV Output | Normal system configuration / Configuration with Otter Rapids connected to 115 kV system |
| FABCW | Flow Away From Bruce Complex and Wind output in Bruce area. | Boundary for Southern Ontario Limits. Voltage collapse |
| BLIP | Buchanan Longwood Input | Voltage Collapse |
| NBLIP | Negative Buchanan Longwood Input | Boundary for Southern Ontario Limits. Voltage Collapse |
| BBO | Bruce B Output | Transient Instability |
| FABCW + NBLIP | Flow Away From Bruce Complex plus Wind + Negative Buchanan Longwood Input | No limit under normal conditions |
| FETT | Flow East To Toronto | Voltage Collapse |
| CLAN | Claireville North | Voltage Stability Limit |
| QFW | Queenston Flow West | Boundary for Southern Ontario Limits, Voltage Collapse, & Thermal Limit |
| FIO | Flow Into Ottawa | Voltage Stability Limit |
| SLW | St. Lawrence Flow West | Stability limit during critical New York outage conditions. |
| FID | Flow into Dobbin and Sidney | These limits are to control post-contingency voltage decline at Dobbin area. The limits can be improved based on the amount of L/R armed. |
| X1P Flow Into Dobbin | X1P Flow Into Dobbin | This limit is to ensure angular stability of Mountain Chute and Chenaux generators. |
| 115 kV Dobbin Area Load | 115 kV Dobbin Area Load | **** No interface limit under normal conditions |
| Chats Falls Area Generation | Chats Falls GS 230 kV Area Generation |  |
| P33C Inflow | P33C Chats Falls Inflow | P33C Chats Falls Inflow is limited to 310 MW when Chelsea generation is greater than 105 MW |
| P33C Inflow Plus Arnprior | P33C Chats Falls Inflow Plus Arnprior Generation | **** No interface limit under normal conditions |
| Madawaska Generation | Madawaska 115 kV Generation | This limit is based on Chats Falls G2 & G3 I/S and connected to C7BM or 230 kV system. The limit can be improved up to 400 MW with maximum G/R armed. |
| Beauharnois Delivery | Beauharnois Delivery | Beauharnois delivery is constrained by transient stability. The limit can be improved up to 800 MW with maximum G/R armed. |
| MacLaren D5A Import | D5A Import From Maclaren | D5A import limit is constrained by transient stability. The All I/S limit is 250 MW. |
| MacLaren D5A Export | D5A Export To Maclaren | The Export Limit of 200 MW is not a security based limit, but is the agreed maximum amount of load that MacLaren may connect. |
| Beauharnois D5A Transfer | D5A Transfer | **** No interface limit under normal conditions |
| TEC | Transfer East From Cherrywood | **** No interface limit under normal conditions |
| CHIP | Chatham inflow | Voltage stability limit |

Table D-2: Operating Security Limits – External Interfaces

| Interface | Description of Interface | Notes |
| --- | --- | --- |
| OMTE | Ontario-Manitoba Transfer East | Thermal limit |
| OMTW | Ontario-Manitoba Transfer West | Thermal limit |
| MPFN | Ontario-Minnesota Transfer North | Thermal limit |
| MPFS | Ontario-Minnesota Transfer South | Thermal limit |
| Ontario to Michigan Winter | Total line flow on B3N, L4D, L51D and J5D from Ontario to Michigan | This limit is based on winter thermal rating at 10 degrees C with 0-4 km/hr wind. Ambient conditions will determine the applicable thermal limit of the tie lines. |
| Michigan to Ontario Winter | Total line flow on B3N, L4D, L51D and J5D from Michigan to Ontario | This limit is based on winter thermal rating at 10 degrees C with 0-4 km/hr wind. Ambient conditions will determine the applicable thermal limit of the tie lines. |
| Ontario to Michigan Summer | Total line flow on B3N, L4D, L51D and J5D from Ontario to Michigan | This limit is based on summer thermal rating at 35 degrees C with 0-4 km/hr wind. Ambient conditions will determine the applicable thermal limit of the tie lines. |
| Michigan to Ontario Summer | Total line flow on B3N, L4D, L51D and J5D from Michigan to Ontario | This limit is based on summer thermal rating at 35 degrees C with 0-4 km/hr wind. Ambient conditions will determine the applicable thermal limit of the tie lines. |
| NY-ONT Stability Limit | New York to Ontario Stability Limit |  |
| Ontario Niagara to New York Winter | Total line flow on PA301, PA302, PA27, BP76, L33P, and L34P from Ontario to New York | This limit is based on winter thermal rating at 10 degrees C with 0-4 km/hr wind. Ambient conditions will determine the applicable thermal limit of the tie lines. |
| New York to Ontario Niagara Winter | Total line flow on PA301, PA302, PA27, BP76, L33P and L34P from New York to Ontario | This limit is based on winter thermal rating at 10 degrees C with 0-4 km/hr wind. Ambient conditions will determine the applicable thermal limit of the tie lines. |
| Ontario Niagara to New York Summer | Total line flow on PA301, PA302, PA27, BP76, L33P, and L34P from Ontario to New York | This limit is based on summer thermal rating at 35 degrees C with 0-4 km/hr wind. Ambient conditions will determine the applicable thermal limit of the tie lines. |
| New York to Ontario Niagara Summer | Total line flow on PA301, PA302, PA27, BP76, L33P, and L34P from New York to Ontario | This limit is based on summer thermal rating at 35 degrees C with 0-4 km/hr wind. Ambient conditions will determine the applicable thermal limit of the tie lines. |
| Ontario to Quebec Beauharnois 230 kV Winter | Line flow on B31L from Ontario to Quebec Beauharnois (radial connection) | Thermal limit of B31L may be more restrictive. |
| Ontario to Quebec Beauharnois 230 kV Summer | Line flow on B31L from Ontario to Quebec Beauharnois (radial connection) | This limit is based on summer thermal rating at 30 degrees C. Ambient conditions will determine the applicable thermal limit of the tie line to a maximum of 470 MW. |
| Quebec Beauharnois 230 kV to Ontario Winter or Summer | Total Line flow on B5D and B31L from Quebec Beauharnois to Ontario (radial connection) | This limit is the same as the interface limit for Beauharnois Delivery. Thermal limits of B5D and B31L may be more restrictive |
| Ontario to Quebec Maclaren - 230 kV - Winter or Summer | Line flow on D5A from Ontario to Maclaren | This limit is the same as the interface limit for D5A Export to Maclaren. Thermal limit of D5A may be more restrictive. |
| Quebec Maclaren to Ontario – 230 kV - Winter or Summer | Line flow on D5A from Maclaren to Ontario | This limit is the same as the interface limit for D5A Import from Maclaren. Thermal limit of D5A may be more restrictive. |
| Ontario to Quebec Masson - 115 kV - Winter or Summer | Line flow on H9A from Ontario to Masson | Concurrent operation of D5A with Maclaren and H9A with Masson is not permitted |
| Quebec Masson to Ontario - 115 kV - Winter or Summer | Line flow on H9A from Masson to Ontario | Concurrent operation of D5A with Maclaren and H9A with Masson is not permitted. Thermal limit of H9A may be more restricted |
| Ontario to Quebec Outaouais – 230kV – Winter or Summer | Line flow on A41T and A42T from Ontario to Outaouais | Limit is the minimum of 1 or 2 below: 1250 MW with two convertors in service or 625 MW with one convertor in service FIO limit – (Ottawa area load and losses) + (Generation in the Ottawa Zone) |
| Quebec Outaouais to Ontario – 230kV – Winter or Summer | Line flow on A41T and A42T from Outaouais to Ontario | Limit is the minimum of 1 or 2 below: 1250 MW with two convertors in service or 625 MW with one convertor in service FIO limit – (Ottawa area load and losses) + (Generation in the Ottawa Zone) |
| Ontario to Quebec Paugan 230 kV Winter or Summer | Line flow on P33C from Ontario to Paugan |  |
| Quebec Paugan to Ontario - 230 kV Winter or Summer | Line flow on P33C from Paugan to Ontario | P33C Chats Falls Inflow is limited to 310 MW when Chelsea generation is greater than 105 MW |
| Ontario to Quebec Quyon 230 kV Winter | Line flow on Q4C from Ontario to Quyon |  |
| Quebec Quyon to Ontario 230 kV Winter | Line flow on Q4C from Quyon to Ontario |  |
| Ontario to Quebec Quyon 230 kV Summer | Line flow on Q4C from Ontario to Quyon |  |
| Quebec Quyon to Ontario 230 kV Summer | Line flow on Q4C from Quyon to Ontario |  |
| Ontario to Quebec Bryson 115 kV Winter or Summer | Line flow on X2Y from Ontario to Bryson |  |
| Quebec Bryson to Ontario - 115 kV Winter or Summer | Line flow on X2Y from Bryson to Ontario |  |
| Quebec Rapide to Ontario (115kV) Import | Line flow on D4Z from Rapide-Des-Isles to Dymond |  |
| Ontario to Quebec Kipawa (115kV) Export | Line flow on A4Z from Antoine to Kipawa |  |

– End of Appendix –

## Generation Reserve Holdback Requirements

Generation reserve holdback (GRH) is an amount of generation capacity and/or electricity storage capacity needed to be held in reserve, to cover for uncertainty in load forecasting, generation or electricity storage availability, and for the effects of special protection schemes and the commissioning of large generation units and electricity storage units, so that load may be supplied with an acceptable level of reliability. The distribution of the GRH throughout a year is based upon a method of mitigating the risk of unsupplied load for the peak hour of each week in a year. The probability of failure of units currently in operation increases as time progresses but tends to level off after about one month.

The GRH required to mitigate the risk due to generation unit and/or electricity storage unit unreliability will, therefore, increase up to a limit as time advances from the present. On occasion, some special protection schemes, and the commissioning of large generation units or electricity storage units, can give rise to the potential for unusually high generation contingencies. When these are taken into account, significant GRH variations from week-to-week can result, especially in the near-term.

Therefore, GRH is comprised of the combination of requirements for operating reserve (OR), load forecast uncertainty (LFU) and additional contingency allowance (ACA) and is dependent on the day in the assessment period. The GRH component of the demand forecast for any given hour or day plays an important role in the decision-making process of the IESO and ultimately, for market participants. For example, the forecast accuracy of the capacity of operating reserve plus the demand required to fulfill uncertainties and contingencies in the operation of the IESO-controlled grid impacts directly on requests for outages by market participants. A consistently adequate supply of generation to meet capacity and energy requirements will be maintained in the near-term.

Table E-1: Generation Reserve Holdback Requirements

| Type of Report | Time Period (beginning from present) | Generation Reserve Holdback (MW) |
| --- | --- | --- |
| Adequacy Report | Day 0-2, where Day 0 is the current day | Operating reserve requirement consisting of 30-minute and 10-minute operating reserve requirements. |
|  | Balance of the first two weeks (3-14 days out) | GRH = operating reserve requirement + LFU + ACA) In this period, the ACA consists of the next largest half contingency beyond the operating reserve requirement. |
|  | Covers a total of 11-17 days from Day 15 out to the end of Week 4 | Linear interpolation between (b) and (d). |
| Period beyond the days of the Adequacy Report | Week 5 (this quantity is not included in the Adequacy Report, but is used to aid in the interpolation for the period from Day 15 out to the end of Week 4 | The Week 5 Required Reserve is calculated and published in the Resources Adequacy Assessment Table, located in the “Reliability Outlook” as posted on the IESO website. |

Total Operating Reserve – Total operating reserve forecast is comprised of the addition of the 30-minute operating reserve requirement and the 10-minute operating reserve requirement.

Load Forecast Uncertainty (LFU) – The process of creating a realistic operational energy plan includes taking into account uncertainty in the major forecast components, including Ontario demand. Sensitivity to extreme weather conditions subjects the power system to large swings in load, particularly during the summer and winter peak periods. Only weather-related uncertainties are considered. LFU is included to reflect this sensitivity in the adequacy assessment reports.

LFU is a statistical measure of deviations from the actual Ontario demand and can be considered as a target bandwidth for the forecasted error. It follows a normal distribution and is obtained from historical data. One standard deviation of error distribution becomes the factor used to determine LFU. The LFU is determined for both Day 3 and for days further out.

In the near-term, the demand forecast is derived using a load forecasting tool (for more information on preparing the demand forecast, see Appendix A). From Day 0 to 10 days out, the current weather forecast is used as the basis for characterizing the forecast day. Beyond 10 days, normal (actual past) weather is used as the basis for characterizing the forecast day.

From Day 0 (current day) to two days out, there is less uncertainty in the weather forecast, therefore the LFU allowance is not included in this period. From three days out and beyond, the weather forecast contains more uncertainty, therefore LFU allowance is included to reflect the uncertainty. As the number of days out increases, uncertainty in the weather forecasted increases.

For three days out to Day 6, the LFU is a statistical measure of the error variability over the three to six-day period. This data set consists of a calculated error (difference) between the forecasted and actual Ontario demand is evaluated to determine one standard deviation for each month. This deviation represents the uncertainty of six days out. As the days out decreases, the uncertainties in the forecasted weather decrease. Therefore, the LFU decreases.

For seven days out and beyond, the LFU is a statistical measure of past monthly Ontario demand peaks and monthly energy usage. This data set consists of 30 years of recorded actual (normal) weather, Ontario demand peaks and energy usage. To use this data, the assumption is made that the weather in the future will be similar to the weather in the past. Again, this data is evaluated to determine a standard deviation for each month using the Ontario demand peaks. This deviation represents the uncertainty for seven days out and beyond.

Additional Contingency Allowance (ACA) – ACA is the forecast for demand to allow for contingencies. The GRH requirements may be increased for special considerations in near-term planning, such as uncertainties in return-to-service dates, known problems of operating units, hydraulic flexibility, levels and types of transactions and prevailing weather conditions. Therefore, operability studies considering generation contingencies may also be required to ensure energy adequacy.

– End of Appendix –

List of Acronyms

| Acronym | Term |
| --- | --- |
| ACA | additional contingency allowance |
| CRO | control room operator |
| DSO | Dispatch Scheduling and Optimization |
| GRH | generation reserve holdback |
| kV | kilovolt |
| LFU | load forecast uncertainty |
| MW | megawatt |
| MWh | megawatt hour |
| NERC | North American Electric Reliability Corporation |
| NISL | net interchange scheduling limit |
| NPCC | Northeast Power Coordinating Council, Inc. |
| SBG | surplus baseload generation |

– End of Section –

References

| Document ID & Link | Document Title |
| --- | --- |
| RUL-6 to RUL-24 | Market Rules for the Ontario Electricity Market |
| MAN-138 | Market Manual 2.8: Reliability Assessments Information Requirements |
| MAN-140 | Market Manual 2.11: Reliability Outlook and Related Information Requirements |
| MAN-123 | Market Manual 7.3: Outage Management |
|  | NPCC Directory 5: Reserve |

– End of Document –

The lists of internal interfaces and interties are in Appendix D.

At its discretion, the IESO may disable the five-minute Variable Generation forecasting tool when the forecast differs from the actual output by at least 50 MW.

Depending on the time frame of assessment, there may be slightly different definitions of baseload generation. This definition is used in the operational time frame.

After the day-ahead market process completes, the IESO will assess pre-dispatch results on an hourly basis. If the IESO determines, with reasonable certainty, that a baseload generation manoeuvre exceeding 50 MW is likely for a future hour, they will issue a Minimum Generation Alert.

At its discretion, the IESO may manually adjust the Ontario demand forecasts provided by the load forecast tools to account for conditions such as, but not limited to, actual weather that differs from forecast weather.

Generation Reserve Holdback is an amount of generating capacity that is needed to be held in reserve. Refer to Appendix E for details.

An estimated value of imports is used prior to the initial pre-dispatch run on Day 1.

Excludes outages to energy limited resources and variable generation resources.

At its discretion, the IESO may manually adjust the variable generation forecast provided by the forecasting entity to account for conditions such as, but not limited to, actual weather that differs from forecast weather.

Due to increased forecast uncertainty for wind quantities below 500 MW for Days 2 to 7, the forecasts provided by the forecasting entity will be reduced by 10% to reduce the likelihood of over-forecasting.

For more details, see the Methodology to Perform Long Term Assessments document available at the Reliability Outlook page of the IESO website.

IESO Ramp Hours are defined as any hour in which the peak demand forecast exceeds the average demand forecast by at least 300 MW.

A week runs Monday – Sunday. The current week is defined as Week 0.