Market Manual

PUBLIC

Market Manual 7: System Operations

# Part 7.3: Outage Management

Issue 3.1

MAN-123

This market manual outlines the process market participants must follow in submitting outage requests for facilities.

December 2, 2026

Document Change History

| Issue | Reason for Issue | Date |
| --- | --- | --- |
| Refer to Issue 49.0 (MDP_PRO_0035) for changes prior to Market Transition. |  |  |
| 1.0 | Market Transition | November 11, 2024 |
| 2.0 | Issued in advance of MRP Go Live – May 1, 2025 | April 25, 2025 |
| 3.0 | Issued for Baseline 54.1 | December 3, 2025 |
| 3.1 | Issued for Baseline 56.1 | December 2, 2026 |

Related Documents

| Document ID | Document Title |
| --- | --- |
| MAN-122 | Market Manual 7.2: Near-Term Assessments and Reports |

Table of Contents

Table of Contents	i

List of Figures	iv

List of Tables	v

Table of Changes	vii

Market Manuals	viii

Market Manual Conventions	viii

1	Introduction	1

1.1	Purpose	1

1.2	Scope	1

1.3	Contact Information	3

2	Outage Management Overview	4

2.1	Market Participant Planned Outages	4

2.2	IESO Planned IT Outages	5

2.3	Confidentiality	5

3	Outage Management Information	6

3.1	Criticality Levels of Equipment	6

3.2	Priority Codes	7

3.2.1	Determining Outage Priority	10

3.3	Purpose Codes	12

3.4	Constraint Codes	15

3.5	Low-Impact Attributes	17

3.5.1	Submission Timelines	17

3.6	Mapping Purpose, Constraint and Priority Codes	17

3.7	Timelines	19

3.7.1	General Requirements	19

3.7.2	Quarterly Advance Approval Process	21

3.7.3	Weekly Advance Approval Process	23

3.7.4	Three-Day Advance Approval Process	24

3.7.5	One-Day Advance Approval Process	25

3.7.6	Auto Advance Approvals	27

3.7.7	Final Approval in Advance	28

3.7.8	Submission Deadlines	29

4	Outage Management Procedures	31

4.1	Facility Registration	31

4.2	Outage Coordination	31

4.2.1	Undesirable Situations	32

4.2.2	Outage Planning Guidelines	32

4.2.3	Conflicting Constraint Codes	34

4.2.4	Conflict Checking	36

4.2.5	IESO Reports	38

4.3	Outage Coordination for Capacity Exports	38

4.3.1	Capacity Seller Requirement to Coordinate with Transmitters Prior to IESO Involvement	39

4.3.2	Capacity Seller Requirement to Coordinate with Transmitters Requiring IESO Involvement	40

4.4	Outage Coordination for Generator-Backed Capacity Import Resources	41

4.5	Outage Submission	43

4.6	Outage Assessment	45

4.6.1	Market Participant Updates	46

4.6.2	Outage Assessment Outcomes	46

4.7	Outage Implementation	49

4.7.1	Planned and Forced Extensions	49

4.7.2	Recall	49

4.7.3	Suspension of Non-Urgent Maintenance or Switching	50

4.8	Outage Completion	50

4.9	Outage Compensation	51

4.9.1	Example A: Market Participant NOT Entitled to Compensation	51

4.9.2	Example B: Market participant Entitled to Compensation	52

4.9.3	Example C: Market Participant Entitled to Compensation	52

5	Outage Reporting Requirements	53

5.1	Generation Facilities and Electricity Storage Facilities	53

5.1.1	Deratings	54

5.1.2	Tests	55

5.1.3	Commissioning Facilities	58

5.1.4	Segregated Mode of Operation	62

5.2	Loads	64

5.2.1	Dispatchable Loads	64

5.2.2	Connected Wholesale Customers	65

5.2.3	Distributors and Transmitters	65

5.2.4	Outages and Non-Performance Event Management for Capacity Auction Resources	65

5.3	All Market Participants	67

5.3.1	Monitoring and Control Equipment	67

5.3.2	System Tests	67

5.3.3	Testing of Ancillary Services	68

5.3.4	Testing Operating Reserve Providers	69

5.3.5	Hold-offs	70

5.3.6	New and Replacement Facilities	71

6	Replacement Energy to Support Planned Outages	72

7	Dispute Resolution	77

Appendix A:	Outage Reporting Requirements	78

Appendix B:	Equipment Classes and Applicable Constraint Codes	83

Appendix C:	Criteria for One-Day Advance Approval, Auto AA and FAA	85

List of Acronyms	91

References	93

List of Figures

Figure 3-1: Quarterly Advance Approval Timeline	21

Figure 3-2: Criteria for ‘At Risk’ Outage Retaining Original Priority	22

Figure 3-3: ‘At Risk’ Outage Reassessment – Example A	22

Figure 3-4: ‘At Risk’ Outage Reassessment – Example B	23

Figure 3-5: Weekly Advance Approval Timeline	24

Figure 3-6: Three-Day Advance Approval Timeline	25

Figure 3-7: One-Day Advance Approval Timeline	26

Figure 4-1: Partial Equipment Outage Example	37

Figure 4-2: Compensation Eligibility – Example A	51

Figure 4-3: Compensation Eligibility – Example B	52

Figure 4-4: Compensation Eligibility – Example C	52

Figure 5-1: Submitting Test Request during Outage	55

Figure 6-1: Purchase of Replacement Energy – Requirements and Confirmation Timeline	74

Figure 6-2: Outage Submission Timeline Example	74

Figure 6-3: Precedence of Outages Based on Purchase of Replacement Energy	75

List of Tables

Table 3-1: Criticality Levels of Equipment	6

Table 3-2: Priority Codes	8

Table 3-3: Outage Approval Example	11

Table 3-4: Outage Rejection Example	11

Table 3-5: Purpose Codes	13

Table 3-6: Constraint Codes	15

Table 3-7: Mapping of Purpose, Constraint and Priority Codes	17

Table 3-8: Advance Approval Timelines and Eligibility	20

Table 3-9: One-Day Advance Approval Eligibility Example	26

Table 3-10: Auto Advance Approval Example	28

Table 3-11: Final Approval in Advance Example	29

Table 3-12: Outage Submission and IESO Review Timeline	29

Table 4-1: Transmission Groupings	33

Table 4-2: Seasonal Time Frame	33

Table 4-3: Sample Outage Planning Guideline	34

Table 4-4: Outage Request Constraint Code Conflicts	35

Table 4-5: Constraint Code Conflict Example	36

Table 4-6: Criteria for Conflict Rationale Acceptance	37

Table 4-7: Applicable Codes for Generator-backed Capacity Import Resources	43

Table 4-8: Information Requirement during Outage Submission	43

Table 4-9: Market Participant Outage Request Updates	46

Table 4-10: Possible Next Steps after Providing Advance Approval	47

Table 4-11: Possible Next Steps after Negotiate to Reschedule	48

Table 4-12: Communication with the IESO Control Room	49

Table 4-13: Outage End Time Adjustment	51

Table 5-1: Example Codes for Electricity Storage Resources when Unable to Withdraw	53

Table 5-2: Example Codes when Submitting Planned Derate Requests	55

Table 5-3: Offer Price Test Example	56

Table 5-4: Operating Reserve Market Participation Example	57

Table 5-5: Example Codes when Submitting Planned Testing Requests	58

Table 5-6: Example Codes for Commissioning Generation Facilities and Commissioning Electricity Storage Facilities	61

Table 5-7: Example Codes When Requesting Planned Segregated Mode of Operation	64

Table 5-8: Example Codes for Planned Outages to Dispatchable Loads	65

Table 5-9: Applicable Codes for Wholesale Customers	65

Table 5-10: Example Codes for Distributors and Transmitters	65

Table 5-11: Applicable Codes for Demand Response Resources	66

Table 5-12: Example Codes for Planned Outages to Monitoring and Control Equipment	67

Table 5-13: Example Codes When Submitting Planned System Test Requests	68

Table 5-14: Implementing and Assessing Reserve Tests	69

Table 5-15: Example Codes When Submitting Planned Hold-off Requests	71

Table 5-16: Example Codes When Requesting Planned Outages to New and Replacement Resources	71

Table 6-1: Replacement Energy Purchase	74

Table B-1: Applicable Constraint Code per Equipment Class	83

Table C-1: Criteria for One-Day Advance Approval, Auto AA and FAA	85

Table of Changes

| Reference | Description of Change |
| --- | --- |
| Section 4.2, 4.2.1 | - Added provisions to support long-term outage planning and coordination. |

Market Manuals

Market manuals set out procedural and administrative details with respect to market rule requirements. Where there is a conflict between the requirements described in a market manual or appended document, and those within the market rules, the market rules shall prevail.

Market Manual Conventions

This market manual uses the following conventions:

the word 'shall' denotes a mandatory requirement;

references to market rule sections and sub-sections may be appreviated in accordance with the following representative format: ‘MR Ch.1 ss.1.1-1.2’  (i.e. market rules, Chapter 1, sections 1.1 to 1.2).

references to market manual sections and sub-sections may be appreviated in accordance with the following representative format: ‘MM 1.5 ss.1.1-1.2’  (i.e. market manual 1.5, sections 1.1 to 1.2).

internal references to sections and sub-sections within this manual take the representative format: ‘sections 1.1 – 1.2’

terms and acronyms used in this market manual in its appended documents that are italicized have the meanings ascribed thereto in MR Ch.11;

data fields are identified in all capitals; and

references to “Day 0” mean the current day, references to “Day 1” mean the day immediately after the current day, references to “Day 2” mean the day two days after the current day, and so on.

– End of Section –

## Introduction

### Purpose

This market manual is provided for market participants as a guide to outage management for facilities and equipment connected to the IESO-controlled grid, or which may affect the operation of the IESO-controlled grid. This includes outages to transmission systems defined as constituting elements of the IESO-controlled grid under the market rules and various operating agreements between the IESO and market participants.

This market manual is intended to provide market participants with a summary of the steps and interfaces involved in the outage management process. The procedures contained in this document serve as a roadmap for generation facilities, transmitters, distributors, electricity storage facilities and wholesale customers that participate in the IESO-administered markets, and reflect the requirements set out in the market rules and applicable IESO policies and standards, as well as standards established by the North American Electric Reliability Corporation (NERC) and criteria established by the Northeast Power Coordinating Council (NPCC).

### Scope

This market manual supplements the following market rules:

MR Ch.1 s.14: Exemptions

MR Ch.3 s.2: Establishment and Staffing of Market Assessment Unit

MR Ch.5 s.5.2: Confidentiality

MR Ch.3 s.6.6.10

MR Ch.4 s.7.7: Reliability, Maintenance and Repair of Monitoring and Control Equipment

MR Ch.4 App.4.2: Requirements for Generation and Electricity Storage Facilities Connected to the IESO-Controlled Grid

MR Ch.5 s.2.5.2

MR Ch.5 s.3.2.1

MR Ch.5 s.3.3: Reliability-Related Information

MR.Ch.5 s.3.4: Obligations of Transmitters

MR.Ch.5 s.3.5: Obligations of Wholesale Customers

MR.Ch.5 s.3.6: Obligations of Generators (Embedded and Non-embedded)

MR.Ch.5 s.3.7: Obligations of Distributors

MR.Ch.5 s.3.8: Obligations of Electricity Storage Participants (Embedded and Non-embedded)

MR Ch.5 s.4.9: Auditing and Testing of Ancillary Services

MR Ch.5 s.4.10: Consequences of Failure to Pass a Test

MR Ch.5 s.6.1: Outage Coordination – Introduction

MR Ch.5 s.6.2: Outage Planning

MR Ch.5 s.6.3: Outage Scheduling with the IESO

MR Ch.5 s.6.4: Submission of Outage Schedules and IESO Approval of Outage Schedules

MR Ch.5 s.6.4A: Return of Equipment or Facilities to Service

MR Ch.5 s.6.5.2

MR Ch.5 s.6.6: Tests

MR Ch.5 s.6.7: Compensation

MR Ch.5 s.7.1: Forecasts Prepared by the IESO

MR Ch.5 s.7.3: Advance Assessments of System Reliability

MR Ch.5 s.7.7.7: Advisory Notices

MR Ch.5 s.10.2.3

MR Ch.7 s.2.2: Facility and Associated Resources Registration

MR Ch.7 s.2.3.2

MR Ch.7 s.3.3.8: Obligation to Revise Dispatch Data

MR Ch.7 s.3.5.6

MR Ch.7 s.19.4: Energy Market Participation for Hourly Demand Response Resources

MR Ch.7 s.19.5: Energy Market Participation for Capacity Dispatchable Load Resources

MR Ch.7 s.19.7: Energy Market Participation for Capacity Generation Resources

MR Ch.7 s.19.9.5: Outage Notification Requirements for System-Backed Capacity Import Resources

MR Ch.7 s.19.9B: Energy Market Participation for Generator-Backed Capacity Import Resources

MR Ch.7 s.19.11: Energy Market Participation for Capacity Storage Resources

MR Ch.7 App.7.7 s.1.3: Scheduling & Scheduling Approval

### Contact Information

Changes to this market manual are managed via the IESO Change Management process. Stakeholders are encouraged to participate in the evolution of this market manual via this process.

To contact the IESO, you can email IESO Customer Relations at customer.relations@IESO.ca or use telephone or mail. Telephone numbers and the mailing address can be found on the IESO website . IESO Customer Relations staff will respond as soon as possible.

– End of Section –

## Outage Management Overview

(MR Ch.5 ss.6.1 – 6.2; MM 7.4 s.2.3)

Outage state – The IESO considers a piece of equipment to be in an outage state when it is:

removed from service;

in a state other than its normal state;

unavailable for connection to the system;

temporarily derated;

restricted in use; or

reduced in performance.

De-staffing and auxiliary equipment – This includes de-staffing of a generation unit or an electricity storage unit during a period when market participants do not expect the unit to be scheduled to provide energy or operating reserve. Auxiliary equipment is also considered to be in an outage state when it is not available for use.

### 2.1	Market Participant Planned Outages

(MR Ch.5 s.6.4.3)

Generator backed capacity import resources – Pursuant to MR Ch.5 s.6.4.3, generator-backed capacity import resources are required to request permission and receive approval for planned outages from the IESO when that outage impacts the resource’s ability to provide its capacity obligation.

Scope of coordination – Market participants with equipment that affects the operation of the IESO-controlled grid may not remove equipment or facilities from service except in accordance with the rules for outage coordination contained in MR Ch.5 s.6.4.3 and this market manual.

Control Room Operations Window – The IESO’s outage management system uses the Control Room Operations Window (CROW) outage coordination and scheduling system. Market participants are required to submit information that provides the IESO with a better understanding of the priority, scope and impact of the outage request as described in section 3.

Processes for advanced approval – Market participants must submit their planned outages into one of four advance approval processes (quarterly, weekly, three-day or one-day) in order to receive advance approval. Each process has a unique set of eligibility criteria and submission/approval deadlines, which are further described in section 3.7.

Processes for notifications and late requests – Forced, urgent, information, and opportunity outages are outages that market participants are unable to submit in accordance with the submission requirements for planned outages. However, market participants must still submit these types of outages to the IESO as either a notification pursuant to MR Ch.5 s.6.3.4 or a late request for advance approval pursuant to MR Ch.5 s.6.4.6 as described in section 3.2.

### 2.2	IESO Planned IT Outages

(MR Ch.5 ss.3.3 and 7.7.7)

IESO communication – Market participants are normally notified about planned Information Technology (IT) outages to market-facing tools and applications through weekly bulletin emails. Details of all planned IT outages are also posted on the IESO Planned IT Outages website. For unforeseen IT outages, market participants are notified via an advisory notice and/or via a message through the Market Participant Interface.

### 2.3	Confidentiality

(MR Ch.3 s.5.2; MR Ch.5 s.6.5.2)

Publication – The Adequacy Reports will aggregate outage information to protect the confidentiality of market participants. All planned transmission system outages will be published for information. This may include transmission elements that are not owned by a transmitter.

Exchange of information – Outage information will only be exchanged with reliability coordinators (RCs) and balancing authorities (BAs) who are signatories to the NERC confidentiality agreement or who are otherwise legally bound to withhold and keep confidential outage information from any person competing with a market participant who provided the information.

Third-party viewership – Market participants may choose to share outage information with other market participants by granting third party viewership of their equipment via Online IESO. A single outage request may contain equipment both with and without third party viewership access. In such cases, third party viewers will only see the equipment to which they have access.

– End of Section –

## Outage Management Information

This section covers the following outage management information:

Criticality Levels of Equipment

Priority Codes

Purpose Codes

Constraint Codes

Low-Impact Attributes

Mapping Purpose, Constraint and Priority Codes

Timelines

### 3.1	Criticality Levels of Equipment

(MR Ch.5 s.6.4)

Criticality – The level of equipment criticality dictates the advance approval timeframe within which a planned outage request must be submitted under MR Ch.5 s.6.4 (refer to Table 3-1). For example, planned outages to critical equipment must be submitted at least 17 days prior to the start of the coverage period (under the Weekly Advance Approval process), whereas planned outages to low-impact equipment must be submitted two days prior to the scheduled date of the outage (under the One-day Advance Approval process). Section 3.7 describes advance approval processes and eligible equipment in further detail.

Online IESO – The IESO notifies market participants of equipment criticality levels via Online IESO, upon completion of facility assessment. When submitting outage requests, market participants are required to identify the impacted equipment and the outage management system will auto-populate the criticality level.

Table 3-1: Criticality Levels of Equipment

| Criticality Level | Description | Examples | Advance Approval Submission Timeline |
| --- | --- | --- | --- |
| Critical Equipment | Equipment that has a material impact on the reliability and/or operability of the IESO-controlled grid or the interconnection when removed from service or restricted. | Equipment that impact power system stability limits | Must be submitted for weekly advance approval May be submitted for quarterly advance approval |
| Non-critical Equipment1 | Equipment that does not typically have a material impact on the reliability and/or operability of the IESO-controlled grid or the interconnection when removed from service or restricted. | Equipment in local areas Generation facilities or electricity storage facilities | Must be submitted for three-day advance approval May be submitted for quarterly advance approval or weekly advance approval |
| Low-impact Equipment | Equipment that has little to no impact on the reliability and/or operability of the IESO-controlled grid or the interconnection when removed from service or restricted. | Loads Duplicated protection relays | Must be submitted for one-day advance approval May be submitted for three-day, quarterly, weekly advance approval |

### 3.2	Priority Codes

(MR Ch.5 ss.6.2.2A, 6.2.2B, 6.3.4 and 6.4.6)

Coding – Priority codes identify the priority of the outage request, as described in Table 3-2. The IESO uses this information to determine the level of urgency to implement the outage and to prioritize competing outage requests. Refer to section 3.2.1 for more information on how the IESO determines outage priority.

Market participants are required to use one of the following priority codes when submitting their outage request.

Note: Priority codes cannot be changed by market participants once they have been submitted.

Table 3-2: Priority Codes

| Priority Codes | Description | Examples | Obligation to Notify IESO |
| --- | --- | --- | --- |
| Forced | Non-discretionary outages on equipment that has been automatically or manually removed from service for equipment protection, public safety, environmental concerns or regulatory requirements are classified as forced outages. Such outages have little to no timing flexibility and have precedence over all priority codes. | Transformer forced out-of-service due to equipment failure | Market participants are required, as far in advance as possible, to promptly notify the IESO of any forced outage (MR Ch.5 s.6.3.4). |
| Urgent | Non-discretionary outages on equipment that must be manually removed from service for equipment protection, public safety, environmental concerns or regulatory requirements are classified as urgent outages. | SF6 breaker low gas alarm that requires a breaker outage for gas top-up within a limited timeframe | Market participants are required to coordinate outage timing with the IESO, where possible, to occur at a date and time that satisfies the market participant’s need and minimizes the impact to the IESO-controlled grid. |
| Planned | Discretionary outage requests that are scheduled to perform preventive maintenance, repairs, inspections, de-staffing and testing for facilities/ equipment are classified as planned outages. | Generation facility or electricity storage facility scheduled maintenance Breaker trip coil test | Market participants must adhere to submission deadlines explained in section 3.7 (MR Ch.5 ss.6.2.2A and 6.2.2B). |
| Opportunity | In cases where market participants are presented with an unexpected opportunity to accomplish work that was not previously planned, they may submit an outage request with the Opportunity priority code. | Additional testing is required to expedite the completion of an in-progress forced outage to a generation facility or electricity storage facility An opportunity to perform maintenance to a that is made grid-incapable by another outage Requests to operate in segregated mode of operation | The IESO is not obligated to consider such submissions, but may do so where the opportunity presents low to negligible risk to the reliability and/or operability of the IESO-controlled grid and or to the IESO. (MR Ch.5 s.6.4.6). |
| Information | Outages that are exempt from submission requirements outlined in Appendix A, but are submitted for informational purposes only, are classified as information outages. | Generation resource or electricity storage resource unavailable for condense Switch on manual operation only | No obligation. Market participants may, as far in advance as possible, notify the IESO of any information outage, using their outage submission tools. |
| Force Extended | This code is not available to market participants when submitting outage requests. However, if the end time of a planned, opportunity, or information outage requests get extended their priority code will be updated to forced extended. | Adverse weather conditions delay the completion of a scheduled outage | Market participants are required to notify the IESO of any forced extension as far in advance as possible, using their outage submission tools and by telephoning the IESO. |

#### Determining Outage Priority

- (MR Ch.5 s.6.4.2)

IESO determination – The IESO determines priority of outages in order to approve, reject, revoke and recall outages in a consistent and uniform manner.

Determination criteria – Outage priority for approval is based on the criteria listed in section 3.2.2.1.

##### Criteria 1: Priority Code

The priority code of an outage request is the primary determinant of outage priority. The order of precedence is as follows:

- Forced

- Urgent

- Planned

- Opportunity

For example, when approving outages, an urgent outage request gets priority over a planned or opportunity outage request.

##### Criteria 2: Advance approval timeframe

Within planned outages, the order of precedence is as follows:

- Outages submitted for quarterly advance approval

- Outages submitted for weekly advance approval

- Outages submitted for three-day advance approval

- Outages submitted for one-day advance approval

For example, a planned outage request submitted for weekly advance approval gets priority over a planned outage request submitted for three-day advance approval. However, an urgent outage request submitted five days ahead of the planned start time gets priority over a planned outage request submitted under the weekly advance approval process.

##### Criteria 3: Priority date

(MR Ch.5 ss.6.4.13 and 6.4.15)

For urgent and opportunity outages, the submission date and time determine outage priority. The earlier the submission, the higher is the priority of the outage request.

For planned outages submitted within the same advance approval timeframe, the submission date and time determine outage priority.

Table 3-3: Outage Approval Example

| If… | Then… |
| --- | --- |
| The following outages are submitted for approval: Outage A: Opportunity outage submitted three days ahead of the planned start time Outage B: Urgent outage submitted five days ahead of the planned start time Outage C: Planned outage submitted for the Weekly Advance Approval process Outage D: Opportunity outage submitted five days ahead of the planned start time Outage E: Planned outage submitted for the Three-Day Advance Approval process | Outage priority will be as follows: Outage B Outage C Outage E Outage D Outage A |

Rejection and revocation – To determine priority when rejecting, revoking advance approval or recalling outages, the IESO shall follow the reverse order of the criteria listed above (MR Ch.5 s.6.4.13). Where an outage conflict exists and one or more conflicting outages are rejected or revoked, the IESO may facilitate communication between the parties.

Table 3-4: Outage Rejection Example

| If… | Then… |
| --- | --- |
| The IESO determines a need to reject the following submitted outage requests: Outage A: Opportunity outage submitted three days ahead of the planned start time Outage B: Urgent outage submitted five days ahead of the planned start time Outage C: Planned outage submitted for the Weekly Advance Approval process Outage D: Opportunity outage submitted five days ahead of the planned start time Outage E: Planned outage submitted for the Three-Day Advance Approval process | Outages will be rejected in the following order: - Outage A Outage D Outage E Outage C Outage B |

Significant changes – If market participants make a significant change to the scope or time window of a previously submitted outage request, the IESO shall revise the priority date with the time at which such change notice was received by the IESO. Changes to the following outage request fields are considered to be significant changes:

Planned Start (if changed to an earlier outage period level start date/time)

Planned End (if changed to a later outage period level2 end date/time)

Equipment Requested (if equipment is added or removed)

Equipment Description

Priority Code

Constraint Information (if change in constraint code, value, and/or measure unit)

Changes to any responses to low-impact questions (refer to section 3.5 for details)

Change to the response to the Telemetry Scaling Impact question

Shortening max recall time – In cases where market participants wish to shorten the max recall time, they must verbally request the IESO to retain the original outage priority.

### 3.3	Purpose Codes

- (MR Ch.5 ss.6.2.2A, 6.2.2B, 6.3.4 and 6.4.6)

Coding – Purpose Codes allow market participants to indicate the reason for the outage request (refer to Table 3-5). This information is used by the IESO to determine the impact and purpose of the outage request. For example, an outage request submitted for a safety concern informs the IESO of the market participant’s urgent need compared to an outage request to conduct maintenance/repair testing which can be planned in advance.

Requirement to select – Market participants are required to select one of the following Purpose Codes when submitting their outage request and input a description of the outage’s purpose in the outage management system.

Availability – Selection of Purpose Codes is based on the Priority Code. For example, ‘Equipment Concern’ code is available only if the market participant is submitting a forced outage or urgent outage. Similarly, the ‘Repair’ code is available only for planned outages. Refer to section 3.6 for a mapping of Purpose and Priority Codes.

Table 3-5: Purpose Codes

| Purpose Code | Description | Example |
| --- | --- | --- |
| Maintenance Repair | Outages implemented to facilitate routine equipment maintenance and repair. | Annual transformer maintenance |
| Replacement | Outages implemented to replace aging or faulty equipment/facilities. In such cases, market participants must ensure the replacement is registered with the IESO as per MM 1.5. The outage to replace the equipment/facility is typically followed by a need to carry out a commissioning outage as explained below. | Breaker replacement |
| Commissioning | Outages implemented to test new or modified equipment/facilities being connected to the IESO-controlled grid for the first time. | Commissioning of new generation facility or electricity storage facility |
| Testing | Outages implemented to facilitate testing of equipment/facilities not considered to be commissioning tests or activities. | Generation facility minimum loading point testing |
| Equipment/Safety/ Regulatory/ Environmental Concerns | Outages implemented for non-discretionary purposes such as public safety, equipment protection, environmental concerns or regulatory requirements. | Generation facility derate due to restrictive forebay operating ranges |
| Favourable (Generation/ Electricity Storage/ Transmission) Outage Condition/Favourable Adequacy Margin/ Expedite Return to Service | Outages having low to negligible risk to the reliability of the IESO-controlled grid and are implemented to accomplish work that would have otherwise been unable to proceed. Note: Market participants may select this code, however the IESO will assess and determine the outage’s impact on the IESO-controlled grid. | Transformer feeder outage during existing outage to connecting circuit |
| Manually/Automatically Removed From Service | Unforeseen outages that result in manual or automatic removal of equipment/facilities from service. | Unit trip from neutral overcurrent |
| Failed to Synch | Unforeseen outages resulting from a failure to synchronize generation units or electricity storage equipment/facilities units to the IESO-controlled grid. | Unit breaker failed to synch |
| Segregated Mode of Operation | Outage to indicate generation or transmission equipment/facilities being disconnected from the IESO-controlled grid and connected to an external system, e.g. Quebec. | Generation facility connected to Quebec |
| Cyber Asset Change/ Relay Setting Change | Outages to indicate hardware/software changes for RTUs, gateways, routers, protection relays etc. intended to separate such requests from other general planned outages. | Software changes for RTU |
| Transmission Equipment Derating | Outages to indicate that a piece of transmission equipment is operating at a reduced equipment rating. | Transformer derating for degraded cooling |
| Switching | Short duration outage required to support the removal of equipment for a separate outage request. | Circuit terminals required for 15 minutes to switch circuit out of service |
| Telco Third Party Threat | Telecommunication outages requested of Hydro One by a third party telecom provider | Third party company to perform protection and control maintenance of Access Multiplexer |
| Self-Bottling | Outages implemented to indicate that a variable generation resource is operating to a reduced maximum generation output due to constraints resulting from transmission element outages within the resource’s facility. Note: This is to ensure that the centralized forecast predicts output of the station proportionate to their available capacity but capped at a derated maximum, rather than proportionate to their derated maximum as would be the case with a normal derate outage request. | 100 MVA variable generation resource normally connected to two 50 MVA transformers, but one transformer is out-of-service |
| Icing | Outages implemented to indicate reduced generation capacity due to icing conditions. | Ice on wind turbines |
| Other | Market participants may use this purpose code for outages being requested for any reason other than those listed above. | Generation resource or electricity storage resource unavailable for Generation Rejection |

### 3.4	Constraint Codes

(MR Ch.5 ss.6.2.2A, 6.2.2B, 6.3.4 and 6.4.6)

Coding – Constraint codes identify the status of the equipment when the outage is under implementation. This information is used to determine the limitations on the equipment to determine the impact of the outage request on the IESO-controlled grid. For example, an ‘In-Service’ code indicates the equipment is available and functional, whereas an ‘Out-of-Service’ code indicates the equipment will be unavailable for the duration of the outage.

Equipment type – Appendix B lists applicable constraint codes based on equipment type.

Requirement to select – Market participants are required to use one of the following constraint codes when submitting their outage request.

Availability – Selection of constraint codes is based on the priority code. For example, INFO and ABNO codes are only available for information outages. Refer to section 3.6 for a mapping of purpose and priority codes.

Table 3-6: Constraint Codes

| Constraint Code | Description | Examples |
| --- | --- | --- |
| Out of Service (OOS) | Equipment is unavailable and removed from service. | Breaker out-of-service |
| In Service (IS) | Equipment is available and in-service. | Normally open switch required in-service |
| Derated To (DRATE) | Equipment cannot operate above a specified capability that is less than its rated capability. | Generation resource or electricity storage resource derated to 50 MW |
| Must Run At (MUSTRUN) | Equipment can only operate at a specified capability that is less than or equal to its rated capability. | Generation resource or electricity storage resource must run at 50 MW |
| Hold Off (HOLDOFF) | Equipment has its reclosing capability blocked. | Circuit hold off |
| Protection Out of Service (PROT OOS) | Equipment’s primary or back-up protection is unavailable in some capacity. | Circuit’s B Protection out-of-service |
| Breaker Fail Protection Out of Service (BF PROT OOS)4 | A breaker’s backup protection is unavailable in some capacity. | Breaker Fail Protection for Breaker A out of service |
| Automatic Voltage Regulation or Power System Stabilizer Out of Service (AVR/PSS OOS)4 | Generation facility’s or, if applicable, electricity storage facility’s AVR or PSS is unavailable in some capacity. | Generation facility or electricity storage facility AVR out-of-service |
| Breaker Trip Coil Test (BTCT) | Breaker is undergoing a protection relay-initiated test operation. | Breaker trip coil test for Breaker A |
| Ancillary Service Out of Service (ASP OOS)4 | Equipment’s ability to provide a contracted ancillary service is restricted in some capacity. | Generation resource or electricity storage resource unavailable for black start, regulation or voltage control |
| Information (INFO) | Equipment has a condition or limitation that does not require approval from IESO. | Generation resource unavailable for condense Derated dispatchable loads with a demand response capacity obligation |
| Available But Not Operating (ABNO) | Mechanism for generation facilities and electricity storage facilities to report they do not expect to participate in the market. | Generation resource or electricity storage resource off-peak demand Generation facility or electricity storage unit de-staffing |

### 3.5	Low-Impact Attributes

(MR Ch.5 ss.6.2.2A, 6.2.2B, 6.3.4 and 6.4.6)

Requirement to answer – During outage request submission, market participants are required to answer certain questions to determine if their outage contains low-impact attributes, thereby making the equipment eligible for one-day advance approval, auto advance approval and/or final approval in advance (further explained in sections 3.7.5, 3.7.6 and 3.7.7, respectively). Low-impact attributes are used by the IESO to further define the scope and impact of the requested equipment.

Additional provisions – Refer to Appendix C for a list of attributes and applicability.

For example: A market participant submitting an outage request for line protection out-of-service will need to specify whether it is only a loss of redundancy. If they answer “Yes”, the equipment is considered to have low-impact attributes.

#### Submission Timelines

(MR Ch.5 ss.6.2.2A, 6.2.2B, 6.3.4 and 6.4.6)

Timelines – The following are the submission timelines for outages on equipment with low-impact attributes:

must be submitted for one-day advance approval;

may be submitted for quarterly, weekly or three-day advance approval; and

may be eligible for auto advance approval and/or final approval in advance

### 3.6	Mapping Purpose, Constraint and Priority Codes

(MR Ch.5 ss.6.2.2A, 6.2.2B, 6.3.4 and 6.4.6)

Coding – Each priority code applies to a set of purpose and constraint codes. Table 3-7 presents a mapping of all codes.

Table 3-7: Mapping of Purpose, Constraint and Priority Codes

| Priority Code | Purpose Codes | Constraint Codes |
| --- | --- | --- |
| Planned | Commissioning Cyber Asset Change Maintenance Other Relay Setting Change Repair Replacement Segregated Mode of Operation Switching Telco Third Party Threat Testing | All except INFO and ABNO |
|  | Self-Bottling | DRATE |
| Urgent | Environmental Concerns Equipment Concerns Other Regulatory Concerns Safety Concerns Switching Telco Third Party Threat | All except INFO and ABNO |
|  | Wind Turbine Icing Event Self-Bottling | DRATE |
| Opportunity | Commissioning Expedite Return to Service Favourable Adequacy Margin Favourable Generation Outage/Electricity Storage Condition Favourable Transmission Outage Condition Other Segregated Mode of Operation Switching Testing | All except INFO and ABNO |
|  | Self-Bottling | DRATE |
| Information | Other Transmission Equipment Derating | INFO ABNO |
| Forced | Automatically Removed From Service Environmental Concerns Equipment Concerns Failed to Synch Manually Removed From Service Other Regulatory Concerns Safety Concerns | All except INFO and ABNO |
|  | Wind Turbine Icing Event Self-Bottling | DRATE |

### Timelines

#### 3.7.1	General Requirements

- (MR Ch.5 ss.6.2.2A, 6.3.4 and 6.4.6)

Time frames – Market participants may request quarterly, weekly, three-day or one-day advance approval for their planned outages (MR Ch.5 s.6.2.2A). This section explains the submission and assessment periods for each advance approval timeframe. Eligibility for advance approval is determined by equipment criticality, as explained in section 3.1.

Study and coverage periods – Each advance approval process is associated with distinct submission, study and coverage periods. For the purposes of outage submission guidelines described in this document:

Study period refers to the period when the IESO assesses planned outage requests submitted for the associated advance approval process. The IESO will notify market participants of its assessment by the end of the study period.

Coverage period refers to the implementation period for outages that receive advance approval within the associated study period.

Submission prior to relevant study period – Market participants must submit outage requests before the start of the associated study period, in order to receive advance approval for implementation during the associated coverage period.

Forced outages – Market participants must submit forced outage notifications when they occur and these will be addressed by the IESO immediately.

Urgent requests – Market participants may submit urgent outage requests at any time. The IESO will study such requests as soon as possible.

Market participants may submit opportunity outage requests at any time. Such requests are considered late planned outage requests. The IESO is not obligated to consider such submissions, but may do so where the opportunity presents (MR Ch.5 s.6.4.6).

Information outages – Market participants may submit information outage requests at any time. The IESO will use reasonable efforts to study such requests.

Table 3-8: Advance Approval Timelines and Eligibility

| Advance Approval Process | Submission Requirement (Prior to Start of Coverage Period) | Approval Deadline (Prior to Start of Coverage Period) | Eligible Equipment |
| --- | --- | --- | --- |
| Quarterly | 3 months prior | 1 month prior | All equipment types may be submitted |
| Weekly | 17 days prior | 10 days prior | Critical equipment must be submitted Non-critical and low-impact equipment may be submitted |
| 3-Day | 5 business days prior | 3 business days prior | Non-critical equipment must be submitted Low-impact equipment may be submitted |
| 1-Day | 2 business days prior | 1 business day prior | Low-impact equipment must be submitted Critical and non-critical equipment with low-impact attributes must be submitted |

##### 3.7.1.1	Submission Timelines for Outages Supporting External Reliability Coordinators

(MR Ch.5 ss.6.2.2A and 6.4.6)

Process for submission – Market participants may be required to conduct outages to support work planned by external reliability coordinators. In cases where market participants are unable to submit such outage requests for advance approval within the deadlines for planned outages, they are required to submit such outages with an ‘Urgent’ priority code and refer to the reliability coordinator work request in the ‘Purpose Description’ field in the outage management system. The IESO will consider it as a planned outage when determining priority. Refer to section 3.2.1 for details on determining outage priority.

Note: The IESO’s obligation to assess such outage requests is based on the interconnection agreement with the external reliability coordinator.

#### 3.7.2	Quarterly Advance Approval Process

- (MR Ch.5 ss. 6.2.2A, 6.4.1B and 6.4.20)

Application – The IESO facilitates long-term planning by offering market participants the option to receive approval for all planned outages up to eight months prior to the scheduled start time via the Quarterly Advance Approval process.

Priority – Outages submitted within this process get the highest priority compared to planned outages submitted under other timeframes, thus granting greater certainty to market participants. Refer to section 3.2.1 for details on determining outage priority.

If an outage request is submitted for the Quarterly Advance Approval process after the submission deadline, the outage management system will automatically place the outage for assessment under the next Quarterly, Weekly, Three-Day or One-Day Advance Approval process, as eligible, based on equipment criticality, ‘Request Weekly AA’ flag and planned start time.

Study and coverage periods – The study and coverage periods for the Quarterly Advance Approval process are as shown in Figure 3-1.

Figure 3-1: Quarterly Advance Approval Timeline

Study period for the Quarterly Advance Approval process begins at 00:00:00 EST on the first day of the period month and ends at 23:59:59 EST on the last day of the period month as shown in Figure 3-1. Coverage period for the Quarterly Advance Approval process begins 00:00:00 EST on the first day of the period month and ends at 23:59:59 EST on the last day of the period month as shown in Figure 3-1.

Note: The timelines for submission and assessment are inclusive of statutory holidays in Ontario and Saturdays and Sundays (Saturdays and Sundays hereafter referred to as weekend days).

IESO response – By the end of the study period, the IESO will either:

provide advance approval, or

place the outage request in the ‘At Risk’ status

Resubmission – Market participants may choose to resubmit an outage placed in the ‘At Risk’ status at the end of a quarterly study period. Resubmitted outage requests will retain the priority date of the original outage request if:

the original outage was scheduled to begin in the first three months of the current coverage period; and

it is resubmitted before the next study period; and

the resubmitted outage is scheduled to begin during the corresponding six-month coverage period.

Figure 3-2: Criteria for ‘At Risk’ Outage Retaining Original Priority

IESO assessment – The IESO will reassess outages placed in the ‘At Risk’ status at the end of the Quarterly study period during the next Quarterly, Weekly, or Three-Day Advance Approval process, as applicable based on equipment criticality and the status of the ‘Request Weekly AA’ flag.

Example A:

Figure 3-3: ‘At Risk’ Outage Reassessment – Example A

Example – In the above figure, the market participant submits a request in September for an outage to critical equipment beginning in April of the following calendar year. The IESO studies the request during the October-November study period and transitions the outage to ‘At Risk’ status.

January-February study period – The IESO will reassess the request during the January-February study period for quarterly advance approval.

| If… | Then… |
| --- | --- |
| The IESO transitions the request to ‘At Risk’ status during the January-February study period | The outage will be reassessed in the next Weekly Advance Approval process |

Example B:

Figure 3-4: ‘At Risk’ Outage Reassessment – Example B

Example – Using the same timelines as Example A, the market participant submits an outage request for non-critical equipment for quarterly advance approval. If the IESO transitions it to ‘At Risk’ status during the October-November and the January-February study periods, the outage will be reassessed during the next Three-Day Advance Approval process.

| If… | Then… |
| --- | --- |
| The outage request has the ‘Request Weekly AA’ flag | The IESO will reassess the request in the next Weekly Advance Approval process following the February study period |

#### 3.7.3	Weekly Advance Approval Process

(MR Ch.5 ss.6.2.2A, 6.4.1C and 6.4.9)

Application – Planned outage requests for critical equipment must be submitted for Weekly Advance Approval. Market participants may also submit planned outage requests containing only non-critical or low-impact equipment under this process by selecting the “Request Weekly AA” flag in the outage management system.

Priority – Outages submitted within this process get a higher priority compared to planned outages submitted under three-day and one-day time frames, thus granting greater certainty to market participants for outages to non-critical or low-impact equipment (that are required to be submitted within the three-day and one-day processes respectively). Refer to section 3.2.1 for details on determining outage priority.

As explained in section 3.1, the criticality of equipment will be auto-populated in the outage management system during outage submission. If outages to critical equipment are not submitted within the Weekly Advance Approval process, the tool’s auto-validation feature will not allow the outage submission to be completed.

Mandatory and optional requests considered together – The IESO will also study outages with critical equipment and non-critical or low impact equipment with the “Request Weekly AA” flag placed in the ‘At Risk’ status from the Quarterly Advance Approval process during this time.

Study and coverage periods – The study and coverage periods for the Weekly Advance Approval process are as shown in Figure 3-5.

Figure 3-5: Weekly Advance Approval Timeline

Study period for the Weekly Advance Approval process begins at 16:00:00 EST on Friday and ends at 15:59:59 EST on the following Friday as shown in Figure 3-5. Coverage period for the Weekly Advance Approval process begins 00:00:00 EST on Monday and ends at 23:59:59 EST on the following Sunday as shown in Figure 3-5.

Note: The timelines for submission and assessment are inclusive of statutory holidays in Ontario and weekend days.

Example – For example, if the outage is scheduled to start on a Monday, the request must be submitted at least 17 days prior to the start of the outage. If the outage is scheduled to start on a Friday, the request must be submitted at least 21 days prior to the start of the outage.

IESO response – By the end of the study period, the IESO will either:

provide a Weekly Advance Approval; or

reject the outage request

Note: Outage requests rejected during the Weekly Advance Approval process will not be reassessed by the IESO. Market participants may resubmit rejected outages as new requests.

Revocation – At this stage, the IESO, based on significant changes in system conditions such as forced outages and changes to Ontario demand forecast, may also revoke quarterly advance approvals if implementation of the outage will impact the reliability of the IESO-controlled grid.

#### 3.7.4	Three-Day Advance Approval Process

(MR Ch.5 ss.6.2.2A, 6.4.1D and 6.4.9)

Application – Planned outage requests for non-critical equipment must be submitted for three-day advance approval.

Optional requests – Market participants may also submit planned outage requests containing only low-impact equipment under this process. Outages submitted within this process get a higher priority compared to planned outages submitted under one-day timeframe, thus granting greater certainty to market participants for outages to low-impact equipment (that are required to be submitted within the one-day process). Refer to section 3.2.1 for details on determining outage priority.

Other requests considered – The IESO will also study outages with non-critical equipment placed in the ‘At Risk’ status from the Quarterly Advance Approval process during this time.

Study and coverage periods – This process repeats daily on business days with study and coverage periods as shown in Figure 3-6.

Figure 3-6: Three-Day Advance Approval Timeline

Note: In Figure 3-6, the timeline on the left illustrates a coverage period that falls on a weekend, and the timeline on the right illustrates a coverage period that falls on a weekday.

Study period for the Three-Day Advance Approval process begins at 16:00:00 EST on business days and ends at 15:59:59 EST, two business days later as shown in Figure 3-6. Coverage period for the Three-Day Advance Approval process begins 00:00:00 EST on the fifth business day after the beginning of the study period, and ends at 23:59:59 EST on the same business day, as shown in Figure 3-6.

IESO response – By the end of the study period, the IESO will either:

provide an advance approval; or

reject the outage request.

Note: Outage requests rejected during the Three-Day Advance Approval process will not be reassessed by the IESO. Market participants may resubmit rejected outages as new requests.

Revocation – At this stage, the IESO may also revoke quarterly and weekly advance approvals if implementation of the outage will impact the reliability and/or operability of the IESO-controlled grid.

#### 3.7.5	One-Day Advance Approval Process

- (MR Ch.5 s.6.4.9)

Application – Planned outage requests containing only low-impact equipment must be submitted for one-day advance approval. Market participants may also submit planned outage requests containing critical and non-critical equipment with low-impact attributes under this process, if eligible. Appendix C lists eligibility criteria for one-day advance approval.

This provides additional flexibility to market participants who are otherwise required to submit outages to critical and non-critical equipment in the Weekly and Three-Day Advance Approval processes, respectively.

Eligibility – Refer to Appendix C for a list of eligibility criteria for One-Day Advance Approval.

Table 3-9: One-Day Advance Approval Eligibility Example

| If… | Then… |
| --- | --- |
| A market participant submits an outage request, less than five business days prior to the scheduled start time, to a generation resource or an electricity storage resource with a ‘Automatic Voltage Regulation or Power System Stabilizer Out of Service (AVR/PSS OOS)’ constraint code and answers “Yes” to the “Only a Loss of Redundancy” question | The outage will be eligible for one-day advance approval. |

Study and coverage periods – The One-Day Advance Approval process repeats daily with study and coverage periods as displayed in Figure 3-7.

Figure 3-7: One-Day Advance Approval Timeline

Note: In Figure 3-7, the timeline on the left illustrates a coverage period that falls on a weekend, and the timeline on the right illustrates a coverage period that falls on a weekday.

Study period for the One-Day Advance Approval process begins at 10:00:00 EST on business days and ends at 07:59:59 EST one business day later, as displayed in Figure 3-7.

Coverage period for the One-Day Advance Approval process begins 00:00:00 EST on the second business day after the beginning of the study period and ends at 23:59:59 EST on the same business day, as displayed in Figure 3-7.

IESO response – By the end of the study period, the IESO will either:

provide an advance approval; or

reject the outage request.

Revocation – At this stage, the IESO may also revoke quarterly, weekly and three-day advance approvals if implementation of the outage will impact the reliability and/or operability of the IESO-controlled grid.

#### 3.7.6	Auto Advance Approvals

Application – Outage requests for low-impact equipment or equipment containing low-impact attributes may be eligible for auto advance approval (Auto AA) when submitted via the outage management system.

Eligibility assessment – Market participants are required to answer certain questions to determine their eligibility for Auto AA. Appendix C, Table C-1, Column D lists the questions that will be asked to market participants during outage request submission to determine eligibility for Auto AA. Based on the answers provided by market participants, the tool will establish eligibility for and grant Auto AA. The tool will also check that there are no conflicting outages, as explained in section 4.2.3.

Exclusions – The IESO also has the ability to mark equipment for exclusion from the Auto AA process. For example, breaker failure protection outage to a critical breaker could be excluded from Auto AA despite correctly responding to the low-impact questions outlined in Appendix C.

Priority – Priority for outages that are granted Auto AA will be based on the time of submission and advance approval process they would have been manually studied in by the IESO. This ensures the priority is aligned with the IESO’s manual assessment of the outage.

Example – For example, if an outage request with non-critical equipment was submitted and auto-approved within the quarterly process it would have a quarterly advance approval priority. However, if the same outage request was submitted and auto-approved after the quarterly submission deadline, it would have a three-day advance approval priority, based on equipment criticality and submission timeframe.

Going back to the example stated in section 3.7.5, the outage request for the generation resource  or, if applicable, electricity storage resource, is deemed eligible for one-day advance approval.

Table 3-10: Auto Advance Approval Example

| If… | Then… |
| --- | --- |
| A market participant submits an outage request, less than five days prior to the scheduled start time, to a generation resource or electricity storage resource with a ‘Automatic Voltage Regulation or Power System Stabilizer Out of Service (AVR/PSS OOS)’ constraint code, and The market participant answers the low-impact question as follows: Only a Loss of Redundancy? = YES | The outage will be granted Auto AA with a one-day advance approval priority |
| A market participant submits an outage request, 18 days prior to the scheduled start time, to a generation resource or electricity storage resource with a ‘Automatic Voltage Regulation or Power System Stabilizer Out of Service (AVR/PSS OOS)’ constraint code, and The market participant answers the low-impact question as follows: Only a Loss of Redundancy? = YES | The outage will be granted Auto AA with a weekly advance approval priority |

Manual assessment – The tool offers certainty to market participants by way of the automated approval, however outage priority will be based on manual assessment.

#### 3.7.7	Final Approval in Advance

Application and eligibility assessment – A subset of outages for low-impact equipment or equipment containing low-impact attributes that are deemed eligible for Auto AA may receive final approval in advance (FAA). The IESO determines eligibility for FAA based on the impact to the IESO-controlled grid, on a case by case basis. Refer to Appendix C for criteria used to grant FAA.

Confirmation – The outage management system will transition the outage request to ‘Auto AA’ status and display a flag for market participants to confirm the outage request is eligible for FAA. On the day of the outage, the tool will automatically transition the outage to ‘Final Approved’ status.

Table 3-11: Final Approval in Advance Example

| If… | Then… |
| --- | --- |
| A market participant submits an outage request, five days prior to the scheduled start time, to a generation resource or electricity storage resource with a ‘Protection Out of Service (PROT OOS)’ constraint code and provides the following answer to the low-impact question: “Only a Loss of Redundancy?” = YES - and Max Recall is ≤ 15 minutes | The outage will be transitioned to ‘Auto AA’ status and a flag will be displayed to confirm the outage is eligible for FAA. On the day of the outage, the outage request will be automatically transitioned to ‘Final Approved’ status. The market participant is not required to request final approval to implement the outage. |

No final approve request needed – Market participants who have received FAA for their outages are not required to request final approval in order to implement the outage.

Revocation – The IESO may revoke the FAA of an outage request if it impacts the reliability and/or operability of the IESO-controlled grid and notify the market participant. In such cases, the market participant must verbally request final approval to commence the outage by telephoning the IESO.

Already scheduled out-of-service – Outage requests submitted for equipment that is already scheduled out-of-service under a single, planned outage request with an ‘Out-of-Service (OOS)’ constraint code will be eligible for FAA provided the new outage request:

contains the same or a subset of the equipment scheduled out-of-service;

has an overall and period level planned start and end date that is the same, or within the same time period, as the existing outage request; and

has been manually selected by the IESO to be eligible for FAA.

#### 3.7.8	Submission Deadlines

Timelines – Table 3-12 displays outage submission and IESO review timelines.

Table 3-12: Outage Submission and IESO Review Timeline

| Timeline | Action |
| --- | --- |
| At least three (3) months prior to coverage period start | Submit outage requests for quarterly advance approval |
| One (1) month prior to coverage period start | IESO approves or transitions the outage into At-Risk status for the quarterly period |
| By 16:00 EST at least 17 days prior to coverage period start | Submit outage requests for weekly advance approval |
| By 16:00 EST One (1) week prior to coverage period start | IESO approves or rejects the request for Weekly Advance Approval. |
| By 16:00 EST Five (5) business days prior to coverage period start | Submit outage request for three-day advance approval |
| By 16:00 EST Three (3) business days prior to coverage period start | IESO approves or rejects the request for three-day advance approval |
| By 10:00 EST Two (2) business days prior to coverage period start | Submit outage request for one-day advance approval |
| By 08:00 EST One (1) business day prior to coverage period start | IESO approves or rejects the request for one-day advance approval |
| Just prior to outage start | Request final approval to begin outage (Not applicable for outages that receive final approval in advance) IESO provides final approval or revokes advance approval |
| After IESO provides final approval | Implement outage |

– End of Section –

## Outage Management Procedures

### Facility Registration

- (MR Ch.1 s.14; MR Ch.5 ss.3.4.1, 3.5.1, 3.6.1, 3.7.1 and 3.8.1)

Information requirements – Market participants are required to submit information regarding new or changes to existing facilities and equipment to the IESO via the online registration process outlined in MM 1.5.

IESO assessment – The IESO will assess the submitted information to determine whether the equipment affects the operation of the IESO-controlled grid and communicate its assessment to market participants via Online IESO. Market participants are notified of their equipment’s criticality level at this point. Changes to the IESO-controlled grid or system operating limits may require the IESO to review and update criticality levels of equipment.

Outage reporting – Market participants whose facilities or equipment are determined to impact the IESO-controlled grid’s reliability will be required to report outages to the IESO. Refer to Appendix A for the detailed criteria that the IESO uses to assess outage-reporting requirements. Outages to system auxiliaries associated with this equipment must also be reported as identified in Appendix A.

Exemptions – Market participants may submit a market rule exemption application according to the process outlined in the MM 2.2 procedure to apply for facility equipment to be entirely or partially exempted. Requests for exemptions from outage reporting are assessed by the IESO on a case-by-case basis as specified in MR Ch.1 s.14. Assessments are communicated to market participants via Online IESO.

Control centres – Market participants may also register one or more control centres via the online registration process to represent the location of their real-time operations. This facilitates the submission of outages that are not associated to a particular station (e.g. SCADA systems).

### Outage Coordination

(MR Ch.5 ss.6.1.1 and 6.1.3)

Role of IESO – The IESO facilitates the outage coordination process for market participants by providing the following:

identifying undesirable situations – refer to section 4.2.1;

outage planning guidelines – confidential reports published by the IESO and embedded in the outage management system;

conflicting constraint codes – embedded in the outage management system;

conflict checking feature – embedded in the outage management system;

outage coordination for capacity exports;

outage coordination for generator-backed capacity import resources; and

IESO Reports – public reports published by the IESO.

Outage planning facilitation meetings – upon request by a market participant, but no more than once per quarter, the IESO may meet to discuss outages planned to start 6 months to 24 months from the current date that require broad sector coordination and will provide recommendations to the market participant following the meeting.

#### Undesirable Situations

- (MR Ch.5 ss.6.1.1 and 6.1.3)

Criteria – When assessing outage requests, the IESO will use the following general criteria to identify any undesirable situations the outage request may result in:

negative impacts on the reliability (security and/or adequacy) and/or operability of the IESO-controlled grid;

capacity and energy shortfalls;

material impact on the operation of the IESO-administered markets; and

periods wherein a number of high consequence outages have been planned coincidentally

Repositioning – Market participants may request to reposition their scheduled outages based on their priority date, to avoid these undesirable situations.

#### Outage Planning Guidelines

(MR Ch.5 ss.6.1.1 and 6.1.3)

Purpose – The IESO will issue confidential outage planning guidelines to facilitate the assessment of grid reliability. The outage planning guidelines will assist market participants to avoid undesirable situations when scheduling outages. The guidelines will provide the following information:

##### Transmission Group

Definition – Transmission Group is the category used to group associated transmission elements and/or generation facilities and/or electricity storage facilities, specified along with the relevant time frame. There are some groups with the same name succeeded by a number. These were created to account for all possible combinations of the elements within that group. For example, if the original Transmission Grouping was defined as Group A, for implementation it was broken down into Group A (1) and Group A (2) as shown below in Table 4-1:

Table 4-1: Transmission Groupings

| Transmission Grouping | Transmission Element | Threshold |  |  |
| --- | --- | --- | --- | --- |
| Group A | Line A/Line B | 1 |  | Original Group |
|  | Line C |  |  |  |
| Group A (1) | Line A | 1 |  | Implemented Groups |
|  | Line C |  |  |  |
| Group A (2) | Line B | 1 |  |  |
|  | Line C |  |  |  |

##### Time Frame

Definition – Time frame refers to the applicable seasonal time frame, specified with the transmission group name. Where not specified, the group will apply throughout the year. Table 4-2 defines seasonal time frames:

Table 4-2: Seasonal Time Frame

| Time Frame | From | To |
| --- | --- | --- |
| All season | 01-Jan | 31-Dec |
| Spring | 15-Mar | 14-May |
| Summer | 15-May | 14-Sep |
| Fall | 15-Sep | 14-Nov |
| Winter | 15-Nov | 14-Mar |

##### Element

Definition – Element refers to the specific piece of equipment within the group.

Note: The bus must be included in the outage request if all bus breakers are out of service. The line disconnect must be included in the outage request if all terminal breakers are out-of-service.

##### Threshold

Definition – Threshold refers to the number of elements from the list that are permitted out-of-service at one time.

Example – For example, a threshold of ‘2’ means only two elements from the list can be scheduled out-of-service at the same time without any conflict.

##### Reason

Definition – Reason refers to the phenomena causing the conflict. This is based on the IESO’s assessment of situations that could potentially:

compromise the reliability of the transmission system;

result in the inability to maintain the system within system operating limits using normal operating procedures; or

result in the inability to restore the transmission system to normal operating conditions following a respected contingency.

Example – For example, phenomena might comprise of pre- and post-contingency thermal concerns, pre- and post-contingency voltage concerns, pre- and post-contingency stability concerns, black start restoration paths, or resource constraints.

##### Distribution

Definition – Distribution refers to the list of market participants who will be notified of the outage planning guideline. The distribution list will only include those market participants that own or operate equipment in the transmission group.

Example – For example, in Table 4-3, all market participants that own or operate any section of Line X will be on the distribution list. Outages for equipment tapped off Line X would not be restricted and therefore, would not be on the distribution list.

Table 4-3: Sample Outage Planning Guideline

| Transmission Group | Transmission Elements | Threshold | Reason | Distribution |
| --- | --- | --- | --- | --- |
| Group 1 | Line X | 1 | Thermal concerns |  |
|  | Line Y |  |  |  |

Access – Market participants will be able to access the guideline at the IESO Reports webpage under Participant Reports. The IESO will periodically review the outage planning guideline and updates will be published as per the Baseline schedule.

#### Conflicting Constraint Codes

(MR Ch.5 ss.6.1.1 and 6.1.3)

Definition – Upon submission of outage requests, the outage management system will check outages for equipment with conflicting constraint codes for the same time period. For example, Generator A has an outage request with ‘ABNO’ constraint code that overlaps with another request for Generator A to be ‘OOS’.

Criteria – Outage requests are considered to be in conflict when all of the following are true:

the outage request priority codes are Forced, Forced Extended, Urgent, Planned or Opportunity;

the outage requests overlap for any length of time;

the outage requests have a status of Submitted, Study, Negotiate, At Risk, Advance Approved, or Implemented; and

the outage request periods share the same equipment and have constraint codes that are flagged to be in conflict with each other as shown in Table 4-4:

Table 4-4: Outage Request Constraint Code Conflicts

|  | OOS | IS | DRATE | HOLDOFF | MUSTRUN | BTCT | PROT OOS | BF PROT OOS | AVR/PSS OOS | ASP OOS | INFO | ABNO |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| OOS |  | X |  |  |  |  |  |  |  |  |  | X |
| IS | X |  |  |  |  |  |  |  |  |  |  | X |
| DRATE |  |  |  |  |  |  |  |  |  |  |  |  |
| HOLD OFF |  |  |  |  |  |  |  |  |  |  |  |  |
| MUST RUN |  |  |  |  |  |  |  |  |  |  |  | X |
| BTCT |  |  |  |  |  | X |  |  |  |  |  |  |
| PROT OOS |  |  |  |  |  |  | X |  |  |  |  |  |
| BF PROT OOS |  |  |  |  |  |  |  | X |  |  |  |  |
| AVR/PSS OOS |  |  |  |  |  |  |  |  | X |  |  |  |
| ASP OOS |  |  |  |  |  |  |  |  |  | X |  |  |
| INFO |  |  |  |  |  |  |  |  |  |  |  |  |
| ABNO | X | X |  |  | X |  |  |  |  |  |  | X |

Additional criteria – In addition to the conditions described above, outage requests that meet any of the following conditions will also be considered to be in conflict:

the outage request’s equipment are on the same undesirable outage combination; or

UFLS validation fails; or

outage requests with BF PROT OOS constraint codes are overlapping at the same stations.

Table 4-5: Constraint Code Conflict Example

| If… | Then… |
| --- | --- |
| Outages for Line 1 A PROT OOS and Line 1 B PROT OOS overlap | The outage management system will display a conflict |
| Line 1 A PROT OOS and Line 2 B PROT OOS overlap | The outage management system will NOT display a conflict |

#### Conflict Checking

(MR Ch.5 ss.6.1.1 and 6.1.3)

Tool interface – The outage planning guidelines and conflicting constraint codes are embedded in the outage management system. If a submitted outage request is in conflict with another outage based on these criteria, the tool will display:

an error message that the outage is in conflict;

ID number of the outage(s) it is in conflict with (details regarding the conflicting outage are classified as confidential information and will be visible to market participants based on viewership rights); and

requirement to provide a rationale for the conflict to be allowed (details on conflict rationale are provided below).

Rescheduling – Market participants may determine the planned times of the conflicting outage(s) (either via the outage ID number or by contacting the IESO) and reschedule the outage to avoid the conflict.

##### Conflict Rationale

Criteria – Outage requests having conflicts may be submitted as long as market participants provide a rationale for doing so. A complete rationale is required for the IESO to consider the outage – that is, for clearance the market participant must identify how the pieces of equipment are related, physical proximity, and the reason why other control actions are not available. Table 4-6 lists criteria for the IESO to consider outages based on conflict rationale.

Table 4-6: Criteria for Conflict Rationale Acceptance

| Advance Approval Process | Acceptable Conflict Rationale Description | Examples |
| --- | --- | --- |
| Quarterly Advance Approval process | Only non-discretionary rationale will be accepted | Clearance Degradation of protection or cooling Vacuum building outage |
| Weekly, Three-Day and One-Day Advance Approval processes | Discretionary rationale may be considered provided there is valid justification | Favourable Ambient Conditions/Short Duration: the reason for the outage conflict is for thermal concerns, but the outage is scheduled overnight during lower load conditions. Pre-contingency Control Actions: transfer load to alleviate thermal concerns or reconfigure transmission system so the contingency sheds load by configuration. Partial Equipment Outages: Situations when only certain sections of the line are being taken out-of-service as shown in the diagram below, here the path critical to the transfer of power is not interrupted. An example of a partial equipment outage is in Figure 4-1. Short Recalls: Conflicts for post-contingency concerns may be resolved by recalling the outage within 15 minutes. |
| Real-time process | Conflicts will only be considered for forced and urgent outages | Forced outage to equipment due to a situation that could potentially endanger the safety of any person, damage equipment, or violate any applicable law (e.g. environmental) |

Figure 4-1: Partial Equipment Outage Example

IESO evaluation – The IESO will evaluate submitted rationale on a case-by-case basis and determine whether to allow the conflict to proceed or require the market participant to reschedule.

Notice to market participants – If the rationale does not meet the criteria described above and is deemed insufficient, the IESO will notify the market participant to reschedule the outage.

#### IESO Reports

The IESO publishes near-term and long-term reports to assist market participants in scheduling their outages when they are more likely to receive approvals:

##### Near-Term Reports

((MR Ch. 5 ss.7.1.1 and 7.3.1)

Adequacy Reports and Transmission Facility All-in-Service Limits Reports and Transmission Facility Outage Limits Reports contain demand forecasts and assessments for Ontario and are published by the IESO for informational purposes. Refer to MM 7.2 for further details on these reports.

##### Long-Term Report

(MR Ch.5 ss.7.1.1.4 and 7.3.1.2)

As per the market rules, the IESO prepares and publishes demand forecast, and a security and adequacy assessment for an 18-month period, on a quarterly basis. Refer to MM 2.11 for further details on this report.

### Outage Coordination for Capacity Exports

(MR Ch.5 ss.6.4.4 and 6.4.13)

Contractual obligations – A Capacity Seller may have obligations with respect to the coordination of outages under applicable agreements with external control areas. Any such obligations are between the Capacity Seller and the external control area or capacity buyer, and are in addition to the obligations that the Capacity Seller has pursuant to the market rules and market manuals.

External control area outage review is independent of IESO review – The IESO will continue to review outage requests in accordance with this market manual. Any additional review of outages by the external control area pursuant to the applicable agreements is independent of the IESO’s review.

Outages to partially committed capacity – All outages and/or derates to a Capacity Resource that have partially committed capacity will be applied proportionally between capacity committed to the external control area and the IESO-administered markets. For example, in a scenario where a generator-backed capacity import resource commits 100 MW to the external control area and 50 MW to the IESO through a capacity obligation, and experiences a 30 MW derate, the derate would be applied according to the 100:50 ratio representative of the allocation of the committed capacity between the external control area and the IESO. The 30 MW derate would correspond to a respective 20 MW and 10 MW supply reduction in the external control area and the IESO, and could limit the transaction associated with the generator-backed capacity import resource to 40 MW. In this example, the generator-backed capacity import resource would submit a 10 MW derate (i.e. derate to 40 MW) to the IESO.

#### 4.3.1	Capacity Seller Requirement to Coordinate with Transmitters Prior to IESO Involvement

(MR Ch.5 ss.6.4.4A and 6.4.9.3)

Additional requirements – Refer to MM 13.1 ss.3: Capacity Seller Requirement to Coordinate with Transmitters for information and requirements relating to coordination with transmitters regarding outages when submitting a capacity export request and prior to a Commitment Period.

Risk of grid-incapability to Capacity Resource – Should a planned outage to a transmission facility arise whereby a Capacity Resource would be rendered Grid-incapable during a Commitment Period, the IESO may reject or revoke the planned outage provided certain conditions are met, including the Capacity Seller having demonstrated that it has made best efforts to work with the transmitter to reschedule the planned outage.

Best efforts – In order to demonstrate to the IESO that it has made best efforts pursuant to MR Ch.5 ss. 6.4.4A.3 or 6.4.9.3.2, a Capacity Seller must communicate with the applicable transmitter as described in MM 13.1 s.3 and as set out below. The following explains the general process that the Prospective Capacity Seller should follow with the transmitter during the Commitment Period to demonstrate to the IESO that reasonable efforts have been made to reschedule a planned outage should such circumstances arise:

Schedule a meeting (or multiple meetings, if necessary) in which it notifies the applicable transmitter of any capacity export commitments and determines if there are existing planned outages (unapproved or approved) that would render the Capacity Resource Grid-incapable at any time during the proposed Commitment Period.

Update the outage request (visible to the applicable transmitter) in the IESO’s CROW system submitted in accordance with MM 13.1 s.3 with an ‘Information’ priority code, indicating the details of any capacity export commitments.

Throughout the Commitment Period, continue to check with the transmitter by, among other things, monitoring the CROW system, to determine if there are any planned outages during the proposed Commitment Period that would render the Capacity Resource Grid-incapable.

Should there be planned outages during the proposed Commitment Period that would render a Capacity Resource Grid-incapable for, work with the transmitter to address the conflict, for instance:

The transmitter may agree to reschedule the planned outage.

The transmitter may accept the risk of potential rejection or revocation of the planned outage in the event that it is determined that the planned outage will, during the Commitment Period, pose an unacceptable risk of an adequacy shortfall to the external control area.

Whenever applicable, update the applicable outage request with the ‘Information’ priority code indicating any changes or new information, including the resolution of any conflicting outages that may arise.

#### 4.3.2	Capacity Seller Requirement to Coordinate with Transmitters Requiring IESO Involvement

- (MR Ch.5 ss.6.4.4A and 6.4.9.3)

Notice to IESO required – The Capacity Seller must notify the IESO where the external control area operator has determined that a transmitter’s planned outage that would render a Capacity Resource Grid-incapable would:

result in an unacceptable risk of an adequacy shortfall to the external control area; and

the transmitter and Capacity Seller are not able to come to an agreement to reschedule the planned outage.

Best efforts – The IESO will assess pursuant to MR Ch.5 ss.6.4.4A.3 or 6.4.9.3.2 whether the Capacity Seller has used its best efforts to reschedule the planned outage with the transmitter and whether any reliability concerns will arise if the transmitter’s planned outage is rejected or revoked.

Outages required for reliability – Examples of transmission outages necessary for reliability include, but are not limited to:

transmission outages that would prevent a future forced outage from occurring (e.g., a load supplied by a single transformer or line that would be forced out-of-service due to equipment concerns).

transmission outages that would leverage opportune generation and load profiles (e.g., matching outages with seasonal generational support).

transmission outages that would restore instantaneous protections and respective communication mediums.

Notice to Capacity Seller – If the IESO determines that the outage is for reliability purposes, the IESO will advise the Capacity Seller who may inform the external control area operator.

Rejection and revocation – If the IESO determines that reasonable efforts have been made and there is no reliability concern, the IESO may reject or revoke the planned outage pursuant to MR Ch.5 s.6.4. The IESO will not, pursuant to this section, recall outages to facilitate called capacity exports or reject or revoke forced outages or urgent outages, or outages that bottle a resource’s output.

### Outage Coordination for Generator-Backed Capacity Import Resources

(MR Ch.5 ss.6.4.1, 6.4.4 and 6.4.13; Ch.7 s.3.5.6)

Prior submission – Generator-backed capacity import resources are required to submit planned outage requests to the IESO for approval prior to submitting the outage request to the external control area operator.

Outages approved prior to capacity obligation – Where an outage request to a generator-backed capacity import resource has been previously approved by the external control area operator for a future obligation period for which the capacity auction has not yet been held, the capacity market participant shall submit a planned outage to the IESO for approval if they secure a capacity obligation in the relevant capacity auction. The planned outage request should be submitted as soon as practical after securing the capacity obligation, and shall be submitted prior to the start of the obligation period. If the outage is rejected by the IESO, the capacity market participant is required to reschedule the outage and resubmit the planned outage request to the IESO for approval. Once the IESO has approved the planned outage request, the capacity market participant shall then submit the outage request, including proof of IESO outage approval, to the external control area operator for approval.

Offers must reflect derated capacity – All outage requests should have the Constraint Code as a derate. All derates to a generator-backed capacity import resource, whether a planned outage or forced outage, shall be applied proportionally between the capacity committed to the IESO and the external control area. Import offers associated with the generator-backed capacity import resource shall reflect the derated capacity to the extent that such generator-backed capacity import resource has been de-rated below its capacity obligation.

Example – For example, in a scenario where a generator-backed capacity import resource commits 100 MW to the external control area and 50 MW to the IESO through a capacity obligation, and experiences a 30 MW derate, the derate would be applied according to the 100:50 ratio representative of the allocation of the committed capacity between the external control area and the IESO. The 30MW de-rate would correspond to a respective 20 MW and 10 MW supply reduction in the external control area and the IESO, and could limit the transaction associated with the generator-backed capacity import resource to 40 MW. In this example, the generator-backed capacity import resource would submit a 10 MW derate (i.e. derate to 40 MW) to the IESO.

Other boundary entity resource offers permitted – Although import offers associated with a generator-backed capacity import resource shall be placed on the applicable boundary entity resource for generator-backed capacity import resources, traders are not excluded from submitting import offers on other boundary entity resources.

External control area outages – In cases where there is a planned transmission outage within the external control area that would directly disconnect the resource from the external grid, when a capacity-backed transaction is scheduled, the IESO will not be required to resolve the conflict. The generator-backed capacity import resource shall work with the transmission owner and or the external control area balancing authority/reliability coordinator to reschedule the planned outage, as per the requirements set out in the applicable external control area’s rules and regulations. Any such obligations are between the generator-backed capacity import resource and the external control area, and are in addition to the obligations that the generator-backed capacity import resource has with the IESO pursuant to the market rules and market manuals.

Example codes – Table 4-7 provides example codes for generator-backed capacity import resources when submitting planned outage requests.

Table 4-7: Applicable Codes for Generator-backed Capacity Import Resources

| Priority Code | Constraint Code | Purpose Code |
| --- | --- | --- |
| Planned | DERATE | Other |

### Outage Submission

(MR Ch.5 ss.6.3.1 and 6.3.6)

Outage management system – Market participants submit outages through the outage management system and the IESO uses that tool to confirm receipt and communicate approval back to the market participant. Market participants access the outage management Application Programmatic Interface (API) either through:

the IESO’s web link located in the IESO Portal, or

their own outage management program.

Included information – Typically, an outage request will include the following information:

Table 4-8: Information Requirement during Outage Submission

| Field Name in the Tool | Information To Be Provided by Market Participants |
| --- | --- |
| Applicant | The market participant that is submitting the information. |
| Single Point of Contact (SPOC) | The request will identify a SPOC for the market participant, either an individual or a position, along with sufficient information to enable effective communication with that SPOC (such as phone, fax, or email). For market participants with direct input to the outage management system, contact information for responsible parties will be on file with the IESO. |
| Priority Code and Purpose Code | Each outage request must contain appropriate priority and purpose codes. Refer to sections 3.2 and 3.3 for more details. |
| Purpose Description | General information about the outage, such as a brief description of the purpose and specific requirements or information pertinent to the outage (for example “Loading levels for a generation facility test”). Any regulatory requirements for an outage must be included in this information. |
| Request Weekly AA | For non-critical or low impact equipment, indicate if the outage is submitted under the Weekly Advance Approval process. |
| Requested Equipment | Sufficient information must be provided to identify and describe, if required, the specific piece of equipment, using the equipment identification and location confirmed by the IESO in MM 1.5. |
| Planned Start and End Date/Time | The submission must include the requested start date, start time, end date and end time. |
| Maximum Recall Time | The submission must include recall time, which is the total amount of time that would be required to return the equipment to service upon a request by the IESO. Market participants may submit optional comments to the IESO to provide more information. |
| Recurrence | This information will describe the periodic nature of the outage, that is, whether the outage is continuous, continuous except for weekends, daily, etc. |
| Constraint Code | Each piece of equipment on the outage request must contain a constraint code to specify the equipment limitations. This will be based on the status of the equipment when the outage is implemented (for example: OOS, IS, MUSTRUN). Refer to section 3.4 for more details. |
| Equipment Description | General information about the equipment, such as a brief description of the status and condition of the equipment pertinent to the outage (for example “Generation resource unavailable for black start”). Any regulatory requirements for an outage must be included in this information. (Mandatory for constraint codes specified in Table 3-4 and equipment classes specified in Table B-1.) |
| MW Impact | Indicate the impact, if any, on real power resources which will result from the outage. This would be the direct impact associated with the specific piece of equipment rather than an indirect impact. |
| MVAR Impact | Indicate the impact, if any, on reactive power resources that will result from the outage. This would be the direct impact associated with the specific piece of equipment rather than an indirect impact. |
| Conflict rationale | This information will be used by the IESO to verify the importance of scheduling the outage in case of conflicts. Note: This field will not be visible to market participants with third party viewership. |
| Market participant to IESO Comments | Market participants shall use this section to notify the IESO of any additional information, including details of their assessment, associated outage requests, switching details, etc. Generation facilities and electricity storage facilities shall also use this section to notify the IESO of any intent to arrange for replacement energy in the form of imports (MR Ch.5 s.6.3.6). When these arrangements are finalized, market participants shall provide the following information: the MW amount and duration; the intertie zone or zones through which the replacement energy is intended to be scheduled, the boundary entity resource that shall submit the offers and schedule the replacement energy if dispatched by the IESO; and information regarding the e-Tag associated with the import, including a unique identifier, tag ID or tag format to be used. Refer to section 6 for details on arrangement of replacement energy. Note: This field will not be visible to market participants with only third party viewership access. |
| Low-impact Questions | Based on the information submitted, market participants may be required to answer a few low-impact questions. This is to determine if the outage is eligible for one-day AA, Auto AA, and/or FAA, as explained in sections 3.7.5, 3.7.6 and 3.7.7, respectively. Appendix C, Table C-1, Column D lists the questions that will be asked to market participants. |

### Outage Assessment

(MR Ch.5 s.6.4.4)

IESO assessment – The IESO assesses outage requests for their potential impact on the reliability and/or operability of the IESO-controlled grid with respect to the following:

reductions in system operating limits; interconnection reliability operating limits or changes in power transfers which encroach on a system operating limit;

will or is reasonably likely to have an adverse impact on the reliable operation of the IESO-controlled grid;

operating limits available and adequate monitoring tools available;

adequate system and area reserve;

adequate pre/post contingency assessment; voltage levels; islanding concerns; equipment limits and control actions;

adequate ancillary services requirements;

system (global) and local area adequacy – capacity and energy;

high-risk operating state, conservative operating state or emergency operating state conditions; and

- redundant supply facilities including station service supply and protection systems

Additional criteria – Refer to MM 7.4 for more details on the IESO’s reliability assessment. The IESO may provide details of their assessment under the ‘IESO to Market Participants Comments’ field in the outage management system.

Note: This field will not be visible to market participants with only third party viewership access.

#### 4.6.1	Market Participant Updates

(MR Ch.5 ss.6.3.1 and 6.4.13)

Revised requests – Market participants may update an outage request while it is being assessed by the IESO. Changes other than the purpose description or comments require notification to the IESO by telephone. The IESO will assess the impact of the change. Revised outage requests will be assessed within the original study period.

Table 4-9: Market Participant Outage Request Updates

| If the update is … | The IESO shall… |
| --- | --- |
| Insignificant, as defined in section 3.2.1 of this market manual | Allow the market participant to update the request. |
| Significant, as defined in section 3.2.1 of this market manual | Allow the market participant to update the request and revise the priority date. |

#### 4.6.2	Outage Assessment Outcomes

The following subsections describe the next steps and associated obligations based on the possible outcomes of the IESO’s assessment of outages.

##### Provide Advance Approval

(MR Ch.5 ss.6.4.3.3, 6.4.8 and 6.4.10)

Next steps – As per the timelines in section 3.7 of this market manual:

Table 4-10: Possible Next Steps after Providing Advance Approval

| Possible Next Step | Associated Obligations |
| --- | --- |
| Final Approval | On the day of the outage, market participants must contact the IESO Control Room via telephone when they are ready to proceed with the outage. The IESO will, in general, provide final approval to a planned outage unless it foresees an adverse reliability impact, based on ongoing security and adequacy assessments. When requesting final approval, market participants should give due consideration to any adjustments to: generation patterns; or injection patterns (for electricity storage facilities); or system configuration required by the IESO prior to removal of equipment from service and the time required to effect these adjustments (MR Ch.5 s.6.4.3.3). Outages that are eligible for FAA will be automatically granted Final Approval at the beginning of the planned start date of the outage. |
| Revocation | Market participants have the option of resubmitting or canceling the outage. The IESO will work with market participants to re-schedule the planned outage to a date and time at which the outage will not likely have an adverse impact on the reliability and/or operability of the IESO-controlled grid. Where practical, the IESO will consider date and time preferences of market participants when re-scheduling the outage (MR Ch.5 s.6.4.10). The original priority date is maintained if market participants resubmit the outage within five business days of being revoked (MR Ch.5 s.6.4.10). |
| Outage Start Delays | Market participants must inform the IESO if they expect their outage to be delayed from starting as scheduled and whether the delay is expected to result in a planned extension. Start of outage delayed by 30 minutes or less: Market participants must notify the IESO Control Room by telephone. Start of outage delayed by greater than 30 minutes: Market participants must notify the IESO Control Room by telephone and update their outage request. |
| Planned Extension | Market participants must submit requests for planned extensions as a new outage request. The new request must reference the outage ID of the on-going planned outage in the outage management system. The IESO will review planned extension requests on a reasonable effort basis if the outage request was scheduled to start and end on the same day. Otherwise the planned extension will be treated as a late submission and either rejected or revoked. The IESO will reject the request for planned extension if it is determined that the extension is likely to adversely impact the reliability and/or operability of the IESO-controlled grid or is likely to require the rescheduling, recall or revocation of a planned outage request previously submitted to the IESO (MR Ch.5 s.6.4.8). In such cases, market participants shall ensure the outage duration does not exceed the originally approved planned outage or the period as advised by the IESO when rejecting the outage request (MR Ch.5 s.6.4.8). |

##### 4.6.2.2	Negotiate to Reschedule

(MR Ch.5 s.6.4.17)

Table 4-11: Possible Next Steps after Negotiate to Reschedule

| Possible Next Step | Associated Obligations |
| --- | --- |
| Reschedule outage for advance approval | Market participants must reschedule the outage following discussions with the IESO. The priority date of the original outage request will be retained during resubmission if completed within study time frame. |
| Cancellation | Market participants must cancel the outage request in the outage management system. |
| Rejection (for outages submitted under the Weekly, Three-Day or One-Day Advance Approval processes) | The IESO will provide market participants with the reason for rejection, subject to applicable confidentiality restrictions. Market participants may submit a new outage request. Original priority date will be retained if resubmitted within five business days and it was the first time that the outage was rejected (MR Ch.5 s.6.4.17). If these conditions are not met, the resubmitted outage request will receive a new priority date. |
| ‘At Risk’ (for outages submitted under the Quarterly Advance Approval process) | The IESO will provide market participants with the reason for placing the outage ‘At Risk’, subject to applicable confidentiality restrictions. The IESO will review the outage during the next Quarterly, Weekly, Three-Day or One-Day assessment window, as explained in section 3.7.2. Market participants may choose to resubmit outages placed ‘At Risk.’ Refer to section 3.7.2 for criteria for retaining original priority for resubmitted outage requests. |

### Outage Implementation

(MR Ch.5 s.6.4B.1)

Communication with IESO control room – Outages that have received final advance approval from the IESO can be placed into implementation. Market participants are required to notify the IESO Control Room to confirm that the outage has commenced by providing actual start times through outage management system, unless otherwise determined by the IESO.

Table 4-12: Communication with the IESO Control Room

| If… | Then… |
| --- | --- |
| After implementation, the market participant wishes to adjust the actual start time of the outage | The market participant must call the IESO Control Room and request that the IESO clears their implementation and must provide the reason for the change. The IESO will assess the validity of the request and if approved, transition the outage to ‘Final Approved’ status which will delete the actual start time. The market participant must input the adjusted actual start time in the outage management system and transition the outage from ‘Final Approved’ to ‘Implemented’ status. |

#### 4.7.1	Planned and Forced Extensions

(MR Ch.5 s.6.3.4)

Forced extensions to planned outages – Market participants have the option of forced extensions, in cases where personnel safety or equipment damage may result. However, forced extensions for planned work will be reviewed for possible violations of the market rules. Forced extensions to planned or forced outages must be electronically updated in the outage management system by market participants and communicated via telephone to the IESO Control Room. If the forced extension is identified by 15:00 EST, one business day prior to the planned end time of the outage, market participants shall, on a reasonable effort basis, also communicate the forced extension to the IESO Market Forecasts & Integration department.

Planned extensions of planned outages – Planned extensions to planned outages must be submitted as new outage requests.

#### 4.7.2	Recall

(MR Ch.5 s.6.4.11)

Scope, reason, and compensation – Any time during implementation, the IESO may recall either the current period or the entire outage, based on sudden or unexpected impacts to the reliability and/or operability of the IESO-controlled grid. The IESO will provide affected market participants with the reason for the recall. Details regarding market participant compensation in cases of outage recall are provided in section 4.9.

Recall as last resort – Market participants will be expected to meet the recall times specified in the original submission for the planned outage. No outage will be recalled unless the IESO has revoked or rejected all other planned outages that have not yet started and which could eliminate the need to recall the outage already in progress.

Replacement energy – Generation resources and electricity storage resources have the option to arrange for replacement energy to preclude being recalled. Further details on replacement energy are provided in section 6.

#### 4.7.3	Suspension of Non-Urgent Maintenance or Switching

(MR Ch.5 s.2.5.2)

IESO authority – If the IESO-controlled grid is in a conservative operating state, the IESO may direct market participants to suspend any non-urgent maintenance or switching activities.

### Outage Completion

(MR Ch.5 s.6.4A)

Process for returning equipment to service – Market participants are required to:

Notify the IESO by telephone when either the current period or the entire planned or forced outage has been completed;

Request IESO approval by telephone to return equipment to service before doing so;

Receive IESO approval to return the equipment to service. The IESO will notify market participants at this time if they wish to direct the operation of equipment to return it to service; and

Notify the IESO when equipment that was the subject of a planned or forced outage has been fully restored to service by providing actual end times through the outage management system, unless otherwise determined by the IESO.

Table 4-13: Outage End Time Adjustment

| If… | Then… |
| --- | --- |
| After completion, the market participant wishes to adjust the actual end time of the outage | The market participant must call the IESO Control Room and request that the IESO clears their completion and must provide the reason for the change. The IESO will assess the validity of the request and if approved, transition the outage to ‘Implemented’ status which will delete the actual end time. The market participant must input the adjusted actual end time in the outage management system and transition the outage from ‘Implemented’ status to ‘Completed’ status. |

### Outage Compensation

(MR Ch.5 s.6.7)

Governing authority – MR Ch.5 s.6.7 governs eligibility for compensation for revoked or recalled outages.

Eligible expenses – Only out-of-pocket costs are eligible for compensation under MR Ch.5 s.6.7.2 of the market rules. These are sunk costs that are unrecoverable and will be incurred again by market participants in order to complete the outage. Items such as overtime costs and equipment rentals are eligible.

Study and coverage periods – The below subsections set out examples showing how the IESO will apply MR Ch.5 s.6.7 to study and coverage periods.

#### 4.9.1	Example A: Market Participant NOT Entitled to Compensation

As displayed in Figure 4-2, the outage is scheduled for May and receives quarterly advance approval in November. The IESO revokes quarterly approval in January. In this case, the market participant is not entitled to compensation because the revocation is done before the next quarterly study period ends in February.

Figure 4-2: Compensation Eligibility – Example A

#### 4.9.2	Example B: Market participant Entitled to Compensation

In this example, the outage is scheduled for May and the IESO revokes quarterly advance approval in March (i.e. after the next quarterly study period ends in February). Therefore, the market participant is entitled to compensation.

Figure 4-3: Compensation Eligibility – Example B

#### 4.9.3	Example C: Market Participant Entitled to Compensation

In this example, the outage is scheduled to start in March which is within the first three months of the quarterly coverage period, therefore even though the IESO revokes the outage before the end of the next quarterly study period in February, the market participant is entitled to compensation.

Figure 4-4: Compensation Eligibility – Example C

Opportunity costs excluded – Generation facilities or electricity storage facilities whose planned outages have advance approval revoked or are recalled are eligible for compensation even though they had successfully arranged for replacement energy. However, the generation facility or electricity storage facility will not be eligible for compensation for any lost opportunity costs associated with the import energy that was secured through the arranged replacement energy.

Submission – Claims for compensation must be submitted using the “Request for Outage Compensation” (IMO_FORM_1350) that is available on the IESO website, and substantiated by receipts or statements detailing each line item. These claims will be subject to audit and verification by the IESO.

– End of Section –

## Outage Reporting Requirements

This section outlines outage reporting requirements that are specific to certain classes of market participants when submitting outage requests to the IESO, unless granted exemption. Each sub-section provides sample priority, purpose and constraint codes that market participants may use when submitting outage requests via the outage management system. For detailed description of these codes, refer to sections 4.2, 4.3 and 4.4. Refer to section 4.6 for a mapping of these codes.

Note: The rules for submission, approval and determining priority as per market rules are applicable for all outage requests.

### Generation Facilities and Electricity Storage Facilities

- (MR Ch.5 ss.3.6.1 and 3.8.1)

Scope of obligation –  Aggregated generation resources and electricity storage resources are required to report forced outages, unit limitations, deratings, de-staffing and any change in status that affects the maximum output of a generation unit or electricity storage unit, the minimum load of a generation unit, or the availability of a generation unit or electricity storage unit to provide ancillary services such as regulation, operating reserve, voltage support, black start capability or must-run contracts.

Storage –  All other outage requests related to the electricity storage resource’s injection capability should follow the applicable generation unit permissions and requirements outlined in this market manual. An electricity storage resource wishing to report its inability to withdraw must update its dispatch data accordingly and submit outage requests as follows:

Table 5-1: Example Codes for Electricity Storage Resources when Unable to Withdraw

| Priority Code | Constraint Code | Purpose Code |
| --- | --- | --- |
| Planned | DRATE | Repair |

Note: This section is intended for the reporting of all outages with the exception of state of charge capability changes in real-time; for such changes refer to MM 4.1.

#### 5.1.1	Deratings

(MR Ch.5 ss.3.6.1 and 3.8.1; MR Ch.7 s.3.3.8)

Reporting requirements – All generation resource and electricity storage resource are required to report outages in the following circumstances:

any planned or forced material reduction in generation resource or electricty storage resource output that causes a derating equal to the greater 2% of rated output or 10 MW;

a component failure, operational limit or other circumstance that will cause the unit to trip if no control actions can be taken before the condition can be repaired as assessed by the generation facility or electricity storage facility; or

a new potential change in unit/plant condition that can cause the loss of multiple units at its facility based on its internal assessment/forecast.

Process for ramping down – A generation facility or electricity storage facility wishing to ramp down for a planned outage is required to follow either of the following methods:

submit and get approval for a planned outage request. The generation resource or electricity storage resource will be ramped down at the submitted ramp rate in advance of the hour in which the outage commences; or

submit derate requests electronically to reflect the capability of the generation resource or electricity storage resource as it ramps down.

Loading delays – Normal loading delays during a generation facility or electricity storage facility start-up are not considered a derating if the generation resource or electricity storage resource is able to ramp towards full load without significant holds. Where a generation resource or electricity storage resource must hold at a specific load for greater than 30 minutes during start-up, this should be considered a derating. The IESO will assess planned deratings required to support a generation resource or electricity storage resource ramp down or start-up on a reasonable effort basis.

Pseudo-units – Combined cycle generation facilities that elect to offer in to the market as a pseudo-unit (PSU) will submit derates and outages on the associated generation units.

Revising dispatch data for short-term outages and derates – A generation resource or electricity storage resource whose outage or derating results in a change of more than the lesser of 2% of rated output or 10 MW is not required to revise its offers pursuant to MR Ch.7 s.3.3.8 if the derating or outage is expected to last less than two hours. Where the market participant had altered the offer to reflect the capability of the resource, the IESO will permit a quantity change or new offer. This change should reflect the capability of the resource in the pre-dispatch schedule. Changes to offers in the mandatory and restricted window will not affect the current hour.

Submission – Market participants are required to use the DRATE or MUSTRUN constraint code when submitting outage requests, Table 5-2 provides an example:

Table 5-2: Example Codes when Submitting Planned Derate Requests

| Priority Code | Constraint Code | Purpose Code |
| --- | --- | --- |
| Planned | DRATE | Maintenance |

#### 5.1.2	Tests

(MR Ch.5 s.6.6.7; MR Ch.7 ss.2.2A and 2.2D)

Process – Generation facilities and electricity storage facilities may request approval to conduct tests during a planned or forced outage. In order for the outage requests and tests to not have conflicting time spans in the outage management system, the following procedure should be followed:

- Revise the end time of the original outage request to coincide with the start of the first test.

- Ensure the first test request has a start time that corresponds to the end time of the outage in the revised outage request.

- Create a second outage request to accommodate all the outage time required in the original outage request and has a start time corresponding to the end time of the first test request. The end time corresponds to the end time of the original outage request, or subsequent pairs of outage/test requests with matching start/end times to cover all the remaining tests as required.

Figure 5-1: Submitting Test Request during Outage

Treatment as commissioning facility – Where testing is extensive and is expected to continue for a minimum of two days, market participants may request that the IESO treat the generation facility or electricity storage facility as a commissioning generation facility or commissioning electricity storage facility (MR Ch.7 ss.2.2A and 2.2D respectively). Requests to be treated as a commissioning generation facility or commissioning electricity storage facility should be made to the IESO through the outage process and to Equipment Registration. Requests of this nature should be made with a minimum of six business days’ notice. Refer to section 5.1.3 for reporting details.

Hydroelectric resources within a compliance aggregate – For tests of hydroelectric generation facilities within a compliance aggregate, market participants must submit a test profile as part of the outage request. The aggregate will be offered to reflect the aggregate output during testing. The aggregate total generation will be maintained at the offer/dispatch level as the test generation facility loads or unloads.

Offers on aggregated resources – Market participants having aggregate units with one of the units being tested would offer, ensuring that the associated price is appropriate to be scheduled, the maximum achievable output for the aggregate, excluding the testing unit and compensate for testing by adjusting units within the aggregate. Non-aggregated generation facilities and non-aggregated electricity storage facilities are required to offer the full capability of the resource and use outage requests to derate the resource to the appropriate test level (MR Ch.5 s.6.6.7).

Suspension and reloading – Often generation facility and electricity storage facility tests are conducted where the test can be suspended and the generation resource or electricity storage resource is then capable of reloading. These tests are treated differently than generation resource and electricity storage resource deratings in that no outage for a derating is required, however market participants are required to submit an outage request in accordance with the submission deadlines outlined in section 3.7 of this market manual indicating the planned test quantities as described in the example below.

Offer price – For any hour in which a market participant’s generation facility or electricity storage facility is expected to undergo a test, market participants must submit an economical offer for the generation/injection that equals the expected hourly average energy delivery of that unit.

Table 5-3: Offer Price Test Example

| If expected generation is… | Then the offer submitted for the hour will be… |
| --- | --- |
| 250 MW for 20 minutes, 175 MW for 10 minutes, and 135 MW for 30 minutes | = 180 MW at an offer price that would ensure the unit is scheduled to deliver 180 MW 250*20 + 175*10 + 135*30 60 |

IESO intervention – However, since the unit is testing, it would not move to the dispatch target, and the IESO operator may have to intervene to adjust for the behaviour of the testing unit.

Storage – Electricity storage facilities wishing to undergo capability testing must submit an outage request outlining the test plan with respect to injection and withdrawal operations. The IESO shall review and coordinate real-time testing requirements including appropriate dispatch data submissions for the injection and withdrawal operation during testing.

Operating reserve market participation – Where the test is instantly recallable, generation facilities and electricity storage facilities are allowed to participate in the operating reserve market. This is acceptable as long as the market participant offers the energy as outlined above (and below) and if the market participant ensures that the operating reserve quantity offered each hour meets the following criteria:

(maximum energy expected to be provided during the hour) + (operating reserve quantity offered during the hour) = (maximum amount that the unit can provide that hour)

Using the example above:

Table 5-4: Operating Reserve Market Participation Example

| If… | The offer submitted for the hour will be… |
| --- | --- |
| Maximum generation per hour is 450 MW | 450 MW (maximum output during the hour) - 250 MW (maximum loading during the hour) = 200 MW of operating reserve at a price of the market participant’s choosing 180 MW at a price to ensure that unit is scheduled 200 to 270 MW of energy at a higher price. |

This energy offer would be scheduled if operating reserve is activated or if there are a shortage of resources that required the energy (at which time, the market participant would be expected to abandon the test to meet their operating reserve dispatch).

No eligibility for compensation – Generation facilities and electricity storage facilities whose test outages are immediately recallable and participate in the operating reserve market are not expected to submit for compensation costs. Rather, it is expected that offers for energy and operating reserve will reflect any compensation for interrupting the test.

Aggregate resources – For tests of aggregate generation resources and electricity storage resources with immediate recall, market participants must provide a test profile via an information request to the IESO. Market participants must offer the aggregate as per the energy they desire to run but would adjust loading of units within the aggregate to obtain the required test levels. Market participants must request approval to synchronize and desynchronize the test unit, but may change the test unit MWs as desired while maintaining the aggregate MWs as offered.

Purpose codes – Market participants are required to use the ‘Testing’ purpose code when submitting outage requests, Table 5-5 provides an example:

Table 5-5: Example Codes when Submitting Planned Testing Requests

| Priority Code | Constraint Code | Purpose Code |
| --- | --- | --- |
| Planned | IS | Testing |

#### 5.1.3	Commissioning Facilities

(MR Ch.7 ss.2.2A, 2.2A.5, 2.2D, 2.2D.5 and 2.3.2)

Treatment of commissioning facilities –

The generation resources that are commissioning within a commissioning generation facility shall be treated by the IESO as self-scheduling generation resources for dispatch purposes.

For its injections of energy, the IESO shall treat a commissioning electricity storage facility for dispatch purposes as a self-scheduling electricity storage resource.

For its withdrawals of energy, the IESO shall treat a commissioning electricity storage facility for dispatch purposes as the resource type for which it is seeking registration, with no requirement to submit bids to withdraw energy.

For settlement purposes, a commissioning resource will be settled by the IESO as the resource type for which it is seeking registration.

All commissioning facilities shall be treated by the IESO as a self-scheduling generation facility or a self-scheduling electricity storage facility for the purposes of outage coordination and shall follow the normal outage scheduling process (MR Ch.7 ss.2.2A.5 and 2.2D.5). The commissioning generation facility or commissioning electricity storage facility shall provide a detailed test plan including the following information, but not limited to:

the expected time of synchronizing to or desynchronizing from the IESO-controlled grid;

energy and reactive output levels and where applicable, levels of withdrawals;

the timing of, and ramp rates associated with, changes in energy and reactive output levels and where applicable, changes in levels of withdrawals;

run-back or trip tests for the commissioning generation facility or commissioning electricity storage facility; and

excitation and power system stabilizer (PSS) tests.

Flexibility and loading profile – The IESO will attempt to provide scheduling flexibility for commissioning generation facilities  and commissioning electricity storage facilities in the same manner as those generation facilities or electricity storage facilities  performing routine testing as per section 5.1.2. Market participants, whose generation units or electricity storage units with planned outages are returning to service from long-term outages, or are commissioning generation units or commissioning electricity storage units, shall provide the IESO with a loading profile before synchronization.

Security and adequacy assessments – The treatment of commissioning facilities in the IESO’s security and adequacy assessments depends on the type of commissioning being performed as follows:

- New generation facilities  and electricity storage facilities, or those returning from long-term outages (mothballing) will be treated as unavailable while commissioning for the purpose of calculating available capacity in the IESO’s adequacy assessments.

A planned outage request should be submitted by market participants that define first synchronization and the expected date of commercial operation.

For electricity storage resources, two planned outage requests must be submitted: one for the injections of energy (where the resource is registered as a dispatchable generation resource or as a self-scheduling generation resource) and the other for the withdraws of energy (where the resource is registered as a dispatchable load or as a price responsive load).

Market participants who do not have variable generation resources should submit, and keep up to date, the expected commissioning test plan (either via an outage request or other format as specified by the IESO) for the duration of the commissioning period. For electricity storage resources, this test plan should include both the injections and withdraws of energy.

Market participants who have variable generation resources, must submit, and keep up to date, the expected commissioning test plan via an outage request for the duration of the commissioning period.

Commissioning generation facilities that do not have variable generation resources should manage all commissioning activities, until commercial operation is declared, with the use of dispatch data as a self-scheduling generation facility. Dispatch data should reflect the most recent update to the commissioning test plan.

All commissioning electricity storage facilities should manage their commissioning activities with their planned outage request that outlines their commissioning test plans with respect to both their injections and their withdraws of energy. This should be accompanied by a self-schedule for the planned injection of energy into the grid. There is no requirement to submit bids, or any other dispatch data, to withdraw energy while commissioning. The self-schedule and planned outage request should reflect the most recent update to the commissioning test plan.

Commissioning generation facilities that have variable generation resources shall offer a forecast output as provided by the IESO.

- Existing generation facilities or electricity storage facilities that are commissioning for the purpose of testing new or modified equipment associated with the respective facility  will be treated as available for the purposes of calculating available capacity in the IESO’s adequacy assessments. In addition,

A planned outage request should be submitted by market participants that define the commissioning period.

While commissioning, market participants who do not have variable generation resources, must manage their injections of energy by the use of dispatch data as a self-scheduling generation facility or self-scheduling electricity storage facility . There is no requirement to submit dispatch data for withdrawals of energy for electricity storage resources, however details on withdrawals of energy must be contained in the planned outage request. Market participants who have variable generation resources, must manage their loading via planned outage requests and offer a forecast output, as provided by the IESO.

Planned outage requests are to be submitted for each stage of the commissioning period that reflects expected output.

Advance notice – For generation facilities and electricity storage facilities planning future commissioning activities, the IESO requires at least three months’ advance notice of these activities, including the expected synchronization date (MR Ch.7 ss.2.2A.5 and 2.2D.5). The expected synchronization date may be revised by market participants as required.

For generation facilities or electricity storage facilities initiating the commissioning process, the IESO requires a minimum of six business days’ notice (MR Ch.7 ss.2.2A and 2.2D). Any such registration for the purposes of commissioning tests shall expire on the completion of these tests.

Submitting dispatch data – To inject energy, a market participant shall submit self-schedules.  To withdraw energy, no submission of dispatch data is necessary.

Aggregate resources – Where the generation facility or electricity storage facility undergoing commissioning testing forms part of a compliance aggregate, the whole aggregate will be treated for dispatch purposes as a self-scheduling facility. The IESO may not approve these requests where the loss of operating reserve from the aggregate causes a reliability concern (MR Ch.7 s.2.3.2).

Deviations from submitted quantities – In the event that the commissioning resource needs to diverge from its submitted self-schedule dispatch data for any reason, the market participant should update the self-schedules outside the real-time market mandatory window as soon as possible. This change must also be reflected in the planned outage request by updating that planned outage with the revised test plan.

Where an electricity storage participant needs to diverge from their test plan by more than 20MW in its planned withdraws of energy, as per Appendix A, they should notify the IESO by updating their planned outage request along with the revised test plan as soon as possible, and before the real-time market mandatory window. Electricity storage participants who determine they cannot meet their test plans for state of charge reasons may reduce their quantities within the real-time market mandatory window as per MR.Ch.7 s.21.5.

Purpose codes – Market participants are required to use the ‘Commissioning’ purpose code when submitting outage requests, Table 5-6 provides an example:

Table 5-6: Example Codes for Commissioning Generation Facilities and Commissioning Electricity Storage Facilities

| Priority Code | Constraint Code | Purpose Code |
| --- | --- | --- |
| Planned | IS | Commissioning |

#### 5.1.4	Segregated Mode of Operation

(MR Ch.7 App.7.7 s.1.3)

Two different timelines – There are two sets of timing requirements for operating units in segregated mode of operation (SMO). The difference depends on whether an outage to a critical transmission element is required.

Classification of requests – The IESO will consider Requests for segregation as opportunity outages unless requested based on the one-day advance approval criteria. To meet the one-day advance criteria, SMO must be requested by 10:00 EST two business days ahead of the dispatch day. The Planned Start and End Date/Time must be on the same calendar date or the Maximum Recall on the outage is 15 minutes.

##### 5.1.4.1	SMO Requiring Outage of a Critical Transmission Element

Timing of requests – Requests for segregation that require an outage to a critical transmission element must be included in the day-ahead market and submitted by 08:00 EPT on the day prior to the dispatch day. The IESO will approve or reject the outage request no later than 10:00 EPT on the day prior to the dispatch day.

Timing and availability of cancellation or revision – Market participants may only cancel or revise requests for segregation that require an outage to a critical transmission element after 08:00 EPT on the day prior to the dispatch day to address a situation that may endanger the safety of any person, damage equipment, or violate any applicable law (SEAL).

Subsequent changes that do not require critical elements to be reconfigured – Once SMO has been approved, changes to the quantity of the export that will not require critical system elements to be reconfigured may be submitted up to two hours prior to the start of the change in real time.

Reconfiguration – Where a request for segregation will require transmission system elements to be reconfigured or removed from service, the IESO will notify the transmitter and enter an outage request in the outage management system to reflect this reconfiguration for the duration required to support the Request for Segregation.

##### 5.1.4.2	SMO Not Requiring Outage of a Critical Transmission Element

Timing of requests – Requests for segregation that do not require an outage to a critical transmission element may be submitted up to two hours prior to the start of the outage. Market participants who intend to have this request scheduled in the day-ahead market must submit their request no later than 09:00 EPT on the day prior to the dispatch day. The IESO will approve or reject the outage requests no later than 90 minutes prior to the implementation of the segregated mode of operation.

Timing and availability of cancellation and revision – Requests for segregation that do not require an outage to a critical transmission element can be cancelled at any time by the market participant and do not require conditions related to the safety of any person, damage to equipment, or violation of any applicable law (SEAL).

Submission process – Market participants use the outage process to submit Requests for Segregation. The IESO will approve or reject these requests based on security and adequacy impact assessments.

Notification by telephone – Along with submitting an outage request for the facilities that are intended to operate in segregated mode, market participants are required to notify the IESO by phone of the request for segregation. The IESO will assess any requests for segregation according to the expected resource adequacy and approved according to the outcome.

Timing of IESO decision – For generator requests for segregation or desegregation, the IESO will provide permission to the market participant to proceed, or reject the request, as soon as possible but not later than such time that allows the transmitter a minimum of 90 minutes to switch the equipment or facilities required to permit the implementation of the SMO.

Reconfiguration – Where a request for segregation will require transmission system elements to be reconfigured or removed from service, the IESO will enter an outage request in the outage management system to reflect this reconfiguration.  The outage will be entered for the duration required to support the request for segregation.

No compensation – Where a previously approved segregation request is revoked or segregation is terminated, no outage compensation will apply.

Required steps - When submitting a request for operation in segregated mode, generation facilities must:

Submit an outage request for their units for the duration of the segregated mode.

Submit a second outage request for the time required to ramp down the units to zero (to be submitted within the hour prior to the start of the first dispatch hour to which the segregated request pertains).

Maintain the offers for their generation resources for each dispatch hour in which these resources will or are intended to operate in segregated mode of operation.

Notify the IESO by phone that the Request for Segregation was submitted (MR Ch.7 App.7.7 s.1.3.5).

Returning from segregation – When units are returning from segregated mode of operation, generation facilities must ensure:

The outage for their units ends at the same time the units are to be reconnected to the IESO-controlled grid.

Valid offers are in the IESO systems for these units, for the hour they will be returning from segregated mode of operation. When submitting their offers, generation facilities must respect the short notice submission criteria as specified in the market rules.

If necessary, to zero their revenue meter while in segregated mode of operation in order to be removed from the IESO’s settlements process.

Notify the IESO by phone of the request for desegregation (MR Ch.7 App.7  ss.1.3.3 and 1.3.4).

Purpose codes – Market participants are required to use the ‘Segregated Mode of Operation’ purpose code when submitting outage requests, Table 5-7 provides an example:

Table 5-7: Example Codes When Requesting Planned Segregated Mode of Operation

| Priority Code | Constraint Code | Purpose Code |
| --- | --- | --- |
| Planned | OOS | Segregated Mode of Operation (SMO) |

### 5.2	Loads

#### 5.2.1	Dispatchable Loads

(MR Ch.5 s.3.5.1)

Required submissions – Any planned outages, forced outages, restrictions, deratings or changes in configuration of power system auxiliaries and transmission facilities operated at 50 kV or higher that form part of, or are, connected to the IESO-controlled grid and which affect the operation of the dispatchable load, must be submitted to the IESO. These outages shall be coordinated and submitted by the owner of the facility required to be on outage. For outages to the transmission element to which the dispatchable load is connected, the transmitter will apply for the outage and coordinate with the customer.

Example – Table 5-8 provides example codes for dispatchable loads when submitting planned outage requests:

Table 5-8: Example Codes for Planned Outages to Dispatchable Loads

| Priority Code | Constraint Code | Purpose Code |
| --- | --- | --- |
| Planned | DRATE | Repair |

#### 5.2.2	Connected Wholesale Customers

(MR Ch.5 s.3.5.1)

Informational purposes – For wholesale customers that are required to submit information about the planned shutdown in advance, approval from the IESO is not required as the outage is supplied for informational purposes only.

Priority, constraint, and purpose codes – Market participants are required to use the codes in Table 5-9 when submitting outage requests:

Table 5-9: Applicable Codes for Wholesale Customers

| Priority Code | Constraint Code | Purpose Code |
| --- | --- | --- |
| Information | INFO | Other |

#### 5.2.3	Distributors and Transmitters

- (MR Ch.5 ss.3.4.1, 3.7.1 and 10.2.3)

Application – For greater clarity, the outage reporting obligations under MR Ch.5 s.3.7.1 include distributors with embedded loads or generation that are not registered with the IESO.

Direct communication for demand management – The actual decrease in MW reduction of demand achieved through any demand control actions must be communicated directly to the IESO Control Room by telephone at the time that the reduction is implemented.

Example – Table 5-10 provides example codes for distributors and transmitters when submitting planned outage requests:

Table 5-10: Example Codes for Distributors and Transmitters

| Priority Code | Constraint Code | Purpose Code |
| --- | --- | --- |
| Planned | OOS | Switching |

#### 5.2.4	Outages and Non-Performance Event Management for Capacity Auction Resources

This sub-section outlines outage management requirements for capacity auction resources with capacity obligations.

##### 5.2.4.1	Dispatchable Capacity Auction Resources (including Capacity Imports)

(MR Ch.7 ss.19.5.5, 19.5.6, 19.7.5, 19.7.6, 19.9.5, 19.9B5, 19.9B.6, 19.11.5 and 19.11.6)

Priority, constraint, and purpose codes – Demand response resources are required to use the codes in Table 5-11 when submitting outage requests:

Table 5-11: Applicable Codes for Demand Response Resources

| Priority Code | Constraint Code | Purpose Code |
| --- | --- | --- |
| Information | INFO | Other |

##### 5.2.4.2	Non-Performance Event Management for Hourly Demand Response Resources

(MR Ch.7 ss.19.4.9 – 19.4.10)

###### HDR Resources with a Capacity Obligation Acquired through the Capacity Auction

Record requirements – Capacity market participants with an hourly demand response (HDR) resource that has a capacity obligation are required to maintain records of all reductions to demand response capacity of 5 MW or greater during an obligation period. The IESO may request the records for a period of one year from the end of the associated commitment period. If requested, these records must be provided to the IESO by email by the deadline defined by the IESO. The records must contain the following details:

description of event

resource name

trade date

hours of reduced capacity

registered capacity of the HDR resource

amount of reduction (MW) to demand response capacity

action taken to manage energy bid

Notice to IESO – For any quantity, capacity market participants whose HDR resources received an activation report with an activation notice on the dispatch day are required to notify the IESO Control Room by telephone as soon as practical if they are unable to provide their activation amount.

Timing of dispatch data revisions – Capacity market participants are required to update bids for HDR resources pursuant to MR Ch.7 s.19.4.10 for any reduction to demand response capacity occurring on the day prior to the dispatch day or dispatch day to reflect the reduced demand response capacity.

Contributor outage submission – Capacity market participants with an HDR resource who wish to submit a contributor outage should do so in accordance with the procedures outlined in MM 12.

### 5.3	All Market Participants

(MR Ch.5 ss.3.2.1 and 3.4.1)

Reliability of individual customer connections – As per market rules and the operating agreements between transmitters and the IESO, the IESO’s outage assessments will not include assessments of impacts to the reliability of individual customer connections. Assessing the reliability of individual customer connections is the role of the transmitter, who is required to:

coordinate outages impacting customer connections; and

recommend changes to transmission configuration and or recall or cancel outages to secure the supply to customer connections during a high-risk operating state or a conservative operating state.

#### 5.3.1	Monitoring and Control Equipment

- (MR Ch.4 ss.7.7.1 – 7.7.4)

Example – Table 5-12 provides example codes for market participants when submitting planned outage requests to monitoring and control equipment:

Table 5-12: Example Codes for Planned Outages to Monitoring and Control Equipment

| Priority Code | Constraint Code | Purpose Code |
| --- | --- | --- |
| Planned | OOS | Other |

#### 5.3.2	System Tests

- (MR Ch.5 s.6.6)

Test coordinator – Where required, arrangements shall be made for a Test Coordinator to be appointed. The name and role of the Test Coordinator shall be specified in the outage submission. The duties of the Test Coordinator include:

defer, limit, or stop the System Test due to unfavorable system conditions or test results;

monitor test conditions in the area involved; and

act as a communicator, and other roles as agreed upon in the outage submission.

Additional outages included in submission – If the outage submission involves additional outages or safety code procedures, the requestor shall ensure that outage requests are submitted by the appropriate market participant(s).

Exclusions – Examples of requirements that will not be considered power system tests and should be arranged in the normal manner for outages include:

routine generation unit and electricity storage unit rejections;

routine protection and control maintenance and testing;

routine commissioning tests; and

Work or testing on hydraulic waterways and storage.

Purpose codes – Market participants are required to use the ‘Testing’ purpose code when submitting outage requests, Table 5-13 provides an example:

Table 5-13: Example Codes When Submitting Planned System Test Requests

| Priority Code | Constraint Code | Purpose Code |
| --- | --- | --- |
| Planned | IS | Testing |

#### 5.3.3	Testing of Ancillary Services

(MR Ch.4 App.4.2; MR Ch.5 s.4.9)

Timing and scheduling – Tests must be successfully completed prior to entering into a contracted ancillary services contract, for a resource providing regulation or black start services, and at least annually thereafter throughout the contract period. Tests shall be arranged and scheduled at a time mutually agreeable to both the ancillary service provider and the IESO in accordance with the outage scheduling processes outlined in this market manual.

Standards and procedures – Performance standards and testing procedures are prescribed in the “IESO – Ancillary Service Provider (ASP) Agreements for Procurement of Certified Black Start Facilities.” Schedule 2 of this Agreement stipulates the required black start performance standards, with Schedule 3 articulating the required testing procedures. MR Ch.4 App.4.2 governs performance standards for contracted reactive support and voltage control.

#### 5.3.4	Testing Operating Reserve Providers

(MR Ch.5 ss.4.9-4.10)

Test assessment – The IESO will assess market participants’ compliance with a test operating reserve dispatch instruction issued in accordance with MR Ch.5 s.4.9.2 according to the relevant operating reserve offer submission data. For the purposes of this manual, a failure to meet an operating reserve target during an operating reserve activation (ORA) will also be deemed as a test failure.

Special requirements and coordination – If dispatchable load facilities providing operating reserve identify special testing requirements, the IESO will coordinate testing within the first week of the market participant’s acceptance in the market as an operating reserve provider, or as soon as possible. Subsequent testing will occur on a periodic basis.

Unannounced tests –  Operating reserve testing is the responsibility of the IESO and is conducted by the control room operators (CROs). The CROs will implement unannounced tests pursuant to MR Ch.5 s.4.9.2 taking into account any resources with poor past performance that require additional testing.

Aggregated resources – If operating reserve testing is implemented on a resource that is part of an aggregate, compliance will be assessed on the output of the aggregate.

Note:	If there is non-compliance to actual reserve activations, the following approach will be used with respect to removing offers.

Table 5-14: Implementing and Assessing Reserve Tests

| If a market participant… | The IESO will… |
| --- | --- |
| Fails an initial reserve test or an ORA, (i.e., fails to meet dispatch target within prescribed time [10 or 30 minutes]) | - (At IESO discretion) direct the market participant to remove its reserve offers on the resource for the remainder of that day and the next day. Allow these changes within the two-hour mandatory window. Retest the unit, normally within a week after it submits reserve offers again. |
| Fails their first retest of the reserve test or an ORA, (i.e., fails to meet dispatch target within prescribed time [10 or 30 minutes]) | - Direct the market participant to remove its reserve offers on the resource for one week. Allow these changes within the two-hour mandatory window. Retest the unit, normally within a week after it submits reserve offers again. |
| Fails their second retest of the reserve test or an ORA, (i.e., fails to meet dispatch target within prescribed time [10 or 30 minutes]) | - Direct the market participant to remove its reserve offers on the resource indefinitely. Allow these changes within the two-hour mandatory window. Initiate follow-up with the involved market participant. As a result of this follow-up, a decision will be made as to whether the facility should be removed from the reserve market, and the circumstances for allowing the return to the reserve market. |
| Fails a reserve test because of an unforeseen forced outage or equipment limitation, and Is NOT a dispatchable load | Request the market participant to submit an outage to derate or force the equipment out-of-service. |
| Fails a reserve test because of an unforeseen forced outage or equipment limitation, and Is a dispatchable load | - Request the market participant to change its energy bid to reflect the derate or force the equipment out-of-service. Request the dispatchable load to remove its reserve offers, as the DSO cannot handle derates on dispatchable loads. (Once the forced outage condition has been repaired) allow the market participant to resubmit its reserve offers within the two-hour mandatory window. |

#### 5.3.5	Hold-offs

(MR Ch.5 ss.3.4.1.3 – 3.4.1.4)

Definition – Hold-offs are restrictions in the use of transmission lines to facilitate maintenance activities. Automatic reclosure is blocked and manual reclosure is restricted until contact is made with the hold-off party. Single and multiple element hold-offs may be granted Auto AA or FAA.

Constraint codes – Market participants are required to use the ‘HOLDOFF’ constraint code when submitting outage requests, Table 5-15 provides an example:

Table 5-15: Example Codes When Submitting Planned Hold-off Requests

| Priority Code | Constraint Code | Purpose Code |
| --- | --- | --- |
| Planned | HOLDOFF | Other |

#### 5.3.6	New and Replacement Facilities

- (MR Ch.5 s.6.4A)

Submission prior to energization or return to service – Market participants are required to report an outage prior to:

energization of any new facility:

energization of any new resource equipment thay may impact the reliability and/or operability of the IESO-controlled grid; or

returning into service replacements of any existing facility equipment impactive on the reliability and/or operability of the IESO-controlled grid.

Not eligible for one-day advance approval – Outage submissions requesting the energization of new facilities are not eligible to be requested for the One-day Advance Approval process, as the timelines of this process do not allow for the IESO to adequately assess the impact of the new facilities. In addition, market participants must ensure that all applicable facility registration requirements are complete, prior to the commencement of any such outage.

Example codes – Table 5-16 provides example codes for market participants when submitting planned outage requests to new and replacement resources:

Table 5-16: Example Codes When Requesting Planned Outages to New and Replacement Resources

| Priority Code | Constraint Code | Purpose Code |
| --- | --- | --- |
| Planned | MUSTRUN | Replacement |

– End of Section –

## Replacement Energy to Support Planned Outages

(MR Ch.3 s.6.6.10A; MR Ch.5 ss.6.3.6 and 6.3.9; MR Ch.7 ss.7.5.8A – 7.5.8B)

Criteria for determining the minimum quantity – Where, based on the IESO’s assessment of security and adequacy, the IESO permits the generation facility or electricity storage facility to arrange for replacement energy, the IESO shall determine the minimum MW amount to be arranged as replacement energy pursuant to MR Ch.5 s.6.3.9 based on the following:

The MW amount of replacement energy shall be no less than the forecast shortfall from the Adequacy Report as determined prior to advance approval being provided or based on more current information in the Adequacy Report;

Where the shortfall occurs beyond the period of 14 days, the IESO will identify the weeks of shortfall and the maximum amount to be arranged for these weeks based on the Day 15 to 34 Adequacy Reports or the Reliability Outlook report prior to advance approval being provided. The generation facility or electricity storage facility should wait until the shortfall is detailed in an Adequacy Report covering the Day 0 to 14 period, to identify the specific shortfall hours and amounts to finalize the amount of replacement energy. In any case, replacement energy must be finalized by the generation facility or electricity storage facility no later than 16:00 EST three business days prior to the commencement of the shortfall week(s); and

Shall not exceed the amount of energy that was agreed to at the time of finalization or 500 MW.

Submission process and required information – Generation facilities and electricity storage facilities shall convey to the IESO their arrangement for replacement energy by way of the comments field in the outage management system with the following information:

the intertie where offers will be submitted;

a unique identifier associated with the e-Tag or a unique e-Tag ID;

the MW amount to be offered and the duration of the offers (if finalized), and the registered market participant associated with a registered facility that is a boundary entity resource that shall submit the offers.

Day-ahead market submission and compliance enforcement – Once the IESO has approved or provided additional direction to the generation facility or electricity storage facility specifying the details of the replacement energy import offers, the generation facility or electricity storage facility whose outage was approved is obligated to ensure that these offers are submitted to the IESO for the day-ahead market. The boundary entity resource who shall provide replacement energy and that is subject to dispatch instructions received from the IESO, is subject to the failed intertie transaction rules in MR Ch.7 ss.7.5.8A and 7.5.8B and MR Ch.3 s.6.6.10A and any compliance guidelines and enforcement.

Intertie scheduling – The IESO may specify the intertie(s) where the replacement energy is to be scheduled in order to meet reliability requirements.

Criteria for determining duration of offers – Pursuant to MR Ch.5 s.6.3.9, the IESO shall determine the duration of offers necessary to support the outage based on the following:

reliability and/or operability impacts on the IESO-controlled grid;

forecast capabilities of the interconnections for the duration of the planned outage; and

forecast adequacy of neighbouring jurisdictions for the duration of the planned outage.

Submission requirements – The duration that replacement energy offers to be submitted to the IESO as part of the pre-dispatch scheduling process shall be:

no less than the period of the shortfall hours applied to each day of the week(s) of the shortfall; and

no greater than the total duration of the outage.

Example – For example, a generation facility or electricity storage facility requests a 300 MW outage over three weeks. A shortfall of 100 MW is identified on the Tuesday of the second week between 9:00 AM to 10:00 AM EST. The IESO will notify the market participant of the shortfall and reject the outage.

In order to get approval for the outage request, the market participant must agree to arrange for replacement energy from 9:00 AM to 10:00 AM EST (shortfall hours) for all days of the second week.

However, the market participant may wait until 16:00 EST three business days prior to the commencement of the second week of the outage, to finalize the amount and hours of replacement energy. By waiting to finalize the amount, the generation facility or electricity storage facility accepts that the purchase amount may increase from the amount forecast when the outage was given advance approval.

Figure 6-1: Purchase of Replacement Energy – Requirements and Confirmation Timeline

Figure 6-2: Outage Submission Timeline Example

Figure 6-2 depicts the submission timeline of three outages creating a shortfall totalling 300 MW. Unit B and Unit C are offered the opportunity to purchase replacement energy.

Table 6-1: Replacement Energy Purchase

| If… | Then… |
| --- | --- |
| Unit B chooses to purchase replacement energy | Unit B is required to purchase 200 MW, to clear shortfall caused by forced outage plus its outage. Unit C is required to purchase 100 MW |
| Unit B chooses not to purchase replacement energy | Outage to Unit B is rejected. Shortfall is reduced to 200 MW Unit C is required to purchase 200 MW, to clear shortfall caused by forced outage plus its outage. |

Priority assessment – Generation facilities and electricity storage facilities that have arranged replacement energy to support their planned outage are assessed based on priority according to the following:

When requesting outage approvals during periods of adequacy concerns, generation facilities  or electricity storage facilities who have arranged for replacement energy to support a planned outage will have a higher priority than outages that have chosen not to arrange replacement energy (and would otherwise be rejected).

Where more than one generation facility and/or electricity storage facility has indicated that they wish to arrange for replacement energy and, because of security or adequacy concerns, advance approval cannot be given to all such generation facilities and/or electricity storage facilities, the generation facility or electricity storage facility with an earlier priority date will be given priority.

Figure 6-3: Precedence of Outages Based on Purchase of Replacement Energy

Where a generation facility  or electricity storage facility is identified to be at risk after the replacement energy confirmation timeline but before the advance approval timeline as detailed in section 3.7, and then confirms the intent to arrange replacement energy before the advance approval timeline, the generation facility  or electricity storage facility shall maintain its priority date relative to outages that confirmed replacement energy before the confirmation timeline.

Where a generation facility  has to be revoked or recalled due to energy shortfalls identified after the advance approval or final approval was granted, precedence will be given based on the priority date, regardless of whether the approval is based on arranging replacement energy.

Where a generation facility or electricity storage facility indicates that they intend to arrange for replacement energy and they do not have priority date precedence over other generation facilities  or electricity storage facilities who may elect to arrange for replacement energy they will be notified that they may not be eligible. A final decision regarding eligibility cannot be made until the outage submission deadline. In this situation, it would be prudent for market participants without priority date precedence to wait until the submission deadline before arranging replacement energy.

– End of Section –

## Dispute Resolution

- (MR Ch.3 s.2)

Application of dispute resolution process to outage management decisions –  The IESO or an Applicant may initiate the Dispute Resolution process in accordance with MR Ch.3 s.2 if either believes the circumstances warrant such action. Specifically, market participants may dispute any decision of the IESO related to outage management, such as rejection of an outage submission, revocation or recall of an approved outage, or denial of outage compensation.

No stay of obligations pending decision – Market participants must continue to follow the direction of the IESO until such time as the Dispute Resolution panel renders a decision.

– End of Section –

## Outage Reporting Requirements

Outages must be coordinated with the IESO, and reported to the IESO, for any of the following facility group elements:

###### Transmission systems operated at voltages of 100 kV or more:

All element outages must be reported to the IESO.

###### Transmission systems operated at voltages less than 100 kV:

Removal of step-down transformers with a low-side voltage less than 100 kV

Involve the unloading of step-down transformers or their individual windings

Require paralleling or separation of buses via operation of bus tie breaker

Result in a load transfer of 20 MW or greater between step-down transformer stations

Adversely affect a generation facility or dispatchable load or electricity storage facility

###### Transmission or distribution reactive elements:

15 MVAR or greater in areas electrically south of Essa TS in Barrie

10 MVAR or greater in areas electrically north of Essa TS in Barrie

Synchronous Condensers and Static VAR Compensators (SVCs)

###### Power system auxiliaries:

Control systems designed to dynamically respond to system conditions such as:

Power system stabilizers (PSSs)

Automatic voltage regulation (AVR)

Operating aids such as:

Circuit auto-reclosure schemes

Voltage reduction facilities

Underfrequency load shedding (ULFS) facilities

Primary or backup protection systems designed to detect and isolate failed or faulted elements

Breaker failure protection

Breaker trip coil test

Remedial action schemes (RAS) that detect identified system conditions and take corrective action such as:

Combined generation facility, or electricity storage facility, load rejection schemes

Reactor tripping schemes

Communication facilities such as:

SCADA

RTUs, ICCP links or telemetry facilities for display of quantities

Market participant dispatch tools and facilities

Communication facilities such as voice, data and protection tone communications

Switchyard auxiliaries such as:

AC and DC station services

Supervisory control facilities or Control Room bench-boards

Multi-breaker air supply systems including compressor plants and cable cooling systems

###### Non-registered facilities or non-registered embedded facilities:

Result in a change of more than 20 MW in demand or supply in an hour from what is typical for that hour (i.e. large industrial customers that periodically shut down plants for maintenance or holidays)

###### Dispatchable load resources/ Wholesale customers/electricity storage resources registered to withdraw (dispatchable and self-scheduling):

Result in changes of more than 20 MW in demand or supply in an hour from what is typical for that hour.

###### Distributors and transmitters:

Result in changes of more than 20 MW in demand or supply in an hour from what is typical for that hour.

Demand control actions, including demand management, voltage reductions and disconnections.

###### Generation resources or electricity storage resources registered to inject energy:

All generation resources or electricity storage resources

Segregated mode of operation (SMO)

Available but not operating (ABNO)

Deratings:

derating equal to the greater of 2% of rated output or 10 MW

holds at a specific load for >30 minutes during start-up

Affects the maximum output or minimum load of a generation unit or electricity storage unit

A component failure, operational limit or other circumstance that will cause the unit to trip

Plant auxiliaries that affect more than a single generation resource or electricity storage unit, or aggregate of generation resources or electricity storage units where the loss of an additional element results in multiple unit/aggregate shutdowns within 48 hours such as:

service air or instrument air

boiler feed pumps

station service

Affects the availability to provide ancillary services such as:

automatic generation control (AGC)

voltage support

black start service

###### Testing:

All tests described in section 5.3.2: System Tests

Testing of generation units or electricity storage units, including:

in-service or commissioning tests

testing of derated units at levels above the derated levels

testing of units currently on outage

tests of facilities providing ancillary services

###### All Equipment:

Hold-off

Energization:

energization of any new facility; or

energization of any new facility equipment impactive on the reliability and/or operability of the IESO-controlled grid; or

returning into service replacements of any existing facility equipment impactive on the reliability and/or operability of the IESO-controlled grid.

– End of Appendix –

## Equipment Classes and Applicable Constraint Codes

Table B-1: Applicable Constraint Code per Equipment Class

| Constraint Code |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Equipment Class | OOS | IS | DRATE | MUSTRUN | HOLDOFF | AVR/PSS OOS | ASP OOS | PROT OOS | BF PROT OOS | BTCT | INFO | ABNO |
| Line | x | x |  |  | x |  |  | x |  |  | x |  |
| Line Section | x | x |  |  | x |  |  | x |  |  | x |  |
| Breaker | x | x |  |  |  |  |  |  | x | x | x |  |
| Disconnect Switch | x | x |  |  |  |  |  |  |  |  | x |  |
| Bus | x | x |  |  |  |  |  | x |  |  | x |  |
| Transformer | x | x |  |  |  |  |  | x |  |  | x |  |
| Reactor | x | x | x |  |  |  |  | x |  |  | x |  |
| Capacitor | x | x | x |  |  |  |  | x |  |  | x |  |
| SVC | x | x | x | x |  |  |  | x |  |  | x |  |
| Converter | x | x | x | x |  |  |  | x |  |  | x |  |
| Filter | x | x | x |  |  |  |  | x |  |  | x |  |
| Phase Shifter | x | x |  |  |  |  |  | x |  |  | x |  |
| Voltage Regulator | x | x |  |  |  |  |  | x |  |  | x |  |
| UFLS Relay | x | x |  |  |  |  |  |  |  |  | x |  |
| Synchronous Condenser | x | x | x | x |  |  |  | x |  |  | x |  |
| Generation Facility, Electricity Storage Facility | x | x | x | x |  | x | x | x |  |  | x | x |
| Load | x | x | x | x |  |  | x | x |  |  | x |  |
| AC/DC Station Service | x | x |  |  |  |  |  |  |  |  | x |  |
| SPS19 | x | x |  |  |  |  |  |  |  |  | x |  |
| Tone Communication Channels19 | x | x |  |  |  |  |  |  |  |  | x |  |
| RTU/ICCP/HUB Equipment19 | x | x |  |  |  |  |  |  |  |  | x |  |
| Other Communication Equipment19 | x | x |  |  |  |  |  |  |  |  | x |  |
| Other Miscellaneous Equipment19 | x | x |  |  |  |  |  |  |  |  | x |  |

– End of Appendix –

## Criteria for One-Day Advance Approval, Auto AA and FAA

Planned outage requests containing only low-impact equipment must be submitted for one-day advance approval. Outage requests containing eligible equipment, with no conflicting outage requests (refer to section 4.2 for outage conflicts) and that satisfy low-impact criteria may be eligible to receive auto advance approval (Auto AA) (i.e. automatically transition to Advance Approved status on submission) and in some cases may also receive final approval in advance (FAA). The eligibility criteria for one-day advance approval, Auto AA and FAA are described in the table below.

Table C-1: Criteria for One-Day Advance Approval, Auto AA and FAA

| A Outage Type | B Equipment Class | C Constraint Code | D Low-impact Attributes | E Additional Conditions | F One-Day Advance Approval | H Auto AA | I FAA |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Generator outage or Electricity storage facility outage | Generation facility or Electricity storage facility | OOS, IS, DRATE, MUST RUN |  | Planned Start and End Date/Time are in the same day or Maximum Recall is 15 minutes or less | Y | N | N |
| Available But Not Operating | Generation facility or Electricity storage facility | ABNO |  | Priority Code = Information | N | Y | N |
| Automatic Voltage Regulation (AVR) or Power System Stabilizer (PSS) | Generation facility or Electricity storage facility | AVR/PSS OOS | Only a Loss of Redundancy?” = YES (Answer) |  | Y | Y | Y |
| Ancillary Services | Generation facility, Load or Electricity facility | ASP OOS |  | Planned Start and End Date/Time are in the same day or Maximum Recall is 15 minutes or less | Y | N | N |
| Primary protections | Line, Line section, Generation facility, or Electricity storage facility, Bus, Transformer, Reactor, Capacitor, SVC, Phase shifter, Voltage regulator, Synchronous Condenser, Converter, Filter, Load | PROT OOS | “Only a Loss of Redundancy?” = YES (Answer) | Maximum Recall is 15 minutes or less | Y | Y | Y |
|  |  |  |  | Maximum Recall is greater than 15 minutes | Y | N | Y |
| Holdoffs | Line, Line section | HOLDOFF |  |  | Y | Y | Y |
| Breaker failure protections | Breaker | BF PROT OOS |  |  | Y | N | N |
|  |  |  | ”Adjacent breakers OOS?” = NO (Answer) AND “Only a Loss of Redundancy?” = YES (Answer) ELSE, IF Question: “Only a Loss of Redundancy?” = NO (Answer) THEN “CTs on both sides of the breaker?” = YES (Answer) | Only one piece of Equipment is on the Outage Request Continuous and ≤ 4 hours in duration No overlapping BF PROT OOS outages at the same station | Y | Y | N |
| Breaker trip coil tests | Breaker | BTCT |  |  | Y | N | N |
| AC/DC station service | AC/DC Station Service | OOS | “Only a Loss of Redundancy?” = YES (Answer) “Does the SS supply Cooling to any equipment on the ICG?” = YES (Answer) | Maximum Recall is 15 minutes or less | Y | N | N |
|  |  | OOS | “Only a Loss of Redundancy?” = YES (Answer) “Does the SS supply Cooling to any equipment on the ICG?” = NO (Answer) | Maximum Recall is 15 minutes or less | Y | Y | Y |
|  |  | IS |  | Maximum Recall is 15 minutes or less | Y | N | N |
| Tone communication channels | Tone Communication Channels | OOS | Only a Loss of Redundancy?” = YES (Answer) “RTU or HUB Affected?” = YES (Answer) | Maximum Recall is 15 minutes or less | Y | N | N |
|  |  | OOS | Only a Loss of Redundancy?” = YES (Answer) “RTU or HUB Affected?” = NO (Answer) | Maximum Recall is 15 minutes or less | Y | Y | Y |
|  |  | IS |  | Maximum Recall is 15 minutes or less | Y | N | N |
| Radial lines | Transmission circuit | OOS, IS, DRATE |  | Facility Class = 3 (Low-impact) | Y | Y | N |
| Transmission facilities operated at voltages < 100 kV | Breaker, Bus, Disconnect Switch, Transformer, Load | OOS, IS, DRATE |  | Facility Class = 3 (Low-impact) | Y | Y | N |
| LV reactive devices | Capacitor, Reactor | OOS |  | Facility Class = 3 (Low-impact) | Y | N | N |
| UFLS equipment | UFLS Relay | OOS |  | Facility Class = 3 (Low-impact) UFLS Validation Threshold passes (i.e. Sum UFLS Area Outages < UFLS Area Outage Margin) | Y | Y | Y |
| Special Protection Scheme | SPS | OOS | Only a Loss of Redundancy?” = YES (Answer) | Maximum Recall is 15 minutes or less | Y | N | N |
|  |  | IS |  | Maximum Recall is 15 minutes or less | Y | N | N |
| RTU/ICCP/HUB Equipment | RTU/ICCP/HUB Equipment | OOS | Only a Loss of Redundancy?” = YES (Answer) | Maximum Recall is 15 minutes or less | Y | N | N |
|  |  | IS |  | Maximum Recall is 15 minutes or less | Y | N | N |
| Other Equipment | Other Communication Equipment, Other Miscellaneous Equipment | OOS | Only a Loss of Redundancy?” = YES (Answer) | Maximum Recall is 15 minutes or less | Y | N | Y |
|  |  | IS |  | Maximum Recall is 15 minutes or less | Y | N | N |

– End of Appendix –

List of Acronyms

| Acronym | Term |
| --- | --- |
| ABNO | available but not operating |
| AGC | automatic generation control |
| ASP OOS | ancillary service out-of-service |
| Auto AA | auto advance approval |
| AVR | automatic voltage regulation |
| AVR/PSS OOS | automatic voltage regulation or power system stabilizer out-of-service |
| BA | balancing authority |
| BF PROT OOS | breaker fail protection out-of-service |
| BTCT | breaker trip coil test |
| CRO | control room operator |
| DAM | day-ahead market |
| DRATE | derated to |
| DSO | Dispatch Scheduling Optimizer |
| EPT | Eastern Prevailing Time |
| EST | Eastern Standard Time |
| FAA | final approval in advance |
| HDR | hourly demand response |
| HOLDOFF | hold off |
| ICCP | Inter-Control Centre Communications Protocol |
| INFO | information |
| IS | in-service |
| kV | kilovolt |
| LV | low voltage |
| MUSTRUN | must run at |
| MVA | megavolt-amp |
| MVAR | megavolt-amp reactive |
| MW | megawatt |
| NERC | North American Electric Reliability Corporation |
| NPCC | Northeast Power Coordinating Council |
| OOS | out-of-service |
| ORA | operating reserve activation |
| PROT OOS | protection out-of-service |
| PSS | power system stabilizer |
| RC | reliability coordinator |
| RTU | remote terminal unit |
| SMO | segregated mode of operation |
| SPS | special protection system |
| SVC | static VAR compensators |
| TS | transmission station |
| UFLS | underfrequency load shedding |
| VAR | volt-amp reactive |

– End of Section –

References

| Document ID | Document Title |
| --- | --- |
| RUL-6 to RUL-24 | Market Rules for the Ontario Electricity Market |
| MAN-108 | Market Manual 1.5: Market Registration Procedures |
| MAN-132 | Market Manual 2.1: Dispute Resolution |
| MAN-133 | Market Manual 2.2: Exemption Application and Assessment |
| MAN-136 | Market Manual 2.6: Treatment of Compliance Issues |
| MAN-137 | Market Manual 2.7: Treatment of Market Surveillance Issues |
| MAN-140 | Market Manual 2.11: Reliability Outlook and Related Information Requirements |
| MAN-110 | Market Manual 4.2: Operation of the Day-Ahead Market |
| MAN-124 | Market Manual 7.4: IESO-Controlled Grid Operating Policies |
| MAN-125 | Market Manual 12.0: Capacity Auctions |
| MAN-168 | Market Manual 13.1: Capacity Export Requests |
| N/A | Electricity Act, 1998 |
| IESO_TPL_0020 | IESO – Ancillary Service Provider (ASP) Agreement for Procurement of Certified Black Start Facilities |
| GDE-259 | Outage Coordination and Scheduling System (OCSS) CROW Web Client User Guide |

– End of Document –

Refer to section 3.7.5 for submission timelines for outage requests to critical and non-critical equipment with low-impact attributes.

Outage period level date/time refers to the date/times of the individual outage periods on the Details tab, not limited to the overall outage date/times.

While the ‘Must Run At’ and the ‘Derated To’ codes represent different limitations, the downstream software process at the IESO’s end will consider both values to mean the maximum capability for the duration of the outage request.

Market participants are required to input a description of the equipment when using this constraint code.

Refer to section 3.7.5 for submission timelines for outage requests to critical and non-critical equipment with low-impact attributes

Statutory holidays and weekend days that precede a business day are included in that business day (i.e. Saturday, Sunday and Monday equal one business day).

Statutory holidays and weekend days that precede a business day are included in that business day (i.e. Saturday, Sunday and Monday equal one business day).

Capitalized terms in this section are defined in MM 13.1 App A: Glossary of Capacity Export Terms.

To setup Third Party Viewership in CROW which makes outage requests visible to the applicable transmitter, the IESO Equipment Registration Specialist (ERS) must follow the steps outlined in the Online IESO Guide for all Contract Roles.

The resource is operating to a reduced maximum generation output due to constraints resulting from transmission element outages. This does not include constraints that limit the resource to 0 MW output.

Refer to the “Outage Management System CROW OCSS Web Client User Guide” for detailed instructions on how to submit an outage request.

The submission of the outage request will fulfill the obligations with respect to the submission of dispatch data as set out in MR Ch.7 App.7.7.

Discretion may be applied in determining whether or not to direct a market participant to remove its reserve offers after a failed activation. The following may be taken into consideration:

- System conditions may exist where available operating reserve is particularly limited (e.g., freshet, tight supply conditions). Removal of reserve offers may lead to potential shortfall.

- A resource that failed to meet the reserve target within the required time may have faced legitimate circumstances that led to the failed activation. If these circumstances have been, or are expected to be rectified, then future activation of reserve is expected to be met without failure.

For the purposes of outage replacement energy, week is defined as weekdays (Monday to Friday excluding holidays). Where shortfalls occur on a weekend or holiday, the IESO will identify this requirement to the generation facility or electricity storage facility and the generation facility or electricity storage facility will be required to arrange for replacement energy to cover these shortfalls.

Facilities that form part of or are connected to the IESO-controlled grid and used for the purpose of transmitting or distributing electricity. These facilities may be owned by a transmitter, wholesale customer, distributor or generator.

Where multiple facilities involve logic that require those facilities be operated together (i.e., both a switch and a breaker are arranged in series and the switch cannot be operated without first opening the breaker), it is only necessary to report on one of those facilities.

The following power system auxiliaries are excluded from outage reporting:

- Switchyard auxiliaries that do not affect, or the loss of an additional element that does not affect, the operation of the IESO-controlled grid or the operation or capability of components of the IESO-controlled grid.

- Step-down transformer station low voltage bus protections and low voltage reactive resource protections (capacitors), unless they cause unavailability of the component and/or a reconfiguration of the IESO-controlled grid.

- Feeder protections and feeder breaker auto-reclosures, unless they create a load transfer during system tests, or restrict access to the IESO-administered markets of embedded facilities.

- Planned visual inspection or measurements of DC back-up power equipment causing no impact to functionality.

- Planned loss of redundancy to telecommunications 48 V DC back-up power equipment battery for testing or DC monitoring sensor replacement/repair with staff onsite, recall of 15 minutes or less, and not impacting functionality of the backup power supply.

- Planned loss of redundancy to power system 125/250 V DC back-up power equipment battery for testing with staff onsite, recall of 15 minutes or less, and not impacting functionality of the back-up power supply.

- Planned outage to one back-up power equipment battery charger with recall of 15 minutes or less and not impacting sustained functionality of the back-up power supply.

If the facility is not registered with the IESO, this responsibility falls on the market participants (i.e. transmission customers for the facility).

Market participants are required to input a description of the equipment for this equipment class, in the outage management system.