POLICY

PUBLIC

Market Manual 7: System Operations

# Part 7.4: IESO-Controlled Grid Operating Policies

Issue 2.1

This market manual provides policy statements for reliable operation of the IESO-controlled grid.

MAN-124

September 9, 2026

Document Change History

| Issue | Reason for Issue | Date |
| --- | --- | --- |
| Refer to Issue 41.0 (IMP_POL_0002) for changes prior to Market Transition. |  |  |
| 1.0 | Market Transition | November 11, 2024 |
| 2.0 | Issue released for Baseline 54.1. | December 3, 2025 |
| 2.1 | Issue released for Baseline 56.0. | September 9, 2026 |

Related Documents

| Document ID | Document Title |
| --- | --- |
| MAN-121 | Market Manual 7.1: IESO-Controlled Grid Operating Procedures |

Table of Contents

Table of Contents	i

List of Figures	v

List of Tables	v

Table of Changes	vi

Market Manuals	viii

Market Manual Conventions	viii

1	Introduction	1

1.1	Purpose	1

1.2	Hierarchy	1

1.3	Scope	2

1.4	Contact Information	3

2	Reliability	4

2.1	Principles	4

2.2	Communications	4

2.2.1	Policies	4

2.3	Outage Management	4

2.3.1	Principles	4

2.3.2	Policy	5

2.4	IESO-Controlled Grid Operating States	5

2.4.1	Principles	5

2.4.2	Normal Operating State	6

2.4.3	High-Risk Operating State	7

2.4.4	Conservative Operating State	7

2.4.5	Emergency Operating State	7

2.5	Degraded Transmission Equipment Performance	8

2.6	Islanding	9

2.7	Grid Control Actions	10

2.7.1	Principles	10

2.7.2	Readiness Programs	10

2.7.3	Network Configuration Change Request	10

2.7.4	Control Actions to Increase Transfer Capability	11

2.7.5	Voltage Control	12

2.7.6	Remedial Action Schemes	12

2.7.7	Voltage Reductions	13

2.7.8	Load Shedding	14

2.7.9	Station Service	15

3	Adequacy	16

3.1	Principles	16

3.2	Resource and Transmission Adequacy	16

3.3	Operating Reserve Policy	17

3.4	Area Reserve for Load Security	17

4	System Security	19

4.1	Principles	19

4.2	Methodology for Deriving System Operating Limits	19

4.3	System Security and Modelling Criteria	21

4.3.1	Principles	21

4.3.2	Study Conditions and System Model	21

4.3.3	Load Representation	22

4.3.4	Thermal	22

4.3.5	Pre-contingency Voltage Range	23

4.3.6	Post-contingency Voltage Range	24

4.3.7	Voltage Stability	25

4.3.8	Transient Stability	26

4.3.9	Small Signal Stability	27

4.3.10	Transient Voltage Response	28

4.3.11	Automatic Reclosure	29

4.3.12	Manual Reclosure	31

4.4	Frequency Regulation	31

4.4.1	Automatic Under Frequency Load Shedding	31

4.5	Restoration of System Security	32

4.5.1	Principles	32

4.5.2	Policies	32

Appendix A:	Recognized Contingencies	34

A.1	Group 1 – Contingencies	34

A.2	Group 2 – Contingencies	35

A.3	Group 3 – Contingencies	35

Appendix B:	Load and Generation Rejection and Generation Runback Selection Criteria	37

B.1	Load Rejection (L/R) Selections	37

B.2	Generation Rejection Selections	38

B.3	Generation Runback Selections	38

Appendix C:	RAS Restrictions during High-Risk Operating State	39

Appendix D:	Special Considerations for Inverter-Based Resources	41

D.1	Minimum Short Circuit Ratio	41

D.2	Resonant Circuit Configurations	42

List of Acronyms	43

References	44

List of Figures

Figure 4-1: Typical Power-Voltage Curves	26

List of Tables

Table 4-1: Pre-Contingency Voltage Limits	24

Table 4-2: Post-Contingency Voltage Range	25

Table 4-3: Acceptable Damping Factors	28

Table C-1: RAS Restrictions during High-Risk Operating State	39

Table of Changes

| Reference | Description of Change |
| --- | --- |
| Appendix A.1.1 | - Updated item (ii) to remove inconsistency between NPCC Directory #1 (Table 3) and MM7.4 Appendix A.1.1 regarding what constitutes exclusion for double-circuit contingency. |

Market Manuals

Market manuals set out procedural and administrative details with respect to market rule requirements. Where there is a conflict between the requirements described in a market manual or appended document, and those within the market rules, the market rules shall prevail.

Market Manual Conventions

The standard conventions followed for market manuals are as follows:

the word 'shall' denotes a mandatory requirement;

references to market rule sections and sub-sections may be appreviated in accordance with the following representative format: ‘MR Ch.1 ss.1.1-1.2’  (i.e. market rules, Chapter 1, sections 1.1 to 1.2).

references to market manual sections and sub-sections may be appreviated in accordance with the following representative format: ‘MM 1.5 ss.1.1-1.2’  (i.e. market manual 1.5, sections 1.1 to 1.2).

internal references to sections and sub-sections within this manual take the representative format: ‘sections 1.1 – 1.2’

terms and acronyms used in this market manual in its appended documents that are italicized have the meanings ascribed thereto in MR Ch.11; and

data fields are identified in all capitals;

– End of Section –

## Introduction

### Purpose

This market manual contains IESO policies for reliable operation of the IESO-controlled grid (ICG). These policies are intended to:

provide guidance for the development of IESO procedures;

provide guidance to IESO operating staff when confronted with an operational situation that is not addressed in an operating procedure or a market rule; and

help market participants meet their obligations to the IESO in the operating time horizon.

To the extent practicable, the IESO will use available market mechanisms to direct reliable operation of the IESO-controlled grid. Where the IESO determines such mechanisms are unable to achieve reliable operation, it will take actions in accordance with the policies contained in this market manual.

These policies apply to the IESO in its role to fulfill its legislated objects to direct the operation and maintain the reliability of IESO-controlled grid and to establish and enforce criteria and standards related to the reliability of the integrated power system.

Operating policies are applied to facilities connected to the IESO-controlled grid.

Procedural details necessary to implement these policies are outside of the scope of this market manual. These details shall be found in the applicable market manual of the MM 7 series.

### Hierarchy

Operating policies shall conform to the Electricity Act 1998, market rules, NERC reliability standards and NPCC directories. When the interpretation of an IESO operating policy is in question, IESO staff shall select the interpretation most consistent with the market rules. When the proper interpretation of a NERC standard is in question, IESO staff shall select the interpretation most consistent with the purpose of the standard and NERC’s objects to maintain the minimum level of reliability. When the proper interpretation of NPCC criteria is in question, IESO staff shall select the interpretation most consistent with NPCC’s reliability objects.

The operating policies of this market manual are built on the foundation that Ontario’s power system is planned and designed in such a way as to satisfy the Ontario Resource and Transmission Assessment Criteria (ORTAC). Where existing equipment is insufficient to satisfy ORTAC criteria, special practices shall be documented in operating instructions and shall be followed until the required equipment is in operation. Special practices may include, but not limited to, voluntary demand management operating procedures, interim operating procedures that form part of a market rule exemption plan, interim operating procedures that form part of a NERC or NPCC corrective action plan.

In case of a discrepancy between this market manual and another manual in the MM 7 series, the policies of this market manual shall apply. In case of discrepancy between this document and a more stringent reliability standard, the reliability standard shall apply.

### Scope

This market manual supplements the following market rules:

MR Ch.1 s.3.1.1: Market Objective

MR Ch.4 App.4.1: IESO-Controlled Grid Performance Standards

MR Ch.4 App.4.3: Requirements for Connected Wholesale Customers and Distributors Connected to the IESO-Controlled Grid

MR Ch.4 App.4.4: Transmitter Requirements

MR Ch.5 s.1.2.1

MR Ch.5 s.2.2: Normal Operating State

MR Ch.5 s.2.3: Emergency Operating State

MR Ch.5 s.2.4: High-Risk Operating State

MR Ch.5 s.2.5: Conservative Operating State

MR Ch.5 s.3.2: Obligations of the IESO

MR Ch.5 s.3.4.1.4

MR Ch.5 s.3.4.1.5

MR Ch.5 s.3.6.1.6

MR Ch.5 s.4.5: Operating Reserve

MR Ch.5 s.4.6: Reactive Support and Voltage Control

MR Ch.5 s.4.9: Auditing and Testing of Ancillary Services

MR Ch.5 s.5.1.2

MR Ch.5 s.5.2.1

MR Ch.5 s.5.2.2

MR Ch.5 s.5.2.4

MR Ch.5 s.5.2.5

MR Ch.5 s.5.2.6

MR Ch.5 s.5.3.2

MR Ch.5 s.5.8: Operation Under an Emergency Operating State

MR Ch.5 s.5.9: Operation Under a High-Risk Operating State

MR Ch.5 s.5.9A: Operation Under a Conservative Operating State

MR Ch.5 s.6.4: Submission of Outage Schedules and IESO Approval of Outage Schedules

MR Ch.5 s.6.5: Information

MR Ch.5 s.7.7.7: Advisory Notices

MR Ch.5 s.8.2: Responsibilities of the IESO

MR Ch.5 s.10.2: Demand Control Initiated by a Market Participant

MR Ch.5 s.10.3: Demand Control Initiated by the IESO in an Emergency Operating State

MR Ch.5 s.10.4: Under-Frequency Load Shedding

### Contact Information

Changes to this market manual are managed via the IESO Change Management process. Stakeholders are encouraged to participate in the evolution of this market manual via this process.

To contact the IESO, you can email IESO Customer Relations at customer.relations@IESO.ca or use telephone or mail. Telephone numbers and the mailing address can be found on the IESO website . IESO Customer Relations staff will respond as soon as possible.

– End of Section –

## Reliability

### Principles

(MR Ch.5 ss.1.2.1, 3.2.1 and 3.2.2)

The IESO-controlled grid shall operate at a level of reliability such that the loss of a major portion of the power system (or unintentional separation of a major portion of the power system) will not result from reasonably foreseeable contingencies. This level of reliability is achieved by operating the IESO-controlled grid to meet adequacy criteria for anticipated demand, system security criteria for specified contingencies, and re-preparation criteria for restoring reliability following contingencies.

### Communications

#### Policies

(MR Ch.5 s.3.2.2)

IESO communication procedures shall comply with NERC reliability standards and NPCC directories related to communications. IESO requirements for communications are published in MM 7.1.

### Outage Management

#### Principles

(MR Ch.5 ss.3.2.2 and 6.4)

Criteria for outage approval– When assessing proposed outages of market participant registered facilities and associated equipment, the IESO shall base outage approval solely on maintaining reliable operation (including overall adequacy and operability) of the IESO-controlled grid. The IESO shall reject, revoke, or recall an outage if it presents a risk to the reliable operation of the IESO-controlled grid.

No customer-specific reliability requirements – Reliability standards do not impose an absolute requirement to maintain a continuous supply of electricity to any specific customer.

#### Policy

(MR Ch.5 ss.3.2.1, 3.2.2, 6.4 and 6.5)

IESO outage coordination within Ontario – The IESO shall deal fairly and appropriately with market participants, and comply with the applicable market rules and market manuals. The IESO will provide market participants with timely and accurate information regarding the IESO-controlled grid to facilitate market participant coordination of outages and provide mechanisms to resolve outage conflicts.

IESO outage coordination outside of Ontario – The IESO shall coordinate outages to equipment external to Ontario with authorities in neighbouring jurisdictions to meet NERC and NPCC obligations, and to satisfy IESO operating agreements with interconnected neighbours.

Transmitter coordination of customer connection outages – The IESO will NOT coordinate outages to individual customer connections. This obligation rests with the associated transmitter.

Switching configurations for less than 15 minutes – For switching configurations expected to last not more than 15 minutes, the only system security criteria that will be observed are:

equipment loading shall be within pre-contingency ratings supplied by asset owners; and

transfers shall be restricted to prevent pre-contingency voltage collapse.

- RAS arming, where available and practical, may be utilized during short duration switching periods to provide added system security beyond what is required by this policy, subject to restrictions listed in Appendix C: RAS Restrictions during High-Risk Operating State.

Additional provisions – The IESO publishes and maintains a market manual for outage management of facilities and equipment connected to the IESO-controlled grid, or which may affect the operation of the IESO-controlled grid. Refer to MM 7.3.

### IESO-Controlled Grid Operating States

#### Principles

(MR Ch.5 ss.1.2.1, 2.2, 2.3, 2.4, 2.5, 3.2.1 and 3.2.2)

Normal, conservative, high-risk, and emergency operating states – The IESO operates under a set of grid operating states based on system conditions and the IESO’s ability to monitor the IESO-controlled grid. The IESO-controlled grid has four operating states: the normal operating state, conservative operating state, high-risk operating state (including safe posture), and emergency operating state. In addition to the operating states, there is system restoration, which occurs immediately following a contingency that results in loss of load, cascading outages, islanding, etc.

Under certain operating conditions (e.g. adverse weather or equipment-related problems), the probability of experiencing certain contingencies increases. The IESO may temporarily and selectively increase the level of system security to improve reliability during a high-risk operating state.

Under stressed conditions (e.g. extreme hot or cold temperatures, anticipating energy or capacity deficiencies, or outages to IESO market or system applications that impact system security), the IESO will seek to minimize potential risks to the IESO-controlled grid or enhance grid resiliency in anticipation of (and after the declaration of) a conservative operating state. The conservative operating state is available to the IESO to help prevent an emergency operating state. Under critical conditions (e.g. experiencing energy or capacity deficiencies, or a security emergency), load shedding may be required. The IESO strives to mitigate or avoid load shedding when in an emergency operating state by maintaining a variety of control actions to be taken in anticipation of (and after the declaration of) an emergency operating state. Refer to the Emergency Operating State Control Actions (EOSCA) list in MM 7.1 App.B.

In high-risk operating states, conservative operating states, and emergency operating states, IESO control actions to maintain system security are more likely to be taken compared to during a normal operating state. These actions are structured to:

preserve system reliability; and

restore normal operation of IESO-administered markets as soon as practicable (MR Ch.5 s.2).

Mitigating impacts to the IESO-administered markets – The IESO will strive to mitigate adverse effects on IESO-administered markets, while at the same time observing the mutual protection and assistance provisions contained in agreements between the IESO and other reliability coordinators and balancing authorities.

#### Normal Operating State

(MR Ch.5 s.2.2)

In a normal operating state, the IESO will supply all non-dispatchable loads and price responsive loads while operating to normal condition limits.

The IESO shall direct market participants to act or to refrain from acting so as to maintain the IESO-controlled grid in a normal operating state (MR Ch.5 s.2.2). The IESO will also act or refrain from acting where doing otherwise is likely to lead to a high-risk or emergency operating state (MR Ch.5 ss.2.3.2, 2.4.2 and 5.1.2.6).

#### High-Risk Operating State

(MR Ch.5 ss.2.4 and 5.9)

In a high-risk operating state, the IESO will temporarily and selectively increase the level of system security by applying high-risk operating limits. The IESO will take actions such as rejection, revocation, or recall of equipment and facility outages when necessary to:

maintain the level of system security required during a high-risk operating state; and

allow, after a recognized contingency, the IESO to re-establish an acceptable level of system security and to re-prepare the IESO-controlled grid within the time permitted by reliability standards.

The conditions under which a high-risk operating state may be declared (along with related policy implementation details) can be found in MM 7.1.

#### Conservative Operating State

(MR Ch.5 ss.2.5 and 5.9A)

The IESO-controlled grid can be operated in a conservative operating state in response to a reliability concern to help prevent an emergency operating state. In a conservative operating state, the IESO may reject, suspend or revoke equipment and facility outages to minimize any potential risks to the IESO-controlled grid that could occur from non-urgent/routine work or switching of equipment. The IESO may also take actions to commit additional resources or recall equipment and resource outages to enhance grid resiliency. Under a conservative operating state, the IESO-controlled grid will be operated within equipment and security limits established for a normal operating state.

For IT-related outages related to the IESO-administered markets and/or system applications or tools that affect system security, the IESO may also take actions such as requesting market participants or neighbouring control area operators to monitor the IESO-controlled grid or interties, respectively, on behalf of the IESO. In addition, market participants may need to implement manual workarounds to fulfill their obligations (e.g. receive and execute verbal dispatch instructions).

The conditions under which a conservative operating state may be declared can be found in MM 7.1.

#### Emergency Operating State

(MR Ch.5 ss.2.3, 5.8 and 10.3)

The IESO shall not plan to operate the IESO-controlled grid in an emergency operating state pre-contingency, including when considering planned outages.

The IESO strives to mitigate or avoid load shedding when in an emergency operating state by publishing and maintaining a hierarchy of control actions to be taken in anticipation of and after the declaration of an emergency operating state (refer to the EOSCA list in MM 7.1). Temporarily and selectively reducing the level of system security by applying emergency condition operating limits is one of the many control actions the IESO can take when in an emergency operating state.

At all times, the minimum acceptable level of IESO-controlled grid system security is the level afforded by observance of emergency condition operating limits. All necessary steps are to be taken, including the interruption of non-dispatchable load or price responsive load, to observe the emergency condition operating limits.

An emergency operating state will generally not be declared when normal or routine control actions can resolve the capacity or energy deficiency, or return the IESO-controlled grid to a studied operating state in a timely manner. Implementation details, including the conditions under which an emergency operating state may be declared can be found in MM 7.1.

### Degraded Transmission Equipment Performance

(MR Ch.5 ss.1.2.1, 3.2.1, 3.2.2, 3.4.1.4, 3.4.1.5 and 3.6.1.6)

Degraded performance examples and IESO actions – A higher than long-term average forced outage rate, unanticipated tripping, or unanticipated failure to trip are typical examples of degraded transmission equipment performance. Where transmission equipment has shown degraded performance, or if degraded performance is anticipated, the IESO may perform control actions such as the following:

reschedule routine maintenance work, except work to remedy degraded performance;

reject or revoke any planned outages with Planned, Opportunity, or Information Priority Code anticipated to have an adverse impact on the IESO-controlled grid, except for planned outages to remedy degraded performance;

recall any planned outages with Planned, Opportunity, or Information Priority Code that may have an adverse impact on the IESO-controlled grid associated with the affected portion of the transmission system;

request staffing at transmission stations during periods of routine switching, during periods of high risk of equipment operation, or on a 24/7 basis depending on the severity of equipment degradation;

adjust IESO system security assessments to account for additional elements anticipated to be removed from service due to equipment degradation;

adjust use of remedial action schemes (RASs) to reduce operation of affected transmission system equipment; or

direct generators and other market participants as required to enhance reliability.

Where time permits, the IESO will discuss control actions with the applicable transmitter before implementation. Affected market participants and reliability coordinators shall be advised as appropriate, which may include publishing information on areas with degraded transmission equipment performance.

### Islanding

(MR Ch.5 ss.1.2.1, 3.2.1, 3.2.2, 3.2.3, 7.7.7 and 8.2.3)

Notice to generators and storage – The IESO shall notify generators and electricity storage participants of outages that would put their units in an electrical island following a single element contingency to inform their operating decisions.

No manual constraints down – The IESO shall NOT manually constrain down resources pre-contingency in order to assist a rapid collapse of an electrical island.

No manual constraints up – The IESO shall NOT manually constrain up resources pre-contingency in order to assist the survival of an electrical island.

IESO actions to assist collapse – The IESO shall take available pre-contingency control actions (other than constraining resources, such as a configuration change or RAS arming) to assist the rapid collapse of an electrical island formed by a single element contingency if:

IESO studies pre-determine that voltage and frequency will not be controlled within acceptable ranges; or

IESO cannot obtain voltage and frequency measurements in the island.

IESO actions to assist survival – The IESO shall take available pre-contingency control actions (other than constraining resources, such as a configuration change or RAS arming) to assist the survival of an electrical island formed by a single element contingency if:

IESO studies pre-determine that voltage and frequency will be controlled within acceptable ranges; and

IESO can obtain voltage and frequency measurements in the island.

Synchronization of Islands – The IESO shall synchronize islands only by using breakers that have synchrocheck relays, or a mechanism of ensuring that the circuit breaker closes only if voltages on both sides of the circuit breaker fulfill conditions of magnitude, phase, and slip frequency.

Special operating practices for islands – If special islanding practices are developed that differ from the above general policy, these practices shall be documented in operating instructions.

### Grid Control Actions

#### Principles

(MR Ch.1 s.3.1.1)

Maximizing transfer capability – To satisfy the objective of the IESO-administered markets, all practicable control actions shall be taken to maximize transfer capability while observing all system security or adequacy constraints.

#### Readiness Programs

(MR Ch.5 ss. 4.9.1 and 4.9.2)

Periodic Testing – To maintain confidence that control actions will be available when called upon, the IESO shall test or require market participants to test facilities that are connected to the IESO-controlled grid. This testing could be to prepare for the next peak season, or to prepare for extreme conditions that are expected in the next few days. For example, voltage reduction, operating reserve activation, and reactive capability will be periodically tested.

Additional provisions – IESO readiness program implementation details can be found in MM 7.1.

#### Network Configuration Change Request

(MR Ch.5 ss.3.2.3 and 6.4)

IESO assessment – The IESO shall assess proposed network configuration requests to manage individual delivery point performance and, through the outage management process, approve proposals that do not:

degrade the reliability of the IESO-controlled grid;

reduce a System Operating Limit (SOL) or transfer capability;

result in inconsistent application of established system security criteria and reliability standards;

impose additional exposure to loss of essential station service supply to nuclear generating stations;

expose the IESO-controlled grid to additional contingencies that have a material adverse effect on the reliability of the IESO-controlled grid;

impose additional risk/restrictions related to post-contingency response to recognized contingencies; and

interfere with the operation of IESO-administered markets (i.e., do not result in changes in generation dispatch or market price).

Inclusion in operating instructions – During normal situations, the IESO will include such advance-approved proposals in its operating instructions ahead of real-time operations.

Abnormal situations – During abnormal situations (e.g., forced outages, responding to contingencies, system restorations, etc.), the IESO may deviate from the above provisions while respecting their intent to the extent possible.

#### Control Actions to Increase Transfer Capability

(MR Ch.5 ss.1.2.1 and 3.2.1)

IESO control actions – Consistent with the principles stated in s.2.7.1, to maximize transfer capability the IESO will assess and may implement control actions such as:

changing reactive dispatch;

changing transformer winding or phase angle taps;

load transfers;

arming RASs;

manually constraining generation resources and electricity storage resources up or down;

opening breakers or switches, including high or low voltage bus tie breakers;

taking equipment off load; or

removing equipment from service.

Transmitter concurrence – The applicable transmitter must concur with control actions that involve removal of a step-down transformer or a bus-tie breaker which reduces supply redundancy to a load facility.

- Transmission reconfiguration – The IESO may prioritize reconfiguring the transmission system to increase system adequacy by alleviating conditions that restrict generation facility or electricity storage facility output with due consideration to reliability of the IESO-controlled grid, supply redundancy to a load facility and delivery point performance.

Implementation exceptions – The IESO will implement these control actions, or include them as part of its operational planning assessment of outage requests, unless the action:

fails to conform to a policy contained in this document;

exposes nuclear generating stations to loss of essential station service supply following an Appendix A, Group 1 contingency; or

causes post-contingency configurations expected to exceed system security restoration timelines.

#### Voltage Control

(MR Ch.5 s.4.6)

System voltage control actions – To maintain IESO-controlled grid voltages within ranges, to respect SOLs, and to respect equipment ratings, the IESO will dispatch the following:

generation unit and electricity storage unit reactive power within unit capability;

reactive control devices subject to operating agreements; and

reactive control devices subject to procurement contracts.

Load facility voltage control actions – The IESO will dispatch the following to meet connected wholesale customer or distributor voltage needs, as long as these actions do not exceed SOLs and equipment ratings:

generation unit and electricity storage unit reactive power within unit capability; and

reactive control devices subject to operating agreements.

#### Remedial Action Schemes

(MR Ch.5 ss.8.2.1, 8.2.2, 8.2.2A and 8.2.3)

RAS operation – The IESO-controlled grid system security must be returned to a secure state within times prescribed by reliability standards following operation of a RAS. The IESO will direct the use of RAS as outlined in transmitter operating agreements.

RAS deployment – A RAS shall not be deployed until it has been classified in the NPCC process as Type I, II, or Limited Impact.

Acceptable use of RAS – The acceptable use cases for RAS are described as follows:

- a Type I RAS may be utilized to increase the security limit of any SOL, including an Interconnection Reliability Operating Limit (IROL);

- a Type II RAS may be utilized to increase the security of the IESO-controlled grid for extreme contingencies, such as the loss of a right-of-way due to a tornado risk or a loss of a station due to a flashover risk; and

- a Limited Impact RAS may be utilized to increase the security limit of an SOL that is not an IROL.

Additional provisions – Specific criteria for selection of load rejection (L/R), generation rejection (G/R), and generation runback are contained in Appendix B. The use of a RAS during a high-risk operating state shall be subject to the restrictions contained in Appendix C.

Exclusion from load rejection – The IESO will allow market participants to request an exclusion from L/R for the following reasons:

public safety hazard;

potential damage to equipment;

potential violation of any applicable law;

outages to equipment directly associated with L/R tripping or restoration; or

outages to equipment which may degrade the integrity of L/R tripping or restoration (such as, but not limited to, relaying or station supervisory control equipment).

Restoration of rejected load – The IESO shall direct the restoration of rejected load. Load may be restored following rejection by interrupting other load (i.e., rotating blackout) as a substitute.

#### Voltage Reductions

(MR Ch.5 ss.4.5.2A, 5.8.1.2, 5.9.1.3 and 10.3.1)

The IESO may direct a market participant to initiate voltage reductions to prevent or to mitigate an emergency operating state resulting from events including:

equipment thermal overloads;

insufficient generation capacity and electricity storage capacity to satisfy non-dispatchable demand;

violations of high-risk, normal, or emergency SOLs; or

an event requiring the IESO to activate operating reserve that is provided by voltage reductions.

#### Load Shedding

(MR Ch.5 ss.5.8.1.2, 5.9.1.3 and 10.3.1)

Purpose of load shedding – Load shedding is a permissible IESO control action to maintain grid integrity, or to respect safety, equipment, or applicable law constraints.

Avoiding or deferring load shedding – When an SOL is exceeded, load shedding may be avoided or deferred by taking the following steps as required:

###### Disregard high-risk limits and apply normal limits.

This step will allow an increase in transfer limits constrained by RAS arming restrictions and other restrictions due to a high-risk operating state.

###### Disregard normal limits and apply emergency condition operating limits.

This step will allow an increase in transfer limits constrained by contingencies involving more than one element.

Conditions requiring load shedding – The IESO shall shed load during an emergency operating state under the following conditions, which are consistent with the minimum acceptable level of reliability:

to alleviate a capacity or energy emergency;

to alleviate or avoid exceeding pre- and post-contingency equipment ratings;

to alleviate or avoid exceeding pre-contingency voltage collapse;

to alleviate or avoid exceeding an IROL; or

if specified by special operating practices for unique circumstances.

Operation outside of known and secure states – Note that when a transfer is near its SOL, both the SOL and its associated boundary conditions (e.g. minimum voltages, flows on other IESO-controlled grid interfaces, or interchange with a neighbouring electricity system etc.) are equally important considerations. When a boundary condition is not satisfied, the security of the IESO-controlled grid is no longer in a known and secure state. In the case of IROLs, this implies an unknown risk of system instability, cascading or uncontrolled separation, and consistent with the NERC “Reliability Guideline on Methods for Establishing IROLs”, must be managed back to a known secure state within 30 minutes (which may require shedding non-dispatchable load).

Selecting which load to shed – When an emergency operating state has been declared and reduction in demand is required to safeguard the reliability of the IESO-controlled grid, the IESO shall direct manual load shedding to reduce demand on the following basis:

Priority customer loads (refer to MM 7.10) such as hospitals and water treatment plants without backup generators, and electrically driven gas compressors should be avoided when determining what load to shed.

The amount and location of load to be shed will be selected to solve the operating problem to maintain an adequate level of IESO-controlled grid adequacy or system security.

When time permits, load cuts via manual rotational load shedding schemes should be spread equitably across the IESO-controlled grid to the extent practicable. Equitable considerations will include magnitude, duration, and frequency of load reductions.

#### Station Service

(MR Ch.5 ss5.2.5 and 6.5.1)

Market participant notification to IESO – When a recognized contingency event, as indicated in Appendix A: Recognized Contingencies, results in the loss of station service supply to a facility, the market participant that owns the facility shall promptly notify the IESO of any adverse impacts, such as:

reduced facility ratings;

loss of control, monitoring, or visibility of equipment; and

any other operational limitations.

Planned or prolonged outages – For planned or prolonged station service outages lasting more than 24 hours and impacting equipment critical to IROLs, the market participant shall: Implement viable redundancy measures within 30 minutes, such as:

activating backup generation;

staffing the station locally; and/or

recalling the outage or preparing affected equipment for quick recall.

– End of Section –

## Adequacy

### Principles

(MR Ch.5 ss.1.2.1 and 3.2.1)

IESO adequacy assessment – The IESO shall maintain an adequate supply of generation and transmission to meet forecast Ontario demand in the operational timeframe. When assessing generation and transmission adequacy, the IESO will consider factors including the following:

demand forecast;

variable generation (e.g., wind and solar) forecast;

load forecast uncertainty;

additional contingency allowance;

operating reserve requirements;

generation, electricity storage and demand response availability forecast, which includes the available but not operating (ABNO) units, and generation external to Ontario and associated tie-line capability;

transmission facility capability forecast;

applicable SOLs; and

acceptable voltage ranges.

### Resource and Transmission Adequacy

(MR Ch.5 ss.7.3.1.4 and 7.3.1.5, Ch.7 ss.12.1.1.6, 12.1.1.7 and 12.1.1.8)

Assessment frequency – When assessing adequacy, the IESO shall compare forecasted demand to available resource capacity and energy, including available resources external to Ontario. The IESO shall assess adequacy for normal operating states on a daily basis in its short-term operating assessments, on a weekly basis in its medium-term assessments, and on a less frequent basis in longer-term assessments. For these operating horizons, criteria to identify an acceptable level of adequacy (and corrective actions if this level cannot be achieved), can be found in MM 7.2.

Criteria for transmission adequacy – When assessing transmission adequacy, the IESO shall compare transmission flow forecasts with the applicable SOLs under an anticipated range of power system conditions. Transmission is adequate if demand forecasts can be supplied without exceeding applicable SOLs, and acceptable system voltages can be maintained.

### Operating Reserve Policy

(MR Ch.5 ss.4.5.1, 4.5.2 and 4.5.5)

Extent of operating reserve scheduling – Operating reserve shall be scheduled (MR Ch.5 s.4.5.1) to ensure resources are available to:

cover or offset unanticipated increases in demand during a dispatch day or dispatch hour;

cover or offset capacity lost due to a forced or urgent outage of generation, injecting electricity storage facilities, or transmission equipment; or

cover uncertainty associated with the performance of generation facilities, electricity storage facilities, or dispatchable loads in responding to IESO dispatch instructions.

Commissioning tests – No additional operating reserve shall be required during a commissioning period when no tests are scheduled that materially increase the risk of unit tripping.

Distribution of operating reserve – Operating reserve shall be scheduled in sufficient quantity and shall be distributed so as to ensure that it can be utilized for any single contingency that results in either generation loss, electricity storage injection loss or both without exceeding equipment or transmission system limitations.

Voltage reductions may be used to provide operating reserve.

### Area Reserve for Load Security

(MR Ch.5 ss.4.5.1, 4.5.2 and 4.5.5)

Area reserves (i.e. reserves that are scheduled or resources that are pre-committed to avoid shedding load) shall be scheduled as follows:

For all SOLs: All available resources shall be committed to avoid shedding load before a contingency.

For IROLs: Non-energy limited resources shall be pre-committed so that following a single-element contingency, the system can be re-prepared within 30 minutes to operate to IROL emergency condition limits, without shedding non-dispatchable load or price responsive load to the extent possible.

Additional area reserve – From time to time, the IESO may choose to carry additional area reserve beyond those required here for circumstances such as extreme weather forecasts, system flexibility events (MM7.1 s.2.4.2), physical security threats, etc.

– End of Section –

## System Security

### 4.1	Principles

(MR Ch.5 ss.3.2.2, 5.1.2, 5.2.1, 5.2.2, 5.2.4, and 5.2.6)

This section describes the level of security that must be achieved so that the risk of loss or separation of a major portion of the interconnected system is reduced to an acceptable level.

The IESO-controlled grid must display satisfactory performance before and after contingency events. All IESO performance criteria must be satisfied, not only the transient and voltage stability criteria, for an operating condition to be deemed stable.

The IESO-controlled grid must be operated such that in a normal, planned state, voltages will be within normal limits, equipment loading will be within continuous ratings as supplied by facility owners, and transfers will be within SOLs. For planned outages with Planned, Opportunity, or Information Priority Code, market participants may provide less restrictive equipment ratings, such as long-term emergency ratings (e.g., 10-day limited time ratings) to be applied pre-contingency pertaining to equipment that they own. Operation within authorized ratings shall be considered sufficient to avoid physical damage, protect safety, and avoid violation of any applicable law unless otherwise notified.

The IESO will use the following policies to develop operational plans, establish SOLs and instructions, and operate the IESO-controlled grid.

### 4.2	Methodology for Deriving System Operating Limits

(MR Ch.5 ss.3.2.2, 5.1.2, 5.2.1, 5.2.2, 5.2.4, and 5.2.6)

SOL and IROL Methodology – System operating limits shall be established in the following manner:

Simulate and monitor the effect of recognized contingency events as follows:

  - Contingencies listed in Appendix A Group 1 shall be monitored on the NPCC-defined bulk power system (BPS), in accordance with NPCC Directory #1.

  - Contingencies listed in Appendix A Group 2 shall be monitored onto the NERC-defined bulk electric system (BES), for the contingency occurring anywhere in Ontario.

  - Contingencies listed in Appendix A Group 3 shall be monitored onto the IESO-controlled grid, for the contingency occurring anywhere in Ontario.

Evaluate the effect of recognized contingency events with respect to security criteria as follows:

  - The resulting performance from 1a shall be evaluated with respect to security criteria for Widespread Voltage Stability, Widespread Transient Stability, Widespread Small Signal Stability, Uncontrolled Separation, and Cascading.

  - The resulting performance from 1b shall be evaluated with respect to all security criteria.

  - The resulting performance from 1c shall be evaluated with respect to all security criteria.

Establish SOLs and identify the subset that are IROLs, as follows:

  - A SOL is established to ensure that the resulting performance from the evaluation in 2 meets the applicable security criteria.

  - An IROL is established in the case that the SOL is securing for Widespread Voltage Stability, Widespread Transient Stability, Widespread Small Signal Stability, Uncontrolled Separation, or Cascading security criteria.

- Reassessing IROLs for prevailing conditions – The IESO may reassess IROLs leading up to, or during, real-time operations, and confirmed to not be IROLs for prevailing conditions. In such circumstances, assessments shall be documented and policies associated with IROLs need not be followed. If the prevailing conditions are such that the IESO-controlled grid is no longer in a known and secure operating state, the IESO shall take control actions that prioritize returning the IESO-controlled grid to a known and secure operating state and not on establishing an SOL or IROL in real-time.

Contingencies outside Ontario – If the IESO becomes aware of a contingency outside Ontario that materially affects the IESO-controlled grid, the IESO will treat that as a recognized contingency for the IESO-controlled grid.

Contingencies inside Ontario – A neighbouring jurisdiction will determine the criteria for assessing effects of contingencies within the IESO-controlled grid on their system.

Special considerations for inverter-based resources – In addition to the security criteria contained within this document, special considerations for inverter-based resources, and requirements to assess electromagnetic transient phenomena are stated in Appendix D: Special Considerations for Inverter-Based Resources.

Communicating equipment critical to IROLs – The IESO fulfills its obligations under NERC Standard FAC-014-4 R5 by ensuring that all elements critical to the derivation of IROLs and associated critical contingencies are documented within operating instructions. Market participants that own or operate facilities containing elements critical to IROLs are provided the subject operating instructions at the time any version of the document is released, and pursuant to operating agreements. Thus, the market participant will always have access to the most current information pursuant to critical elements, and in alignment with timelines established in the NERC requirements.

### 4.3	System Security and Modelling Criteria

#### 4.3.1	Principles

(MR Ch.5 ss.5.2.1, 5.2.2, 5.2.4, and 5.2.6)

Overview – The derivation of SOLs shall be done in accordance with the system security and modelling criteria described in the following sections.

#### 4.3.2	Study Conditions and System Model

(MR Ch.5 ss.5.2.1, 5.2.2, 5.2.4, and 5.2.6)

Expected conditions – The study conditions used shall cover expected operating conditions (e.g. generation dispatch and load levels) and shall reflect changes to system topology (e.g. facility outages).

Model Extent – The study model for determining SOLs must include at least the entire reliability coordinator area, as well as the critical modelling details from other reliability coordinator areas that would impact the facility or facilities under study.

Model detail – The study model must contain a sufficient amount of detail, including representation of the physical and control characteristics of modelled facilities, to ensure fulfillment of the IESO’s mandate to operate the IESO-controlled grid reliably.

#### 4.3.3	Load Representation

(MR Ch.5 ss.5.2.1, 5.2.2, 5.2.4, and 5.2.6)

Pre-contingency – Constant megavolt-amp (MVA) load models shall be used to assess a pre-contingency state.

Post-contingency – Voltage-dependent load models may be used to assess a post-contingency state before and after tap-changer action. The default voltage-dependent load model shall be used unless a different model has been approved by the IESO. The default voltage dependant for active (P) and reactive (Q) load shall be defined as follows:

PV=0.5 ×P0×VV0+0.5×P0×VV02

QV=Q0×VV02   V0 P0, Q0 are pre-contingency values

In areas where representation of load is critical, such as areas with a material amount of motor load or where post-contingency voltage decline is expected to be more than 10%, a detailed representation of transient load behaviour should be attempted.

#### 4.3.4	Thermal

(MR Ch.5 ss. 5.2.1, 5.2.2, 5.2.4, 5.2.5, and 5.2.6)

##### 4.3.4.1	Equipment Loading Criteria

Pre-contingency criteria – Prior to a contingency event, steady state flow through equipment comprising the IESO-controlled grid shall be within continuous ratings provided by the relevant market participants. Limited time ratings may be used in special circumstances, such as switching, so long as the application is acceptable to the relevant market participants via documented instruction or during real-time conditions.

Post-contingency criteria – Following a contingency event, steady-state flow through equipment comprising the IESO-controlled grid shall be within applicable emergency ratings provided by the relevant market participants.

##### 4.3.4.2	Cascading Criteria

Demonstrably contained – Following a contingency, if steady-state flow through equipment comprising the IESO-controlled grid overloads equipment and causes it to trip, successive overloading and tripping shall be demonstrably contained (i.e. bounded) such that a new steady-state is reached, and the remaining portion of the IESO-controlled grid meets applicable security criteria. Particularly, the magnitude of any net loss of load or supply shall not result in a redistribution of flow that results in an adverse impact to interties.

Simulation considerations – For the purpose of simulations testing cascading, equipment that is loaded in excess of the emergency rating provided by the market participant shall be assumed to trip. Assuming the equipment trips is reasonably conservative to account for the probability of either overcurrent relay activation, fault isolation due to underbrush contact, or the market participant exercising their authority to remove equipment from service in accordance with MR Ch.5 ss.1.2.3 and 6.1.6.

##### 4.3.4.3	Thermal Rating Policy

Respect equipment ratings – The IESO shall not deliberately operate or plan to operate equipment comprising the IESO-controlled grid in excess of thermal ratings for such equipment as communicated to the IESO by relevant market participants.

Use of limited time ratings – Limited time ratings shall be utilized only if control actions are available to reduce loading to a longer time rating within the interval afforded by a limited time rating. For example, a 15-minute rating may only be utilized if control actions are available to reduce loading to a longer term rating (e.g. a 10-day rating) within 15 minutes. Post-contingency loading shall not exceed the shortest applicable limited time rating.

Monitoring – Thermal IROLs shall be identified in advance of real-time operation to establish whether overloading of equipment results in unbounded cascading. Typically, the limit values of thermal SOLs are established in real-time operation by the IESO’s real-time operating tools based on the facility ratings submitted by market participants. The scope of thermal monitoring will be established in operating agreements between IESO and transmitters.

#### 4.3.5	Pre-contingency Voltage Range

(MR Ch.5 ss.5.2.1, 5.2.2, 5.2.4, and 5.2.6)

IESO-controlled grid ranges – The IESO-controlled grid shall be operated in the voltage ranges shown in Table 4-1 under pre-contingency conditions and following re-preparation unless affected equipment owners have agreed to a wider range.

Transmission and distribution ranges – For transmission voltages, the values are from MR Ch.4. For distribution voltages, the values are based on Canadian Standards Association (CSA) Standard 235.

Table 4-1: Pre-Contingency Voltage Limits

| Nominal Bus Voltage | Transmission Stations |  |  | Transformer Station (Load Facility) Low Voltage at 44 kV, 27.6 kV, 13.8 kV |
| --- | --- | --- | --- | --- |
|  | 500 kV | 230 kV | 115 kV |  |
| Maximum Continuous | 550 kV | 250 kV | 127 kV* | 106% of nominal |
| Minimum Continuous | 490 kV | 220 kV | 113 kV | 98% of nominal |

*	In portions of northern Ontario, the maximum continuous voltage for the 115 kV system can be as high as 138 kV.

Exceptions – Exceptions to maximum and minimum voltages must be documented in relevant operating instructions.

#### 4.3.6	Post-contingency Voltage Range

(MR Ch.5 ss.5.2.1, 5.2.2, 5.2.4, and 5.2.6)

Post-contingency limits – IESO-controlled grid voltages following recognized contingencies (i.e., after the contingency has been cleared, automatic schemes have acted, and the IESO-controlled grid has reached a new steady state) shall be limited to the values and applicability as shown in Table 4-2.

Greater post-contingency maximum voltages may be observed if the equipment owner has agreed to different voltage limits. Operating instructions must document exceptions to voltage limits.

If post-contingency voltages on the low-voltage side of load transformer station are observed to decline by greater than 10%, the IESO shall inform the transmitter of the voltage performance. This is in recognition that load power quality is the responsibility of the transmitter. If the suppressed voltage performance is determined to be unacceptable by either the transmitter (per power quality requirements from the OEB’s transmission system code or other relevant reliability standards) or the IESO (per the policies contained herein), the IESO shall establish a boundary condition to prevent more than 10% voltage decline at the low-voltage side of the load transformer station.

Table 4-2: Post-Contingency Voltage Range

|  | Nominal Bus Voltage |  |  | Applicability |
| --- | --- | --- | --- | --- |
|  | 500 kV | 230 kV | 115 kV |  |
| Post-contingency Maximum | 575 kV | 263 kV | 133 kV* | Only at transmission stations and at points of interconnection of generation facilities and electricity storage facilities, for a duration of up to 30 minutes |
| Post-contingency Minimum | 450 kV | 207 kV | 104 kV | Only at point of interconnection of generation facilities and electricity storage facilities |

*	Where the maximum continuous voltage for the 115kV system is above 133kV, the post-contingency maximum voltage limit is the same as the applicable maximum continuous voltage.

#### 4.3.7	Voltage Stability

(MR Ch.5 ss.5.2.1, 5.2.2, 5.2.4, and 5.2.6)

Overview – For acceptable voltage stability, the IESO shall apply the following security criteria and policy.

##### 4.3.7.1	Local Voltage Stability Criteria

Local Criteria – For all anticipated operating states, voltage stability shall be demonstrated in accordance with the voltage stability policy.

##### 4.3.7.2	Widespread Voltage Stability Criteria

Demonstrably Contained – Successive loss of equipment that experience voltage collapse and trip due to low voltage, distance relay or other protection activations, shall be demonstrably contained, i.e., bounded, such that a new steady state is reached, and the remaining portion of the IESO-controlled grid demonstrates performance that meets applicable security criteria. Particularly, the magnitude of any net loss of load or supply shall not result in a redistribution of flow that results in an adverse impact to interties. Analysis shall be demonstrated in accordance with the voltage stability policy.

##### 4.3.7.3	Voltage Stability Policy

Power-voltage analysis – Voltage stability for power transfers for all anticipated operating states shall be demonstrated using power-voltage (PV) analysis accordingly:

a power transfer corresponding to Point 'A', which if increased by 10%, is less than the power at the critical point of the pre-contingency PV curve; and

a power transfer corresponding to Point 'B', which if increased by 10%, is less than the power at the critical point of the post-contingency PV curve.

Power-voltage curves – When producing a pre-contingency PV curve, manual actions such as reactive shunt switching together with transformer tap-changer action, are permitted. When producing a post-contingency PV curve, only automatic control actions (e.g. generation automatic voltage regulation (AVR), RASs, and automatic under-load tap-changes) shall be modelled.

Figure 4-1: Typical Power-Voltage Curves

#### 4.3.8	Transient Stability

(MR Ch.5 ss.5.2.1, 5.2.2, 5.2.4, and 5.2.6)

Overview – For acceptable transient angle stability, the IESO shall apply the following security criteria and policy.

##### 4.3.8.1	Local Transient Stability Criteria

All supply resources remain synchronized – No generation unit or electricity storage unit shall pull out of synchronism for any Group 3 contingencies in Appendix A with due regard to reclosure.

##### 4.3.8.2	Widespread Transient Stability Criteria

Demonstrably contained – For all applicable contingencies in Appendix A, any generation units or electricity storage units that pull out of synchronism (and trip due to protection activation) shall not result in unbounded successive loss of equipment. Any loss of equipment shall be demonstrably contained such that a new steady state is reached, and the remaining portion of the IESO-controlled grid demonstrates performance that meets applicable security criteria. Particularly, the magnitude of any net loss of load or supply shall not result in a redistribution of flow that results in an adverse impact to interties.

##### 4.3.8.3	Transient Stability Policy

Disconnection vs. loss of synchronism – A generation unit or electricity storage unit that is disconnected from the IESO-controlled grid as a result of fault clearing action or by rejection from a RAS is not considered pulling out of synchronism.

Required margin – Transient angle stability shall be maintained if the critical parameter is increased by 10% to allow margin.

Simulation – The 10% increase in the critical parameter can be simulated by generation or load changes beyond the forecast load or generation capabilities even after eliminating station service load. Conditions at margin shall be as realistic as reasonably achievable. The use of negative values of local load is preferable to increasing local generation beyond its maximum capability. Negative load used for margin must have a constant MVA characteristic.

Simulating operating times – Design operating times of fault detectors, auxiliary relays, trip modules, communication media, breakers, etc., may be used for calculating switching times when reliable field-measured data are not available.

#### 4.3.9	Small Signal Stability

(MR Ch.5 ss.5.2.1, 5.2.2, 5.2.4, and 5.2.6)

Overview – For acceptable small signal stability, the IESO shall apply the following security criteria and policy.

##### 4.3.9.1	Local Small Signal Stability Criteria

Damped behaviour intra-area – For all anticipated operating states, generation units or electricity storage units shall demonstrate sufficiently damped behaviour, in accordance with the small signal stability policy.

##### 4.3.9.2	Widespread Small Signal Stability Criteria

Damped behaviour inter-area – For all anticipated operating states, inter-area oscillations shall demonstrate sufficiently damped behaviour. That is, a coherent group of generation units or electricity storage units shall not oscillate against any other group(s) of generation units or electricity storage units in external control area(s) in a manner that does not meet the damping requirements governed by each reliability coordinator of the respective control area(s). Damping requirements for the IESO-controlled grid are per the small signal stability policy, below.

##### 4.3.9.3	Small Signal Stability Policy

Damping factors – The required damping factors at various conditions on the IESO-controlled grid are tabulated in Table 4-3.

Table 4-3: Acceptable Damping Factors

| System Condition | Damping Factor |
| --- | --- |
| Pre-contingency | > 0.03 |
| Post-contingency: Before any automatic response | > 0.00 |
| Post-contingency: After automatic responses, before manual system adjustments | > 0.01 |
| Following re-preparation of the system: After system adjustments | > 0.03 |

Calculating damping factors – For swings characterized by a single dominant mode of oscillation, the damping may be calculated directly from the oscillation envelope. For a damping factor of 0.03, the magnitude of oscillations must be reduced to 39% of initial values within five periods. For a damping factor of 0.01, the magnitude of oscillations must be reduced to 39% of initial values within 15 periods. For swings not characterized by a single dominant mode, then the damping factors should be derived via a more detailed modal analysis.

#### 4.3.10	Transient Voltage Response

(MR Ch.5 ss.5.2.1, 5.2.2, 5.2.4, and 5.2.6)

Overview – Following fault clearing, or the loss of an element without a fault, the transient voltage response shall not result in the protective relays activating with due regard for the margins specified below.

##### 4.3.10.1	Local Relay Margin Criteria

Local element relay margins – For any Group 3 contingencies in Appendix A with due regard to reclosure, the margin on all relays, generator loss of excitation and out-of-step protections on generating units, or those associated with transformer backup protections, must be at least 15% on all instantaneous relays, and 0% on all timed relays having a time delay setting less than or equal to 0.4 seconds. For all relays having a time delay setting greater than 0.4 seconds, the apparent impedance may enter the timed tripping characteristic, provided that there is a margin of 50% on time. That is, the apparent impedance does not remain within the tripping characteristic for a period of time greater than one-half of the relay time delay setting. The margin on all system relays, such as change of power relays, must be at least 10%.

##### 4.3.10.2	Uncontrolled Separation Criteria

Demonstrably contained – For all applicable contingencies in Appendix A with due regard to reclosure, the consequence of protective relays activating shall not result in uncontrolled separation of a portion of the system. That is, any separation (including islanding) due to protective relays activating shall be demonstrably contained such that a new steady state is reached, that any electrical island is treated in accordance with section 2.6, and the remaining portion of the IESO-controlled grid demonstrates performance that meets applicable security criteria. The magnitude of any redistribution of flow due to the separation (including any net loss of load or supply from the collapse of an island) shall not result in an adverse impact to interties.

Uncontrolled separation relay margin – The margin on all instantaneous and timed distance relays at stations that, if activated risk uncontrolled separation, including generator loss of excitation and out-of-step relaying, must be at least 20% and 10% respectively.

#### 4.3.11	Automatic Reclosure

(MR Ch.5 ss.5.1.2 and 5.2.1, 5.2.2, 5.2.4, and 5.2.6)

Application – The IESO will use automatic reclosure to more quickly restore the integrity of the IESO-controlled grid following contingencies that are not permanent. Experience has shown many faults on the overhead transmission circuits to be temporary. Automatic reclosure for transformer, bus, or cable protection should only be approved in exceptional circumstances, as these faults are more likely to be permanent.

Two stages of reclosure – Automatic reclosure is normally comprised of two stages; re-energization from a single preferred breaker with under-voltage supervision and time delay followed by reclosing of the remaining breakers with synchrocheck supervision.

Settings and selection requirements – Circuits are normally automatically re-energized following a fault clearing by protection systems. Upon successful re-energization, the remaining breakers shall be automatically reclosed. Failure to automatically re-energize from the single preferred breaker is deemed to be unsuccessful reclosure. The following sub-sections outline settings and selection requirements for automatic reclosure:

##### 4.3.11.1	Re-energization

A faulted circuit should be automatically re-energized from a single preferred breaker with under-voltage supervision and a minimum time delay of five seconds. Automatic re-energization shall be initiated following damping of system oscillations. Stability-sensitive areas should have a nominal time delay of 10 seconds or longer to initiate automatic re-energization. Areas where studies indicate that higher speed reclosure has no material adverse effects on the system security of the IESO-controlled grid, re-energizing with a time delay of less than five seconds is permitted.

The breaker chosen for the re-energization of the circuit shall be the one that would result in the least disruption in the event of a breaker failure upon an unsuccessful re-energization. Experience has shown there is a higher-than-average risk of breaker failure in an open-close-open sequence.

The re-energizing breaker shall be at a terminal remote from steam turbine units. If possible, re-energizing should be initiated at a breaker at a terminal remote from generation units.

Automatic re-energization time delay settings for adjacent transmission circuits on common towers are selected to mitigate the risk of re-energizing onto two faulted circuits at the same time.

##### 4.3.11.2	Reclosing of the Remaining Breakers

- The remaining breakers shall automatically reclose with synchrocheck supervision. Where there is no electrically close generating station, voltage presence supervision with a nominal time delay of 0.5 seconds may be used.

- Automatic reclosing must not result in a sudden power change exceeding 0.5 per unit of its MVA rating on steam turbine generation units rated greater than 10 MVA. Market participant agreement shall be obtained prior to allowing a higher value of sudden power change.

- Automatic reclosure shall not be used to re-synchronize a generation unit that has separated from the transmission system.

On those circuits where only high speed (i.e. less than one second) unsupervised automatic reclosure is available, it should normally be blocked.

Withstanding unsuccessful automatic re-energization – System operating limits shall be derived such that the system must successfully withstand an unsuccessful automatic re-energization (i.e., an open-close-open sequence) operation.

#### 4.3.12	Manual Reclosure

(MR Ch.5 ss.5.1.2, 5.2.1, 5.2.2, 5.2.4, and 5.2.6)

Application – Following an unsuccessful automatic reclosure, or an outage, a circuit will normally be manually re-energized from the preferred breaker used for automatic reclosure.

Withstanding manual energization – The IESO-controlled grid must be able to withstand manual energization of a faulted element without prior readjustment of generation levels, unless specific operating instructions to the contrary are provided. Manual reclosure of the remaining breakers after energization must not result in a sudden power change exceeding 0.5 per unit of its MVA rating on steam turbine generation units rated greater than 10 MVA. Market participant agreement shall be obtained prior to allowing a higher value of sudden power change.

### 4.4	Frequency Regulation

(MR Ch.5 App.4.2)

Requirements – Generation facilities and electricity storage facilities are required to be able to operate within the range of frequencies specified in MR Ch. 4 App. 4.2: Requirements for Generation and Electricity Storage Facilities Connected to the IESO-controlled Grid. This appendix also specifies the required settings for speed/frequency regulation.

Additional provisions – MM 7.1 explains how generators and electricity storage participants are required to operate during abnormal system frequencies.

#### Automatic Under Frequency Load Shedding

(MR Ch.5 s.10.4.1)

IESO administration – The IESO shall administer an automatic under-frequency load shedding (UFLS) program to stabilize frequency. This program shall take into consideration the manner in which the IESO-controlled grid is likely to separate in the event of a system disturbance, compensation for early generation tripping, and planned outages with Planned, Opportunity, or Information Priority Code to UFLS equipment.

Additional provisions and priority customers – IESO requirements for the UFLS program are contained in MM 7.1. Priority customer loads (refer to MM 7.10) such as hospitals and water treatment plants without backup generators, and electrically driven gas compressors should be considered by distributors and connected wholesale customers when satisfying UFLS program requirements.

### Restoration of System Security

#### Principles

(MR Ch.5 s.5.10.2)

Re-prepare as soon as possible – The IESO shall use all appropriate means to re-prepare the system to satisfy SOLs corresponding to emergency condition operating limits as soon as possible. The IESO will endeavour to shorten the duration of an emergency operating state.

Control actions have foreseen and acceptable consequences – The consequences of control actions to return to a studied operating state must be both foreseen and acceptable. The intentional loss of a major portion of the system, or the intentional separation of a major portion of the system, are unacceptable consequences.

#### Policies

(MR Ch.5 s.5.10.2)

Minimum acceptable level of security– The minimum acceptable level of IESO-controlled grid system security is the level afforded by observance of emergency condition operating limits. All necessary steps are to be taken, including the interruption of non-dispatchable load and price responsive load, in accordance with section 2.7.8 of this market manual to observe emergency condition operating limits.

Time to re-prepare IROLs – The IESO shall use all available means to re-prepare IROLs to emergency condition operating limits within the IROL Tv following any respected contingency. In the case of IROLs that secure the system for thermal cascading, the IROL Tv is the time associated with the limited time rating of the overloaded equipment. In the case of all other IROLs, the IROL Tv is 30 minutes. The re-preparation time period starts following the occurrence of the contingency.

Re-preparation plans for IROLs – The IESO must have plans to re-prepare IROLs to emergency condition operating limits within the IROL Tv following the occurrence of respected contingencies. Re-preparation plans shall not utilize control actions that increase non-dispatchable load and price responsive load shedding until resources have been committed in accordance with the Area Reserve criteria in section 3.4 of this market manual.

Power system restoration plan – The IESO publishes and maintains a power system restoration plan for Ontario in the event of a complete or partial blackout of the IESO-controlled grid (refer to MM 7.8).

– End of Section –

## Recognized Contingencies

Recognized contingencies applicable to elements that form the BPS and BES are, at a minimum, specified by NPCC and NERC, respectively. Additional recognized contingencies applicable to the IESO-controlled grid are specified by the IESO. The consequences of Group 1, Group 2, and Group 3 contingencies shall be applied in accordance with s.4.2 with due regard for how auxiliaries at generation, electricity storage and transmission stations are supplied by the IESO-controlled grid. If the recognized contingencies within this document are inconsistent with other reliability standards, such as due to any updates by NERC or NPCC, the most stringent of the subject recognized contingencies is adopted.

Single-element contingencies result in the clearing of a single protection zone, with the exception of inadvertent breaker opening contingencies. A single protection zone may comprise more than one element. To restore system security, it can be assumed that only one element was faulted, and the other elements comprised within a single protection zone can return to service. The timing of the return to service depends upon the particulars associated with the fault location. System security must be restored considering all elements that cannot be returned to service within 30 minutes.

When the IESO-controlled grid is in a high-risk operating state, the IESO may operate the system to withstand contingencies more severe than those specified below for a normal operating state.

### A.1	Group 1 – Contingencies

A.1.1	Normal Operating State

When the IESO-controlled grid is in a normal operating state, the Group 1 contingencies are:

- A permanent three-phase fault on any element with normal fault clearing.

- Simultaneous permanent single-phase-to-ground faults on the same or different phases of each of two adjacent transmission circuits on a multiple transmission circuit tower, with normal fault clearing. This excludes conditions that are considered an acceptable risk documented in NPCC Directory #1.

- A permanent single-phase-to-ground fault on any element with delayed fault clearing.

- Loss of any element or circuit breaker without a fault.

- A permanent single-phase-to-ground fault on a circuit breaker, with normal fault clearing.

- Simultaneous permanent loss of both poles of a direct current bipolar facility.

- The failure of a circuit breaker associated with a RAS to operate when required following the loss of any element or circuit breaker without a fault, or a permanent single-phase-to-ground fault (with normal fault clearing) on any element.

A.1.2	Emergency Operating State

When the IESO-controlled grid is in an emergency operating state, the Group 1 contingencies are:

- A permanent three-phase fault on any element with normal fault clearing.

- A permanent single-phase-to-ground fault on any element with normal fault clearing.

- Single pole block with normal clearing in a monopolar or bipolar high voltage direct current (HVDC) system.

- Loss of any element or circuit breaker without a fault.

### A.2	Group 2 – Contingencies

When the IESO-controlled grid is in a normal operating state or emergency operating state the Group 2 contingencies are:

- A permanent three-phase fault on any element with normal fault clearing.

- A permanent single-phase-to-ground fault on any element with normal fault clearing

- Loss of any element or circuit breaker without a fault.

- Single pole block with normal clearing in a monopolar or bipolar HVDC system.

### A.3	Group 3 – Contingencies

When the IESO-controlled grid is in a normal or emergency operating state, the Group 3 contingencies are:

- A permanent phase-to-phase-to-ground fault on any element with normal fault clearing.

- A permanent single-phase-to-ground fault on any element with normal fault clearing

- Loss of any element or circuit breaker without a fault.

– End of Appendix –

## Load and Generation Rejection and Generation Runback Selection Criteria

### B.1	Load Rejection (L/R) Selections

L/R should be selected to satisfy the following in order of priority:

- System security: L/R selections must satisfy system security requirements for specific station and/or a specific megawatt requirement (to within an acceptable deadband). L/R must be selected such that the resulting transmission conditions do not prevent L/R actions to alleviate the system security concerns. L/R selections in the vicinity of a natural or man-made disaster must not hamper emergency measures.

- Sensitivity: Priority customer loads (refer to Market Manual 7.10: Ontario Electricity Emergency Plan) such as hospitals and water treatment plants without backup generators, and electrically driven gas compressors should be avoided when determining what load to shed.

- Minimize Number of Stations: The number of stations selected for rejection should be minimized.

- Trip History: L/R selections should attempt to equalize the number of L/R operations for each station over the long term and minimize the exposure of any station to two successive L/R operations.

- Area Fairness: Where L/R may be available for selection in more than one area, the stations selected for L/R should be distributed among each participating area. This distribution should be in approximate proportion to the percentage of the total load supplied by all areas involved in the scheme.

Opening bus tie breakers to increase non-dispatchable load or price responsive load lost by configuration shall be considered as L/R.

L/R selections will be minimized where affected IESO-controlled grid delivery points are not within reliability performance standards.

L/R selected to relieve post-contingency thermal overloading shall be:

- Sufficient to comply with the thermal rating policy.

- Sufficient to prevent loading beyond the long-time ratings if the lack of fast-acting control actions combined with the complexities of post-rejection operation will jeopardize respecting long-time ratings within the appropriate “limited” time.

### B.2	Generation Rejection Selections

- Generation Rejection (G/R) should be selected to satisfy the following in order of priority:

- System Security: G/R requirements must satisfy system security requirements for specific unit selections and/or specific megawatt requirement (to within an acceptable deadband).

- Minimize Number of Units: The number of units selected and total amount selected for G/R should be minimized within the constraints imposed by plant and system operating conditions.

- Trip History: Selections should attempt to equalize the number of unit trips based on history.

- G/R selections for single element contingency events shall be minimized.

- G/R selected to relieve post-contingency thermal overloading shall be:

- Sufficient to comply with the thermal rating policy.

- Sufficient to prevent loading beyond the long-time ratings if the lack of fast-acting control actions combined with the complexities of post-rejection operation will jeopardize respecting long-time ratings within the appropriate “limited” time.

- G/R selections should avoid manual corrective measures following a G/R operation,

- G/R selections should be made on a reasonable effort basis to address market participant resource concerns such as the:

- Maximum number of units selected within a single control center,

- Minimum number of unselected generation units, and

- Unavailability or preferences of specific units for G/R selection.

### B.3	Generation Runback Selections

All policies in place for G/R apply equally to Generation Runback.

– End of Appendix –

## RAS Restrictions during High-Risk Operating State

During a high-risk operating state, there is a significantly higher than normal probability of one or more contingency events and associated consequences (MR Ch.5 s.2.4.1). Since RAS are complex systems that have unique risks, restrictions are placed on their use in a high-risk operating state to mitigate adverse impacts to the IESO-controlled grid.

The following contingency types apply to 115 kV, 230 kV and 500 kV systems. Table C-1: RAS Restrictions during High-Risk Operating State

| Contingency Type | High-Risk Operating State Due to Adverse Weather within the Weather Advisory Area (refer to notes A, B, C and D) | High-Risk Operating State Due to Conditions not within the Weather Advisory Area (refer to notes A, B and C) |
| --- | --- | --- |
| Recognized Double Element | No restrictions to G/R or L/R | The primary concern is adverse effects of a false RAS operation. The following restrictions therefore apply: G/R or runback is permissible provided its use is minimized. L/R is permissible, provided IESO-controlled grid system security criteria could not otherwise be satisfied. |
| Recognized Single Element | G/R or runback is permissible, provided: Arming is limited to outage periods or short-duration periods, or Its magnitude is reduced during adverse weather periods G/R is permissible, provided the only other alternative is to remove the unit from service, or the unit would be automatically removed from service as a result of the initiating contingency. L/R is permissible provided IESO-controlled grid system security criteria could not otherwise be satisfied. |  |

A RAS must NOT be utilized if a fail-to-trip condition is suspected.

A RAS may be selectively used to provide additional system security beyond normal criteria, provided the restrictions in  Table C-1 are observed.

The restrictions in this table do not apply to RAS selections for extreme contingencies.

The Weather Advisory Area is within 50 km of the circuits for which the RAS is selected.

– End of Appendix –

## Special Considerations for Inverter-Based Resources

To maintain system security for all foreseeable operating conditions, it is necessary to give special consideration for the electromagnetic transient (EMT) phenomena that may result from inverter-based resources (IBR); namely sub-synchronous resonance (SSR) and sub-synchronous control interactions (SSCI). Phenomena such as SSR and SSCI can result in units pulling out of synchronism unexpectedly or underdamped oscillatory response, among other things, which can result in security criteria to not be met or equipment damage.

Assessing phenomena such as SSR and SSCI requires the application of EMT assessment techniques, which have significant computational and time demands, and so, it is not practical to perform EMT assessment for all foreseeable operating conditions. Instead, bright-line criteria are used to restrict operating configurations that have an unacceptable risk of SSR and SSCI, or to trigger EMT assessment on an as-needed basis.

These criteria do not guarantee security against SSR or SSCI, and so, the IESO has discretion to take any control action to prevent or correct SSR or SSCI during real-time operation of the IESO-controlled grid.

### D.1	Minimum Short Circuit Ratio

The IESO shall use short-circuit ratio (SCR) to assess if there is an unacceptable risk of SSR, SSCI or other EMT phenomena. The IESO shall consider the effects of all recognized contingencies included in Appendix A: Recognized Contingencies in determining SCR. The following criteria apply:

- The SCR of IBRs shall not be allowed to fall below 5.

- For SCR of IBRs below 7, a facility-based assessment shall be done. If time permits, the IESO may perform a detailed EMT study to confirm whether there is an unacceptable risk of SSR or SSCI. If time does not permit, IESO will take necessary actions to prevent the SCR of the IBR from falling below 7. For example, during the outage management process, this may correspond to rejection of an outage.

SCR is calculated as the following:

SCRk=AFLkPmax, k

Where,

SCRk is the short-circuit ratio of IBR facility “k”;

AFLk is the available fault level at the point of interconnection of IBR facility “k”; and

Pmax,k is the registered maximum rated active power of IBR facility “k”.

### D.2	Resonant Circuit Configurations

Configurations that result in IBR to be connected radially with series compensation shall be avoided. Due regard shall be given to post-contingency configurations.

– End of Appendix –

List of Acronyms

| Acronym | Term |
| --- | --- |
| ABNO | available but not operating |
| AVR | automatic voltage regulation |
| BES | bulk electric system |
| BPS | bulk power system |
| DESN | dual element spot network |
| EOSCA | emergency operating state control actions |
| G/R | generation rejection |
| HVDC | high voltage direct current |
| IROL | interconnection reliability operating limit |
| kV | kilovolt |
| L/R | load rejection |
| MM | market manual |
| MR | market rules |
| MVA | megavolt-amp |
| NERC | North American Electric Reliability Corporation |
| NPCC | Northeast Power Coordinating Council, Inc. |
| ORTAC | Ontario Resource and Transmission Assessment Criteria |
| PV | power-voltage |
| RAS | remedial action scheme |
| SOL | system operating limit |
| UFLS | under-frequency load shedding |

– End of Section –

References

| Document ID & Link | Document Title |
| --- | --- |
| RUL-6 to RUL-24 | Market Rules for the Ontario Electricity Market |
| MAN-108 | Market Manual 1.5: Market Registration Procedures |
| MAN-138 | Market Manual 2.8: Reliability Assessments Information Requirements |
| MAN-111 | Market Manual 4.3: Operation of the Real-Time Markets |
| MAN-122 | Market Manual 7.2: Near-Term Assessments and Reports |
| MAN-123 | Market Manual 7.3: Outage Management |
| MAN-157 | Market Manual 7.8: Ontario Power System Restoration Plan |
| MAN-158 | Market Manual 7.10: Ontario Electricity Emergency Plan |
| MAN-161 | Market Manual 11.2: Ontario Reliability Compliance Program |
| IMO_REQ_0041 | Ontario Resource and Transmission Assessment Criteria (ORTAC). |

– End of Document –

Refer to NERC Glossary of Terms. System Operating Limit is used interchangeably with security limit.

Refer to NERC glossary of terms

Remaining security criteria need not be evaluated, as NPCC Directory #1 allows for the loss of small or radial portions of the system, provided consequence is demonstrably contained to the IESO-controlled grid and the rest of the BPS demonstrates acceptable performance. The security criteria listed are consistent with the aforementioned requirement.

Refer to NERC Glossary of Terms

An element is defined as generation unit, transmission circuit, transformer, shunt device, or bus section.

See Appendix 4.2 of MR Ch.4.