## Menu
Annual Planning Outlook
Transfer Capabilities Across Major Interfaces and Interties
December 2021
Transfer Capability and Limiting Phenomenon for Major Internal Interfaces
Table 1: Major Internal Interface All-in-Service Transfer Capabilities
Table 2: Major Internal Interface N-1 Transfer Capabilities
Transfer Capability and Limiting Phenomenon for Interties between Ontario and Neighbouring Jurisdictions
Table 3: Interconnection All-in-Service Transfer Capabilities
Disclaimer: All transmission transfer capabilities and related details about the limiting phenomena are based on the best information available to the IESO at the time of publication of the 2021 APO. These values may change as new and/or updated information and assumptions become available. All values represent the Transmission Transfer Capabilities respecting the planning requirements per applicable standards/criteria, and should not be interpreted as System Operating Limits.

## Table 1
Back to main menu
Table 1: Major Internal Interface All-in-Service Transfer Capabilities
Interface | Capability (MW) | Limiting Phenomenon | Limiting Contingency (Alternate, where applicable) | Limiting Element (Alternate, where applicable) | Note
BLIP | 2,020 - 3,700 | Thermal | Varies by year | Varies by year | Summer limitation
NBLIP | 570-1,550 | Thermal | Varies by year | Varies by year | Summer limitation; Pre-contingency overloading
QFW | 2400 | Thermal | Q25BM+ Q29HM | Q24HM | Summer limitation; QFW reinforcement, Q26M & Q35M in-service (I/S)
FABCW | 7600 | None | None | None | Resources maxed before reaching a limitation
FETT | 4,230 - 5,200 | Thermal | Hurontario L21L30 (L19L29) | R19TH (R21H) | Summer limitation; dependent on generation patterns
TEC | 3100 | Thermal | Chats Falls AL22 | P15C | Summer limitation; Maximum transfer capability not expected to be reached (i.e., not limiting)
FIO | 2950 | None | None | None | Year round limitation HVDC export maxed before reaching a limitation Local thermal phenomenon can possibly be more restrictive under certain conditions
FN | 1965 | Voltage Decline | Hanmer PL503/PL504 | Hanmer 500kV | Year round limitation
FS | 2030 | Voltage Collapse | Hanmer PL503/PL504 | Hanmer 500kV | Year round limitation
EWTE | 350 | Voltage Decline | A23P+A24P | Mississagi 230 kV | Year round limitation E-W Tie reinforcement I/S
EWTW | 500 | Voltage Magnitude | A21L+A22L | Mackenzie 230 kV | Year round limitation E-W Tie reinforcement I/S
MISSW | 510 - 585 | Voltage Decline | A23P+A24P | Mississagi 230 kV | Year round limitation E-W Tie reinforcement I/S
Disclaimer: All transmission transfer capabilities and related details about the limiting phenomena are based on the best information available to the IESO at the time of publication of the 2021 APO. These values may change as new and/or updated information and assumptions become available. All values represent the Transmission Transfer Capabilities respecting the planning requirements per applicable standards/criteria, and should not be interpreted as System Operating Limits.
Back to main menu

## Table 2
Back to main menu
Table 2: Major Internal Interface N-1 Transfer Capabilities
Interface | Capability (MW) | Limiting Phenomenon | Outage | Limiting Contingency | Limiting Element | Note
BLIP | 2,030 - 3,700 | Thermal | Varies by year | Varies by year | Varies by year | Summer limitation
NBLIP | 580 - 1,175 | Thermal | Varies by year | Varies by year | Varies by year | Summer limitation
QFW | 2,000 | Thermal | Any QFW circuit | Any | Any | Summer limitation
FABCW | 7600 | - | Any | - | - | Resources maxed before reaching a limitation Assumes use of generation rejection per Bruce Remedial Action Scheme
FETT | 2,580 - 3,350 | Thermal | M570V | B560V + M571V | R21TH / R19TH | Summer limitation; dependent on generation patterns
FIO | 1630 | Voltage Collapse | X521A | X522A + E34M | Hawthorne 230 kV | Year round limitation
FN | 560 | Thermal | X503E | X504E | D5H | Summer limitation
FS | 760 | Thermal | X503E | X504E | D5H | Year round limitation, Loss of Synchronism
MISSW | 465 | Voltage Decline | X74P | A23P+A24P | Third Line 230 kV | Year round limitation
Disclaimer: All transmission transfer capabilities and related details about the limiting phenomena are based on the best information available to the IESO at the time of publication of the 2021 APO. These values may change as new and/or updated information and assumptions become available. All values represent the Transmission Transfer Capabilities respecting the planning requirements per applicable standards/criteria, and should not be interpreted as System Operating Limits.
Back to main menu

## Table 3
Back to main menu
Table 3: Interconnection All-in-Service Transfer Capabilities
Interconnection | Capability (MW) | Limiting Phenomenon | Limiting Contingency (Alternate, where applicable) | Limiting Element (Alternate, where applicable) | Note
Ontario to Manitoba | 250 | Thermal | K21W (K22W) | K22W (K21W) | Summer limitation; capability can be reduced during certain operating conditions
Manitoba to Ontario | 250 | Thermal | K21W (K22W) | K22W (K21W) | Summer limitation; capability can be reduced during certain operating conditions
Ontario to Minnesota | 150 | Thermal | None | F3M | Summer limitation; pre-contingency
Minnesota to Ontario | 150 | Thermal | None | F3M | Summer limitation; pre-contingency
Ontario to Michigan | 1500 | Thermal | B3N | St. Clair DM | Summer limitation
Michigan to Ontario | 1300 | Thermal | St. Clair DM (L28C+L29C) | B3N (J5D) | Summer limitation
Ontario to New York @ Niagara | 1950 | Thermal | PA301/PA302 | PA27 | Summer limitation
New York to Ontario @ Niagara | 1550 | Thermal | PA301/PA302 | PA27 | Summer limitation
Ontario to New York @ St. Lawrence | 450 | Thermal | St. Lawrence L31L33 | L34P | Summer limitation
New York to Ontario @ St. Lawrence | 350 | Thermal | B31L+L24A | L21H | Summer limitation
Ontario to Quebec @ HVDC | 1250 | Converter Limitation | - | - | -
Quebec to Ontario @ HVDC | 1250 | Converter Limitation | - | - | -
Ontario to Quebec @ B31L + B5D | 470 | External | - | - | Limitation in Quebec power system
Quebec to Ontario @ B31L + B5D | 400 | Stability | - | - | Beauharnois transient stability
Disclaimer: All transmission transfer capabilities and related details about the limiting phenomena are based on the best information available to the IESO at the time of publication of the 2021 APO. These values may change as new and/or updated information and assumptions become available. All values represent the Transmission Transfer Capabilities respecting the planning requirements per applicable standards/criteria, and should not be interpreted as System Operating Limits.
Back to main menu