## Menu
Reliability Outlook
2026-09-17
2026 Q3 Outlook
From October 2026 – March 2028
1.0 Demand Forecast: First 18 Months
Table 1.1 Firm: Historical and Forecast Energy Summary
Table 1.1 Planned: Historical and Forecast Energy Summary
Table 1.1.1 Firm: Monthly Peak and Energy Demand
Table 1.1.1 Planned: Monthly Peak and Energy Demand | NOTE(S):
Table 1.1.2 Firm: Weekly Coincident Peak Demand by Zone
Table 1.1.2 Planned: Weekly Coincident Peak Demand by Zone | 1. Demand Forecast, Supply Forecast, and Transmission Outlook Considerations
Table 1.1.3 Firm: Weekly Energy Demand by Zone | The demand models use actual demand, weather, and economic data through the end of July 2026. The latest business intelligence regarding large step loads was incorporated in mid‑July 2026. Actual weather and demand data for August 2026, which were observed after demand modeling, are also included in the tables for informational purposes.
Table 1.1.3 Planned: Weekly Energy Demand by Zone
Table 1.2 Firm: Forecasted Seasonal Peaks
Table 1.2 Planned: Forecasted Seasonal Peaks | b) This Reliability Outlook includes planned generator outages over the 18‑month period, submitted by market participants to the IESO’s outage management system by August 27, 2026.
Table 1.3: Large Step Load Impacts, Firm and Planned Demand
Table 1.4 Firm: Weekly Energy and Peak Demand Forecast | c) This Reliability Outlook includes planned transmission outages that were submitted to the IESO’s outage management system by late August 2026.
Table 1.4 Planned: Weekly Energy and Peak Demand Forecast
Table 1.4.1: Weekly Weather and Demand History
Table 1.4.2: Monthly Weather and Demand History | 2. Table 4.2 - FETT Interface
Table 1.4.3: Monthly Consumption by Market Participant Type | Consistent with the Q2 Reliability Outlook, the FETT limit continues to reflect the impact of the Darlington VBO.
Table 1.4.4: Economic Assumptions
Table 1.4.5: Estimate of Contracted Embedded Generation Capacity (MW)
2.0 Resource Supply Forecast: First 18 Months
Table 2.1: Existing Grid-Connected Resource Capacity
Table 2.2: Committed Generation and Electricity Storage Resources Status over the 18-month Reliability Outlook Period
Table 2.3: Monthly Historical Hydroelectric Median Values for Expected Weather Conditions
Table 2.4: Monthly Wind Capacity Contribution Values
Table 2.5: Monthly Solar Capacity Contribution Values
Table 2.6: Monthly Off-Peak Wind Capacity Contribution Values
Table 2.7: Summary of Available Resources under Expected Weather
3.0 Resource Adequacy Assessment: First 18 Months
Table 3.1 Firm: Summary of Zonal Energy for Firm Scenario, Expected Weather
Table 3.2 Planned: Summary of Zonal Energy for Planned Scenario, Expected Weather
Table 3.3 Firm: Ontario Energy Production by Fuel Type for the Firm Scenario, Expected Weather
Table 3.4 Planned: Ontario Energy Production by Fuel Type for the Planned Scenario, Expected Weather
Table 3.5: Assessment of Resource Adequacy: Expected Weather, Firm Scenario
Table 3.6: Assessment of Resource Adequacy: Expected Weather, Planned Scenario
Table 3.7: Zonal Bottled Generation: Expected Weather, Both Scenarios
Table 3.8: Energy Production Capability Forecast
Table 3.9: Reductions by Fuel Type: Expected Weather, Firm Scenario
Table 3.10: Reductions by Fuel Type: Expected Weather, Planned Scenario
Table 3.11: Firm Scenario - Expected Weather: Ontario Monthly Energy Production by Fuel Type
Table 3.12: Planned Scenario - Expected Weather: Ontario Monthly Energy Production by Fuel Type
Figure 3.1: Reserve Above Requirement
4.0 Transmission
Table 4.1: Transmission Projects
Table 4.2: Interface Limits with All Elements in Service
Table 4.3: Interconnection Flow Limits
Table 4.4: Bruce Zone Transmission Outages
Table 4.5: East Zone Transmission Outages
Table 4.6: Essa Zone Transmission Outages
Table 4.7: Niagara Zone Transmission Outages
Table 4.8: Northeast Zone Transmission Outages
Table 4.9: Northwest Zone Transmission Outages
Table 4.10: Ottawa Zone Transmission Outages
Table 4.11: Southwest Zone Transmission Outages
Table 4.12: Toronto Zone Transmission Outages
Table 4.13: West Zone Transmission Outages
Table 4.14: External Interties Transmission Outages

## Table 1.1 Firm
Back to main menu
Table 1.1 Firm: Historical and Forecast Energy Summary
Year | Normal Weather Energy (TWh) | % Growth in Energy
2006 | 152.349 | -1.858%
2007 | 151.6029 | -0.4897%
2008 | 148.9203 | -1.769%
2009 | 140.59 | -5.594%
2010 | 141.7415 | 0.819%
2011 | 141.0103 | -0.5158%
2012 | 140.7232 | -0.2036%
2013 | 140.4483 | -0.1954%
2014 | 139.4864 | -0.6848%
2015 | 136.3504 | -2.248%
2016 | 135.9259 | -0.3113%
2017 | 132.1965 | -2.744%
2018 | 135.5109 | 2.507%
2019 | 134.6666 | -0.6231%
2020 | 131.9143 | -2.044%
2021 | 133.7042 | 1.357%
2022 | 136.6504 | 2.204%
2023 | 138.0378 | 1.015%
2024 | 141.0947 | 2.215%
2025 | 145.3951 | 3.048%
2026 (Forecast) | 147.6659 | 1.562%
2027 (Forecast) | 147.834 | 0.1138%
Back to main menu

## Table 1.1 Planned
Back to main menu
Table 1.1 Planned: Historical and Forecast Energy Summary
Year | Normal Weather Energy (TWh) | % Growth in Energy
2006 | 152.349 | -1.858%
2007 | 151.6029 | -0.4897%
2008 | 148.9203 | -1.769%
2009 | 140.59 | -5.594%
2010 | 141.7415 | 0.819%
2011 | 141.0103 | -0.5158%
2012 | 140.7232 | -0.2036%
2013 | 140.4483 | -0.1954%
2014 | 139.4864 | -0.6848%
2015 | 136.3504 | -2.248%
2016 | 135.9259 | -0.3113%
2017 | 132.1965 | -2.744%
2018 | 135.5109 | 2.507%
2019 | 134.6666 | -0.6231%
2020 | 131.9143 | -2.044%
2021 | 133.7042 | 1.357%
2022 | 136.6504 | 2.204%
2023 | 138.0378 | 1.015%
2024 | 141.0947 | 2.215%
2025 | 145.3951 | 3.048%
2026 (Forecast) | 147.7116 | 1.593%
2027 (Forecast) | 149.3185 | 1.088%
Back to main menu

## Table 1.1.1 Firm
Back to main menu
Table 1.1.1 Firm: Monthly Peak and Energy Demand
Forecasted Peak and Energy Demand
| Peak Demand (MW) |  |  | Energy Demand (GWh)
Month | Current Forecast | Previous Forecast | Weather Corrected Actual | Current Forecast | Previous Forecast | Weather Corrected Actual
2012-01-01 | 22160.0997 | 22160.0997 | 22084.7322 | 13280.0235 | 13280.0235 | 12932.2873
2012-02-01 | 21813.8691 | 21813.8691 | 20756.8677 | 12202.5791 | 12202.5791 | 11380.2015
2012-03-01 | 20708.9072 | 20708.9072 | 20595.0545 | 12264.8125 | 12264.8125 | 11726.1779
2012-04-01 | 18745.092 | 18745.092 | 19830.1533 | 10866.5786 | 10866.5786 | 10883.4994
2012-05-01 | 19038.2309 | 19038.2309 | 19736.9901 | 10943.6824 | 10943.6824 | 10838.5019
2012-06-01 | 22569.1521 | 22569.1521 | 22832.4909 | 11398.2442 | 11398.2442 | 11511.081
2012-07-01 | 23298.1422 | 23298.1422 | 23630.2664 | 12319.3311 | 12319.3311 | 13057.6199
2012-08-01 | 22956.5741 | 22956.5741 | 22726.501 | 12419.0386 | 12419.0386 | 12373.2613
2012-09-01 | 20506.0631 | 20506.0631 | 20370.1157 | 10811.3017 | 10811.3017 | 10900.4102
2012-10-01 | 18345.9037 | 18345.9037 | 18684.153 | 11199.8353 | 11199.8353 | 11149.8822
2012-11-01 | 20571.5606 | 20571.5606 | 20258.2258 | 11629.6439 | 11629.6439 | 11663.449
2012-12-01 | 21693.287 | 21693.287 | 20910.8981 | 12612.0073 | 12612.0073 | 12306.8289
2012 | 23298.1422 | 23298.1422 | 23630.2664 | 141947.0782 | 141947.0782 | 140723.2004
2013-01-31 | 22013.997 | 22013.997 | 22610 | 13314.3055 | 13314.3055 | 13061.0693
2013-02-28 | 21773.6201 | 21773.6201 | 21333.0082 | 11819.7381 | 11819.7381 | 11668.8474
2013-03-31 | 20634.9497 | 20634.9497 | 20784.4526 | 12283.0437 | 12283.0437 | 11869.9986
2013-04-30 | 18492.3312 | 18492.3312 | 19284.8182 | 11018.1303 | 11018.1303 | 11090.2932
2013-05-31 | 19100.9692 | 19100.9692 | 18341.9804 | 10932.3105 | 10932.3105 | 10533.5712
2013-06-30 | 22499.2459 | 22499.2459 | 22719.4401 | 11406.4319 | 11406.4319 | 11283.4325
2013-07-31 | 23212.9348 | 23212.9348 | 24352.1456 | 12479.5529 | 12479.5529 | 12736.3503
2013-08-31 | 22359.7987 | 22359.7987 | 23255.371 | 12227.7513 | 12227.7513 | 12084.9413
2013-09-30 | 20513.3592 | 20513.3592 | 20422.3176 | 11015.3041 | 11015.3041 | 10767.0057
2013-10-31 | 18388.3002 | 18388.3002 | 18981.007 | 11279.1846 | 11279.1846 | 11114.0467
2013-11-30 | 20326.4941 | 20326.4941 | 20034.8189 | 11686.9287 | 11686.9287 | 11709.7788
2013-12-31 | 21395.0558 | 21395.0558 | 21184.5386 | 12699.9803 | 12699.9803 | 12528.9266
2013 | 23212.9348 | 23212.9348 | 24352.1456 | 142162.6617 | 142162.6617 | 140448.2614
2014-01-31 | 22319.8106 | 22319.8106 | 22043.8439 | 13356.427 | 13356.427 | 13409.7767
2014-02-28 | 20964.0592 | 20964.0592 | 21218.2216 | 11748.3799 | 11748.3799 | 11812.9441
2014-03-31 | 19906 | 19906 | 20728.4579 | 12054.5719 | 12054.5719 | 12242.1563
2014-04-30 | 17649 | 17649 | 19249.9632 | 10731.1367 | 10731.1367 | 11038.5265
2014-05-31 | 18964 | 18964 | 18750.4605 | 10790.2174 | 10790.2174 | 10546.4252
2014-06-30 | 22469.55 | 22469.55 | 20705.1957 | 11346.2756 | 11346.2756 | 11140.5499
2014-07-31 | 22948.69 | 22948.69 | 22294.8035 | 12360.0815 | 12360.0815 | 12324.9268
2014-08-31 | 21403.44 | 21403.44 | 21644.3547 | 11992.5131 | 11992.5131 | 11819.2371
2014-09-30 | 19023.2704 | 19023.2704 | 19449.0766 | 10579.5258 | 10579.5258 | 10671.4853
2014-10-31 | 18638.7361 | 18638.7361 | 18447.2196 | 11126.7565 | 11126.7565 | 10814.1957
2014-11-30 | 20302.34 | 20302.34 | 19923.2587 | 11497.4835 | 11497.4835 | 11410.1121
2014-12-31 | 21237.74 | 21237.74 | 21582.6701 | 12769.4956 | 12769.4956 | 12256.0958
2014 | 22948.69 | 22948.69 | 22294.8035 | 140352.8643 | 140352.8643 | 139486.4317
2015-01-31 | 22293.59 | 22293.59 | 21503.4489 | 13068.9431 | 13068.9431 | 12937.1182
2015-02-28 | 21016.81 | 21016.81 | 19709.6284 | 11528.5197 | 11528.5197 | 11740.7311
2015-03-31 | 19840.93 | 19840.93 | 20109.8817 | 11856.8161 | 11856.8161 | 11748.227
2015-04-30 | 18121.2 | 18121.2 | 19362.8308 | 10542.0267 | 10542.0267 | 10624.618
2015-05-31 | 19370.33 | 19370.33 | 17881.7583 | 10635.9243 | 10635.9243 | 10231.5964
2015-06-30 | 22276.64 | 22276.64 | 20554.6293 | 11410.2692 | 11410.2692 | 10908.724
2015-07-31 | 22888.49 | 22888.49 | 22638.5319 | 12174.2184 | 12174.2184 | 12273.6405
2015-08-31 | 21463.69 | 21463.69 | 22383 | 11821.2763 | 11821.2763 | 11782.7212
2015-09-30 | 18485 | 18485 | 19299.6325 | 10512.648 | 10512.648 | 10718.9879
2015-10-31 | 18339 | 18339 | 18444.3181 | 11150.1256 | 11150.1256 | 10731.7474
2015-11-30 | 20306 | 20306 | 19631.9089 | 11595.0899 | 11595.0899 | 10867.5486
2015-12-31 | 21160.04 | 21160.04 | 20418.0801 | 12611.2501 | 12611.2501 | 11784.7123
2015 | 22888.49 | 22888.49 | 22638.5319 | 138907.1073 | 138907.1073 | 136350.3725
2016-01-31 | 22360.24 | 22360.24 | 21249.7402 | 12982.1466 | 12982.1466 | 12523.599
2016-02-28 | 20985.25 | 20985.25 | 20194.6163 | 11806.8997 | 11806.8997 | 11502.97
2016-03-31 | 20075.21 | 20075.21 | 20324.618 | 11758.7447 | 11758.7447 | 11445.7227
2016-04-30 | 17405.08 | 17405.08 | 18912.1728 | 10309.6515 | 10309.6515 | 10578.9099
2016-05-31 | 19235.65 | 19235.65 | 19707.6447 | 10530.0143 | 10530.0143 | 10115.8584
2016-06-30 | 22315.7305 | 22315.7305 | 21568.912 | 11378.6081 | 11378.6081 | 11141.3797
2016-07-31 | 22599.9414 | 22599.9414 | 22288.7672 | 11896.1402 | 11896.1402 | 12345.0421
2016-08-31 | 21440.3166 | 21440.3166 | 22375.997 | 11771.834 | 11771.834 | 12295.9028
2016-09-30 | 18289 | 18289 | 19712.7154 | 10401.8861 | 10401.8861 | 10659.2295
2016-10-31 | 18079 | 18079 | 18394.9922 | 10947.5325 | 10947.5325 | 10453.1463
2016-11-30 | 20296 | 20296 | 19544.7667 | 11524.026 | 11524.026 | 10913.6011
2016-12-31 | 20888 | 20888 | 20286.7849 | 12430.7427 | 12430.7427 | 11950.5536
2016 | 22599.9414 | 22599.9414 | 22375.997 | 137738.2263 | 137738.2263 | 135925.9151
2017-01-31 | 21913.73 | 21913.73 | 20965.9674 | 12818.8508 | 12818.8508 | 12369.7298
2017-02-28 | 20966.2287 | 20966.2287 | 20379.4501 | 11294.713 | 11294.713 | 10787.4931
2017-03-31 | 20137.3 | 20137.3 | 18692.3503 | 11824.0632 | 11824.0632 | 11413.3465
2017-04-30 | 17969.79 | 17969.79 | 18482.7844 | 10366.7129 | 10366.7129 | 10105.7565
2017-05-31 | 19193.19 | 19193.19 | 18260.3078 | 10576.9018 | 10576.9018 | 10012.8427
2017-06-30 | 22454.87 | 22454.87 | 21144.8187 | 11159.3312 | 11159.3312 | 10682.999
2017-07-31 | 22492.73 | 22492.73 | 22152.8524 | 11984.7355 | 11984.7355 | 11851.6211
2017-08-31 | 22376.43 | 22376.43 | 21323.3584 | 12105.5471 | 12105.5471 | 11513.597
2017-09-30 | 19490.21 | 19490.21 | 17821.4732 | 10494.2948 | 10494.2948 | 10155.927
2017-10-31 | 18030.62 | 18030.62 | 17407.7858 | 10942.7953 | 10942.7953 | 10260.3837
2017-11-30 | 20230.97 | 20230.97 | 19195.4397 | 11371.7451 | 11371.7451 | 10946.7668
2017-12-31 | 20901.44 | 20901.44 | 21439.6493 | 12303.6865 | 12303.6865 | 12096.0133
2017 | 22492.73 | 22492.73 | 22152.8524 | 137243.3774 | 137243.3774 | 132196.4765
2018-01-31 | 21618.93 | 21618.93 | 20177.5339 | 12685.9178 | 12685.9178 | 12679.8037
2018-02-28 | 20242.21 | 20242.21 | 20042.2165 | 11074.1738 | 11074.1738 | 11081.1365
2018-03-31 | 19551.97 | 19551.97 | 19330.8728 | 11423.555 | 11423.555 | 11267.3415
2018-04-30 | 17669.81 | 17669.81 | 18107.9593 | 10157.8502 | 10157.8502 | 10586.2978
2018-05-31 | 18817.47 | 18817.47 | 19262.1307 | 10289.6502 | 10289.6502 | 10081.137
2018-06-30 | 21890.0001 | 21890.0001 | 20626.9619 | 10863.4062 | 10863.4062 | 10980.4534
2018-07-31 | 22076.0001 | 22076.0001 | 22409.0792 | 11652.7714 | 11652.7714 | 12483.776
2018-08-31 | 21946.0001 | 21946.0001 | 21385.6483 | 11685.5744 | 11685.5744 | 12040.5393
2018-09-30 | 19019 | 19019 | 19505.5646 | 10189.9802 | 10189.9802 | 10579.1906
2018-10-31 | 17788 | 17788 | 17751.4152 | 10750.0648 | 10750.0648 | 10526.7735
2018-11-30 | 19828 | 19828 | 19266.3918 | 11170.7506 | 11170.7506 | 11184.9393
2018-12-31 | 20503 | 20503 | 20375.1864 | 12007.3958 | 12007.3958 | 12019.553
2018 | 22076.0001 | 22076.0001 | 22409.0792 | 133951.0905 | 133951.0905 | 135510.9416
2019-01-31 | 21506 | 21506 | 21058.2817 | 12973.2132 | 12973.2132 | 12688.8389
2019-02-28 | 20008 | 20008 | 20420.3692 | 11162.2057 | 11162.2057 | 11212.4836
2019-03-31 | 19457 | 19457 | 19573.6921 | 11522.1982 | 11522.1982 | 11458.0531
2019-04-30 | 17548 | 17548 | 18796.3299 | 10252.9314 | 10252.9314 | 10432.2785
2019-05-31 | 18663 | 18663 | 17977.0308 | 10412.0446 | 10412.0446 | 10218.7126
2019-06-30 | 21623 | 21623 | 21239.1838 | 10939.3571 | 10939.3571 | 10608.5215
2019-07-31 | 22061 | 22061 | 21120.5208 | 11763.9974 | 11763.9974 | 12446.1887
2019-08-31 | 21200 | 21200 | 22490.4547 | 11598.2109 | 11598.2109 | 11798.5843
2019-09-30 | 19469.84 | 19469.84 | 18958.9757 | 10564.4926 | 10564.4926 | 10167.6302
2019-10-31 | 17559 | 17559 | 18814.592 | 10788.0047 | 10788.0047 | 10446.8836
2019-11-30 | 19597 | 19597 | 19001.8635 | 11194.6524 | 11194.6524 | 11094.2081
2019-12-31 | 20307 | 20307 | 20974 | 12086.6766 | 12086.6766 | 12094.1802
2019 | 22061 | 22061 | 22490.4547 | 135257.9849 | 135257.9849 | 134666.5633
2020-01-31 | 21185.0004 | 21185.0004 | 21137.8728 | 12859.4588 | 12859.4588 | 12460.9405
2020-02-28 | 19917.0004 | 19917.0004 | 19776.0281 | 11586.6754 | 11586.6754 | 11253.1814
2020-03-31 | 19377.0004 | 19377.0004 | 19680.948 | 11522.322 | 11522.322 | 11058.3098
2020-04-30 | 17302.0004 | 17302.0004 | 16515.7848 | 10229.1483 | 10229.1483 | 9383.3554
2020-05-31 | 17426 | 17426 | 18761.2836 | 9434.378 | 9434.378 | 9306.4436
2020-06-30 | 20034 | 20034 | 20741.8718 | 10274.389 | 10274.389 | 10596.6512
2020-07-31 | 22364.4404 | 22364.4404 | 24057.7367 | 11731.6936 | 11731.6936 | 12529.7172
2020-08-31 | 21631.4406 | 21631.4406 | 25317.7535 | 11441.5908 | 11441.5908 | 12338.1938
2020-09-30 | 20312.4408 | 20312.4408 | 19254.2062 | 10356.1124 | 10356.1124 | 10011.2355
2020-10-31 | 17039.9727 | 17039.9727 | 17587.3164 | 10040.7873 | 10040.7873 | 10349.5982
2020-11-30 | 18891.9134 | 18891.9134 | 19416.1975 | 10531.6058 | 10531.6058 | 10693.8532
2020-12-31 | 19805.1651 | 19805.1651 | 20975.3455 | 11815.0887 | 11815.0887 | 11932.8039
2020 | 22364.4404 | 22364.4404 | 25317.7535 | 131823.25 | 131823.25 | 131914.2838
2021-01-31 | 21176.0005 | 21176.0005 | 20951.6431 | 12539.1611 | 12539.1611 | 12307.6071
2021-02-28 | 20760.0005 | 20760.0005 | 20175.4672 | 11073.4765 | 11073.4765 | 11144.3783
2021-03-31 | 19384.0005 | 19384.0005 | 19868.2566 | 11497.7125 | 11497.7125 | 11249.5616
2021-04-30 | 17070.0009 | 17070.0009 | 17618.7846 | 10244.8035 | 10244.8035 | 10097.7166
2021-05-31 | 18055.3342 | 18055.3342 | 18021.5172 | 10152.0681 | 10152.0681 | 9986.9371
2021-06-30 | 22162.0009 | 22162.0009 | 21528.4908 | 10747.5852 | 10747.5852 | 10840.8856
2021-07-31 | 22413.0005 | 22413.0005 | 22251.4821 | 11806.5074 | 11806.5074 | 11970.9832
2021-08-31 | 22235.0005 | 22235.0005 | 21854.4728 | 11706.2663 | 11706.2663 | 12072.0791
2021-09-30 | 21212.0005 | 21212.0005 | 18979.8917 | 10472.6839 | 10472.6839 | 10401.3058
2021-10-31 | 17270.7147 | 17270.7147 | 17606.8602 | 10365.0376 | 10365.0376 | 10429.4829
2021-11-30 | 19227.38 | 19227.38 | 19684.7166 | 10886.7659 | 10886.7659 | 11017.3258
2021-12-31 | 20088.8968 | 20088.8968 | 21331.5579 | 11984.4925 | 11984.4925 | 12185.9418
2021 | 22413.0005 | 22413.0005 | 22251.4821 | 133476.5604 | 133476.5604 | 133704.2048
2022-01-31 | 20983.6671 | 20983.6671 | 21334.1018 | 12536.9576 | 12536.9576 | 12928.5532
2022-02-28 | 20446.0004 | 20446.0004 | 20782.3287 | 11208.712 | 11208.712 | 11400.5165
2022-03-31 | 19401.3338 | 19401.3338 | 19941.2707 | 11617.5125 | 11617.5125 | 11793.6956
2022-04-30 | 17251.0005 | 17251.0005 | 17752.3935 | 10239.112 | 10239.112 | 10311.1592
2022-05-31 | 18269.0005 | 18269.0005 | 20136.0014 | 10372.2878 | 10372.2878 | 10137.6947
2022-06-30 | 22161.0005 | 22161.0005 | 22101.7092 | 10967.9836 | 10967.9836 | 11002.2267
2022-07-31 | 22542.0005 | 22542.0005 | 22484.9516 | 11893.9057 | 11893.9057 | 12411.016
2022-08-31 | 22430.0005 | 22430.0005 | 23477.9346 | 12028.3221 | 12028.3221 | 11998.9314
2022-09-30 | 21489.0005 | 21489.0005 | 20446.2276 | 10551.0851 | 10551.0851 | 10678.4907
2022-10-31 | 17559.0005 | 17559.0005 | 17724.6236 | 10603.0084 | 10603.0084 | 10447.0825
2022-11-30 | 19812.0005 | 19812.0005 | 19389.6575 | 11151.0711 | 11151.0711 | 11128.3255
2022-12-31 | 20241.0005 | 20241.0005 | 20584.5241 | 12191.9609 | 12191.9609 | 12412.7534
2022 | 22542.0005 | 22542.0005 | 23477.9346 | 135361.9188 | 135361.9188 | 136650.4453
2023-01-31 | 21170.3338 | 21170.3338 | 21435.1399 | 12663.6554 | 12663.6554 | 13052.768
2023-02-28 | 20892.3338 | 20892.3338 | 20433.0112 | 11375.0622 | 11375.0622 | 11325.8235
2023-03-31 | 19701.0485 | 19701.0485 | 19000.8853 | 11846.6528 | 11846.6528 | 11814.7494
2023-04-30 | 17785.9996 | 17785.9996 | 19103.3719 | 10349.2653 | 10349.2653 | 10374.8437
2023-05-31 | 18869.9996 | 18869.9996 | 18001.5877 | 10418.8057 | 10418.8057 | 10473.6584
2023-06-30 | 21884.9996 | 21884.9996 | 22417.4764 | 10652.496 | 10652.496 | 11230.6805
2023-07-31 | 22445.9996 | 22445.9996 | 23368.3724 | 11858.9002 | 11858.9002 | 12455.0186
2023-08-31 | 22396.9996 | 22396.9996 | 21865.1956 | 12249.9171 | 12249.9171 | 12005.3253
2023-09-30 | 21479.9996 | 21479.9996 | 21317.3942 | 10718.9739 | 10718.9739 | 10685.1004
2023-10-31 | 17668.0452 | 17668.0452 | 19208.5675 | 10593.967 | 10593.967 | 10757.1302
2023-11-30 | 19742.0453 | 19742.0453 | 20453.2108 | 11007.299 | 11007.299 | 11478.5016
2023-12-31 | 20346.0453 | 20346.0453 | 21211.1571 | 12018.94 | 12018.94 | 12384.2261
2023 | 22445.9996 | 22445.9996 | 23368.3724 | 135753.9345 | 135753.9345 | 138037.826
2024-01-31 | 21418.2553 | 21418.2553 | 21405.4347 | 12929.406 | 12929.406 | 13208.8176
2024-02-28 | 20987.7553 | 20987.7553 | 20022.691 | 11956.6273 | 11956.6273 | 11729.9509
2024-03-31 | 19645.2454 | 19645.2454 | 18939.8337 | 11836.2413 | 11836.2413 | 11632.2959
2024-04-30 | 17839.6154 | 17839.6154 | 18586.0743 | 10616.6408 | 10616.6408 | 10650.6806
2024-05-31 | 19148.7554 | 19148.7554 | 19498.7984 | 10660.6544 | 10660.6544 | 10640.585
2024-06-30 | 22502.1655 | 22502.1655 | 22585.2284 | 10892.6773 | 10892.6773 | 11334.1111
2024-07-31 | 22729.3704 | 22729.3704 | 23182.1746 | 12334.9116 | 12334.9116 | 12956.8035
2024-08-31 | 22592.9271 | 22592.9271 | 22518.533 | 12432.5962 | 12432.5962 | 12419.372
2024-09-30 | 21998.022 | 21998.022 | 21462.7165 | 11042.347 | 11042.347 | 10932.1478
2024-10-31 | 17976.8176 | 17976.8176 | 18603.2901 | 11073.6096 | 11073.6096 | 11048.6213
2024-11-30 | 20217.9361 | 20217.9361 | 19942.2233 | 11500.099 | 11500.099 | 11494.5336
2024-12-31 | 21036.6297 | 21036.6297 | 21342.8087 | 12626.6472 | 12626.6472 | 13046.7703
2024 | 22729.3704 | 22729.3704 | 23182.1746 | 139902.4576 | 139902.4576 | 141094.6899
2025-01-31 | 21835.8361 | 21835.8361 | 22379.5336 | 13253.9945 | 13253.9945 | 13661.657
2025-02-28 | 21259.4124 | 21259.4124 | 21116.0479 | 11671.9004 | 11671.9004 | 12130.7045
2025-03-31 | 20000.0174 | 20000.0174 | 19614.4739 | 12058.4394 | 12058.4394 | 12091.2745
2025-04-30 | 18154.8411 | 18154.8411 | 19246.3001 | 10619.601 | 10619.601 | 10891.1786
2025-05-31 | 19064.5516 | 19064.5516 | 18891.1849 | 10649.1943 | 10649.1943 | 10886.6628
2025-06-30 | 22279.0506 | 22279.0506 | 22678.4237 | 11223.7937 | 11223.7937 | 11544.6629
2025-07-31 | 23249.8525 | 23168.1551 | 23249.8525 | 13471.3387 | 12424.9641 | 13471.3387
2025-08-31 | 23530.1953 | 22782.3554 | 23530.1953 | 12734.6294 | 12363.8608 | 12734.6294
2025-09-30 | 21192.8937 | 21288.0486 | 21192.8937 | 11125.7506 | 11069.0052 | 11125.7506
2025-10-31 | 18572.3296 | 18320.7967 | 18572.3296 | 11323.7934 | 11076.979 | 11323.7934
2025-11-30 | 19963.3073 | 20153.1936 | 19963.3073 | 12004.1764 | 11562.3458 | 12004.1764
2025-12-31 | 21487.8851 | 21447.1157 | 21487.8851 | 13529.2595 | 12900.8568 | 13529.2595
2025 | 23530.1953 | 23168.1551 | 23530.1953 | 143665.8713 | 140874.935 | 145395.0883
2026-01-31 | 22160.5721 | 22550.57 | 22160.5721 | 13936.0376 | 13826.1993 | 13936.0376
2026-02-28 | 21428.1773 | 21686.2 | 21428.1773 | 12322.8763 | 12168.7162 | 12322.8763
2026-03-31 | 19889.5794 | 20412.11 | 19889.5794 | 12592.449 | 12554.0826 | 12592.449
2026-04-30 | 19288.6539 | 18337.2522 | 19288.6539 | 11195.2801 | 10995.8665 | 11195.2801
2026-05-31 | 19401.3919 | 19510.8225 | 19401.3919 | 11155.5649 | 11100.8529 | 11155.5649
2026-06-30 | 23371.3311 | 23042.9438 | 23371.3311 | 11932.5336 | 11828.0828 | 11932.5336
2026-07-31 | 24298.8266 | 23592.6172 | 24298.8266 | 13701.3716 | 12841.511 | 13701.3716
2026-08-31 | 23142.9682 | 22878.6943 | 23142.9682 | 13018.1365 | 12548.2185 | 13018.1365
2026-09-30 | 21567.0555 | 21567.0555 |  | 11316.3439 | 11316.3439
2026-10-31 | 18862.7813 | 18776.2167 |  | 11326.8967 | 11361.2904
2026-11-30 | 20891.5646 | 20782.6292 |  | 11926.7512 | 11941.9091
2026-12-31 | 21893.8444 | 21776.078 |  | 13241.6164 | 13237.142
2026 | 24298.8266 | 23592.6172 | 24298.8266 | 147665.8577 | 145720.2151 | 99854.2496
2027-01-31 | 22834.2677 | 22691.8172 |  | 13805.2838 | 13819.6005
2027-02-28 | 21945.5438 | 21828.0782 |  | 12244.6823 | 12216.558
2027-03-31 | 20658.6868 | 20549.573 |  | 12580.4232 | 12602.6329
2027-04-30 | 18651.8386 | 18549.026 |  | 11139.0608 | 11156.5115
2027-05-31 | 19895.1824 | 19799.6603 |  | 11145.2331 | 11191.4602
2027-06-30 | 23036.0398 | 22933.15 |  | 11807.6343 | 11863.8487
2027-07-31 | 24036.005 | 23950.1198 |  | 12944.1204 | 13113.7809
2027-08-31 | 23480.884 | 23398.2764 |  | 12884.6746 | 12909.1628
2027-09-30 | 22058.3713 | 21969.6568 |  | 11607.953 | 11649.7134
2027-10-31 | 19344.2102 | 19242.8644 |  | 11676.3464 | 11695.8399
2027-11-30 | 21497.1134 | 21389.042 |  | 12343.2198 | 12357.4073
2027-12-31 | 22514.7827 | 22399.3819 |  | 13655.3202 | 13663.8436
2027 | 24036.005 | 23950.1198 |  | 147833.952 | 148240.3597
2028-01-31 | 23771.6909 |  |  | 14466.5554
2028-02-28 | 22823.9422 |  |  | 13270.2791
2028-03-31 | 21486.7882 |  |  | 13248.2486
Back to main menu

## Table 1.1.1 Planned
Back to main menu
Table 1.1.1 Planned: Monthly Peak and Energy Demand
Forecasted Peak and Energy Demand
| Peak Demand (MW) |  |  | Energy Demand (GWh)
Month | Current Forecast | Previous Forecast | Weather Corrected Actual | Current Forecast | Previous Forecast | Weather Corrected Actual
2012-01-01 | 22160.0997 | 22160.0997 | 22084.7322 | 13280.0235 | 13280.0235 | 12932.2873
2012-02-01 | 21813.8691 | 21813.8691 | 20756.8677 | 12202.5791 | 12202.5791 | 11380.2015
2012-03-01 | 20708.9072 | 20708.9072 | 20595.0545 | 12264.8125 | 12264.8125 | 11726.1779
2012-04-01 | 18745.092 | 18745.092 | 19830.1533 | 10866.5786 | 10866.5786 | 10883.4994
2012-05-01 | 19038.2309 | 19038.2309 | 19736.9901 | 10943.6824 | 10943.6824 | 10838.5019
2012-06-01 | 22569.1521 | 22569.1521 | 22832.4909 | 11398.2442 | 11398.2442 | 11511.081
2012-07-01 | 23298.1422 | 23298.1422 | 23630.2664 | 12319.3311 | 12319.3311 | 13057.6199
2012-08-01 | 22956.5741 | 22956.5741 | 22726.501 | 12419.0386 | 12419.0386 | 12373.2613
2012-09-01 | 20506.0631 | 20506.0631 | 20370.1157 | 10811.3017 | 10811.3017 | 10900.4102
2012-10-01 | 18345.9037 | 18345.9037 | 18684.153 | 11199.8353 | 11199.8353 | 11149.8822
2012-11-01 | 20571.5606 | 20571.5606 | 20258.2258 | 11629.6439 | 11629.6439 | 11663.449
2012-12-01 | 21693.287 | 21693.287 | 20910.8981 | 12612.0073 | 12612.0073 | 12306.8289
2012 | 23298.1422 | 23298.1422 | 23630.2664 | 141947.0782 | 141947.0782 | 140723.2004
2013-01-31 | 22013.997 | 22013.997 | 22610 | 13314.3055 | 13314.3055 | 13061.0693
2013-02-28 | 21773.6201 | 21773.6201 | 21333.0082 | 11819.7381 | 11819.7381 | 11668.8474
2013-03-31 | 20634.9497 | 20634.9497 | 20784.4526 | 12283.0437 | 12283.0437 | 11869.9986
2013-04-30 | 18492.3312 | 18492.3312 | 19284.8182 | 11018.1303 | 11018.1303 | 11090.2932
2013-05-31 | 19100.9692 | 19100.9692 | 18341.9804 | 10932.3105 | 10932.3105 | 10533.5712
2013-06-30 | 22499.2459 | 22499.2459 | 22719.4401 | 11406.4319 | 11406.4319 | 11283.4325
2013-07-31 | 23212.9348 | 23212.9348 | 24352.1456 | 12479.5529 | 12479.5529 | 12736.3503
2013-08-31 | 22359.7987 | 22359.7987 | 23255.371 | 12227.7513 | 12227.7513 | 12084.9413
2013-09-30 | 20513.3592 | 20513.3592 | 20422.3176 | 11015.3041 | 11015.3041 | 10767.0057
2013-10-31 | 18388.3002 | 18388.3002 | 18981.007 | 11279.1846 | 11279.1846 | 11114.0467
2013-11-30 | 20326.4941 | 20326.4941 | 20034.8189 | 11686.9287 | 11686.9287 | 11709.7788
2013-12-31 | 21395.0558 | 21395.0558 | 21184.5386 | 12699.9803 | 12699.9803 | 12528.9266
2013 | 23212.9348 | 23212.9348 | 24352.1456 | 142162.6617 | 142162.6617 | 140448.2614
2014-01-31 | 22319.8106 | 22319.8106 | 22043.8439 | 13356.427 | 13356.427 | 13409.7767
2014-02-28 | 20964.0592 | 20964.0592 | 21218.2216 | 11748.3799 | 11748.3799 | 11812.9441
2014-03-31 | 19906 | 19906 | 20728.4579 | 12054.5719 | 12054.5719 | 12242.1563
2014-04-30 | 17649 | 17649 | 19249.9632 | 10731.1367 | 10731.1367 | 11038.5265
2014-05-31 | 18964 | 18964 | 18750.4605 | 10790.2174 | 10790.2174 | 10546.4252
2014-06-30 | 22469.55 | 22469.55 | 20705.1957 | 11346.2756 | 11346.2756 | 11140.5499
2014-07-31 | 22948.69 | 22948.69 | 22294.8035 | 12360.0815 | 12360.0815 | 12324.9268
2014-08-31 | 21403.44 | 21403.44 | 21644.3547 | 11992.5131 | 11992.5131 | 11819.2371
2014-09-30 | 19023.2704 | 19023.2704 | 19449.0766 | 10579.5258 | 10579.5258 | 10671.4853
2014-10-31 | 18638.7361 | 18638.7361 | 18447.2196 | 11126.7565 | 11126.7565 | 10814.1957
2014-11-30 | 20302.34 | 20302.34 | 19923.2587 | 11497.4835 | 11497.4835 | 11410.1121
2014-12-31 | 21237.74 | 21237.74 | 21582.6701 | 12769.4956 | 12769.4956 | 12256.0958
2014 | 22948.69 | 22948.69 | 22294.8035 | 140352.8643 | 140352.8643 | 139486.4317
2015-01-31 | 22293.59 | 22293.59 | 21503.4489 | 13068.9431 | 13068.9431 | 12937.1182
2015-02-28 | 21016.81 | 21016.81 | 19709.6284 | 11528.5197 | 11528.5197 | 11740.7311
2015-03-31 | 19840.93 | 19840.93 | 20109.8817 | 11856.8161 | 11856.8161 | 11748.227
2015-04-30 | 18121.2 | 18121.2 | 19362.8308 | 10542.0267 | 10542.0267 | 10624.618
2015-05-31 | 19370.33 | 19370.33 | 17881.7583 | 10635.9243 | 10635.9243 | 10231.5964
2015-06-30 | 22276.64 | 22276.64 | 20554.6293 | 11410.2692 | 11410.2692 | 10908.724
2015-07-31 | 22888.49 | 22888.49 | 22638.5319 | 12174.2184 | 12174.2184 | 12273.6405
2015-08-31 | 21463.69 | 21463.69 | 22383 | 11821.2763 | 11821.2763 | 11782.7212
2015-09-30 | 18485 | 18485 | 19299.6325 | 10512.648 | 10512.648 | 10718.9879
2015-10-31 | 18339 | 18339 | 18444.3181 | 11150.1256 | 11150.1256 | 10731.7474
2015-11-30 | 20306 | 20306 | 19631.9089 | 11595.0899 | 11595.0899 | 10867.5486
2015-12-31 | 21160.04 | 21160.04 | 20418.0801 | 12611.2501 | 12611.2501 | 11784.7123
2015 | 22888.49 | 22888.49 | 22638.5319 | 138907.1073 | 138907.1073 | 136350.3725
2016-01-31 | 22360.24 | 22360.24 | 21249.7402 | 12982.1466 | 12982.1466 | 12523.599
2016-02-28 | 20985.25 | 20985.25 | 20194.6163 | 11806.8997 | 11806.8997 | 11502.97
2016-03-31 | 20075.21 | 20075.21 | 20324.618 | 11758.7447 | 11758.7447 | 11445.7227
2016-04-30 | 17405.08 | 17405.08 | 18912.1728 | 10309.6515 | 10309.6515 | 10578.9099
2016-05-31 | 19235.65 | 19235.65 | 19707.6447 | 10530.0143 | 10530.0143 | 10115.8584
2016-06-30 | 22315.7305 | 22315.7305 | 21568.912 | 11378.6081 | 11378.6081 | 11141.3797
2016-07-31 | 22599.9414 | 22599.9414 | 22288.7672 | 11896.1402 | 11896.1402 | 12345.0421
2016-08-31 | 21440.3166 | 21440.3166 | 22375.997 | 11771.834 | 11771.834 | 12295.9028
2016-09-30 | 18289 | 18289 | 19712.7154 | 10401.8861 | 10401.8861 | 10659.2295
2016-10-31 | 18079 | 18079 | 18394.9922 | 10947.5325 | 10947.5325 | 10453.1463
2016-11-30 | 20296 | 20296 | 19544.7667 | 11524.026 | 11524.026 | 10913.6011
2016-12-31 | 20888 | 20888 | 20286.7849 | 12430.7427 | 12430.7427 | 11950.5536
2016 | 22599.9414 | 22599.9414 | 22375.997 | 137738.2263 | 137738.2263 | 135925.9151
2017-01-31 | 21913.73 | 21913.73 | 20965.9674 | 12818.8508 | 12818.8508 | 12369.7298
2017-02-28 | 20966.2287 | 20966.2287 | 20379.4501 | 11294.713 | 11294.713 | 10787.4931
2017-03-31 | 20137.3 | 20137.3 | 18692.3503 | 11824.0632 | 11824.0632 | 11413.3465
2017-04-30 | 17969.79 | 17969.79 | 18482.7844 | 10366.7129 | 10366.7129 | 10105.7565
2017-05-31 | 19193.19 | 19193.19 | 18260.3078 | 10576.9018 | 10576.9018 | 10012.8427
2017-06-30 | 22454.87 | 22454.87 | 21144.8187 | 11159.3312 | 11159.3312 | 10682.999
2017-07-31 | 22492.73 | 22492.73 | 22152.8524 | 11984.7355 | 11984.7355 | 11851.6211
2017-08-31 | 22376.43 | 22376.43 | 21323.3584 | 12105.5471 | 12105.5471 | 11513.597
2017-09-30 | 19490.21 | 19490.21 | 17821.4732 | 10494.2948 | 10494.2948 | 10155.927
2017-10-31 | 18030.62 | 18030.62 | 17407.7858 | 10942.7953 | 10942.7953 | 10260.3837
2017-11-30 | 20230.97 | 20230.97 | 19195.4397 | 11371.7451 | 11371.7451 | 10946.7668
2017-12-31 | 20901.44 | 20901.44 | 21439.6493 | 12303.6865 | 12303.6865 | 12096.0133
2017 | 22492.73 | 22492.73 | 22152.8524 | 137243.3774 | 137243.3774 | 132196.4765
2018-01-31 | 21618.93 | 21618.93 | 20177.5339 | 12685.9178 | 12685.9178 | 12679.8037
2018-02-28 | 20242.21 | 20242.21 | 20042.2165 | 11074.1738 | 11074.1738 | 11081.1365
2018-03-31 | 19551.97 | 19551.97 | 19330.8728 | 11423.555 | 11423.555 | 11267.3415
2018-04-30 | 17669.81 | 17669.81 | 18107.9593 | 10157.8502 | 10157.8502 | 10586.2978
2018-05-31 | 18817.47 | 18817.47 | 19262.1307 | 10289.6502 | 10289.6502 | 10081.137
2018-06-30 | 21890.0001 | 21890.0001 | 20626.9619 | 10863.4062 | 10863.4062 | 10980.4534
2018-07-31 | 22076.0001 | 22076.0001 | 22409.0792 | 11652.7714 | 11652.7714 | 12483.776
2018-08-31 | 21946.0001 | 21946.0001 | 21385.6483 | 11685.5744 | 11685.5744 | 12040.5393
2018-09-30 | 19019 | 19019 | 19505.5646 | 10189.9802 | 10189.9802 | 10579.1906
2018-10-31 | 17788 | 17788 | 17751.4152 | 10750.0648 | 10750.0648 | 10526.7735
2018-11-30 | 19828 | 19828 | 19266.3918 | 11170.7506 | 11170.7506 | 11184.9393
2018-12-31 | 20503 | 20503 | 20375.1864 | 12007.3958 | 12007.3958 | 12019.553
2018 | 22076.0001 | 22076.0001 | 22409.0792 | 133951.0905 | 133951.0905 | 135510.9416
2019-01-31 | 21506 | 21506 | 21058.2817 | 12973.2132 | 12973.2132 | 12688.8389
2019-02-28 | 20008 | 20008 | 20420.3692 | 11162.2057 | 11162.2057 | 11212.4836
2019-03-31 | 19457 | 19457 | 19573.6921 | 11522.1982 | 11522.1982 | 11458.0531
2019-04-30 | 17548 | 17548 | 18796.3299 | 10252.9314 | 10252.9314 | 10432.2785
2019-05-31 | 18663 | 18663 | 17977.0308 | 10412.0446 | 10412.0446 | 10218.7126
2019-06-30 | 21623 | 21623 | 21239.1838 | 10939.3571 | 10939.3571 | 10608.5215
2019-07-31 | 22061 | 22061 | 21120.5208 | 11763.9974 | 11763.9974 | 12446.1887
2019-08-31 | 21200 | 21200 | 22490.4547 | 11598.2109 | 11598.2109 | 11798.5843
2019-09-30 | 19469.84 | 19469.84 | 18958.9757 | 10564.4926 | 10564.4926 | 10167.6302
2019-10-31 | 17559 | 17559 | 18814.592 | 10788.0047 | 10788.0047 | 10446.8836
2019-11-30 | 19597 | 19597 | 19001.8635 | 11194.6524 | 11194.6524 | 11094.2081
2019-12-31 | 20307 | 20307 | 20974 | 12086.6766 | 12086.6766 | 12094.1802
2019 | 22061 | 22061 | 22490.4547 | 135257.9849 | 135257.9849 | 134666.5633
2020-01-31 | 21185.0004 | 21185.0004 | 21137.8728 | 12859.4588 | 12859.4588 | 12460.9405
2020-02-28 | 19917.0004 | 19917.0004 | 19776.0281 | 11586.6754 | 11586.6754 | 11253.1814
2020-03-31 | 19377.0004 | 19377.0004 | 19680.948 | 11522.322 | 11522.322 | 11058.3098
2020-04-30 | 17302.0004 | 17302.0004 | 16515.7848 | 10229.1483 | 10229.1483 | 9383.3554
2020-05-31 | 17426 | 17426 | 18761.2836 | 9434.378 | 9434.378 | 9306.4436
2020-06-30 | 20034 | 20034 | 20741.8718 | 10274.389 | 10274.389 | 10596.6512
2020-07-31 | 22364.4404 | 22364.4404 | 24057.7367 | 11731.6936 | 11731.6936 | 12529.7172
2020-08-31 | 21631.4406 | 21631.4406 | 25317.7535 | 11441.5908 | 11441.5908 | 12338.1938
2020-09-30 | 20312.4408 | 20312.4408 | 19254.2062 | 10356.1124 | 10356.1124 | 10011.2355
2020-10-31 | 17039.9727 | 17039.9727 | 17587.3164 | 10040.7873 | 10040.7873 | 10349.5982
2020-11-30 | 18891.9134 | 18891.9134 | 19416.1975 | 10531.6058 | 10531.6058 | 10693.8532
2020-12-31 | 19805.1651 | 19805.1651 | 20975.3455 | 11815.0887 | 11815.0887 | 11932.8039
2020 | 22364.4404 | 22364.4404 | 25317.7535 | 131823.25 | 131823.25 | 131914.2838
2021-01-31 | 21176.0005 | 21176.0005 | 20951.6431 | 12539.1611 | 12539.1611 | 12307.6071
2021-02-28 | 20760.0005 | 20760.0005 | 20175.4672 | 11073.4765 | 11073.4765 | 11144.3783
2021-03-31 | 19384.0005 | 19384.0005 | 19868.2566 | 11497.7125 | 11497.7125 | 11249.5616
2021-04-30 | 17070.0009 | 17070.0009 | 17618.7846 | 10244.8035 | 10244.8035 | 10097.7166
2021-05-31 | 18055.3342 | 18055.3342 | 18021.5172 | 10152.0681 | 10152.0681 | 9986.9371
2021-06-30 | 22162.0009 | 22162.0009 | 21528.4908 | 10747.5852 | 10747.5852 | 10840.8856
2021-07-31 | 22413.0005 | 22413.0005 | 22251.4821 | 11806.5074 | 11806.5074 | 11970.9832
2021-08-31 | 22235.0005 | 22235.0005 | 21854.4728 | 11706.2663 | 11706.2663 | 12072.0791
2021-09-30 | 21212.0005 | 21212.0005 | 18979.8917 | 10472.6839 | 10472.6839 | 10401.3058
2021-10-31 | 17270.7147 | 17270.7147 | 17606.8602 | 10365.0376 | 10365.0376 | 10429.4829
2021-11-30 | 19227.38 | 19227.38 | 19684.7166 | 10886.7659 | 10886.7659 | 11017.3258
2021-12-31 | 20088.8968 | 20088.8968 | 21331.5579 | 11984.4925 | 11984.4925 | 12185.9418
2021 | 22413.0005 | 22413.0005 | 22251.4821 | 133476.5604 | 133476.5604 | 133704.2048
2022-01-31 | 20983.6671 | 20983.6671 | 21334.1018 | 12536.9576 | 12536.9576 | 12928.5532
2022-02-28 | 20446.0004 | 20446.0004 | 20782.3287 | 11208.712 | 11208.712 | 11400.5165
2022-03-31 | 19401.3338 | 19401.3338 | 19941.2707 | 11617.5125 | 11617.5125 | 11793.6956
2022-04-30 | 17251.0005 | 17251.0005 | 17752.3935 | 10239.112 | 10239.112 | 10311.1592
2022-05-31 | 18269.0005 | 18269.0005 | 20136.0014 | 10372.2878 | 10372.2878 | 10137.6947
2022-06-30 | 22161.0005 | 22161.0005 | 22101.7092 | 10967.9836 | 10967.9836 | 11002.2267
2022-07-31 | 22542.0005 | 22542.0005 | 22484.9516 | 11893.9057 | 11893.9057 | 12411.016
2022-08-31 | 22430.0005 | 22430.0005 | 23477.9346 | 12028.3221 | 12028.3221 | 11998.9314
2022-09-30 | 21489.0005 | 21489.0005 | 20446.2276 | 10551.0851 | 10551.0851 | 10678.4907
2022-10-31 | 17559.0005 | 17559.0005 | 17724.6236 | 10603.0084 | 10603.0084 | 10447.0825
2022-11-30 | 19812.0005 | 19812.0005 | 19389.6575 | 11151.0711 | 11151.0711 | 11128.3255
2022-12-31 | 20241.0005 | 20241.0005 | 20584.5241 | 12191.9609 | 12191.9609 | 12412.7534
2022 | 22542.0005 | 22542.0005 | 23477.9346 | 135361.9188 | 135361.9188 | 136650.4453
2023-01-31 | 21170.3338 | 21170.3338 | 21435.1399 | 12663.6554 | 12663.6554 | 13052.768
2023-02-28 | 20892.3338 | 20892.3338 | 20433.0112 | 11375.0622 | 11375.0622 | 11325.8235
2023-03-31 | 19701.0485 | 19701.0485 | 19000.8853 | 11846.6528 | 11846.6528 | 11814.7494
2023-04-30 | 17785.9996 | 17785.9996 | 19103.3719 | 10349.2653 | 10349.2653 | 10374.8437
2023-05-31 | 18869.9996 | 18869.9996 | 18001.5877 | 10418.8057 | 10418.8057 | 10473.6584
2023-06-30 | 21884.9996 | 21884.9996 | 22417.4764 | 10652.496 | 10652.496 | 11230.6805
2023-07-31 | 22445.9996 | 22445.9996 | 23368.3724 | 11858.9002 | 11858.9002 | 12455.0186
2023-08-31 | 22396.9996 | 22396.9996 | 21865.1956 | 12249.9171 | 12249.9171 | 12005.3253
2023-09-30 | 21479.9996 | 21479.9996 | 21317.3942 | 10718.9739 | 10718.9739 | 10685.1004
2023-10-31 | 17668.0452 | 17668.0452 | 19208.5675 | 10593.967 | 10593.967 | 10757.1302
2023-11-30 | 19742.0453 | 19742.0453 | 20453.2108 | 11007.299 | 11007.299 | 11478.5016
2023-12-31 | 20346.0453 | 20346.0453 | 21211.1571 | 12018.94 | 12018.94 | 12384.2261
2023 | 22445.9996 | 22445.9996 | 23368.3724 | 135753.9345 | 135753.9345 | 138037.826
2024-01-31 | 21418.2553 | 21418.2553 | 21405.4347 | 12929.406 | 12929.406 | 13208.8176
2024-02-28 | 20987.7553 | 20987.7553 | 20022.691 | 11956.6273 | 11956.6273 | 11729.9509
2024-03-31 | 19645.2454 | 19645.2454 | 18939.8337 | 11836.2413 | 11836.2413 | 11632.2959
2024-04-30 | 17839.6154 | 17839.6154 | 18586.0743 | 10616.6408 | 10616.6408 | 10650.6806
2024-05-31 | 19148.7554 | 19148.7554 | 19498.7984 | 10660.6544 | 10660.6544 | 10640.585
2024-06-30 | 22502.1655 | 22502.1655 | 22585.2284 | 10892.6773 | 10892.6773 | 11334.1111
2024-07-31 | 22729.3249 | 22729.3249 | 23182.1746 | 12334.9116 | 12334.9116 | 12956.8035
2024-08-31 | 22604.8475 | 22604.8475 | 22518.533 | 12446.9545 | 12446.9545 | 12419.372
2024-09-30 | 22015.6938 | 22015.6938 | 21462.7165 | 11057.7009 | 11057.7009 | 10932.1478
2024-10-31 | 17976.8176 | 17976.8176 | 18603.2901 | 11073.6096 | 11073.6096 | 11048.6213
2024-11-30 | 20217.9361 | 20217.9361 | 19942.2233 | 11500.099 | 11500.099 | 11494.5336
2024-12-31 | 21036.6297 | 21036.6297 | 21342.8087 | 12626.6472 | 12626.6472 | 13046.7703
2024 | 22729.3249 | 22729.3249 | 23182.1746 | 139932.1699 | 139932.1699 | 141094.6899
2025-01-31 | 21856.1165 | 21856.1165 | 22379.5336 | 13268.2621 | 13268.2621 | 13661.657
2025-02-28 | 21278.651 | 21278.651 | 21116.0479 | 11685.5171 | 11685.5171 | 12130.7045
2025-03-31 | 20023.5778 | 20023.5778 | 19614.4739 | 12075.4951 | 12075.4951 | 12091.2745
2025-04-30 | 18154.8411 | 18154.8411 | 19246.3001 | 10619.601 | 10619.601 | 10891.1786
2025-05-31 | 19064.5516 | 19064.5516 | 18891.1849 | 10649.1943 | 10649.1943 | 10886.6628
2025-06-30 | 22279.0506 | 22279.0506 | 22678.4237 | 11223.7937 | 11223.7937 | 11544.6629
2025-07-31 | 23249.8525 | 23171.0268 | 23249.8525 | 13471.3387 | 12427.0436 | 13471.3387
2025-08-31 | 23530.1953 | 22852.8201 | 23530.1953 | 12734.6294 | 12416.3112 | 12734.6294
2025-09-30 | 21192.8937 | 21301.525 | 21192.8937 | 11125.7506 | 11078.9473 | 11125.7506
2025-10-31 | 18572.3296 | 18359.0116 | 18572.3296 | 11323.7934 | 11105.4864 | 11323.7934
2025-11-30 | 19963.3073 | 20191.9546 | 19963.3073 | 12004.1764 | 11589.9091 | 12004.1764
2025-12-31 | 21487.8851 | 21485.0415 | 21487.8851 | 13529.2595 | 12929.668 | 13529.2595
2025 | 23530.1953 | 23171.0268 | 23530.1953 | 143710.8115 | 141069.229 | 145395.0883
2026-01-31 | 22160.5721 | 22588.04 | 22160.5721 | 13936.0376 | 13853.6597 | 13936.0376
2026-02-28 | 21428.1773 | 21723.91 | 21428.1773 | 12322.8763 | 12193.5192 | 12322.8763
2026-03-31 | 19889.5794 | 20449.45 | 19889.5794 | 12592.449 | 12581.543 | 12592.449
2026-04-30 | 19288.6539 | 18337.2522 | 19288.6539 | 11195.2801 | 10995.8665 | 11195.2801
2026-05-31 | 19401.3919 | 19510.8225 | 19401.3919 | 11155.5649 | 11100.8529 | 11155.5649
2026-06-30 | 23371.3311 | 23042.9438 | 23371.3311 | 11932.5336 | 11828.0828 | 11932.5336
2026-07-31 | 24298.8266 | 25887.8938 | 24298.8266 | 13701.3716 | 12841.511 | 13701.3716
2026-08-31 | 23142.9682 | 24633.2911 | 23142.9682 | 13018.1365 | 12548.2185 | 13018.1365
2026-09-30 | 21567.0555 | 23695.055 |  | 11316.3439 | 11316.3439
2026-10-31 | 18862.7813 | 20487.639 |  | 11326.6607 | 11361.2904
2026-11-30 | 20927.2292 | 21612.749 |  | 11949.1042 | 11968.0337
2026-12-31 | 21934.7075 | 22847.9235 |  | 13265.2493 | 13268.4915
2026 | 24298.8266 | 25887.8938 | 24298.8266 | 147711.6078 | 145857.4132 | 99854.2496
2027-01-31 | 22874.0071 | 23777.0674 |  | 13871.3177 | 13850.95
2027-02-28 | 22000.2222 | 23027.1006 |  | 12258.128 | 12254.1775
2027-03-31 | 20716.8157 | 21594.0663 |  | 12624.7655 | 12647.7763
2027-04-30 | 18724.3017 | 19475.9858 |  | 11176.5269 | 11208.7608
2027-05-31 | 19992.5417 | 22105.2101 |  | 11222.4221 | 11264.7095
2027-06-30 | 23142.3696 | 25054.7551 |  | 11894.2787 | 11941.298
2027-07-31 | 24207.0367 | 26481.5876 |  | 13196.7287 | 13246.6702
2027-08-31 | 23675.1467 | 25328.8031 |  | 13016.3209 | 13058.1801
2027-09-30 | 22285.3821 | 24386.1515 |  | 11779.8375 | 11816.5387
2027-10-31 | 19586.0009 | 21093.501 |  | 11676.3464 | 11877.1804
2027-11-30 | 21769.1423 | 22448.0716 |  | 12343.2198 | 12556.166
2027-12-31 | 22807.8842 | 23664.8896 |  | 13655.3202 | 13883.5042
2027 | 24207.0367 | 26481.5876 |  | 148715.2122 | 149605.9118
2028-01-31 | 24068.9723 |  |  | 14466.5554
2028-02-28 | 23121.2236 |  |  | 13270.2791
2028-03-31 | 21784.0696 |  |  | 13248.2486
Back to main menu

## Table 1.1.2 Firm
Back to main menu
Table 1.1.2 Firm: Weekly Coincident Peak Demand by Zone
Week Ending | Firm Hourly Coincident Peak Demand (MW)
| Bruce | East | Essa | Niagara | NorthEast | NorthWest | Ottawa | SouthWest | Toronto | West | Ontario | Load Forecast Uncertainty
2026-10-04 23:00 | 80.9878 | 1168.0192 | 1267.0159 | 642.6956 | 1252.1271 | 365.8079 | 1067.6182 | 3822.5309 | 6569.7258 | 2180.022 | 18416.5505 | 1286.6837
2026-10-11 23:00 | 77.4364 | 1215.624 | 1326.9678 | 634.1696 | 1308.2054 | 410.735 | 1145.0738 | 3520.475 | 6316.2877 | 1935.2738 | 17890.2486 | 882.9634
2026-10-18 23:00 | 89.5639 | 1225.7629 | 1322.0967 | 635.4218 | 1320.2331 | 431.5907 | 1089.391 | 3624.7102 | 6234.0547 | 1916.6032 | 17889.4282 | 621.6189
2026-10-25 23:00 | 94.4878 | 1244.6665 | 1330.7362 | 629.9842 | 1342.7808 | 455.9426 | 1128.6862 | 3638.5492 | 6338.1382 | 1962.2579 | 18166.2294 | 478.5323
2026-11-01 23:00 | 92.1783 | 1302.4173 | 1384.0587 | 632.4376 | 1384.9361 | 441.4868 | 1202.2885 | 3674.0133 | 6375.9063 | 1951.1729 | 18440.896 | 481.021
2026-11-08 23:00 | 98.7978 | 1262.9558 | 1397.1888 | 679.4772 | 1325.7705 | 473.6514 | 1179.0503 | 3790.0861 | 6546.5511 | 2239.2078 | 18992.7367 | 511.8928
2026-11-15 23:00 | 103.3604 | 1361.63 | 1491.9786 | 679.3701 | 1412.0643 | 476.8693 | 1267.0671 | 3855.9159 | 6712.5704 | 2129.5902 | 19490.4162 | 678.7943
2026-11-22 23:00 | 108.8976 | 1441.5605 | 1598.0345 | 683.2363 | 1445.8271 | 496.1091 | 1322.1085 | 3846.722 | 6910.3628 | 2221.1643 | 20074.0228 | 658.7797
2026-11-29 23:00 | 111.8864 | 1437.5204 | 1578.0949 | 712.7828 | 1458.2517 | 519.0431 | 1286.4755 | 4105.0855 | 7046.7911 | 2332.4246 | 20588.3561 | 563.3826
2026-12-06 23:00 | 120.6246 | 1442.3931 | 1710.9464 | 721.6696 | 1489.8994 | 530.0634 | 1368.1828 | 4146.5546 | 7119.1296 | 2302.1783 | 20951.6418 | 574.4685
2026-12-13 23:00 | 127.2624 | 1496.5822 | 1763.8069 | 716.1403 | 1530.6667 | 589.1001 | 1386.6777 | 4172.7721 | 7137.9466 | 2357.4856 | 21278.4406 | 695.2815
2026-12-20 23:00 | 119.5736 | 1504.8525 | 1790.4978 | 735.2954 | 1564.2883 | 595.6455 | 1428.7566 | 4214.5106 | 7161.2284 | 2366.6168 | 21481.2655 | 720.7754
2026-12-27 23:00 | 123.1637 | 1489.0889 | 1768.1348 | 713.8875 | 1486.6713 | 546.5935 | 1401.7482 | 4087.3217 | 7006.0962 | 2285.0998 | 20907.8056 | 733.6377
2027-01-03 23:00 | 115.9954 | 1568.8011 | 1924.4784 | 705.2301 | 1630.0636 | 593.4904 | 1487.649 | 3916.611 | 6881.0231 | 2232.1678 | 21055.51 | 745.3972
2027-01-10 23:00 | 127.584 | 1595.5212 | 1813.3201 | 742.8763 | 1622.1234 | 583.4275 | 1457.1338 | 4339.8808 | 7303.9081 | 2368.2263 | 21954.0014 | 839.238
2027-01-17 23:00 | 131.6626 | 1603.2537 | 1805.2609 | 727.2901 | 1586.2103 | 566.5738 | 1497.7814 | 4311.4272 | 7242.8717 | 2361.05 | 21833.3817 | 860.5587
2027-01-24 23:00 | 136.0207 | 1643.9083 | 1854.8162 | 732.0844 | 1641.073 | 574.7483 | 1480.4209 | 4304.677 | 7249.4508 | 2292.92 | 21910.1197 | 895.9273
2027-01-31 23:00 | 133.4797 | 1563.4155 | 1807.1762 | 746.9547 | 1627.0774 | 584.7763 | 1405.1845 | 4399.7215 | 7264.5871 | 2353.6742 | 21886.0471 | 855.394
2027-02-07 23:00 | 122.1352 | 1542.8442 | 1742.1752 | 734.7935 | 1609.3271 | 544.0295 | 1439.634 | 4201.1462 | 7229.8559 | 2222.3002 | 21388.241 | 772.8935
2027-02-14 23:00 | 121.8864 | 1526.7835 | 1783.8803 | 734.1524 | 1641.3135 | 585.4147 | 1434.3832 | 4178.8181 | 7229.1149 | 2147.7787 | 21383.5257 | 770.5583
2027-02-21 23:00 | 122.9874 | 1513.3954 | 1714.8027 | 711.2606 | 1592.0701 | 556.4424 | 1437.5051 | 4109.7502 | 7227.6924 | 2114.0264 | 21099.9325 | 773.8925
2027-02-28 23:00 | 123.949 | 1470.8704 | 1701.3937 | 723.3458 | 1569.2521 | 562.8937 | 1387.2295 | 4158.904 | 7076.615 | 2175.7884 | 20950.2416 | 706.4679
2027-03-07 23:00 | 121.0799 | 1445.8215 | 1683.3157 | 683.7743 | 1623.2174 | 553.5657 | 1353.0134 | 4026.6058 | 6863.2553 | 2076.4029 | 20430.052 | 693.4034
2027-03-14 23:00 | 118.3114 | 1399.5116 | 1648.5699 | 669.752 | 1633.001 | 560.4561 | 1369.9848 | 3834.8562 | 6765.8994 | 1985.6154 | 19985.9579 | 692.5436
2027-03-21 23:00 | 114.0424 | 1313.1277 | 1538.5178 | 683.8686 | 1537.1353 | 493.8096 | 1251.8247 | 3889.299 | 6710.0566 | 2024.7382 | 19556.42 | 645.7194
2027-03-28 23:00 | 106.0182 | 1312.0674 | 1473.9728 | 665.8098 | 1547.503 | 476.2459 | 1234.6138 | 3764.1245 | 6514.0424 | 1955.3208 | 19049.7186 | 557.4301
2027-04-04 23:00 | 108.2788 | 1223.8897 | 1379.9034 | 662.3738 | 1488.3613 | 471.1105 | 1195.1956 | 3747.024 | 6403.6496 | 2015.9633 | 18695.75 | 563.7263
2027-04-11 23:00 | 106.8974 | 1178.2736 | 1331.8212 | 654.91 | 1412.7712 | 438.3033 | 1153.8541 | 3714.9675 | 6273.2589 | 1976.3766 | 18241.4338 | 572.4089
2027-04-18 23:00 | 107.231 | 1166.3577 | 1304.1791 | 634.7813 | 1368.6654 | 409.9399 | 1110.5982 | 3701.3058 | 6178.5135 | 1940.238 | 17921.8099 | 722.1483
2027-04-25 23:00 | 108.9673 | 1166.321 | 1336.1808 | 616.1923 | 1378.377 | 420.7907 | 1103.8029 | 3540.1861 | 6182.0774 | 1811.448 | 17664.3435 | 649.2901
2027-05-02 23:00 | 106.6003 | 1147.5524 | 1266.2512 | 621.3692 | 1338.8424 | 408.2067 | 1103.2198 | 3585.4375 | 6081.9166 | 1822.23 | 17481.6261 | 618.0966
2027-05-09 23:00 | 104.4904 | 1071.1031 | 1314.416 | 575.9604 | 1259.499 | 424.02 | 1049.3734 | 3592.2066 | 6091.2835 | 1919.2643 | 17401.6166 | 751.4404
2027-05-16 23:00 | 99.7092 | 1149.0413 | 1381.8525 | 575.8511 | 1339.268 | 413.801 | 1099.7205 | 3442.2859 | 6145.8535 | 1827.4103 | 17474.7934 | 973.2914
2027-05-23 23:00 | 93.1461 | 1110.0286 | 1295.9029 | 615.518 | 1271.9152 | 424.4896 | 1200.5213 | 3587.0519 | 6365.1646 | 1939.1982 | 17902.9364 | 1472.3085
2027-05-30 23:00 | 75.6546 | 957.363 | 1157.1109 | 662.1598 | 1153.9423 | 400.2735 | 1107.023 | 3720.4046 | 6737.8876 | 2228.6874 | 18200.5066 | 2046.43
2027-06-06 23:00 | 94.3472 | 1033.9823 | 1295.9941 | 655.8129 | 1183.7458 | 371.773 | 1453.4009 | 3786.989 | 7065.4223 | 2105.6942 | 19047.1617 | 2189.0527
2027-06-13 23:00 | 86.2675 | 1233.1479 | 1555.0863 | 683.5672 | 1243.6997 | 400.1767 | 1385.7408 | 3786.4644 | 6964.533 | 2207.9683 | 19546.6517 | 2174.8052
2027-06-20 23:00 | 89.8886 | 1136.8627 | 1456.0826 | 700.4492 | 1158.3086 | 406.4816 | 1545.9086 | 3860.1506 | 7937.9449 | 2309.8372 | 20601.9147 | 2121.4987
2027-06-27 23:00 | 82.064 | 1359.3655 | 1748.6099 | 755.0468 | 1174.4021 | 431.2161 | 1437.0842 | 4291.9962 | 7667.5508 | 2532.712 | 21480.0477 | 1747.2331
2027-07-04 23:00 | 85.438 | 1112.9108 | 1475.5034 | 770.7853 | 1154.3669 | 383.0259 | 1452.3068 | 4274.8579 | 8202.9631 | 2568.6262 | 21480.7844 | 1719.5156
2027-07-11 23:00 | 78.5616 | 1421.9953 | 1677.183 | 766.4566 | 1270.4845 | 426.3498 | 1531.7532 | 4599.872 | 7837.2993 | 2633.6572 | 22243.6125 | 1801.4393
2027-07-18 23:00 | 87.0626 | 1425.9705 | 1777.3293 | 812.1237 | 1235.6875 | 420.7117 | 1504.881 | 4242.4573 | 8420.6638 | 2520.1433 | 22447.0308 | 1775.6573
2027-07-25 23:00 | 80.3922 | 1322.7878 | 1544.053 | 791.6608 | 1167.4529 | 395.285 | 1497.0023 | 4664.0893 | 8324.4273 | 2667.8542 | 22455.0049 | 1797.2623
2027-08-01 23:00 | 77.5656 | 1346.1515 | 1597.204 | 797.2848 | 1158.1252 | 388.2538 | 1434.5259 | 4556.789 | 8364.5869 | 2676.7635 | 22397.25 | 1682.3813
2027-08-08 23:00 | 82.2456 | 1325.9454 | 1568.1723 | 779.7526 | 1190.362 | 383.0754 | 1390.0895 | 4383.3402 | 8088.7408 | 2652.4524 | 21844.1762 | 1791.3331
2027-08-15 23:00 | 89.2214 | 1198.4784 | 1505.0771 | 803.0775 | 1192.5701 | 389.837 | 1389.6868 | 4465.0305 | 7989.8205 | 2784.1869 | 21806.9862 | 1665.2249
2027-08-22 23:00 | 103.7789 | 1281.6673 | 1602.3498 | 767.4358 | 1177.0946 | 448.1668 | 1389.2822 | 4340.148 | 7727.3967 | 2774.2629 | 21611.583 | 1492.6724
2027-08-29 23:00 | 91.1178 | 1169.3051 | 1436.7152 | 773.7988 | 1245.7534 | 413.3018 | 1380.7806 | 4467.9436 | 8037.5072 | 2628.0004 | 21644.2238 | 1410.9283
2027-09-05 23:00 | 95.6653 | 1186.924 | 1423.325 | 762.4285 | 1241.8261 | 433.2348 | 1379.7394 | 4313.204 | 7758.2252 | 2703.0319 | 21297.6041 | 1751.292
2027-09-12 23:00 | 100.5116 | 1211.6378 | 1354.4312 | 713.9713 | 1213.7323 | 422.8876 | 1172.8055 | 4039.2277 | 7390.2275 | 2582.9943 | 20202.4268 | 1992.2755
2027-09-19 23:00 | 83.4571 | 1141.3008 | 1393.4958 | 683.7213 | 1253.5109 | 431.8898 | 1126.6215 | 3697.2406 | 7529.5881 | 2386.2626 | 19727.0885 | 1765.6296
2027-09-26 23:00 | 82.6949 | 1122.9036 | 1329.2049 | 666.7503 | 1248.8582 | 419.5841 | 1199.9372 | 3712.8674 | 7089.2459 | 2378.5949 | 19250.6414 | 1655.7554
2027-10-03 23:00 | 79.2055 | 1270.1747 | 1404.1425 | 626.7629 | 1387.0526 | 432.5565 | 1308.4564 | 3502.7145 | 6835.7923 | 2128.0888 | 18974.9467 | 1356.9127
2027-10-10 23:00 | 75.3681 | 1195.91 | 1304.464 | 658.9439 | 1302.5862 | 423.5264 | 1053.1088 | 3749.3357 | 6334.312 | 2310.5514 | 18408.1065 | 929.7257
2027-10-17 23:00 | 83.7711 | 1183.8982 | 1283.9998 | 657.116 | 1329.003 | 407.7877 | 1166.2665 | 3673.5052 | 6504.6078 | 2258.5248 | 18548.48 | 572.6735
2027-10-24 23:00 | 94.4029 | 1199.2222 | 1305.0264 | 662.2427 | 1320.0846 | 446.3373 | 1113.1539 | 3820.9003 | 6370.6824 | 2309.8744 | 18641.9272 | 476.2054
2027-10-31 23:00 | 97.5346 | 1270.1128 | 1372.2507 | 649.9341 | 1346.8741 | 492.4895 | 1145.1603 | 3795.973 | 6441.3335 | 2305.454 | 18917.1167 | 490.5013
2027-11-07 23:00 | 100.7592 | 1347.5854 | 1452.1186 | 663.3077 | 1403.9682 | 477.1527 | 1244.918 | 3774.4704 | 6722.0653 | 2284.5049 | 19470.8504 | 502.6296
2027-11-14 23:00 | 101.5759 | 1344.6954 | 1477.048 | 685.7132 | 1394.9188 | 513.9401 | 1215.3587 | 3923.5958 | 6821.7392 | 2439.1022 | 19917.6873 | 636.9291
2027-11-21 23:00 | 110.7751 | 1427.3739 | 1590.1322 | 704.3142 | 1454.2135 | 509.3736 | 1282.876 | 3955.8586 | 6991.6971 | 2480.4468 | 20507.061 | 669.9536
2027-11-28 23:00 | 109.4182 | 1449.476 | 1615.3118 | 726.5263 | 1504.0581 | 552.4953 | 1337.9105 | 4082.0889 | 7213.3345 | 2477.579 | 21068.1986 | 577.0918
2027-12-05 23:00 | 120.5717 | 1467.1409 | 1729.5157 | 718.1568 | 1543.622 | 560.0418 | 1425.4553 | 4125.9608 | 7198.9638 | 2506.4987 | 21395.9275 | 567.2473
2027-12-12 23:00 | 121.3476 | 1463.9005 | 1761.0337 | 746.8078 | 1497.6427 | 552.4526 | 1402.901 | 4275.5121 | 7330.9009 | 2611.6013 | 21764.1002 | 682.0237
2027-12-19 23:00 | 123.0425 | 1512.622 | 1807.3595 | 744.8941 | 1573.7088 | 621.5091 | 1440.9172 | 4274.9965 | 7301.5694 | 2586.1717 | 21986.7908 | 717.176
2027-12-26 23:00 | 132.555 | 1637.094 | 1941.9175 | 759.9571 | 1669.4647 | 616.6247 | 1486.9574 | 4214.827 | 6981.5092 | 2578.4248 | 22019.3312 | 725.9742
2028-01-02 23:00 | 129.72 | 1607.9691 | 1809.3052 | 750.7353 | 1655.209 | 528.466 | 1525.0197 | 4127.4164 | 7109.803 | 2526.9412 | 21770.5847 | 840.6813
2028-01-09 23:00 | 128.256 | 1570.3457 | 1790.9643 | 771.1931 | 1579.8937 | 515.561 | 1475.656 | 4499.5645 | 7474.8355 | 2623.7444 | 22430.0144 | 832.7654
2028-01-16 23:00 | 134.3334 | 1614.4138 | 1858.7032 | 765.7918 | 1683.2768 | 636.6756 | 1459.5985 | 4614.1869 | 7494.3708 | 2579.7922 | 22841.1432 | 851.079
2028-01-23 23:00 | 135.9435 | 1609.4837 | 1864.424 | 781.2244 | 1712.929 | 636.6449 | 1443.6426 | 4618.0207 | 7503.5243 | 2604.8773 | 22910.7145 | 877.6907
2028-01-30 23:00 | 133.9767 | 1559.8416 | 1854.7985 | 798.9161 | 1646.6851 | 628.0826 | 1437.0539 | 4591.9299 | 7686.07 | 2578.523 | 22915.8775 | 838.0983
2028-02-06 23:00 | 128.7886 | 1598.2313 | 1839.4251 | 770.8051 | 1752.3111 | 589.8399 | 1513.9353 | 4428.3823 | 7582.2691 | 2400.0262 | 22604.0142 | 807.4963
2028-02-13 23:00 | 127.0933 | 1534.3237 | 1746.2142 | 768.653 | 1677.2477 | 579.9897 | 1409.3749 | 4433.8343 | 7439.4567 | 2539.4438 | 22255.6314 | 759.2133
2028-02-20 23:00 | 126.8368 | 1559.226 | 1758.6138 | 769.1412 | 1673.7373 | 554.5843 | 1479.3725 | 4380.9368 | 7558.9207 | 2451.6206 | 22312.99 | 693.2416
2028-02-27 23:00 | 122.6559 | 1425.1755 | 1656.0416 | 791.0448 | 1555.0764 | 488.6731 | 1404.9859 | 4323.1444 | 7440.6182 | 2525.4798 | 21732.8956 | 710.6081
2028-03-05 23:00 | 124.0667 | 1490.4953 | 1647.8998 | 741.5184 | 1675.233 | 555.8726 | 1414.8055 | 4207.5428 | 7295.8274 | 2398.1689 | 21551.4304 | 679.6193
2028-03-12 23:00 | 118.6878 | 1409.1659 | 1600.8112 | 734.8183 | 1652.5569 | 537.202 | 1295.6397 | 4187.4001 | 7150.2038 | 2299.8386 | 20986.3242 | 665.7664
2028-03-19 23:00 | 114.8795 | 1389.5792 | 1540.851 | 708.969 | 1583.5955 | 500.2212 | 1377.1713 | 4049.4726 | 7013.2868 | 2278.6939 | 20556.72 | 649.0147
2028-03-26 23:00 | 103.2958 | 1353.2229 | 1487.5786 | 683.0693 | 1598.8283 | 467.5863 | 1343.5619 | 3975.8692 | 6813.4256 | 2184.8411 | 20011.279 | 574.4507
2028-04-02 23:00 | 106.7921 | 1318.4524 | 1462.488 | 653.6177 | 1622.5264 | 498.9583 | 1321.8521 | 3883.4515 | 6650.7494 | 2096.831 | 19615.719 | 550.7432
Back to main menu

## Table 1.1.2 Planned
Back to main menu
Table 1.1.2 Planned: Weekly Coincident Peak Demand by Zone
Week Ending | Planned Hourly Coincident Peak Demand (MW)
| Bruce | East | Essa | Niagara | NorthEast | NorthWest | Ottawa | SouthWest | Toronto | West | Ontario | Load Forecast Uncertainty
2026-10-04 23:00 | 81.2686 | 1172.0681 | 1271.4079 | 644.9235 | 1256.4676 | 367.076 | 1071.3191 | 3835.7815 | 6592.4994 | 2187.5789 | 18480.3905 | 1286.6837
2026-10-11 23:00 | 77.7859 | 1221.1102 | 1332.9565 | 637.0317 | 1314.1094 | 412.5887 | 1150.2416 | 3536.3631 | 6344.7936 | 1944.0078 | 17970.9886 | 882.9634
2026-10-18 23:00 | 89.9923 | 1231.6254 | 1328.4199 | 638.4608 | 1326.5474 | 433.6548 | 1094.6012 | 3642.0462 | 6263.8704 | 1925.7698 | 17974.9882 | 621.6189
2026-10-25 23:00 | 94.852 | 1249.4639 | 1335.8654 | 632.4124 | 1347.9564 | 457.6999 | 1133.0366 | 3652.5736 | 6362.5679 | 1969.8212 | 18236.2494 | 478.5323
2026-11-01 23:00 | 92.591 | 1308.2482 | 1390.2552 | 635.2691 | 1391.1365 | 443.4633 | 1207.6711 | 3690.4619 | 6404.4512 | 1959.9083 | 18523.4558 | 481.4489
2026-11-08 23:00 | 99.2125 | 1268.2568 | 1403.0531 | 682.3291 | 1331.3351 | 475.6395 | 1183.999 | 3840.5941 | 6574.0286 | 2248.6063 | 19107.0541 | 511.8591
2026-11-15 23:00 | 103.8571 | 1368.1737 | 1499.1488 | 682.635 | 1418.8504 | 479.161 | 1273.1563 | 3909.1937 | 6744.8296 | 2139.8246 | 19618.8302 | 678.7435
2026-11-22 23:00 | 109.3043 | 1446.9445 | 1604.0028 | 685.7881 | 1451.227 | 497.962 | 1327.0463 | 3896.4628 | 6936.1717 | 2229.4599 | 20184.3693 | 658.6618
2026-11-29 23:00 | 112.2926 | 1442.7393 | 1583.8241 | 715.3705 | 1463.5458 | 520.9275 | 1291.146 | 4155.8607 | 7072.3741 | 2340.8924 | 20698.9728 | 563.3282
2026-12-06 23:00 | 121.2565 | 1449.9488 | 1719.9089 | 725.45 | 1497.704 | 532.84 | 1375.3498 | 4209.8966 | 7156.4221 | 2314.2379 | 21103.0147 | 574.6287
2026-12-13 23:00 | 127.8774 | 1503.8148 | 1772.331 | 719.6013 | 1538.0641 | 591.9471 | 1393.3792 | 4233.7178 | 7172.4428 | 2368.8788 | 21422.0544 | 695.2725
2026-12-20 23:00 | 120.2011 | 1512.7494 | 1799.8936 | 739.154 | 1572.4971 | 598.7713 | 1436.2542 | 4277.8974 | 7198.8078 | 2379.0359 | 21635.2619 | 720.8401
2026-12-27 23:00 | 123.699 | 1495.5617 | 1775.8205 | 716.9906 | 1493.1336 | 548.9694 | 1407.8413 | 4146.6319 | 7036.5503 | 2295.0327 | 21040.2309 | 733.6643
2027-01-03 23:00 | 115.9976 | 1568.8302 | 1924.514 | 705.2431 | 1630.0938 | 593.5014 | 1487.6765 | 3957.6236 | 6881.1506 | 2232.2092 | 21096.84 | 745.4172
2027-01-10 23:00 | 128.3609 | 1605.2359 | 1824.361 | 747.3995 | 1632.0001 | 586.9798 | 1466.0059 | 4406.3632 | 7348.3797 | 2382.6458 | 22127.7316 | 839.2781
2027-01-17 23:00 | 132.5108 | 1613.5821 | 1816.8907 | 731.9754 | 1596.4289 | 570.2238 | 1507.4304 | 4380.017 | 7289.5315 | 2376.2603 | 22014.8508 | 860.7019
2027-01-24 23:00 | 136.8231 | 1653.6055 | 1865.7574 | 736.4029 | 1650.7535 | 578.1387 | 1489.1536 | 4370.5999 | 7292.2141 | 2306.4456 | 22079.8942 | 896.0175
2027-01-31 23:00 | 134.3334 | 1573.4144 | 1818.7341 | 751.7319 | 1637.4834 | 588.5163 | 1414.1714 | 4467.7883 | 7311.0483 | 2368.7273 | 22065.9489 | 855.4361
2027-02-07 23:00 | 122.7653 | 1550.8041 | 1751.1635 | 738.5845 | 1617.63 | 546.8362 | 1447.0614 | 4277.8323 | 7267.1565 | 2233.7656 | 21553.5993 | 772.9729
2027-02-14 23:00 | 122.5406 | 1534.9773 | 1793.4537 | 738.0923 | 1650.1219 | 588.5564 | 1442.081 | 4257.0367 | 7267.911 | 2159.3051 | 21554.0759 | 770.5988
2027-02-21 23:00 | 123.635 | 1521.3653 | 1723.8333 | 715.0063 | 1600.4543 | 559.3727 | 1445.0754 | 4186.6547 | 7265.7554 | 2125.1595 | 21266.312 | 773.9416
2027-02-28 23:00 | 124.5918 | 1478.4985 | 1710.2174 | 727.0971 | 1577.3904 | 565.8129 | 1394.4239 | 4236.4615 | 7113.3154 | 2187.0724 | 21114.8814 | 706.5304
2027-03-07 23:00 | 113.0507 | 1436.8572 | 1631.9896 | 707.8514 | 1586.8198 | 527.2834 | 1370.8481 | 4089.455 | 7023.2493 | 2085.0358 | 20572.4402 | 693.1901
2027-03-14 23:00 | 118.8248 | 1405.5844 | 1655.7234 | 672.6582 | 1640.087 | 562.888 | 1375.9294 | 3913.0024 | 6795.2582 | 1994.2314 | 20134.1872 | 692.4794
2027-03-21 23:00 | 114.0455 | 1313.1629 | 1538.559 | 683.8869 | 1537.1765 | 493.8229 | 1251.8582 | 3948.3295 | 6710.2363 | 2024.7924 | 19615.87 | 645.6295
2027-03-28 23:00 | 106.4661 | 1317.6108 | 1480.2002 | 668.6228 | 1554.0411 | 478.258 | 1239.8299 | 3840.0181 | 6541.5638 | 1963.5819 | 19190.1927 | 557.3216
2027-04-04 23:00 | 108.2776 | 1223.8757 | 1379.8876 | 662.3662 | 1488.3442 | 471.1051 | 1195.1819 | 3807.3852 | 6403.5763 | 2015.9402 | 18755.94 | 563.0472
2027-04-11 23:00 | 107.4462 | 1184.3235 | 1338.6595 | 658.2726 | 1420.0251 | 440.5538 | 1159.7786 | 3806.4285 | 6305.4691 | 1986.5244 | 18407.4814 | 572.3502
2027-04-18 23:00 | 107.7088 | 1171.5541 | 1309.9895 | 637.6094 | 1374.763 | 411.7662 | 1115.5462 | 3790.905 | 6206.04 | 1948.8821 | 18074.7643 | 721.9412
2027-04-25 23:00 | 109.4752 | 1171.7566 | 1342.408 | 619.064 | 1384.8008 | 422.7518 | 1108.9471 | 3630.6418 | 6210.8885 | 1819.8901 | 17820.6238 | 648.9735
2027-05-02 23:00 | 107.0949 | 1152.8774 | 1272.1269 | 624.2525 | 1345.055 | 410.1009 | 1108.3391 | 3675.1468 | 6110.1385 | 1830.6857 | 17635.8177 | 617.76
2027-05-09 23:00 | 104.9364 | 1075.6755 | 1320.0269 | 578.419 | 1264.8755 | 425.83 | 1053.853 | 3679.0914 | 6117.2859 | 1956.1708 | 17576.1644 | 750.8795
2027-05-16 23:00 | 86.1612 | 891.4084 | 1209.2235 | 617.3936 | 1179.5929 | 368.488 | 1172.1048 | 3677.3369 | 6381.8535 | 2078.9507 | 17662.5135 | 972.4517
2027-05-23 23:00 | 93.5784 | 1115.1807 | 1301.9178 | 618.3749 | 1277.8186 | 426.4599 | 1206.0934 | 3675.7898 | 6394.708 | 1978.2825 | 18088.2039 | 1471.4394
2027-05-30 23:00 | 76.0484 | 962.3464 | 1163.1341 | 665.6065 | 1159.949 | 402.3571 | 1112.7855 | 3809.5699 | 6772.9607 | 2269.386 | 18394.1435 | 2045.232
2027-06-06 23:00 | 94.8703 | 1039.7158 | 1303.1805 | 659.4495 | 1190.3098 | 373.8345 | 1461.4601 | 3879.8305 | 7104.6008 | 2147.1465 | 19254.3984 | 2188.7105
2027-06-13 23:00 | 86.6768 | 1238.9985 | 1562.4643 | 686.8104 | 1249.6004 | 402.0753 | 1392.3154 | 3879.3074 | 6997.5761 | 2254.6875 | 19750.5121 | 2175.094
2027-06-20 23:00 | 90.2629 | 1141.5974 | 1462.1467 | 703.3663 | 1163.1326 | 408.1744 | 1552.3468 | 3947.9872 | 7971.0038 | 2356.3994 | 20796.4175 | 2121.177
2027-06-27 23:00 | 82.3806 | 1364.6095 | 1755.3555 | 757.9596 | 1178.9325 | 432.8796 | 1442.628 | 4381.6606 | 7697.1297 | 2577.8688 | 21671.4044 | 1746.888
2027-07-04 23:00 | 80.776 | 1289.074 | 1577.5195 | 798.7612 | 1191.7582 | 416.002 | 1276.3724 | 4523.6787 | 7937.2098 | 2618.8735 | 21710.0254 | 1711.8556
2027-07-11 23:00 | 78.8386 | 1427.0089 | 1683.0963 | 769.1589 | 1274.9639 | 427.853 | 1537.1538 | 4752.9948 | 7864.9314 | 2684.7671 | 22500.7666 | 1800.6045
2027-07-18 23:00 | 87.3631 | 1430.8927 | 1783.4643 | 814.927 | 1239.9529 | 422.164 | 1510.0756 | 4399.3422 | 8449.7305 | 2571.2914 | 22709.2037 | 1774.9502
2027-07-25 23:00 | 80.7014 | 1327.8765 | 1549.9928 | 794.7063 | 1171.944 | 396.8056 | 1502.7611 | 4816.8545 | 8356.4507 | 2719.8546 | 22717.9474 | 1796.8101
2027-08-01 23:00 | 77.557 | 1346.0025 | 1597.0272 | 797.1965 | 1157.9969 | 388.2108 | 1434.367 | 4690.1375 | 8363.6606 | 2718.5741 | 22570.73 | 1681.1032
2027-08-08 23:00 | 82.5985 | 1331.6357 | 1574.9022 | 783.099 | 1195.4705 | 384.7194 | 1396.0551 | 4552.4287 | 8123.4539 | 2713.5695 | 22137.9324 | 1790.9277
2027-08-15 23:00 | 89.5949 | 1203.496 | 1511.3784 | 806.4397 | 1197.563 | 391.4691 | 1395.5049 | 4636.1013 | 8023.2711 | 2845.4964 | 22100.3148 | 1664.8922
2027-08-22 23:00 | 91.9283 | 1267.2425 | 1585.759 | 745.6946 | 1264.9963 | 424.5722 | 1487.0228 | 4233.0247 | 8210.1222 | 2585.0169 | 21895.3796 | 1492.4076
2027-08-29 23:00 | 91.4277 | 1173.2817 | 1441.6013 | 776.4304 | 1249.99 | 414.7073 | 1385.4765 | 4633.1987 | 8064.8417 | 2687.2447 | 21918.2 | 1410.5912
2027-09-05 23:00 | 86.9206 | 1244.4422 | 1468.3899 | 788.7634 | 1206.8645 | 386.0549 | 1107.1672 | 4740.9704 | 7762.6775 | 2821.6594 | 21613.91 | 1748.9354
2027-09-12 23:00 | 100.9644 | 1217.0966 | 1360.5333 | 717.188 | 1219.2005 | 424.7928 | 1178.0894 | 4226.6572 | 7423.5228 | 2653.1565 | 20521.2016 | 1992.3492
2027-09-19 23:00 | 83.8661 | 1146.8943 | 1400.3253 | 687.0722 | 1259.6543 | 434.0065 | 1132.1431 | 3887.9223 | 7566.4904 | 2457.0063 | 20055.3807 | 1765.5005
2027-09-26 23:00 | 83.0936 | 1128.317 | 1335.6128 | 669.9646 | 1254.8788 | 421.6069 | 1205.7219 | 3908.9245 | 7123.4222 | 2450.5501 | 19582.0923 | 1654.9728
2027-10-03 23:00 | 95.2118 | 1242.8278 | 1381.8773 | 651.4767 | 1339.0509 | 402.7022 | 1204.6361 | 3903.3237 | 6745.3248 | 2315.0203 | 19281.4516 | 1356.5285
2027-10-10 23:00 | 75.7445 | 1201.8819 | 1310.978 | 662.2345 | 1309.0908 | 425.6413 | 1058.3677 | 3956.1458 | 6365.9433 | 2379.4985 | 18745.5262 | 929.5953
2027-10-17 23:00 | 83.742 | 1183.4872 | 1283.5541 | 656.8878 | 1328.5417 | 407.6461 | 1165.8616 | 3861.6971 | 6502.3497 | 2315.8427 | 18789.61 | 572.6236
2027-10-24 23:00 | 94.8236 | 1204.5654 | 1310.841 | 665.1934 | 1325.9663 | 448.326 | 1118.1136 | 4024.695 | 6399.0673 | 2377.1734 | 18968.765 | 476.0174
2027-10-31 23:00 | 98.0068 | 1276.2616 | 1378.8941 | 653.0806 | 1353.3946 | 494.8737 | 1150.7042 | 3999.9779 | 6472.5172 | 2373.5398 | 19251.2504 | 490.4295
2027-11-07 23:00 | 101.2212 | 1353.7648 | 1458.7774 | 666.3494 | 1410.4061 | 479.3407 | 1250.6267 | 4009.5394 | 6752.8897 | 2354.3057 | 19837.221 | 502.599
2027-11-14 23:00 | 106.4032 | 1340.8625 | 1504.7405 | 697.3274 | 1383.4336 | 503.2044 | 1198.2215 | 4188.6838 | 6808.4542 | 2562.4349 | 20293.766 | 636.9083
2027-11-21 23:00 | 103.0766 | 1395.5096 | 1553.0367 | 704.5524 | 1453.568 | 538.2944 | 1266.5435 | 4259.3928 | 7010.6252 | 2586.3687 | 20870.9678 | 669.8476
2027-11-28 23:00 | 110.4595 | 1457.3694 | 1600.6035 | 724.1927 | 1483.233 | 541.6644 | 1350.2263 | 4312.142 | 7201.118 | 2637.9002 | 21418.9089 | 577.0965
2027-12-05 23:00 | 119.9102 | 1494.6443 | 1721.8796 | 715.5781 | 1551.1708 | 588.5779 | 1441.7559 | 4377.8803 | 7213.9696 | 2566.1838 | 21791.5504 | 568.5158
2027-12-12 23:00 | 121.8986 | 1470.5475 | 1769.0299 | 750.1988 | 1504.443 | 554.9611 | 1409.271 | 4536.5001 | 7364.1876 | 2681.069 | 22162.1065 | 682.0553
2027-12-19 23:00 | 123.6675 | 1520.3046 | 1816.539 | 748.6773 | 1581.7016 | 624.6657 | 1448.2355 | 4536.6524 | 7338.6538 | 2656.5441 | 22395.6415 | 717.1713
2027-12-26 23:00 | 123.5976 | 1569.1295 | 1873.2402 | 735.3927 | 1622.5106 | 573.8166 | 1533.5009 | 4413.5235 | 7327.7872 | 2644.4541 | 22416.9529 | 726.024
2028-01-02 23:00 | 130.4066 | 1616.4806 | 1818.8825 | 754.7092 | 1663.9706 | 531.2633 | 1533.0921 | 4398.8111 | 7147.4376 | 2598.8121 | 22193.8656 | 841.1043
2028-01-09 23:00 | 129.0029 | 1579.49 | 1801.3932 | 775.6839 | 1589.0936 | 518.5632 | 1484.2489 | 4772.8104 | 7518.362 | 2696.931 | 22865.579 | 832.768
2028-01-16 23:00 | 135.2692 | 1625.661 | 1871.6522 | 771.1269 | 1695.0037 | 641.1111 | 1469.7671 | 4888.7823 | 7546.5819 | 2654.5962 | 23299.5517 | 851.035
2028-01-23 23:00 | 136.7684 | 1619.2492 | 1875.7364 | 785.9644 | 1723.3221 | 640.5077 | 1452.4019 | 4888.7364 | 7549.0518 | 2677.5714 | 23349.3097 | 877.6793
2028-01-30 23:00 | 134.7771 | 1569.1609 | 1865.88 | 803.6893 | 1656.5232 | 631.8351 | 1445.6396 | 4866.7279 | 7731.9905 | 2651.9116 | 23358.1352 | 838.0789
2028-02-06 23:00 | 129.5773 | 1608.0183 | 1850.6892 | 775.5253 | 1763.0417 | 593.4519 | 1523.2061 | 4698.4848 | 7628.7005 | 2471.6799 | 23042.3751 | 807.4976
2028-02-13 23:00 | 127.8418 | 1543.3598 | 1756.4982 | 773.1798 | 1687.1255 | 583.4055 | 1417.6752 | 4701.9171 | 7483.2699 | 2611.1184 | 22685.3911 | 759.2648
2028-02-20 23:00 | 126.8083 | 1558.8751 | 1758.218 | 768.9682 | 1673.3606 | 554.4595 | 1479.0396 | 4624.8553 | 7557.2197 | 2508.4757 | 22610.28 | 693.2416
2028-02-27 23:00 | 123.2924 | 1432.5708 | 1664.6348 | 795.1495 | 1563.1457 | 491.2088 | 1412.2764 | 4593.8277 | 7479.2277 | 2596.7756 | 22152.1095 | 710.642
2028-03-05 23:00 | 124.7899 | 1499.1832 | 1657.5052 | 745.8406 | 1684.9977 | 559.1127 | 1423.0522 | 4475.2497 | 7338.3538 | 2469.1505 | 21977.2354 | 679.6253
2028-03-12 23:00 | 119.3042 | 1416.4843 | 1609.1249 | 738.6346 | 1661.1394 | 539.9919 | 1302.3685 | 4454.0472 | 7187.338 | 2369.1884 | 21397.6214 | 665.8097
2028-03-19 23:00 | 114.8475 | 1389.1913 | 1540.4209 | 708.771 | 1583.1534 | 500.0815 | 1376.7868 | 4293.8522 | 7011.3289 | 2335.6064 | 20854.04 | 649.0546
2028-03-26 23:00 | 103.8395 | 1360.3461 | 1495.4091 | 686.665 | 1607.2444 | 470.0476 | 1350.6343 | 4241.9897 | 6849.2909 | 2253.8161 | 20419.2827 | 574.4789
2028-04-02 23:00 | 107.4123 | 1326.1094 | 1470.9815 | 657.4136 | 1631.9494 | 501.856 | 1329.5288 | 4150.8819 | 6689.3741 | 2166.4088 | 20031.9158 | 550.6866
Back to main menu

## Table 1.1.3 Firm
Back to main menu
Table 1.1.3 Firm: Weekly Energy Demand by Zone
Week Ending | Firm Weekly Normal Energy (GWh)
| Bruce | East | Essa | Niagara | NorthEast | NorthWest | Ottawa | SouthWest | Toronto | West | Ontario
2026-10-04 23:00 | 11.9139 | 149.8626 | 169.2239 | 90.2267 | 202.4926 | 61.1669 | 150.0665 | 511.4228 | 901.1604 | 290.8577 | 2538.394
2026-10-11 23:00 | 12.2489 | 157.5188 | 175.4479 | 91.5928 | 201.4921 | 66.0295 | 149.9342 | 503.683 | 880.0579 | 289.0537 | 2527.0586
2026-10-18 23:00 | 12.6837 | 158.8446 | 176.7705 | 91.2951 | 201.399 | 67.1172 | 147.1089 | 504.4105 | 861.5632 | 289.8671 | 2511.0598
2026-10-25 23:00 | 13.3173 | 164.2434 | 181.1422 | 92.9582 | 204.0964 | 67.6814 | 153.5414 | 519.0514 | 888.3811 | 298.8744 | 2583.2872
2026-11-01 23:00 | 12.283 | 163.2878 | 182.8663 | 95.4636 | 205.6699 | 65.7927 | 160.7303 | 527.7925 | 911.1911 | 306.4084 | 2631.4856
2026-11-08 23:00 | 13.6178 | 166.9135 | 187.6855 | 97.1943 | 210.6754 | 72.6578 | 161.7179 | 534.0793 | 922.9033 | 321.3998 | 2688.8446
2026-11-15 23:00 | 13.6391 | 174.6963 | 195.497 | 99.1704 | 215.6251 | 73.9448 | 167.7315 | 544.7433 | 937.131 | 324.8483 | 2747.0268
2026-11-22 23:00 | 14.9467 | 186.8177 | 211.5585 | 100.5437 | 226.3309 | 76.3266 | 174.3987 | 550.4709 | 965.4269 | 327.5792 | 2834.3998
2026-11-29 23:00 | 15.7057 | 195.8748 | 217.7319 | 104.3875 | 224.5412 | 79.9609 | 175.9235 | 564.4849 | 980.4222 | 341.3605 | 2900.393
2026-12-06 23:00 | 16.8699 | 196.1245 | 231.3197 | 106.2957 | 228.5747 | 82.4597 | 182.8841 | 586.0896 | 995.3864 | 348.7446 | 2974.7488
2026-12-13 23:00 | 17.5464 | 203.5887 | 245.3948 | 106.592 | 235.2108 | 87.9845 | 187.5822 | 593.8551 | 999.3188 | 346.3154 | 3023.3886
2026-12-20 23:00 | 16.968 | 205.668 | 247.0764 | 107.1696 | 239.4809 | 87.0612 | 197.7083 | 592.8413 | 998.7089 | 350.9382 | 3043.6207
2026-12-27 23:00 | 17.5981 | 203.3918 | 243.7876 | 104.3658 | 228.1895 | 81.7357 | 186.8749 | 570.2763 | 970.0862 | 339.2323 | 2945.5382
2027-01-03 23:00 | 16.7637 | 209.0333 | 248.8921 | 102.5005 | 246.1378 | 90.2254 | 192.3225 | 559.7098 | 942.142 | 332.874 | 2940.6012
2027-01-10 23:00 | 18.034 | 216.5546 | 252.1502 | 109.5174 | 248.8353 | 89.6863 | 196.7013 | 619.1712 | 1020.612 | 351.2046 | 3122.467
2027-01-17 23:00 | 18.5758 | 220.6591 | 253.5621 | 109.7593 | 243.9814 | 86.6368 | 203.0703 | 619.9696 | 1032.3627 | 354.01 | 3142.587
2027-01-24 23:00 | 19.7689 | 225.7212 | 261.2952 | 109.393 | 254.587 | 87.6404 | 206.4038 | 611.6736 | 1039.7662 | 349.9907 | 3166.2401
2027-01-31 23:00 | 19.6643 | 219.6458 | 255.0192 | 110.5433 | 254.0255 | 90.4436 | 202.9498 | 623.5184 | 1037.2378 | 351.57 | 3164.6176
2027-02-07 23:00 | 17.6665 | 209.3944 | 245.7241 | 109.4998 | 251.7984 | 85.596 | 199.9835 | 602.973 | 1032.1345 | 341.2243 | 3095.9945
2027-02-14 23:00 | 17.2173 | 208.8037 | 242.5777 | 110.6679 | 252.0087 | 88.5332 | 196.7698 | 602.002 | 1033.481 | 338.434 | 3090.4953
2027-02-21 23:00 | 18.0638 | 203.0814 | 239.1577 | 107.7034 | 250.8061 | 85.9111 | 194.4862 | 584.8289 | 1005.7593 | 337.1784 | 3026.9762
2027-02-28 23:00 | 17.8352 | 196.3679 | 231.0921 | 110.1092 | 242.144 | 81.7101 | 191.6174 | 600.1925 | 1014.5945 | 339.9082 | 3025.5711
2027-03-07 23:00 | 17.0081 | 192.0348 | 225.6265 | 102.7392 | 248.19 | 86.6182 | 183.9878 | 580.8086 | 984.0405 | 324.4038 | 2945.4577
2027-03-14 23:00 | 15.7503 | 175.2985 | 209.2068 | 102.0997 | 242.1518 | 82.3197 | 180.1108 | 576.7992 | 973.1288 | 328.651 | 2885.5168
2027-03-21 23:00 | 15.744 | 171.4386 | 204.5857 | 100.9281 | 235.1505 | 77.3865 | 177.3189 | 562.6707 | 958.677 | 314.8721 | 2818.772
2027-03-28 23:00 | 16.2649 | 170.7659 | 199.9236 | 96.2998 | 229.3816 | 75.2989 | 172.3169 | 539.0984 | 921.6001 | 303.9101 | 2724.8604
2027-04-04 23:00 | 15.2242 | 165.4594 | 192.2202 | 96.1363 | 222.5269 | 73.6687 | 169.1439 | 538.2823 | 906.1705 | 304.6398 | 2683.4722
2027-04-11 23:00 | 15.2091 | 159.729 | 185.7223 | 95.1415 | 212.4498 | 68.8765 | 162.4279 | 535.8132 | 903.4663 | 297.1095 | 2635.9451
2027-04-18 23:00 | 14.4341 | 151.4476 | 177.2736 | 92.9134 | 208.6197 | 70.7409 | 156.3471 | 528.1152 | 884.0834 | 291.8522 | 2575.8271
2027-04-25 23:00 | 14.8598 | 150.2475 | 176.7587 | 90.8706 | 204.6369 | 66.2472 | 152.97 | 515.6766 | 884.6225 | 288.5214 | 2545.4111
2027-05-02 23:00 | 15.1445 | 147.0791 | 179.0857 | 89.251 | 202.4047 | 65.5385 | 153.3336 | 509.6289 | 878.7293 | 281.4734 | 2521.6686
2027-05-09 23:00 | 15.1228 | 144.1603 | 178.4391 | 88.5554 | 188.4893 | 64.3896 | 148.2076 | 514.0037 | 869.7718 | 291.5959 | 2502.7356
2027-05-16 23:00 | 14.8128 | 145.062 | 179.0999 | 88.3921 | 193.616 | 64.4484 | 150.15 | 507.2131 | 868.3514 | 289.1591 | 2500.3048
2027-05-23 23:00 | 13.7777 | 140.079 | 176.4347 | 88.5856 | 195.3839 | 65.6986 | 154.8068 | 512.0637 | 883.0715 | 288.5278 | 2518.4294
2027-05-30 23:00 | 12.4342 | 133.5476 | 169.9682 | 89.29 | 193.8003 | 62.0603 | 151.0372 | 509.7073 | 885.5112 | 281.0031 | 2488.3594
2027-06-06 23:00 | 12.986 | 146.9333 | 180.7502 | 93.7975 | 188.7101 | 61.1719 | 160.4685 | 525.335 | 933.0584 | 308.2523 | 2611.4634
2027-06-13 23:00 | 13.073 | 151.4841 | 188.2936 | 95.3312 | 181.9712 | 59.2254 | 168.2096 | 533.5878 | 941.2038 | 323.5036 | 2655.8833
2027-06-20 23:00 | 12.0976 | 153.2597 | 191.2075 | 99.3279 | 183.5786 | 60.0622 | 179.3317 | 556.6888 | 992.7391 | 329.1606 | 2757.4539
2027-06-27 23:00 | 11.2967 | 159.8995 | 202.108 | 102.575 | 182.7575 | 61.4 | 176.7091 | 581.3766 | 1004.6558 | 341.2005 | 2823.9788
2027-07-04 23:00 | 10.9452 | 163.108 | 198.093 | 101.2151 | 190.5998 | 61.3196 | 172.9597 | 558.1024 | 1033.5885 | 331.4057 | 2821.3371
2027-07-11 23:00 | 10.9417 | 170.8181 | 208.6891 | 103.599 | 179.2277 | 58.9182 | 184.2732 | 588.4046 | 1064.6846 | 348.1165 | 2917.6727
2027-07-18 23:00 | 11.2957 | 169.6365 | 205.9708 | 104.4018 | 195.0761 | 64.906 | 180.6338 | 598.5542 | 1084.8641 | 361.5726 | 2976.9116
2027-07-25 23:00 | 11.9488 | 163.9919 | 199.7276 | 104.8335 | 200.8229 | 67.8869 | 175.2605 | 623.856 | 1058.598 | 372.8889 | 2979.8151
2027-08-01 23:00 | 11.8962 | 173.2315 | 207.0869 | 105.7496 | 188.4718 | 61.846 | 181.297 | 596.5772 | 1078.1723 | 362.6238 | 2966.9522
2027-08-08 23:00 | 12.4155 | 173.2251 | 204.2704 | 105.9326 | 194.5213 | 60.7571 | 178.8056 | 579.1346 | 1047.1759 | 357.1416 | 2913.3798
2027-08-15 23:00 | 13.2813 | 161.5324 | 190.6195 | 104.5163 | 204.703 | 65.623 | 167.7857 | 599.4206 | 1020.579 | 373.8815 | 2901.9424
2027-08-22 23:00 | 12.801 | 165.3801 | 194.0711 | 105.4517 | 192.9921 | 63.6244 | 167.4883 | 585.8218 | 1026.2315 | 357.3777 | 2871.2397
2027-08-29 23:00 | 13.2264 | 165.1956 | 192.6883 | 103.0696 | 205.9791 | 65.2225 | 170.466 | 576.2235 | 1018.9154 | 351.4504 | 2862.4368
2027-09-05 23:00 | 14.3116 | 163.1406 | 185.6198 | 101.3186 | 204.3398 | 63.2078 | 162.8904 | 570.4897 | 990.824 | 356.2201 | 2812.3625
2027-09-12 23:00 | 13.2568 | 153.7935 | 173.8961 | 95.9874 | 193.7307 | 62.6519 | 152.6851 | 543.0106 | 937.6219 | 346.2036 | 2672.8375
2027-09-19 23:00 | 12.8338 | 150.522 | 171.6347 | 94.2874 | 196.4504 | 61.5993 | 150.9398 | 542.6823 | 948.0574 | 342.4218 | 2671.429
2027-09-26 23:00 | 12.6949 | 152.6328 | 174.6295 | 92.1447 | 200.1213 | 62.877 | 157.3149 | 526.2519 | 941.6256 | 329.3539 | 2649.6465
2027-10-03 23:00 | 11.3546 | 149.3142 | 169.997 | 90.6352 | 206.6203 | 65.7282 | 160.6946 | 510.5863 | 939.6058 | 322.5812 | 2627.1174
2027-10-10 23:00 | 11.7729 | 154.864 | 174.9774 | 93.3063 | 210.2824 | 65.5423 | 152.2365 | 513.4071 | 908.8291 | 326.7585 | 2611.9764
2027-10-17 23:00 | 11.862 | 157.1544 | 172.7944 | 92.6707 | 205.535 | 65.9861 | 152.7614 | 507.5987 | 897.2796 | 329.4719 | 2593.1143
2027-10-24 23:00 | 13.2931 | 164.2833 | 181.3269 | 95.6047 | 200.3484 | 69.161 | 152.825 | 530.9311 | 904.6437 | 351.1016 | 2663.5188
2027-10-31 23:00 | 13.3592 | 168.1934 | 184.7135 | 96.3956 | 208.1841 | 75.1244 | 155.9426 | 534.2968 | 921.272 | 351.875 | 2709.3565
2027-11-07 23:00 | 13.3664 | 165.8947 | 186.6611 | 98.7146 | 216.3861 | 74.6793 | 165.3433 | 541.9372 | 952.781 | 356.8145 | 2772.5781
2027-11-14 23:00 | 14.8848 | 180.6287 | 203.0066 | 99.9763 | 214.5309 | 78.4679 | 162.493 | 551.6838 | 954.5865 | 365.0104 | 2825.2689
2027-11-21 23:00 | 14.6622 | 186.0269 | 209.8104 | 103.0728 | 221.8786 | 78.6454 | 174.7805 | 563.2952 | 986.3128 | 377.1391 | 2915.6237
2027-11-28 23:00 | 15.0124 | 193.4959 | 218.2851 | 107.0284 | 233.1069 | 83.303 | 179.7379 | 572.0918 | 1005.084 | 372.9874 | 2980.1328
2027-12-05 23:00 | 16.0603 | 195.8204 | 230.3677 | 107.9806 | 233.8576 | 86.2033 | 187.4503 | 587.1532 | 1016.029 | 386.6937 | 3047.6161
2027-12-12 23:00 | 16.9919 | 200.8046 | 242.475 | 108.6664 | 237.5615 | 90.3943 | 190.0395 | 600.9877 | 1027.4122 | 388.551 | 3103.8841
2027-12-19 23:00 | 17.1521 | 206.4995 | 248.8766 | 109.5915 | 240.8156 | 90.7572 | 197.716 | 604.7652 | 1024.1545 | 388.0026 | 3128.3309
2027-12-26 23:00 | 17.7755 | 211.922 | 254.605 | 108.9997 | 247.1178 | 96.8287 | 195.8879 | 603.469 | 1020.4175 | 382.3316 | 3139.3548
2028-01-02 23:00 | 16.6411 | 203.8272 | 244.9999 | 106.4485 | 248.6727 | 88.1932 | 193.3366 | 574.4486 | 980.464 | 378.6431 | 3035.6748
2028-01-09 23:00 | 17.4026 | 217.2988 | 250.9562 | 115.3202 | 256.2536 | 84.8014 | 203.4475 | 630.8988 | 1032.3623 | 383.2967 | 3192.0381
2028-01-16 23:00 | 18.4872 | 223.2233 | 256.5116 | 118.2857 | 265.8853 | 94.1782 | 205.8352 | 658.2605 | 1069.955 | 395.7831 | 3306.4052
2028-01-23 23:00 | 19.7069 | 229.7378 | 262.8847 | 118.8116 | 269.1485 | 96.1196 | 209.7611 | 656.6226 | 1075.2197 | 391.1068 | 3329.1192
2028-01-30 23:00 | 19.3299 | 220.1124 | 252.1523 | 120.5204 | 259.4954 | 88.8416 | 208.4794 | 666.4921 | 1098.3081 | 399.9978 | 3333.7293
2028-02-06 23:00 | 18.2221 | 214.1993 | 248.8666 | 118.1624 | 261.941 | 90.9414 | 202.0232 | 646.3798 | 1079.2997 | 378.4082 | 3258.4438
2028-02-13 23:00 | 17.9655 | 212.3508 | 243.3761 | 118.0521 | 261.3872 | 90.0872 | 199.9983 | 640.9892 | 1067.4156 | 388.694 | 3240.316
2028-02-20 23:00 | 18.5342 | 208.9234 | 244.0906 | 115.8237 | 260.1694 | 84.9873 | 205.2585 | 630.0964 | 1075.0291 | 374.4339 | 3217.3465
2028-02-27 23:00 | 18.1031 | 200.2954 | 232.4106 | 115.6965 | 250.8398 | 79.287 | 202.5094 | 615.8821 | 1057.2457 | 379.6845 | 3151.9541
2028-03-05 23:00 | 17.4731 | 192.3206 | 224.7051 | 110.4336 | 263.0058 | 87.5421 | 197.8693 | 617.6178 | 1045.1804 | 360.1095 | 3116.2574
2028-03-12 23:00 | 16.4604 | 185.3146 | 216.2583 | 111.439 | 252.1471 | 81.7091 | 186.259 | 615.1614 | 1032.1427 | 355.0578 | 3051.9494
2028-03-19 23:00 | 15.7866 | 175.0267 | 202.7738 | 108.7354 | 243.2123 | 75.4312 | 186.6896 | 594.9785 | 1018.2843 | 361.9532 | 2982.8714
2028-03-26 23:00 | 15.8324 | 164.1371 | 192.572 | 106.3572 | 240.1626 | 74.6531 | 180.8507 | 595.0831 | 995.7386 | 356.031 | 2921.4178
2028-04-02 23:00 | 16.0885 | 164.6539 | 194.6895 | 103.4987 | 239.4904 | 76.8525 | 178.1027 | 576.8952 | 977.0283 | 335.5185 | 2862.8183
Back to main menu

## Table 1.1.3 Planned
Back to main menu
Table 1.1.3 Planned: Weekly Energy Demand by Zone
Week Ending | Planned Weekly Normal Energy (GWh)
| Bruce | East | Essa | Niagara | NorthEast | NorthWest | Ottawa | SouthWest | Toronto | West | Ontario
2026-10-04 23:00 | 11.9139 | 149.8626 | 169.2239 | 90.2267 | 202.4926 | 61.1669 | 150.0665 | 511.4228 | 901.1604 | 290.8577 | 2538.394
2026-10-11 23:00 | 12.2489 | 157.5188 | 175.4479 | 91.5928 | 201.4921 | 66.0295 | 149.9342 | 503.683 | 880.0579 | 289.0537 | 2527.0586
2026-10-18 23:00 | 12.6837 | 158.8446 | 176.7705 | 91.2951 | 201.399 | 67.1172 | 147.1089 | 504.4105 | 861.5632 | 289.8671 | 2511.0598
2026-10-25 23:00 | 13.3173 | 164.2434 | 181.1422 | 92.9582 | 204.0964 | 67.6814 | 153.5414 | 519.0514 | 888.3811 | 298.8744 | 2583.2872
2026-11-01 23:00 | 12.2829 | 163.2873 | 182.8656 | 95.4632 | 205.6692 | 65.7924 | 160.7297 | 528.6894 | 911.1879 | 306.4074 | 2632.3751
2026-11-08 23:00 | 13.6171 | 166.9047 | 187.6755 | 97.1891 | 210.6642 | 72.6539 | 161.7093 | 540.2839 | 922.8537 | 321.3827 | 2694.934
2026-11-15 23:00 | 13.6383 | 174.6868 | 195.4863 | 99.1649 | 215.6133 | 73.9407 | 167.7222 | 550.9539 | 937.0791 | 324.8307 | 2753.1161
2026-11-22 23:00 | 14.9467 | 186.8175 | 211.5581 | 100.5435 | 226.3305 | 76.3265 | 174.3983 | 556.5641 | 965.4249 | 327.5789 | 2840.4892
2026-11-29 23:00 | 15.706 | 195.8782 | 217.7356 | 104.3892 | 224.5451 | 79.9622 | 175.9265 | 570.5345 | 980.4386 | 341.3664 | 2906.4823
2026-12-06 23:00 | 16.8696 | 196.1211 | 231.3157 | 106.2938 | 228.5709 | 82.4582 | 182.8809 | 593.0886 | 995.3689 | 348.7387 | 2981.7064
2026-12-13 23:00 | 17.5472 | 203.5985 | 245.4065 | 106.5971 | 235.2221 | 87.9886 | 187.5911 | 600.8228 | 999.3663 | 346.3321 | 3030.4725
2026-12-20 23:00 | 16.9678 | 205.666 | 247.074 | 107.1686 | 239.4786 | 87.0603 | 197.7063 | 599.9487 | 998.6992 | 350.935 | 3050.7045
2026-12-27 23:00 | 17.5986 | 203.3979 | 243.795 | 104.3689 | 228.1963 | 81.7382 | 186.8806 | 577.2883 | 970.1156 | 339.2426 | 2952.6221
2027-01-03 23:00 | 16.764 | 209.0366 | 248.896 | 102.5021 | 246.1417 | 90.2269 | 192.3254 | 566.7735 | 942.1568 | 332.8794 | 2947.7023
2027-01-10 23:00 | 18.0341 | 216.5561 | 252.1519 | 109.5182 | 248.8372 | 89.687 | 196.7026 | 626.221 | 1020.6184 | 351.2073 | 3129.5337
2027-01-17 23:00 | 18.5752 | 220.6526 | 253.5545 | 109.756 | 243.9742 | 86.6342 | 203.0642 | 627.1117 | 1032.3317 | 353.9996 | 3149.6537
2027-01-24 23:00 | 19.7689 | 225.7212 | 261.2951 | 109.3929 | 254.587 | 87.6403 | 206.4036 | 618.7419 | 1039.7652 | 349.9907 | 3173.3068
2027-01-31 23:00 | 19.664 | 219.6432 | 255.0161 | 110.5419 | 254.0226 | 90.4426 | 202.9473 | 630.616 | 1037.2247 | 351.566 | 3171.6843
2027-02-07 23:00 | 17.6664 | 209.394 | 245.7236 | 109.4996 | 251.798 | 85.5958 | 199.983 | 612.3831 | 1032.1321 | 341.2237 | 3105.3994
2027-02-14 23:00 | 17.2166 | 208.7948 | 242.5673 | 110.6631 | 251.9981 | 88.5295 | 196.7612 | 611.5143 | 1033.4358 | 338.4197 | 3099.9002
2027-02-21 23:00 | 18.0638 | 203.081 | 239.1571 | 107.7032 | 250.8058 | 85.911 | 194.4856 | 594.2395 | 1005.7562 | 337.178 | 3036.3811
2027-02-28 23:00 | 17.8344 | 196.3592 | 231.0818 | 110.1043 | 242.1335 | 81.7065 | 191.6088 | 609.7051 | 1014.5488 | 339.8935 | 3034.976
2027-03-07 23:00 | 16.8478 | 191.7677 | 223.3784 | 103.9367 | 242.7597 | 84.81 | 184.6638 | 591.3714 | 989.1512 | 326.9829 | 2955.6698
2027-03-14 23:00 | 15.7473 | 175.2651 | 209.1666 | 102.0801 | 242.1056 | 82.304 | 180.0761 | 587.4543 | 972.9412 | 328.5886 | 2895.7288
2027-03-21 23:00 | 15.7416 | 171.4133 | 204.5554 | 100.9131 | 235.1159 | 77.375 | 177.2927 | 573.2167 | 958.5347 | 314.8256 | 2828.984
2027-03-28 23:00 | 16.2651 | 170.7681 | 199.9261 | 96.3009 | 229.3844 | 75.2998 | 172.3189 | 549.2844 | 921.6107 | 303.914 | 2735.0725
2027-04-04 23:00 | 15.2245 | 165.464 | 192.2255 | 96.1389 | 222.5332 | 73.6708 | 169.1484 | 549.5236 | 906.1935 | 304.6482 | 2694.7706
2027-04-11 23:00 | 15.2093 | 159.7319 | 185.7255 | 95.1431 | 212.4538 | 68.8777 | 162.4307 | 547.9712 | 903.4812 | 297.1153 | 2648.1399
2027-04-18 23:00 | 14.4334 | 151.4407 | 177.2653 | 92.909 | 208.61 | 70.7375 | 156.3397 | 540.4071 | 884.0404 | 291.8388 | 2588.0218
2027-04-25 23:00 | 14.8591 | 150.2413 | 176.7511 | 90.8667 | 204.6283 | 66.2444 | 152.9635 | 527.9562 | 884.5852 | 288.5099 | 2557.6058
2027-05-02 23:00 | 15.1447 | 147.0822 | 179.0887 | 89.2525 | 202.4084 | 65.5397 | 153.3365 | 521.673 | 878.7453 | 282.8412 | 2535.1122
2027-05-09 23:00 | 15.1232 | 144.1642 | 178.4438 | 88.5576 | 188.4946 | 64.3914 | 148.2115 | 525.752 | 869.7937 | 296.3277 | 2519.2597
2027-05-16 23:00 | 13.047 | 135.1675 | 170.7711 | 88.6851 | 192.491 | 62.4654 | 152.7568 | 523.9793 | 884.1548 | 293.311 | 2516.829
2027-05-23 23:00 | 13.7759 | 140.0621 | 176.4129 | 88.5746 | 195.3599 | 65.6905 | 154.7871 | 524.006 | 882.9593 | 293.3253 | 2534.9535
2027-05-30 23:00 | 12.4302 | 133.506 | 169.9147 | 89.2618 | 193.7392 | 62.0406 | 150.9892 | 521.8896 | 885.2292 | 285.8831 | 2504.8836
2027-06-06 23:00 | 12.9829 | 146.8983 | 180.7068 | 93.7748 | 188.6651 | 61.1571 | 160.4289 | 537.8199 | 932.8298 | 314.0979 | 2629.3614
2027-06-13 23:00 | 13.0734 | 151.4888 | 188.2981 | 95.3339 | 181.9762 | 59.2271 | 168.2118 | 545.7582 | 941.2257 | 329.3718 | 2673.9648
2027-06-20 23:00 | 12.0982 | 153.2685 | 191.2175 | 99.3334 | 183.5892 | 60.0656 | 179.3399 | 568.8217 | 992.7887 | 335.0126 | 2775.5354
2027-06-27 23:00 | 11.2987 | 159.928 | 202.143 | 102.593 | 182.7898 | 61.4108 | 176.7391 | 593.3488 | 1004.828 | 346.9811 | 2842.0603
2027-07-04 23:00 | 10.8698 | 158.6969 | 194.9561 | 103.3403 | 181.426 | 59.7836 | 170.9093 | 598.9043 | 1015.7163 | 351.6184 | 2846.221
2027-07-11 23:00 | 10.9482 | 170.9206 | 208.8136 | 103.6605 | 179.3343 | 58.9531 | 184.3819 | 610.5921 | 1065.3164 | 354.7582 | 2947.679
2027-07-18 23:00 | 11.2923 | 169.5874 | 205.9094 | 104.3702 | 195.0183 | 64.8865 | 180.5783 | 622.2443 | 1084.5327 | 368.4985 | 3006.9178
2027-07-25 23:00 | 11.9387 | 163.8537 | 199.5584 | 104.7444 | 200.653 | 67.8293 | 175.1113 | 648.4557 | 1057.6997 | 379.9772 | 3009.8214
2027-08-01 23:00 | 11.8963 | 173.2329 | 207.0874 | 105.7497 | 188.473 | 61.8461 | 181.2965 | 620.0679 | 1078.1704 | 369.6473 | 2997.4674
2027-08-08 23:00 | 12.4164 | 173.2384 | 204.2852 | 105.9399 | 194.5357 | 60.7615 | 178.8175 | 604.4712 | 1047.2464 | 365.3124 | 2947.0247
2027-08-15 23:00 | 13.2721 | 161.4211 | 190.4868 | 104.443 | 204.5607 | 65.5773 | 167.6674 | 625.9857 | 1019.8618 | 382.3111 | 2935.5872
2027-08-22 23:00 | 13.0255 | 170.4514 | 203.3279 | 103.4398 | 194.8243 | 62.1727 | 180.8506 | 582.5252 | 1039.9435 | 354.3237 | 2904.8845
2027-08-29 23:00 | 13.2205 | 165.1231 | 192.6023 | 103.0233 | 205.8884 | 65.1933 | 170.3889 | 602.385 | 1018.455 | 359.8019 | 2896.0817
2027-09-05 23:00 | 13.2721 | 159.2559 | 182.0841 | 101.5856 | 203.7428 | 64.4929 | 158.5354 | 612.2356 | 984.2666 | 370.2824 | 2849.7535
2027-09-12 23:00 | 13.2598 | 153.8297 | 173.9363 | 96.0097 | 193.775 | 62.6663 | 152.719 | 571.8113 | 937.8347 | 355.9319 | 2711.7736
2027-09-19 23:00 | 12.8345 | 150.5323 | 171.6439 | 94.2936 | 196.4641 | 61.603 | 150.9459 | 571.7436 | 948.0917 | 352.2125 | 2710.3651
2027-09-26 23:00 | 12.6931 | 152.6131 | 174.6055 | 92.1316 | 200.0944 | 62.8682 | 157.292 | 555.5942 | 941.4865 | 339.2042 | 2688.5827
2027-10-03 23:00 | 11.7659 | 150.6413 | 172.8032 | 92.6511 | 200.1345 | 62.6637 | 153.4454 | 549.702 | 930.5374 | 342.6249 | 2666.9695
2027-10-10 23:00 | 11.7669 | 154.7873 | 174.8897 | 93.2593 | 210.1776 | 65.5093 | 152.1601 | 545.5965 | 908.3714 | 336.3836 | 2652.9018
2027-10-17 23:00 | 11.8566 | 157.0833 | 172.7156 | 92.6282 | 205.4423 | 65.9561 | 152.691 | 539.7187 | 896.8662 | 339.0818 | 2634.0396
2027-10-24 23:00 | 13.2941 | 164.298 | 181.3425 | 95.6132 | 200.3683 | 69.1671 | 152.8377 | 562.239 | 904.7189 | 360.5653 | 2704.4441
2027-10-31 23:00 | 13.3587 | 168.1899 | 184.7088 | 96.3932 | 208.1809 | 75.1228 | 155.9381 | 565.7755 | 921.2456 | 361.3684 | 2750.2818
2027-11-07 23:00 | 13.3567 | 165.7773 | 186.5279 | 98.6438 | 216.2317 | 74.6258 | 165.2247 | 579.6944 | 952.0968 | 366.7793 | 2818.9584
2027-11-14 23:00 | 13.822 | 177.5422 | 200.9059 | 101.1427 | 217.4836 | 76.951 | 165.7273 | 588.2423 | 961.3616 | 368.4705 | 2871.6492
2027-11-21 23:00 | 15.1031 | 188.7137 | 212.2685 | 102.9873 | 224.4847 | 81.5929 | 176.5014 | 600.5503 | 978.9445 | 380.8574 | 2962.004
2027-11-28 23:00 | 14.4279 | 189.5735 | 210.6081 | 107.7034 | 227.8427 | 82.9434 | 175.9885 | 614.7247 | 1007.2758 | 395.425 | 3026.5131
2027-12-05 23:00 | 17.0236 | 201.1258 | 237.9464 | 106.2848 | 235.184 | 88.9486 | 189.427 | 621.4073 | 1012.7992 | 386.1683 | 3096.3148
2027-12-12 23:00 | 16.9864 | 200.7401 | 242.3972 | 108.6311 | 237.4866 | 90.3657 | 189.9778 | 641.7257 | 1027.0772 | 398.102 | 3153.4898
2027-12-19 23:00 | 17.1501 | 206.4768 | 248.849 | 109.5794 | 240.7896 | 90.7473 | 197.6938 | 645.0982 | 1024.0413 | 397.511 | 3177.9366
2027-12-26 23:00 | 16.8328 | 212.7768 | 253.5085 | 108.8474 | 250.3115 | 91.7442 | 205.1488 | 635.8622 | 1018.2318 | 395.6966 | 3188.9605
2028-01-02 23:00 | 16.6304 | 203.6981 | 244.8459 | 106.3812 | 248.5157 | 88.1386 | 193.2142 | 615.8001 | 979.8468 | 388.2556 | 3085.3266
2028-01-09 23:00 | 17.4005 | 217.2734 | 250.9268 | 115.3066 | 256.2235 | 84.7913 | 203.4237 | 671.5874 | 1032.2414 | 392.8067 | 3241.9813
2028-01-16 23:00 | 18.4857 | 223.2057 | 256.4911 | 118.2764 | 265.8642 | 94.1705 | 205.8188 | 698.8811 | 1069.8692 | 405.2856 | 3356.3484
2028-01-23 23:00 | 19.7096 | 229.7694 | 262.9209 | 118.8279 | 269.1858 | 96.1329 | 209.7897 | 696.8021 | 1075.367 | 400.5573 | 3379.0625
2028-01-30 23:00 | 19.3183 | 219.9806 | 252.0013 | 120.4482 | 259.3408 | 88.7884 | 208.3543 | 708.1703 | 1097.6492 | 409.6213 | 3383.6726
2028-02-06 23:00 | 18.2227 | 214.2069 | 248.8756 | 118.1669 | 261.9507 | 90.9448 | 202.0305 | 686.7658 | 1079.34 | 387.8833 | 3308.3871
2028-02-13 23:00 | 17.9606 | 212.2945 | 243.3114 | 118.0209 | 261.3179 | 90.0632 | 199.9451 | 681.9753 | 1067.1321 | 398.2381 | 3290.2592
2028-02-20 23:00 | 18.5342 | 208.9241 | 244.0909 | 115.8238 | 260.1699 | 84.9872 | 205.2589 | 670.553 | 1075.0302 | 383.9175 | 3267.2898
2028-02-27 23:00 | 18.0947 | 200.2029 | 232.3031 | 115.6429 | 250.7241 | 79.2503 | 202.4158 | 657.2388 | 1056.7553 | 389.2696 | 3201.8974
2028-03-05 23:00 | 17.4713 | 192.3022 | 224.6832 | 110.4227 | 262.9802 | 87.5334 | 197.85 | 658.2639 | 1045.0774 | 369.6162 | 3166.2007
2028-03-12 23:00 | 16.4537 | 185.2404 | 216.1708 | 111.394 | 252.0453 | 81.6759 | 186.1833 | 656.3732 | 1031.7223 | 364.6339 | 3101.8927
2028-03-19 23:00 | 15.77 | 174.8454 | 202.563 | 108.6222 | 242.9589 | 75.3522 | 186.4954 | 637.3359 | 1017.2211 | 371.6505 | 3032.8147
2028-03-26 23:00 | 15.818 | 163.99 | 192.3989 | 106.2611 | 239.9461 | 74.5854 | 180.6878 | 637.1399 | 994.8402 | 365.6937 | 2971.3611
2028-04-02 23:00 | 16.0829 | 164.5988 | 194.6236 | 103.4637 | 239.4103 | 76.8263 | 178.0426 | 617.9441 | 976.6971 | 345.0721 | 2912.7615
Back to main menu

## Table 1.2 Firm
Back to main menu
Table 1.2 Firm: Forecasted Seasonal Peaks
Season | Firm Normal Weather Peak (MW) | Firm Extreme Weather Peak (MW)
Winter 2026-27 | 22834.2677 | 23876.1145
Summer 2027 | 24036.005 | 26401.2855
Winter 2027-28 | 23771.6909 | 24759.5932
Back to main menu

## Table 1.2 Planned
Back to main menu
Table 1.2 Planned: Forecasted Seasonal Peaks
Season | Planned Normal Weather Peak (MW) | Planned Extreme Weather Peak (MW)
Winter 2026-27 | 22874.0071 | 23917.6025
Summer 2027 | 24207.0367 | 26571.4861
Winter 2027-28 | 24068.9723 | 25056.8746
Back to main menu

## Table 1.3
Back to main menu
Table 1.3: Large Step Load Impacts, Firm and Planned Demand
| Firm |  | Planned
Demand Forecast | Energy (GWh) | Peak (MW) | Energy (GWh) | Peak (MW)
Winter 2026-27 | 601.0349 | 349.7562 | 701.3536 | 405.4428
Summer 2027 | 1008.687 | 518.1354 | 1368.0429 | 716.8142
Winter 2027-28 | 1508.9755 | 819.9268 | 2144.6696 | 1159.2465
Back to main menu

## Table 1.4 Firm
Back to main menu
Table 1.4 Firm: Weekly Energy and Peak Demand Forecast
Week | Firm Normal Peak | Firm Extreme Peak | Load Forecast Uncertainty | Firm Normal Energy Demand
Week Ending | (MW) | (MW) | (MW) | (GWh)
2026-10-04 23:00 | 18416.5505 | 21397.0133 | 1286.6837 | 2538.394
2026-10-11 23:00 | 17890.2486 | 19878.7393 | 882.9634 | 2527.0586
2026-10-18 23:00 | 17889.4282 | 19166.4213 | 621.6189 | 2511.0598
2026-10-25 23:00 | 18166.2294 | 19130.3797 | 478.5323 | 2583.2872
2026-11-01 23:00 | 18440.896 | 19393.9431 | 481.021 | 2631.4856
2026-11-08 23:00 | 18992.7367 | 20019.2015 | 511.8928 | 2688.8446
2026-11-15 23:00 | 19490.4162 | 20893.8907 | 678.7943 | 2747.0268
2026-11-22 23:00 | 20074.0228 | 21394.6677 | 658.7797 | 2834.3998
2026-11-29 23:00 | 20588.3561 | 21667.1643 | 563.3826 | 2900.393
2026-12-06 23:00 | 20951.6418 | 22056.144 | 574.4685 | 2974.7488
2026-12-13 23:00 | 21278.4406 | 22639.9048 | 695.2815 | 3023.3886
2026-12-20 23:00 | 21481.2655 | 22903.0806 | 720.7754 | 3043.6207
2026-12-27 23:00 | 20907.8056 | 22372.7169 | 733.6377 | 2945.5382
2027-01-03 23:00 | 21055.51 | 22544.9913 | 745.3972 | 2940.6012
2027-01-10 23:00 | 21954.0014 | 23629.1595 | 839.238 | 3122.467
2027-01-17 23:00 | 21833.3817 | 23557.2083 | 860.5587 | 3142.587
2027-01-24 23:00 | 21910.1197 | 23719.2866 | 895.9273 | 3166.2401
2027-01-31 23:00 | 21886.0471 | 23613.0709 | 855.394 | 3164.6176
2027-02-07 23:00 | 21388.241 | 22915.2363 | 772.8935 | 3095.9945
2027-02-14 23:00 | 21383.5257 | 22913.054 | 770.5583 | 3090.4953
2027-02-21 23:00 | 21099.9325 | 22632.2177 | 773.8925 | 3026.9762
2027-02-28 23:00 | 20950.2416 | 22346.4396 | 706.4679 | 3025.5711
2027-03-07 23:00 | 20430.052 | 21772.3849 | 693.4034 | 2945.4577
2027-03-14 23:00 | 19985.9579 | 21301.9581 | 692.5436 | 2885.5168
2027-03-21 23:00 | 19556.42 | 20846.7211 | 645.7194 | 2818.772
2027-03-28 23:00 | 19049.7186 | 20084.5182 | 557.4301 | 2724.8604
2027-04-04 23:00 | 18695.75 | 19822.2094 | 563.7263 | 2683.4722
2027-04-11 23:00 | 18241.4338 | 19349.2412 | 572.4089 | 2635.9451
2027-04-18 23:00 | 17921.8099 | 19392.4606 | 722.1483 | 2575.8271
2027-04-25 23:00 | 17664.3435 | 18970.9293 | 649.2901 | 2545.4111
2027-05-02 23:00 | 17481.6261 | 18729.763 | 618.0966 | 2521.6686
2027-05-09 23:00 | 17401.6166 | 18989.7659 | 751.4404 | 2502.7356
2027-05-16 23:00 | 17474.7934 | 19616.7486 | 973.2914 | 2500.3048
2027-05-23 23:00 | 17902.9364 | 21346.9586 | 1472.3085 | 2518.4294
2027-05-30 23:00 | 18200.5066 | 23047.2393 | 2046.43 | 2488.3594
2027-06-06 23:00 | 19047.1617 | 24039.6943 | 2189.0527 | 2611.4634
2027-06-13 23:00 | 19546.6517 | 24381.5826 | 2174.8052 | 2655.8833
2027-06-20 23:00 | 20601.9147 | 25105.8658 | 2121.4987 | 2757.4539
2027-06-27 23:00 | 21480.0477 | 24871.2538 | 1747.2331 | 2823.9788
2027-07-04 23:00 | 21480.7844 | 24824.8262 | 1719.5156 | 2821.3371
2027-07-11 23:00 | 22243.6125 | 25794.3047 | 1801.4393 | 2917.6727
2027-07-18 23:00 | 22447.0308 | 25917.4258 | 1775.6573 | 2976.9116
2027-07-25 23:00 | 22455.0049 | 25956.3743 | 1797.2623 | 2979.8151
2027-08-01 23:00 | 22397.25 | 25759.0487 | 1682.3813 | 2966.9522
2027-08-08 23:00 | 21844.1762 | 25444.8033 | 1791.3331 | 2913.3798
2027-08-15 23:00 | 21806.9862 | 25146.0751 | 1665.2249 | 2901.9424
2027-08-22 23:00 | 21611.583 | 24541.0374 | 1492.6724 | 2871.2397
2027-08-29 23:00 | 21644.2238 | 24330.256 | 1410.9283 | 2862.4368
2027-09-05 23:00 | 21297.6041 | 24742.5874 | 1751.292 | 2812.3625
2027-09-12 23:00 | 20202.4268 | 24496.6885 | 1992.2755 | 2672.8375
2027-09-19 23:00 | 19727.0885 | 23640.8329 | 1765.6296 | 2671.429
2027-09-26 23:00 | 19250.6414 | 23129.6182 | 1655.7554 | 2649.6465
2027-10-03 23:00 | 18974.9467 | 22118.5144 | 1356.9127 | 2627.1174
2027-10-10 23:00 | 18408.1065 | 20524.2055 | 929.7257 | 2611.9764
2027-10-17 23:00 | 18548.48 | 19692.8181 | 572.6735 | 2593.1143
2027-10-24 23:00 | 18641.9272 | 19603.0334 | 476.2054 | 2663.5188
2027-10-31 23:00 | 18917.1167 | 19884.5061 | 490.5013 | 2709.3565
2027-11-07 23:00 | 19470.8504 | 20475.6264 | 502.6296 | 2772.5781
2027-11-14 23:00 | 19917.6873 | 21216.8781 | 636.9291 | 2825.2689
2027-11-21 23:00 | 20507.061 | 21856.0015 | 669.9536 | 2915.6237
2027-11-28 23:00 | 21068.1986 | 22179.3619 | 577.0918 | 2980.1328
2027-12-05 23:00 | 21395.9275 | 22482.0036 | 567.2473 | 3047.6161
2027-12-12 23:00 | 21764.1002 | 23099.0023 | 682.0237 | 3103.8841
2027-12-19 23:00 | 21986.7908 | 23405.7558 | 717.176 | 3128.3309
2027-12-26 23:00 | 22019.3312 | 23458.8194 | 725.9742 | 3139.3548
2028-01-02 23:00 | 21770.5847 | 23424.2897 | 840.6813 | 3035.6748
2028-01-09 23:00 | 22430.0144 | 24086.3475 | 832.7654 | 3192.0381
2028-01-16 23:00 | 22841.1432 | 24543.4203 | 851.079 | 3306.4052
2028-01-23 23:00 | 22910.7145 | 24673.8876 | 877.6907 | 3329.1192
2028-01-30 23:00 | 22915.8775 | 24584.3592 | 838.0983 | 3333.7293
2028-02-06 23:00 | 22604.0142 | 24235.6726 | 807.4963 | 3258.4438
2028-02-13 23:00 | 22255.6314 | 23751.1704 | 759.2133 | 3240.316
2028-02-20 23:00 | 22312.99 | 23698.2519 | 693.2416 | 3217.3465
2028-02-27 23:00 | 21732.8956 | 23138.7728 | 710.6081 | 3151.9541
2028-03-05 23:00 | 21551.4304 | 22864.5744 | 679.6193 | 3116.2574
2028-03-12 23:00 | 20986.3242 | 22241.0754 | 665.7664 | 3051.9494
2028-03-19 23:00 | 20556.72 | 21853.6059 | 649.0147 | 2982.8714
2028-03-26 23:00 | 20011.279 | 21089.1295 | 574.4507 | 2921.4178
2028-04-02 23:00 | 19615.719 | 20683.9999 | 550.7432 | 2862.8183
Back to main menu

## Table 1.4 Planned
Back to main menu
Table 1.4 Planned: Weekly Energy and Peak Demand Forecast
Week | Planned Normal Peak | Planned Extreme Peak | Load Forecast Uncertainty | Planned Normal Energy Demand
Week Ending | (MW) | (MW) | (MW) | (GWh)
2026-10-04 23:00 | 18480.3905 | 21460.8533 | 1286.6837 | 2538.394
2026-10-11 23:00 | 17970.9886 | 19959.4793 | 882.9634 | 2527.0586
2026-10-18 23:00 | 17974.9882 | 19251.9813 | 621.6189 | 2511.0598
2026-10-25 23:00 | 18236.2494 | 19200.3997 | 478.5323 | 2583.2872
2026-11-01 23:00 | 18523.4558 | 19478.717 | 481.4489 | 2632.3751
2026-11-08 23:00 | 19107.0541 | 20133.4984 | 511.8591 | 2694.934
2026-11-15 23:00 | 19618.8302 | 21022.3413 | 678.7435 | 2753.1161
2026-11-22 23:00 | 20184.3693 | 21504.6799 | 658.6618 | 2840.4892
2026-11-29 23:00 | 20698.9728 | 21777.6626 | 563.3282 | 2906.4823
2026-12-06 23:00 | 21103.0147 | 22207.8822 | 574.6287 | 2981.7064
2026-12-13 23:00 | 21422.0544 | 22783.5063 | 695.2725 | 3030.4725
2026-12-20 23:00 | 21635.2619 | 23057.1917 | 720.8401 | 3050.7045
2026-12-27 23:00 | 21040.2309 | 22505.2268 | 733.6643 | 2952.6221
2027-01-03 23:00 | 21096.84 | 22586.3612 | 745.4172 | 2947.7023
2027-01-10 23:00 | 22127.7316 | 23802.9967 | 839.2781 | 3129.5337
2027-01-17 23:00 | 22014.8508 | 23739.1689 | 860.7019 | 3149.6537
2027-01-24 23:00 | 22079.8942 | 23889.2774 | 896.0175 | 3173.3068
2027-01-31 23:00 | 22065.9489 | 23793.0251 | 855.4361 | 3171.6843
2027-02-07 23:00 | 21553.5993 | 23080.7163 | 772.9729 | 3105.3994
2027-02-14 23:00 | 21554.0759 | 23083.6391 | 770.5988 | 3099.9002
2027-02-21 23:00 | 21266.312 | 22798.6653 | 773.9416 | 3036.3811
2027-02-28 23:00 | 21114.8814 | 22511.2093 | 706.5304 | 3034.976
2027-03-07 23:00 | 20572.4402 | 21914.3251 | 693.1901 | 2955.6698
2027-03-14 23:00 | 20134.1872 | 21450.0446 | 692.4794 | 2895.7288
2027-03-21 23:00 | 19615.87 | 20905.9915 | 645.6295 | 2828.984
2027-03-28 23:00 | 19190.1927 | 20224.7627 | 557.3216 | 2735.0725
2027-04-04 23:00 | 18755.94 | 19881.0425 | 563.0472 | 2694.7706
2027-04-11 23:00 | 18407.4814 | 19515.1572 | 572.3502 | 2648.1399
2027-04-18 23:00 | 18074.7643 | 19544.9625 | 721.9412 | 2588.0218
2027-04-25 23:00 | 17820.6238 | 19126.5333 | 648.9735 | 2557.6058
2027-05-02 23:00 | 17635.8177 | 18883.1964 | 617.76 | 2535.1122
2027-05-09 23:00 | 17576.1644 | 19163.1114 | 750.8795 | 2519.2597
2027-05-16 23:00 | 17662.5135 | 19802.9831 | 972.4517 | 2516.829
2027-05-23 23:00 | 18088.2039 | 21530.6091 | 1471.4394 | 2534.9535
2027-05-30 23:00 | 18394.1435 | 23237.6586 | 2045.232 | 2504.8836
2027-06-06 23:00 | 19254.3984 | 24248.0781 | 2188.7105 | 2629.3614
2027-06-13 23:00 | 19750.5121 | 24587.7852 | 2175.094 | 2673.9648
2027-06-20 23:00 | 20796.4175 | 25299.6856 | 2121.177 | 2775.5354
2027-06-27 23:00 | 21671.4044 | 25061.929 | 1746.888 | 2842.0603
2027-07-04 23:00 | 21710.0254 | 25033.7005 | 1711.8556 | 2846.221
2027-07-11 23:00 | 22500.7666 | 26049.7502 | 1800.6045 | 2947.679
2027-07-18 23:00 | 22709.2037 | 26178.2302 | 1774.9502 | 3006.9178
2027-07-25 23:00 | 22717.9474 | 26218.5643 | 1796.8101 | 3009.8214
2027-08-01 23:00 | 22570.73 | 25929.9746 | 1681.1032 | 2997.4674
2027-08-08 23:00 | 22137.9324 | 25737.4465 | 1790.9277 | 2947.0247
2027-08-15 23:00 | 22100.3148 | 25438.794 | 1664.8922 | 2935.5872
2027-08-22 23:00 | 21895.3796 | 24824.2171 | 1492.4076 | 2904.8845
2027-08-29 23:00 | 21918.2 | 24603.5148 | 1410.5912 | 2896.0817
2027-09-05 23:00 | 21613.91 | 25052.0467 | 1748.9354 | 2849.7535
2027-09-12 23:00 | 20521.2016 | 24816.6708 | 1992.3492 | 2711.7736
2027-09-19 23:00 | 20055.3807 | 23969.9904 | 1765.5005 | 2710.3651
2027-09-26 23:00 | 19582.0923 | 23460.2775 | 1654.9728 | 2688.5827
2027-10-03 23:00 | 19281.4516 | 22424.129 | 1356.5285 | 2666.9695
2027-10-10 23:00 | 18745.5262 | 20861.0324 | 929.5953 | 2652.9018
2027-10-17 23:00 | 18789.61 | 19933.8483 | 572.6236 | 2634.0396
2027-10-24 23:00 | 18968.765 | 19929.4557 | 476.0174 | 2704.4441
2027-10-31 23:00 | 19251.2504 | 20218.5678 | 490.4295 | 2750.2818
2027-11-07 23:00 | 19837.221 | 20842.0905 | 502.599 | 2818.9584
2027-11-14 23:00 | 20293.766 | 21593.1658 | 636.9083 | 2871.6492
2027-11-21 23:00 | 20870.9678 | 22219.6295 | 669.8476 | 2962.004
2027-11-28 23:00 | 21418.9089 | 22530.0944 | 577.0965 | 3026.5131
2027-12-05 23:00 | 21791.5504 | 22880.3471 | 568.5158 | 3096.3148
2027-12-12 23:00 | 22162.1065 | 23497.0492 | 682.0553 | 3153.4898
2027-12-19 23:00 | 22395.6415 | 23814.5904 | 717.1713 | 3177.9366
2027-12-26 23:00 | 22416.9529 | 23856.6031 | 726.024 | 3188.9605
2028-01-02 23:00 | 22193.8656 | 23848.5812 | 841.1043 | 3085.3266
2028-01-09 23:00 | 22865.579 | 24521.8836 | 832.768 | 3241.9813
2028-01-16 23:00 | 23299.5517 | 25001.6939 | 851.035 | 3356.3484
2028-01-23 23:00 | 23349.3097 | 25112.4702 | 877.6793 | 3379.0625
2028-01-30 23:00 | 23358.1352 | 25026.5869 | 838.0789 | 3383.6726
2028-02-06 23:00 | 23042.3751 | 24674.0464 | 807.4976 | 3308.3871
2028-02-13 23:00 | 22685.3911 | 24181.0844 | 759.2648 | 3290.2592
2028-02-20 23:00 | 22610.28 | 23995.5419 | 693.2416 | 3267.2898
2028-02-27 23:00 | 22152.1095 | 23558.0937 | 710.642 | 3201.8974
2028-03-05 23:00 | 21977.2354 | 23290.3701 | 679.6253 | 3166.2007
2028-03-12 23:00 | 21397.6214 | 22652.4706 | 665.8097 | 3101.8927
2028-03-19 23:00 | 20854.04 | 22151.0057 | 649.0546 | 3032.8147
2028-03-26 23:00 | 20419.2827 | 21497.2094 | 574.4789 | 2971.3611
2028-04-02 23:00 | 20031.9158 | 21100.0688 | 550.6866 | 2912.7615
Back to main menu

## Table 1.4.1
Back to main menu
Table 1.4.1: Weekly Weather and Demand History
Week Number | Week Ending | Actual Energy (GWh) | Weekly Average Temperature (°C) | Peak Day | Actual Peak (MW) | Peak Day Temperature (°C)
19 | 2003-05-11 | 2675.239 | 13.4714 | 2003-05-05 | 18741 | 13.1
20 | 2003-05-18 | 2632.509 | 11.8333 | 2003-05-12 | 18362 | 11.1
21 | 2003-05-25 | 2571.07 | 13.4762 | 2003-05-20 | 18599 | 15.7
22 | 2003-06-01 | 2649.124 | 15.0952 | 2003-05-29 | 18226 | 24.2
23 | 2003-06-08 | 2665.141 | 16.219 | 2003-06-04 | 18410 | 16.1
24 | 2003-06-15 | 2678.946 | 18.0381 | 2003-06-11 | 19042 | 24.6
25 | 2003-06-22 | 2742.722 | 19.4 | 2003-06-18 | 19935 | 22.6
26 | 2003-06-29 | 3084.92 | 25.8857 | 2003-06-26 | 24753 | 33.3
27 | 2003-07-06 | 2992.491 | 25.419 | 2003-07-04 | 23199 | 31.3
28 | 2003-07-13 | 2852.473 | 21.5524 | 2003-07-08 | 22167 | 28.6
29 | 2003-07-20 | 2847.944 | 21.2667 | 2003-07-14 | 21133 | 28
30 | 2003-07-27 | 2885.618 | 22.5905 | 2003-07-25 | 20868 | 28.7
31 | 2003-08-03 | 2897.737 | 22.3905 | 2003-07-30 | 21414 | 28.3
32 | 2003-08-10 | 3017.672 | 23.3 | 2003-08-07 | 22326 | 26.9
33 | 2003-08-17 | 2723.58 | 22.1 | 2003-08-14 | 23932 | 31
34 | 2003-08-24 | 2750.549 | 23.4048 | 2003-08-21 | 20709 | 31.7
35 | 2003-08-31 | 2853.562 | 21.7952 | 2003-08-26 | 21951 | 30
36 | 2003-09-07 | 2703.488 | 20.1095 | 2003-09-03 | 19841 | 23.2
37 | 2003-09-14 | 2870.007 | 20.7381 | 2003-09-11 | 20699 | 26.8
38 | 2003-09-21 | 2785.104 | 17.9857 | 2003-09-15 | 20233 | 19.6
39 | 2003-09-28 | 2698.174 | 15.6048 | 2003-09-22 | 19269 | 18.4
40 | 2003-10-05 | 2734.489 | 8.3905 | 2003-10-02 | 18929 | 9.4
41 | 2003-10-12 | 2696.531 | 15.3286 | 2003-10-09 | 18922 | 23.6
42 | 2003-10-19 | 2672.208 | 9.2952 | 2003-10-14 | 19092 | 16.2
43 | 2003-10-26 | 2799.532 | 7.4905 | 2003-10-23 | 19738 | 5.4
44 | 2003-11-02 | 2803.196 | 9.2762 | 2003-10-28 | 20426 | 9.7
45 | 2003-11-09 | 2900.177 | 4.019 | 2003-11-04 | 20899 | 4.7
46 | 2003-11-16 | 2927.031 | 4.5857 | 2003-11-13 | 21169 | 2
47 | 2003-11-23 | 2875.998 | 8.0048 | 2003-11-17 | 20954 | 5.3
48 | 2003-11-30 | 2975.154 | 4.1333 | 2003-11-24 | 21504 | 13.4
49 | 2003-12-07 | 2646.415 | -2.919 | 2003-12-02 | 22026 | -5.6
50 | 2003-12-14 | 3161.767 | -0.07619 | 2003-12-08 | 22584 | 1.4
51 | 2003-12-21 | 3602.808 | -0.2619 | 2003-12-15 | 22524 | 1.1
52 | 2003-12-28 | 2643.779 | 3.3333 | 2003-12-22 | 20772 | 5.9
1 | 2004-01-04 | 2717.783 | 4.4048 | 2003-12-30 | 19967 | 3
2 | 2004-01-11 | 3371.766 | -10.2286 | 2004-01-09 | 23998 | -18.3
3 | 2004-01-18 | 3441.886 | -10.7095 | 2004-01-15 | 24877 | -19.7
4 | 2004-01-25 | 3452.82 | -12.0905 | 2004-01-19 | 23728 | -8.7
5 | 2004-02-01 | 3428.432 | -8.3667 | 2004-01-26 | 24659 | -12.8
6 | 2004-02-08 | 3246.898 | -3.9905 | 2004-02-04 | 22494 | -3.9
7 | 2004-02-15 | 3235.171 | -4.1857 | 2004-02-09 | 22239 | 2.1
8 | 2004-02-22 | 3167.121 | -1.7619 | 2004-02-16 | 22792 | -5.7
9 | 2004-02-29 | 3050.511 | 0.28571 | 2004-02-23 | 21479 | -1.2
10 | 2004-03-07 | 2977.639 | 5.0048 | 2004-03-03 | 20620 | 5.8
11 | 2004-03-14 | 3038.073 | -0.10476 | 2004-03-08 | 21125 | 0.2
12 | 2004-03-21 | 3064.243 | -1.1333 | 2004-03-16 | 21476 | -3.1
13 | 2004-03-28 | 2933.927 | 5.9476 | 2004-03-22 | 21429 | -2.8
14 | 2004-04-04 | 2856.708 | 5.4857 | 2004-04-01 | 19881 | 5.2
15 | 2004-04-11 | 2757.816 | 4.5952 | 2004-04-05 | 19965 | 3.2
16 | 2004-04-18 | 2750.228 | 8.3476 | 2004-04-13 | 19339 | 4.2
17 | 2004-04-25 | 2704.802 | 10.5048 | 2004-04-21 | 18430 | 20
18 | 2004-05-02 | 2727.854 | 11.5095 | 2004-04-27 | 18771 | 5.8
19 | 2004-05-09 | 2708.043 | 9.719 | 2004-05-03 | 18664 | 8.3
20 | 2004-05-16 | 2745.619 | 18.7143 | 2004-05-13 | 20218 | 27.3
21 | 2004-05-23 | 2670.063 | 15.8571 | 2004-05-20 | 18943 | 23.6
22 | 2004-05-30 | 2605.734 | 14.3905 | 2004-05-25 | 18349 | 13.6
23 | 2004-06-06 | 2660.545 | 15.7048 | 2004-05-31 | 18508 | 13.2
24 | 2004-06-13 | 2887.122 | 20.4048 | 2004-06-09 | 23153 | 31.3
25 | 2004-06-20 | 2888.011 | 19.9476 | 2004-06-14 | 21752 | 27.3
26 | 2004-06-27 | 2761.454 | 18.481 | 2004-06-24 | 20108 | 25.8
27 | 2004-07-04 | 2745.2 | 20.8762 | 2004-06-30 | 19465 | 23.9
28 | 2004-07-11 | 2789.817 | 20.5143 | 2004-07-05 | 19911 | 20.8
29 | 2004-07-18 | 2908.264 | 22.6857 | 2004-07-12 | 22092 | 27.4
30 | 2004-07-25 | 2975.51 | 21.9143 | 2004-07-22 | 23831 | 30.1
31 | 2004-08-01 | 2924.264 | 21.5 | 2004-07-29 | 21709 | 26.7
32 | 2004-08-08 | 2841.852 | 20.7905 | 2004-08-03 | 23071 | 28.6
33 | 2004-08-15 | 2822.098 | 19.7857 | 2004-08-10 | 21120 | 26.5
34 | 2004-08-22 | 2802.037 | 19.7381 | 2004-08-18 | 20534 | 25.5
35 | 2004-08-29 | 3020.753 | 22.519 | 2004-08-27 | 22554 | 27.6
36 | 2004-09-05 | 2940.62 | 21.4238 | 2004-09-03 | 21395 | 28.4
37 | 2004-09-12 | 2839.863 | 20.6571 | 2004-09-07 | 21019 | 24.6
38 | 2004-09-19 | 2865.462 | 18.3095 | 2004-09-15 | 21740 | 25.8
39 | 2004-09-26 | 2885.929 | 20.4905 | 2004-09-23 | 21431 | 27.5
40 | 2004-10-03 | 2771.707 | 16.1 | 2004-09-27 | 19918 | 23.6
41 | 2004-10-10 | 2739.189 | 15.4238 | 2004-10-07 | 19509 | 26.8
42 | 2004-10-17 | 2707.201 | 10.481 | 2004-10-14 | 19253 | 13.4
43 | 2004-10-24 | 2819.211 | 8.4 | 2004-10-18 | 19704 | 8.8
44 | 2004-10-31 | 2793.89 | 11.381 | 2004-10-27 | 19492 | 11.4
45 | 2004-11-07 | 2855.622 | 7.7952 | 2004-11-04 | 20642 | 6.2
46 | 2004-11-14 | 2961.444 | 3.3857 | 2004-11-09 | 21076 | 1.4
47 | 2004-11-21 | 2880.44 | 8.8286 | 2004-11-15 | 20707 | 13.4
48 | 2004-11-28 | 3001.181 | 4.2905 | 2004-11-24 | 21769 | 3.4
49 | 2004-12-05 | 3085.202 | 2.0143 | 2004-12-03 | 22046 | -0.6
50 | 2004-12-12 | 3622.393 | 2.1286 | 2004-12-06 | 23352 | -1.7
51 | 2004-12-18 | 2800.887 | -3.7286 | 2004-12-14 | 23436 | -4.9
52 | 2004-12-26 | 3162.779 | -7.8762 | 2004-12-20 | 24809 | -12.3
53 | 2005-01-02 | 2907.357 | -0.25714 | 2004-12-27 | 21226 | -8.5
1 | 2005-01-09 | 3184.351 | -1.2714 | 2005-01-06 | 23183 | -2.7
2 | 2005-01-16 | 3215.38 | -1.7 | 2005-01-11 | 22615 | -1.6
3 | 2005-01-23 | 3527.552 | -13.9905 | 2005-01-18 | 24307 | -14.5
4 | 2005-01-30 | 3421.373 | -9.7857 | 2005-01-27 | 24291 | -14.6
5 | 2005-02-06 | 3165.178 | -1.5905 | 2005-01-31 | 22574 | -1.5
6 | 2005-02-13 | 3141.846 | -1.8048 | 2005-02-09 | 22244 | -3.9
7 | 2005-02-20 | 3212.867 | -2.7238 | 2005-02-18 | 22232 | -9.3
8 | 2005-02-27 | 3229.884 | -5.4238 | 2005-02-24 | 22328 | -5.7
9 | 2005-03-06 | 3169.752 | -3.019 | 2005-02-28 | 22106 | 1.8
10 | 2005-03-13 | 3205.601 | -4.2143 | 2005-03-08 | 22684 | -8.5
11 | 2005-03-20 | 3043.77 | -0.7619 | 2005-03-14 | 20989 | -0.8
12 | 2005-03-27 | 2884.713 | 2.181 | 2005-03-23 | 20899 | 1.5
13 | 2005-04-03 | 2873.583 | 6.4333 | 2005-03-28 | 19566 | 6.6
14 | 2005-04-10 | 2777.064 | 9.6524 | 2005-04-04 | 19276 | 10.9
15 | 2005-04-17 | 2705.24 | 9.9 | 2005-04-11 | 18600 | 7.9
16 | 2005-04-24 | 2733.207 | 10.4952 | 2005-04-20 | 18469 | 16.2
17 | 2005-05-01 | 2760.182 | 7.9714 | 2005-04-25 | 19320 | 6.5
18 | 2005-05-08 | 2661.14 | 10.4952 | 2005-05-02 | 18469 | 8.6
19 | 2005-05-15 | 2664.748 | 12.5952 | 2005-05-11 | 18520 | 22.6
20 | 2005-05-22 | 2633.858 | 12.9 | 2005-05-16 | 18288 | 11
21 | 2005-05-29 | 2614.715 | 16.5381 | 2005-05-26 | 18610 | 24.2
22 | 2005-06-05 | 2822.357 | 20.0714 | 2005-06-02 | 19972 | 26
23 | 2005-06-12 | 3339.343 | 26.3952 | 2005-06-10 | 24469 | 30.5
24 | 2005-06-19 | 2967.375 | 20.219 | 2005-06-14 | 24901 | 29.7
25 | 2005-06-26 | 3086.688 | 23.9857 | 2005-06-24 | 23657 | 34
26 | 2005-07-03 | 3201.62 | 25.3905 | 2005-06-27 | 25922 | 31.6
27 | 2005-07-10 | 3047.491 | 24.081 | 2005-07-04 | 23149 | 29.5
28 | 2005-07-17 | 3478.761 | 28.4 | 2005-07-13 | 25872 | 34.6
29 | 2005-07-24 | 3345.132 | 26.5381 | 2005-07-18 | 25545 | 33.3
30 | 2005-07-31 | 3059.465 | 23.3286 | 2005-07-25 | 25053 | 33.8
31 | 2005-08-07 | 3304.047 | 26.2429 | 2005-08-04 | 24979 | 32.8
32 | 2005-08-14 | 3294.582 | 25.0333 | 2005-08-09 | 25638 | 32.9
33 | 2005-08-21 | 3046.904 | 22.5143 | 2005-08-15 | 22081 | 27.6
34 | 2005-08-28 | 2960.83 | 21.0952 | 2005-08-26 | 21349 | 27.4
35 | 2005-09-04 | 3014.828 | 21.8524 | 2005-08-29 | 22761 | 28.4
36 | 2005-09-11 | 2896.404 | 20.4048 | 2005-09-07 | 22170 | 27.5
37 | 2005-09-18 | 3053.565 | 22.3429 | 2005-09-13 | 23689 | 30.1
38 | 2005-09-25 | 2907.237 | 20.0476 | 2005-09-21 | 20979 | 28.5
39 | 2005-10-02 | 2755.984 | 16.7381 | 2005-09-26 | 19927 | 22.3
40 | 2005-10-09 | 2805.329 | 16.7238 | 2005-10-04 | 20676 | 25.8
41 | 2005-10-16 | 2663.132 | 12.9905 | 2005-10-12 | 19064 | 13.2
42 | 2005-10-23 | 2759.787 | 8.8429 | 2005-10-20 | 19120 | 11.9
43 | 2005-10-30 | 2835.05 | 7.419 | 2005-10-26 | 19803 | 8.1
44 | 2005-11-06 | 2777.496 | 11.9 | 2005-11-02 | 19773 | 12.3
45 | 2005-11-13 | 2809.872 | 9.0571 | 2005-11-10 | 20392 | 5.7
46 | 2005-11-20 | 2905.28 | 4.1619 | 2005-11-17 | 21171 | 2.7
47 | 2005-11-27 | 3058.861 | -2.4381 | 2005-11-24 | 22566 | -6.3
48 | 2005-12-04 | 3000.238 | 2.119 | 2005-12-02 | 21616 | -0.8
49 | 2005-12-11 | 3199.968 | -3.7476 | 2005-12-07 | 22958 | -4.3
50 | 2005-12-17 | 2855.631 | -5.3 | 2005-12-12 | 23626 | -9.8
51 | 2005-12-25 | 3103.127 | -1.3286 | 2005-12-19 | 23257 | -4.7
52 | 2006-01-01 | 3208.112 | -1.0048 | 2005-12-29 | 20147 | 0.8
1 | 2006-01-08 | 3060.448 | -0.042857 | 2006-01-06 | 21905 | -5.2
2 | 2006-01-15 | 3046.688 | 1.5524 | 2006-01-09 | 21700 | 2.6
3 | 2006-01-22 | 3134.613 | 0.28571 | 2006-01-17 | 22861 | 0.7
4 | 2006-01-29 | 3075.232 | 0.77619 | 2006-01-26 | 22236 | -3.7
5 | 2006-02-05 | 3002.114 | 2.7476 | 2006-01-31 | 21295 | 1.3
6 | 2006-02-12 | 3166.709 | -5.3429 | 2006-02-08 | 22080 | -6.1
7 | 2006-02-19 | 3166.361 | -3.5857 | 2006-02-16 | 22079 | -0.9
8 | 2006-02-26 | 3126.432 | -2.5857 | 2006-02-20 | 21828 | -3.4
9 | 2006-03-05 | 3153.109 | -4.1429 | 2006-02-27 | 22114 | -4.1
10 | 2006-03-12 | 2943.659 | 4.2857 | 2006-03-06 | 20835 | 0.3
11 | 2006-03-19 | 2983.336 | 0.83333 | 2006-03-15 | 20716 | 2.6
12 | 2006-03-26 | 2968.069 | 0.92857 | 2006-03-20 | 21034 | -1.7
13 | 2006-04-02 | 2778.61 | 8.4048 | 2006-03-27 | 19548 | 11.5
14 | 2006-04-09 | 2829.331 | 5.1476 | 2006-04-04 | 19558 | 6.6
15 | 2006-04-16 | 2607.914 | 12.0143 | 2006-04-12 | 18530 | 16.9
16 | 2006-04-23 | 2642.006 | 11.7 | 2006-04-18 | 17818 | 15.5
17 | 2006-04-30 | 2668.331 | 9.481 | 2006-04-25 | 18633 | 7.2
18 | 2006-05-07 | 2607.266 | 14.1619 | 2006-05-04 | 18132 | 23
19 | 2006-05-14 | 2619.082 | 15.5762 | 2006-05-10 | 18225 | 23.4
20 | 2006-05-21 | 2603.746 | 12.0571 | 2006-05-16 | 17933 | 14.1
21 | 2006-05-28 | 2631.006 | 15.8857 | 2006-05-26 | 18581 | 18.8
22 | 2006-06-04 | 3030.444 | 22.6476 | 2006-05-30 | 24823 | 32.8
23 | 2006-06-11 | 2789.813 | 18.2381 | 2006-06-07 | 21130 | 27.1
24 | 2006-06-18 | 2952.481 | 22.1714 | 2006-06-17 | 21455 | 33.3
25 | 2006-06-25 | 3012.124 | 22.1429 | 2006-06-22 | 23082 | 30.6
26 | 2006-07-02 | 2974.16 | 23.3619 | 2006-06-28 | 22172 | 26.2
27 | 2006-07-09 | 2898.73 | 23.0667 | 2006-07-04 | 22330 | 28.9
28 | 2006-07-16 | 3145.2 | 24.8476 | 2006-07-14 | 23664 | 30
29 | 2006-07-23 | 3182.345 | 23.8095 | 2006-07-17 | 25658 | 33.8
30 | 2006-07-30 | 3285.355 | 25.7 | 2006-07-26 | 24177 | 30.5
31 | 2006-08-06 | 3356.688 | 26.619 | 2006-08-01 | 26768 | 36.4
32 | 2006-08-13 | 2889.38 | 21.7667 | 2006-08-09 | 21246 | 26.2
33 | 2006-08-20 | 2979.046 | 22.2429 | 2006-08-18 | 22702 | 30.4
34 | 2006-08-27 | 2879.36 | 20.9048 | 2006-08-22 | 21273 | 27.5
35 | 2006-09-03 | 2772.402 | 18.5286 | 2006-08-28 | 20529 | 23.6
36 | 2006-09-10 | 2694.952 | 18.6381 | 2006-09-08 | 19896 | 28
37 | 2006-09-17 | 2712.798 | 17.819 | 2006-09-13 | 18845 | 20.9
38 | 2006-09-24 | 2692.215 | 16.4619 | 2006-09-19 | 19775 | 18.1
39 | 2006-10-01 | 2653.947 | 13.1095 | 2006-09-27 | 18522 | 22.3
40 | 2006-10-08 | 2637.776 | 13.3524 | 2006-10-03 | 18796 | 23.3
41 | 2006-10-15 | 2621.631 | 9.7952 | 2006-10-12 | 18710 | 7.8
42 | 2006-10-22 | 2704.531 | 10.2095 | 2006-10-17 | 19000 | 12.2
43 | 2006-10-29 | 2780.566 | 5.0286 | 2006-10-25 | 19176 | 7.8
44 | 2006-11-05 | 2810.968 | 5.2762 | 2006-11-02 | 20205 | 4.4
45 | 2006-11-12 | 2770.862 | 7.5476 | 2006-11-07 | 20025 | 10.8
46 | 2006-11-19 | 2833.259 | 5.619 | 2006-11-13 | 20552 | 5.4
47 | 2006-11-26 | 2852.001 | 3.9476 | 2006-11-20 | 21129 | 1.5
48 | 2006-12-03 | 2903.458 | 6.3714 | 2006-12-01 | 20698 | 3.6
49 | 2006-12-10 | 3088.927 | -1.5333 | 2006-12-07 | 22656 | -5.5
50 | 2006-12-17 | 3355.996 | 6.6714 | 2006-12-11 | 21675 | 4.9
51 | 2006-12-23 | 2520.519 | 4.1619 | 2006-12-19 | 21351 | 4.4
52 | 2006-12-30 | 2682.677 | 0.95714 | 2006-12-29 | 19804 | -2.6
1 | 2007-01-07 | 2759.189 | 6.181 | 2007-01-03 | 20288 | 7.6
2 | 2007-01-14 | 3014.616 | 0.18095 | 2007-01-10 | 22026 | -3
3 | 2007-01-21 | 3180.515 | -5.5381 | 2007-01-16 | 22888 | -8.6
4 | 2007-01-28 | 3233.013 | -7.2095 | 2007-01-25 | 23328 | -13.1
5 | 2007-02-04 | 3255.384 | -8.5762 | 2007-01-29 | 22753 | -6.3
6 | 2007-02-11 | 3311.569 | -9.3238 | 2007-02-05 | 23640 | -10.5
7 | 2007-02-18 | 3308.032 | -10.5905 | 2007-02-13 | 23639 | -14
8 | 2007-02-25 | 3134.21 | -3.1619 | 2007-02-19 | 22345 | -5.3
9 | 2007-03-04 | 3045.905 | -1.4905 | 2007-03-01 | 21475 | -0.8
10 | 2007-03-11 | 3143.056 | -4.8762 | 2007-03-06 | 22772 | -12.5
11 | 2007-03-18 | 2924.953 | 2.9381 | 2007-03-16 | 20225 | -2.4
12 | 2007-03-25 | 2927.949 | 2.819 | 2007-03-20 | 20535 | -2.3
13 | 2007-04-01 | 2749.563 | 7.9619 | 2007-03-26 | 18807 | 19.2
14 | 2007-04-08 | 2814.703 | 0.95238 | 2007-04-05 | 19409 | -3
15 | 2007-04-15 | 2872.975 | 3.2143 | 2007-04-11 | 19680 | 4.1
16 | 2007-04-22 | 2680.61 | 11.6571 | 2007-04-16 | 19250 | 5.2
17 | 2007-04-29 | 2634.277 | 12.4524 | 2007-04-27 | 18211 | 16.8
18 | 2007-05-06 | 2572.418 | 11.681 | 2007-05-01 | 17888 | 9.7
19 | 2007-05-13 | 2603.987 | 16.381 | 2007-05-11 | 18478 | 20.5
20 | 2007-05-20 | 2605.33 | 14.1667 | 2007-05-15 | 19025 | 28.4
21 | 2007-05-27 | 2682.48 | 18.5143 | 2007-05-25 | 20875 | 27.4
22 | 2007-06-03 | 2917.633 | 21.7143 | 2007-05-31 | 21316 | 27.5
23 | 2007-06-10 | 2731.849 | 18.0048 | 2007-06-08 | 21794 | 31.2
24 | 2007-06-17 | 3052.251 | 24 | 2007-06-13 | 23299 | 29.7
25 | 2007-06-24 | 2875.267 | 21.2381 | 2007-06-18 | 22883 | 28.3
26 | 2007-07-01 | 3058.01 | 23.4048 | 2007-06-26 | 25628 | 34.2
27 | 2007-07-08 | 2763.077 | 22.1952 | 2007-07-06 | 20184 | 28.2
28 | 2007-07-15 | 2900.476 | 22.9286 | 2007-07-09 | 24173 | 33.7
29 | 2007-07-22 | 2832.297 | 22.1333 | 2007-07-18 | 21283 | 27.5
30 | 2007-07-29 | 3006.625 | 22.9667 | 2007-07-26 | 22020 | 27.5
31 | 2007-08-05 | 3270.026 | 26.6905 | 2007-08-02 | 25418 | 34.5
32 | 2007-08-12 | 3077.078 | 24.8095 | 2007-08-08 | 24012 | 31.7
33 | 2007-08-19 | 2869.053 | 21.7476 | 2007-08-16 | 22156 | 29.6
34 | 2007-08-26 | 2921.618 | 22.1381 | 2007-08-24 | 23409 | 32.8
35 | 2007-09-02 | 2932.442 | 22.4333 | 2007-08-29 | 24663 | 33.5
36 | 2007-09-09 | 2943.478 | 23.1 | 2007-09-07 | 23710 | 32.9
37 | 2007-09-16 | 2692.56 | 16.3429 | 2007-09-10 | 19512 | 23
38 | 2007-09-23 | 2761.954 | 19.4286 | 2007-09-21 | 20122 | 27.5
39 | 2007-09-30 | 2779.605 | 19.219 | 2007-09-25 | 22133 | 32.8
40 | 2007-10-07 | 2737.832 | 19.5238 | 2007-10-05 | 19206 | 24.3
41 | 2007-10-14 | 2644.804 | 14.4048 | 2007-10-09 | 18915 | 22.2
42 | 2007-10-21 | 2634.581 | 15.6286 | 2007-10-16 | 18570 | 12.8
43 | 2007-10-28 | 2652.985 | 11.981 | 2007-10-22 | 18634 | 24.8
44 | 2007-11-04 | 2684.867 | 9.0667 | 2007-11-01 | 18869 | 8.9
45 | 2007-11-11 | 2815.137 | 4.181 | 2007-11-07 | 20267 | 3.1
46 | 2007-11-18 | 2825.038 | 5.4 | 2007-11-12 | 20217 | 10.4
47 | 2007-11-25 | 2957.028 | 0.92857 | 2007-11-22 | 21494 | -3.4
48 | 2007-12-02 | 3497.435 | -0.97143 | 2007-11-28 | 21582 | -0.3
49 | 2007-12-09 | 3127.851 | -3.8143 | 2007-12-05 | 22385 | -7.9
50 | 2007-12-15 | 2735.781 | -2.8905 | 2007-12-11 | 22334 | 1.1
51 | 2007-12-23 | 2596.65 | 0.37143 | 2007-12-17 | 22585 | -3.4
52 | 2007-12-30 | 3120.152 | -0.18095 | 2007-12-27 | 19369 | 2.4
1 | 2008-01-06 | 2932.004 | -3.0143 | 2008-01-03 | 22307 | -7.7
2 | 2008-01-13 | 2878.326 | 5.8143 | 2008-01-10 | 20540 | 3.6
3 | 2008-01-20 | 3072.046 | -3.1762 | 2008-01-15 | 21303 | -0.8
4 | 2008-01-27 | 3182.096 | -5.7905 | 2008-01-21 | 22612 | -7.4
5 | 2008-02-03 | 3068.717 | -1.8905 | 2008-01-30 | 22270 | -8
6 | 2008-02-10 | 3024.216 | -1.8333 | 2008-02-06 | 21276 | -1.7
7 | 2008-02-17 | 3155.123 | -6.4333 | 2008-02-11 | 22834 | -9.3
8 | 2008-02-24 | 3046.81 | -4.7286 | 2008-02-20 | 21645 | -6.8
9 | 2008-03-02 | 3095.645 | -5.3 | 2008-02-27 | 21953 | -10.1
10 | 2008-03-09 | 2996.993 | -1.719 | 2008-03-04 | 20576 | -1.6
11 | 2008-03-16 | 2919.677 | -0.99524 | 2008-03-10 | 20185 | -0.7
12 | 2008-03-23 | 2852.89 | -0.5381 | 2008-03-18 | 19865 | 3
13 | 2008-03-30 | 2876.386 | 0.47143 | 2008-03-25 | 20067 | 2.6
14 | 2008-04-06 | 2775.843 | 5.519 | 2008-03-31 | 19196 | 5.3
15 | 2008-04-13 | 2704.624 | 8.2429 | 2008-04-11 | 19187 | 5.2
16 | 2008-04-20 | 2603.618 | 13.819 | 2008-04-14 | 18166 | 9.7
17 | 2008-04-27 | 2562.259 | 16.2286 | 2008-04-22 | 17791 | 20.9
18 | 2008-05-04 | 2615.088 | 8.1095 | 2008-04-28 | 18242 | 6.9
19 | 2008-05-11 | 2533.921 | 12.3333 | 2008-05-07 | 17750 | 15.6
20 | 2008-05-18 | 2538.939 | 13.2619 | 2008-05-14 | 17662 | 17
21 | 2008-05-25 | 2519.535 | 12.1619 | 2008-05-21 | 17701 | 9.4
22 | 2008-06-01 | 2585.264 | 16.3 | 2008-05-26 | 18453 | 26.9
23 | 2008-06-08 | 2844.201 | 22.0524 | 2008-06-06 | 21341 | 32.7
24 | 2008-06-15 | 2954.631 | 22.3952 | 2008-06-09 | 24001 | 33.1
25 | 2008-06-22 | 2684.657 | 17.0095 | 2008-06-16 | 19710 | 22.9
26 | 2008-06-29 | 2916.525 | 22.3238 | 2008-06-27 | 22302 | 27
27 | 2008-07-06 | 2712.781 | 20.6429 | 2008-07-02 | 20429 | 27.8
28 | 2008-07-13 | 3034.078 | 23.9381 | 2008-07-08 | 23224 | 30.7
29 | 2008-07-20 | 3049.678 | 23.9714 | 2008-07-17 | 23622 | 30
30 | 2008-07-27 | 2886.07 | 22.2333 | 2008-07-21 | 21078 | 24.8
31 | 2008-08-03 | 2954.73 | 23.0905 | 2008-07-31 | 21710 | 26.4
32 | 2008-08-10 | 2790.248 | 19.9571 | 2008-08-05 | 22376 | 26.1
33 | 2008-08-17 | 2764.063 | 20.4524 | 2008-08-14 | 19560 | 23.4
34 | 2008-08-24 | 2917.179 | 21.581 | 2008-08-18 | 22296 | 29.4
35 | 2008-08-31 | 2751.703 | 19.8095 | 2008-08-25 | 19101 | 20.4
36 | 2008-09-07 | 2871.959 | 21.281 | 2008-09-03 | 22900 | 30.3
37 | 2008-09-14 | 2702.472 | 18.6619 | 2008-09-14 | 18875 | 28
38 | 2008-09-21 | 2650.985 | 16.3952 | 2008-09-17 | 18274 | 23
39 | 2008-09-28 | 2666.45 | 17.1333 | 2008-09-25 | 18980 | 23.5
40 | 2008-10-05 | 2586.319 | 11.6524 | 2008-10-02 | 18029 | 12.6
41 | 2008-10-12 | 2584.606 | 13.0429 | 2008-10-08 | 18514 | 14.6
42 | 2008-10-19 | 2523.674 | 11.7952 | 2008-10-15 | 18128 | 15.9
43 | 2008-10-26 | 2640.237 | 7.7905 | 2008-10-21 | 18772 | 5.9
44 | 2008-11-02 | 2677.429 | 5.8095 | 2008-10-29 | 19171 | 3.3
45 | 2008-11-09 | 2591.332 | 10.4714 | 2008-11-03 | 18815 | 15.6
46 | 2008-11-16 | 2677.321 | 5.9429 | 2008-11-11 | 19640 | 5.6
47 | 2008-11-23 | 2922.821 | -3.3476 | 2008-11-19 | 20906 | -1.6
48 | 2008-11-30 | 2866.8 | 1.8238 | 2008-11-24 | 20878 | 3.8
49 | 2008-12-07 | 3373.616 | -1.7048 | 2008-12-04 | 20833 | 0.9
50 | 2008-12-14 | 3069.714 | -2.4048 | 2008-12-08 | 22230 | -3.7
51 | 2008-12-21 | 2183.151 | -5.1 | 2008-12-19 | 21903 | -8.9
52 | 2008-12-28 | 3488.556 | -0.44286 | 2008-12-22 | 21582 | -7.7
1 | 2009-01-04 | 2364.119 | -4.2571 | 2009-01-04 | 19721 | -2.1
2 | 2009-01-11 | 3024.795 | -5.7524 | 2009-01-08 | 21006 | -4.5
3 | 2009-01-18 | 3221.451 | -10.2429 | 2009-01-15 | 22804 | -11.3
4 | 2009-01-25 | 3120.821 | -8.0571 | 2009-01-20 | 22018 | -10.4
5 | 2009-02-01 | 3076.809 | -6.6524 | 2009-01-26 | 22003 | -8.9
6 | 2009-02-08 | 2983.238 | -5.0857 | 2009-02-04 | 21876 | -13.1
7 | 2009-02-15 | 2829.295 | 0.82857 | 2009-02-09 | 19841 | 2.6
8 | 2009-02-22 | 2852.638 | -3.1286 | 2009-02-19 | 20313 | -5.2
9 | 2009-03-01 | 2918.702 | -4.0571 | 2009-02-23 | 20882 | -6.1
10 | 2009-03-08 | 2865.83 | -0.40952 | 2009-03-02 | 21266 | -9.6
11 | 2009-03-15 | 2771.815 | 0.61429 | 2009-03-12 | 19558 | -3.4
12 | 2009-03-22 | 2607.907 | 4.3143 | 2009-03-19 | 18039 | 3.2
13 | 2009-03-29 | 2607.578 | 5.3143 | 2009-03-23 | 18345 | 1.6
14 | 2009-04-05 | 2566.444 | 6.6429 | 2009-03-30 | 18071 | 4.9
15 | 2009-04-12 | 2522.072 | 3.2905 | 2009-04-07 | 18329 | -0.5
16 | 2009-04-19 | 2427.499 | 10.4667 | 2009-04-13 | 16813 | 5.8
17 | 2009-04-26 | 2441.504 | 10.3286 | 2009-04-20 | 17644 | 5.6
18 | 2009-05-03 | 2369.714 | 13.219 | 2009-04-28 | 16573 | 10.4
19 | 2009-05-10 | 2381.014 | 14.1143 | 2009-05-07 | 16491 | 18.6
20 | 2009-05-17 | 2347.918 | 13.0524 | 2009-05-11 | 16538 | 13.2
21 | 2009-05-24 | 2324.301 | 17.9429 | 2009-05-21 | 17123 | 28.6
22 | 2009-05-31 | 2342.86 | 14.281 | 2009-05-25 | 17618 | 18.3
23 | 2009-06-07 | 2373.702 | 14.9619 | 2009-06-01 | 16474 | 15.3
24 | 2009-06-14 | 2393.083 | 16.7762 | 2009-06-11 | 16801 | 19.8
25 | 2009-06-21 | 2471.227 | 18.6476 | 2009-06-16 | 17669 | 23.4
26 | 2009-06-28 | 2827.027 | 23.3 | 2009-06-24 | 22403 | 30.7
27 | 2009-07-05 | 2429.956 | 19.0667 | 2009-06-29 | 18263 | 22.6
28 | 2009-07-12 | 2535.934 | 20.3619 | 2009-07-10 | 18804 | 25.9
29 | 2009-07-19 | 2495.28 | 19.519 | 2009-07-16 | 19044 | 27
30 | 2009-07-26 | 2542.821 | 20.1619 | 2009-07-20 | 18226 | 23.8
31 | 2009-08-02 | 2628.104 | 22.6857 | 2009-07-28 | 19678 | 27.4
32 | 2009-08-09 | 2560.875 | 20.9905 | 2009-08-04 | 20188 | 26.4
33 | 2009-08-16 | 2991.132 | 24.2952 | 2009-08-10 | 22022 | 29.9
34 | 2009-08-23 | 2953.422 | 23.9762 | 2009-08-17 | 24005 | 31.2
35 | 2009-08-30 | 2573.979 | 18.8048 | 2009-08-25 | 19558 | 25.5
36 | 2009-09-06 | 2550 | 19.1238 | 2009-09-03 | 18676 | 23.7
37 | 2009-09-13 | 2569.99 | 20.0429 | 2009-09-08 | 19551 | 25.1
38 | 2009-09-20 | 2494.128 | 16.5238 | 2009-09-14 | 18364 | 25
39 | 2009-09-27 | 2551.282 | 18.4286 | 2009-09-23 | 19258 | 27.2
40 | 2009-10-04 | 2445.95 | 11.2571 | 2009-10-01 | 17454 | 11.4
41 | 2009-10-11 | 2468.75 | 10.6286 | 2009-10-07 | 17436 | 12.4
42 | 2009-10-18 | 2540.442 | 4.7 | 2009-10-15 | 18320 | 4.1
43 | 2009-10-25 | 2553.259 | 10.3524 | 2009-10-22 | 18089 | 15.7
44 | 2009-11-01 | 2549.81 | 10.719 | 2009-10-26 | 18029 | 11.7
45 | 2009-11-08 | 2588.982 | 6.7429 | 2009-11-04 | 18972 | 5.9
46 | 2009-11-15 | 2553.776 | 8.6048 | 2009-11-09 | 18511 | 18.6
47 | 2009-11-22 | 2605.388 | 6.7571 | 2009-11-19 | 19067 | 9.6
48 | 2009-11-29 | 2640.481 | 6.1714 | 2009-11-24 | 19159 | 7.6
49 | 2009-12-06 | 2733.895 | 2.6714 | 2009-11-30 | 19685 | 3.7
50 | 2009-12-13 | 3384.411 | -1.4952 | 2009-12-10 | 21496 | -2.7
51 | 2009-12-20 | 3363.008 | -3.1857 | 2009-12-16 | 21747 | -3.8
52 | 2009-12-27 | 1989.13 | -2.0048 | 2009-12-22 | 21296 | -5.7
53 | 2010-01-03 | 2796.407 | -6.0238 | 2010-01-03 | 20770 | -8.6
1 | 2010-01-10 | 3076.419 | -7.5952 | 2010-01-04 | 21982 | -7.3
2 | 2010-01-17 | 2937.308 | -1.3429 | 2010-01-11 | 21483 | -4.7
3 | 2010-01-24 | 2897.403 | -0.53333 | 2010-01-20 | 20700 | -2.5
4 | 2010-01-31 | 3024.325 | -5.6381 | 2010-01-28 | 21864 | -7
5 | 2010-02-07 | 3008.541 | -4.8048 | 2010-02-01 | 21246 | -3.6
6 | 2010-02-14 | 2984.921 | -4.1476 | 2010-02-09 | 21018 | -3.9
7 | 2010-02-21 | 2846.377 | -0.30476 | 2010-02-17 | 20254 | 0.4
8 | 2010-02-28 | 2886.967 | -1.319 | 2010-02-25 | 20690 | -5.8
9 | 2010-03-07 | 2737.389 | 1.7714 | 2010-03-01 | 19282 | 2
10 | 2010-03-14 | 2623.207 | 6.7714 | 2010-03-08 | 18194 | 13.6
11 | 2010-03-21 | 2530.337 | 9.1429 | 2010-03-15 | 17362 | 12.1
12 | 2010-03-28 | 2652.551 | 3.4762 | 2010-03-25 | 18335 | 8.6
13 | 2010-04-04 | 2403.602 | 12.3048 | 2010-03-29 | 17597 | 8.4
14 | 2010-04-11 | 2494.844 | 10.6048 | 2010-04-09 | 17422 | 3.6
15 | 2010-04-18 | 2465.674 | 10.8905 | 2010-04-12 | 16709 | 13.1
16 | 2010-04-25 | 2447.052 | 11.5762 | 2010-04-21 | 16662 | 17.4
17 | 2010-05-02 | 2436.561 | 14.5476 | 2010-04-27 | 16607 | 9.4
18 | 2010-05-09 | 2477.159 | 13.0619 | 2010-05-05 | 17328 | 26.9
19 | 2010-05-16 | 2452.8 | 10.8143 | 2010-05-13 | 17005 | 11.3
20 | 2010-05-23 | 2470.298 | 18.5524 | 2010-05-20 | 17924 | 28.3
21 | 2010-05-30 | 2863.471 | 24.0429 | 2010-05-26 | 22806 | 31.4
22 | 2010-06-06 | 2736.188 | 20.3905 | 2010-05-31 | 20859 | 27.6
23 | 2010-06-13 | 2517.432 | 17.1 | 2010-06-11 | 17458 | 22.7
24 | 2010-06-20 | 2668.044 | 21.9286 | 2010-06-18 | 19093 | 25
25 | 2010-06-27 | 2793.61 | 22.2571 | 2010-06-23 | 21498 | 28.3
26 | 2010-07-04 | 2545.158 | 21.0905 | 2010-06-28 | 21240 | 28.9
27 | 2010-07-11 | 3196.825 | 26.9619 | 2010-07-08 | 24507 | 33.3
28 | 2010-07-18 | 3102.44 | 25.1238 | 2010-07-15 | 23587 | 28.9
29 | 2010-07-25 | 3004.401 | 24.5714 | 2010-07-21 | 22164 | 30.1
30 | 2010-08-01 | 2842.254 | 22.3952 | 2010-07-27 | 22449 | 28.3
31 | 2010-08-08 | 2931.57 | 24.3286 | 2010-08-04 | 23582 | 31.5
32 | 2010-08-15 | 3119.634 | 25.1429 | 2010-08-10 | 23426 | 29.4
33 | 2010-08-22 | 2797.864 | 22.019 | 2010-08-16 | 20994 | 27
34 | 2010-08-29 | 2729.423 | 21.1619 | 2010-08-29 | 20028 | 30.1
35 | 2010-09-05 | 3027.002 | 23.8286 | 2010-08-31 | 24566 | 32.9
36 | 2010-09-12 | 2502.796 | 18.1857 | 2010-09-07 | 19337 | 29.6
37 | 2010-09-19 | 2489.772 | 15.7571 | 2010-09-13 | 17472 | 23.6
38 | 2010-09-26 | 2539.512 | 17.6952 | 2010-09-24 | 18721 | 30.5
39 | 2010-10-03 | 2473.737 | 13.3762 | 2010-09-27 | 17513 | 15.7
40 | 2010-10-10 | 2460.436 | 14.119 | 2010-10-04 | 17452 | 12
41 | 2010-10-17 | 2431.16 | 10.9381 | 2010-10-13 | 17484 | 14.8
42 | 2010-10-24 | 2522.859 | 9.1714 | 2010-10-21 | 17759 | 7.7
43 | 2010-10-31 | 2506.893 | 11.4571 | 2010-10-26 | 17556 | 20.5
44 | 2010-11-07 | 2607.736 | 4.3 | 2010-11-05 | 18079 | 3.2
45 | 2010-11-14 | 2579.985 | 6.2429 | 2010-11-08 | 18433 | 10
46 | 2010-11-21 | 2623.409 | 5.5333 | 2010-11-18 | 18798 | 6.2
47 | 2010-11-28 | 2720.021 | 4.019 | 2010-11-25 | 19835 | 4.2
48 | 2010-12-05 | 2793.795 | 1.2 | 2010-12-02 | 20038 | 0.8
49 | 2010-12-12 | 2920.398 | -2.4 | 2010-12-08 | 21364 | -3.6
50 | 2010-12-19 | 3433.803 | -6.3476 | 2010-12-13 | 22099 | -11.6
51 | 2010-12-26 | 2822.777 | -4.6714 | 2010-12-21 | 20800 | -3.7
52 | 2011-01-02 | 2228.135 | 0.57143 | 2010-12-28 | 19037 | -0.7
1 | 2011-01-09 | 2924.562 | -4.4905 | 2011-01-06 | 20762 | -3.2
2 | 2011-01-16 | 3035.07 | -7.1476 | 2011-01-12 | 21182 | -7.7
3 | 2011-01-23 | 3110.626 | -9.0762 | 2011-01-17 | 21671 | -7.1
4 | 2011-01-30 | 3041.869 | -4.9571 | 2011-01-24 | 22531 | -9
5 | 2011-02-06 | 3045.758 | -7.2619 | 2011-01-31 | 21756 | -10.7
6 | 2011-02-13 | 2994.743 | -6.8476 | 2011-02-08 | 21510 | -9.9
7 | 2011-02-20 | 2838.845 | -0.033333 | 2011-02-15 | 20475 | -4.9
8 | 2011-02-27 | 2903.379 | -3.9714 | 2011-02-22 | 20461 | -3.9
9 | 2011-03-06 | 2872.379 | -1.1667 | 2011-03-02 | 20490 | -4.3
10 | 2011-03-13 | 2819.458 | 0.45238 | 2011-03-07 | 19974 | -2.1
11 | 2011-03-20 | 2658.262 | 4.1524 | 2011-03-14 | 18508 | 2.7
12 | 2011-03-27 | 2775.701 | -1.9524 | 2011-03-23 | 19208 | -4.5
13 | 2011-04-03 | 2648.138 | 3.5 | 2011-03-28 | 18693 | 2.2
14 | 2011-04-10 | 2564.081 | 7.4286 | 2011-04-05 | 17726 | 5.2
15 | 2011-04-17 | 2519.186 | 7.8381 | 2011-04-13 | 16945 | 11.2
16 | 2011-04-24 | 2501.655 | 6.5 | 2011-04-18 | 17763 | 3.7
17 | 2011-05-01 | 2420.774 | 10.4619 | 2011-04-26 | 16703 | 11.6
18 | 2011-05-08 | 2412.314 | 11.2286 | 2011-05-03 | 17036 | 7
19 | 2011-05-15 | 2392.347 | 14.6667 | 2011-05-13 | 16340 | 25.8
20 | 2011-05-22 | 2423.044 | 15.981 | 2011-05-16 | 16671 | 10.2
21 | 2011-05-29 | 2375.854 | 16.781 | 2011-05-26 | 16587 | 20.2
22 | 2011-06-05 | 2563.83 | 20.5857 | 2011-05-31 | 20689 | 29.3
23 | 2011-06-12 | 2660.324 | 21.2 | 2011-06-08 | 22533 | 33.3
24 | 2011-06-19 | 2568.452 | 19.8048 | 2011-06-16 | 18715 | 24.7
25 | 2011-06-26 | 2647.068 | 20.9238 | 2011-06-21 | 19867 | 25.6
26 | 2011-07-03 | 2627.884 | 22.2429 | 2011-06-28 | 19718 | 26.3
27 | 2011-07-10 | 2869.302 | 24.2762 | 2011-07-06 | 21238 | 29.2
28 | 2011-07-17 | 3001.318 | 25.819 | 2011-07-12 | 22605 | 31.7
29 | 2011-07-24 | 3340.465 | 28.8381 | 2011-07-21 | 25285 | 37.5
30 | 2011-07-31 | 2944.723 | 25.1714 | 2011-07-29 | 21553 | 31.4
31 | 2011-08-07 | 2980.877 | 24.7476 | 2011-08-02 | 21933 | 31.3
32 | 2011-08-14 | 2786.159 | 22.2286 | 2011-08-08 | 21737 | 26.2
33 | 2011-08-21 | 2857.856 | 23.8857 | 2011-08-18 | 21317 | 29.9
34 | 2011-08-28 | 2679.356 | 21.9095 | 2011-08-24 | 19849 | 27.9
35 | 2011-09-04 | 2834.56 | 23.3381 | 2011-09-02 | 21374 | 28.3
36 | 2011-09-11 | 2513.313 | 18.5333 | 2011-09-09 | 18252 | 25.2
37 | 2011-09-18 | 2549.873 | 16.4429 | 2011-09-12 | 19983 | 28.5
38 | 2011-09-25 | 2534.472 | 18.0286 | 2011-09-21 | 17934 | 21.7
39 | 2011-10-02 | 2528.475 | 15.5333 | 2011-09-26 | 18464 | 24.1
40 | 2011-10-09 | 2468.478 | 15.981 | 2011-10-03 | 17372 | 14
41 | 2011-10-16 | 2452.727 | 15.4476 | 2011-10-11 | 17674 | 22.7
42 | 2011-10-23 | 2487.87 | 9.7476 | 2011-10-19 | 17644 | 11.7
43 | 2011-10-30 | 2552.612 | 6.6667 | 2011-10-27 | 18178 | 4.7
44 | 2011-11-06 | 2534.665 | 8.0762 | 2011-11-01 | 17812 | 12.7
45 | 2011-11-13 | 2539.151 | 9.9667 | 2011-11-11 | 18180 | 5.5
46 | 2011-11-20 | 2565.766 | 7.581 | 2011-11-17 | 18729 | 4.3
47 | 2011-11-27 | 2623.685 | 6.381 | 2011-11-22 | 19370 | 1.3
48 | 2011-12-04 | 2700.273 | 4.1476 | 2011-11-29 | 19553 | 5.6
49 | 2011-12-11 | 2791.724 | 0.80476 | 2011-12-07 | 19881 | 1.2
50 | 2011-12-18 | 2774.329 | 2.681 | 2011-12-12 | 19666 | 6.5
51 | 2011-12-25 | 3136.682 | 0.8619 | 2011-12-20 | 20144 | -1.3
52 | 2012-01-01 | 2196.658 | -0.25238 | 2011-12-29 | 19407 | -2.8
1 | 2012-01-08 | 2822.035 | -1.7476 | 2012-01-03 | 21615 | -14.3
2 | 2012-01-15 | 2860.282 | -1.8952 | 2012-01-15 | 20042 | -7.5
3 | 2012-01-22 | 2975.382 | -2.3333 | 2012-01-18 | 20836 | -4.5
4 | 2012-01-29 | 2851.318 | 0.95238 | 2012-01-25 | 20096 | -0.9
5 | 2012-02-05 | 2790.934 | 1.7286 | 2012-01-30 | 20173 | -1.4
6 | 2012-02-12 | 2836.756 | -1.7524 | 2012-02-07 | 19731 | -0.3
7 | 2012-02-19 | 2774.69 | 0.64286 | 2012-02-14 | 19527 | 1
8 | 2012-02-26 | 2751.527 | 0.98095 | 2012-02-21 | 19456 | 3
9 | 2012-03-04 | 2791.485 | 1.4048 | 2012-02-29 | 19773 | 1.3
10 | 2012-03-11 | 2740.816 | 3.3857 | 2012-03-05 | 20341 | -2.8
11 | 2012-03-18 | 2477.837 | 11.5429 | 2012-03-12 | 17582 | 11.8
12 | 2012-03-25 | 2440.227 | 16.0571 | 2012-03-22 | 17270 | 23.7
13 | 2012-04-01 | 2573.313 | 3.9857 | 2012-03-26 | 17978 | 2.6
14 | 2012-04-08 | 2430.949 | 7.7857 | 2012-04-03 | 17337 | 10.7
15 | 2012-04-15 | 2487.758 | 9.9 | 2012-04-10 | 17665 | 8
16 | 2012-04-22 | 2459.347 | 11.1857 | 2012-04-17 | 16991 | 10.4
17 | 2012-04-29 | 2503.789 | 6.6048 | 2012-04-23 | 17691 | 4.1
18 | 2012-05-06 | 2429.049 | 12.8714 | 2012-04-30 | 17429 | 9.4
19 | 2012-05-13 | 2391.626 | 15.7048 | 2012-05-07 | 16606 | 15.3
20 | 2012-05-20 | 2425.019 | 17.3905 | 2012-05-15 | 16943 | 23.7
21 | 2012-05-27 | 2612.829 | 22.3619 | 2012-05-25 | 19995 | 30.7
22 | 2012-06-03 | 2571.502 | 18.3714 | 2012-05-28 | 20922 | 28.6
23 | 2012-06-10 | 2556.36 | 19.8429 | 2012-06-10 | 19088 | 29
24 | 2012-06-17 | 2718.756 | 21.6 | 2012-06-11 | 21312 | 27.7
25 | 2012-06-24 | 3033.376 | 25.3905 | 2012-06-20 | 23783 | 34.2
26 | 2012-07-01 | 2828.257 | 24.1095 | 2012-06-29 | 21988 | 32.4
27 | 2012-07-08 | 3062.451 | 26.4571 | 2012-07-04 | 23801 | 35.9
28 | 2012-07-15 | 3032.484 | 25.3476 | 2012-07-13 | 22707 | 32.3
29 | 2012-07-22 | 3051.299 | 25.5857 | 2012-07-17 | 24470 | 36.2
30 | 2012-07-29 | 2979.547 | 24.8476 | 2012-07-23 | 23530 | 34.1
31 | 2012-08-05 | 3109.533 | 25.8952 | 2012-08-03 | 23013 | 30.1
32 | 2012-08-12 | 2765.755 | 22.2143 | 2012-08-08 | 22190 | 28.2
33 | 2012-08-19 | 2704.955 | 21.1524 | 2012-08-16 | 20235 | 26.8
34 | 2012-08-26 | 2825.816 | 23.1095 | 2012-08-24 | 21121 | 28.7
35 | 2012-09-02 | 2825.634 | 23.1286 | 2012-08-31 | 21766 | 32.6
36 | 2012-09-09 | 2779.356 | 21.1286 | 2012-09-06 | 21168 | 27.1
37 | 2012-09-16 | 2571.289 | 18.7333 | 2012-09-13 | 19869 | 28.7
38 | 2012-09-23 | 2464.238 | 14.9238 | 2012-09-17 | 17723 | 23.2
39 | 2012-09-30 | 2445.948 | 13.9 | 2012-09-25 | 17165 | 22
40 | 2012-10-07 | 2466.144 | 14.5524 | 2012-10-03 | 17669 | 18.5
41 | 2012-10-14 | 2487.466 | 9.6857 | 2012-10-11 | 17849 | 12.8
42 | 2012-10-21 | 2473.934 | 11.2143 | 2012-10-15 | 17828 | 11
43 | 2012-10-28 | 2522.418 | 10.6476 | 2012-10-24 | 17874 | 11.4
44 | 2012-11-04 | 2619.849 | 5.0095 | 2012-10-29 | 18597 | 4.3
45 | 2012-11-11 | 2665.5 | 4.9714 | 2012-11-06 | 19302 | 2.7
46 | 2012-11-18 | 2623.09 | 5.5857 | 2012-11-13 | 19161 | 3
47 | 2012-11-25 | 2632.78 | 5.5667 | 2012-11-19 | 18772 | 8.4
48 | 2012-12-02 | 2803.389 | 1.6 | 2012-11-26 | 20012 | 2.5
49 | 2012-12-09 | 2345.457 | 3.6524 | 2012-12-05 | 20217 | 1.5
50 | 2012-12-16 | 3198.076 | 2.019 | 2012-12-11 | 20413 | -1
51 | 2012-12-23 | 3164.706 | 2.6952 | 2012-12-20 | 19846 | 2.6
52 | 2012-12-29 | 2659.264 | -3.1286 | 2012-12-27 | 19078 | -3.1
1 | 2013-01-06 | 2409.875 | -2.2571 | 2013-01-02 | 20601 | -2.8
2 | 2013-01-13 | 2742.03 | 4.7095 | 2013-01-07 | 20172 | 0.3
3 | 2013-01-20 | 2868.518 | -2.2524 | 2013-01-17 | 20779 | -7.3
4 | 2013-01-27 | 3164.884 | -9.9381 | 2013-01-24 | 22423 | -11.6
5 | 2013-02-03 | 2948.027 | -1.8524 | 2013-01-31 | 20602 | -2.6
6 | 2013-02-10 | 3044.013 | -6.3143 | 2013-02-04 | 21493 | -5.8
7 | 2013-02-17 | 2878.093 | -2.5857 | 2013-02-12 | 20053 | 0.6
8 | 2013-02-24 | 2887.399 | -2.9762 | 2013-02-20 | 20805 | -5.5
9 | 2013-03-03 | 2805.264 | -1.3714 | 2013-02-27 | 19831 | 1.5
10 | 2013-03-10 | 2712.272 | 1.7524 | 2013-03-04 | 19863 | -1.8
11 | 2013-03-17 | 2714.361 | 0 | 2013-03-14 | 19065 | 0.1
12 | 2013-03-24 | 2752.129 | -1.081 | 2013-03-20 | 19269 | -1.3
13 | 2013-03-31 | 2517.294 | 5.8 | 2013-03-27 | 18211 | 6.9
14 | 2013-04-07 | 2632.151 | 2.6 | 2013-04-02 | 18820 | 2.5
15 | 2013-04-14 | 2618.614 | 5.0667 | 2013-04-11 | 18375 | 0.1
16 | 2013-04-21 | 2511.671 | 9.0619 | 2013-04-15 | 17215 | 12.6
17 | 2013-04-28 | 2451.728 | 9.219 | 2013-04-24 | 17430 | 12.3
18 | 2013-05-05 | 2371.425 | 17.0143 | 2013-04-29 | 16558 | 13.1
19 | 2013-05-12 | 2398.106 | 15.1762 | 2013-05-08 | 16570 | 21.8
20 | 2013-05-19 | 2365.876 | 14.0905 | 2013-05-13 | 16480 | 10.8
21 | 2013-05-26 | 2410.307 | 15.9429 | 2013-05-21 | 18107 | 24.6
22 | 2013-06-02 | 2602.253 | 21.0667 | 2013-05-31 | 20372 | 29.9
23 | 2013-06-09 | 2403.479 | 15.5667 | 2013-06-06 | 16509 | 14.8
24 | 2013-06-16 | 2505.328 | 19.4238 | 2013-06-12 | 17635 | 22.4
25 | 2013-06-23 | 2631.536 | 20.8857 | 2013-06-23 | 20041 | 31.9
26 | 2013-06-30 | 2860.767 | 23.5286 | 2013-06-24 | 22541 | 31.6
27 | 2013-07-07 | 2765.496 | 23.0667 | 2013-07-04 | 21251 | 27.8
28 | 2013-07-14 | 2882.921 | 23.6619 | 2013-07-10 | 21645 | 30.5
29 | 2013-07-21 | 3288.153 | 27.4 | 2013-07-17 | 24708 | 34.3
30 | 2013-07-28 | 2622.999 | 20.181 | 2013-07-23 | 20105 | 27.4
31 | 2013-08-04 | 2542.321 | 20.2667 | 2013-08-01 | 18382 | 25.7
32 | 2013-08-11 | 2601.064 | 21.5238 | 2013-08-08 | 20078 | 26.5
33 | 2013-08-18 | 2565.818 | 19.9714 | 2013-08-12 | 18022 | 23
34 | 2013-08-25 | 2844.42 | 23.7048 | 2013-08-21 | 22146 | 31.4
35 | 2013-09-01 | 2990.963 | 24.1476 | 2013-08-29 | 22809 | 28.2
36 | 2013-09-08 | 2490.095 | 18.4952 | 2013-09-04 | 18164 | 25.3
37 | 2013-09-15 | 2667.838 | 18.9095 | 2013-09-10 | 22545 | 33.9
38 | 2013-09-22 | 2468.567 | 15.1048 | 2013-09-20 | 17696 | 23.5
39 | 2013-09-29 | 2439.383 | 15.6 | 2013-09-26 | 17321 | 20.5
40 | 2013-10-06 | 2523.773 | 17.9048 | 2013-10-02 | 17992 | 24.6
41 | 2013-10-13 | 2431.049 | 13.5048 | 2013-10-09 | 17386 | 17.6
42 | 2013-10-20 | 2428.382 | 12.4619 | 2013-10-15 | 17497 | 17.1
43 | 2013-10-27 | 2568.283 | 6.6905 | 2013-10-24 | 18084 | 8.3
44 | 2013-11-03 | 2575.664 | 4.3048 | 2013-10-29 | 18356 | 6.6
45 | 2013-11-10 | 2613.409 | 6.2381 | 2013-11-04 | 18791 | 5.2
46 | 2013-11-17 | 2658.795 | 5.3476 | 2013-11-12 | 19763 | 0.5
47 | 2013-11-24 | 2766.996 | 1.0286 | 2013-11-24 | 19790 | -5.2
48 | 2013-11-30 | 2510.417 | -1.4143 | 2013-11-28 | 20469 | -3.3
49 | 2013-12-08 | 2843.653 | 0.71905 | 2013-12-02 | 20029 | 2.5
50 | 2013-12-15 | 3088.18 | -7.5905 | 2013-12-12 | 21727 | -7.8
51 | 2013-12-22 | 2533.378 | -3.0143 | 2013-12-16 | 21867 | -8.3
52 | 2013-12-29 | 3428.571 | -3.4048 | 2013-12-24 | 18960 | -9.9
1 | 2014-01-05 | 2980.559 | -9.9143 | 2014-01-02 | 22342 | -17.9
2 | 2014-01-12 | 3047.657 | -6.2667 | 2014-01-07 | 22725 | -17.4
3 | 2014-01-19 | 2893.573 | -1.0524 | 2014-01-15 | 20465 | -1.2
4 | 2014-01-26 | 3255.467 | -13.2571 | 2014-01-22 | 22717 | -14.4
5 | 2014-02-02 | 3111.181 | -7.5 | 2014-01-28 | 22377 | -12.8
6 | 2014-02-09 | 3095.934 | -9.9333 | 2014-02-05 | 21296 | -6.8
7 | 2014-02-16 | 3077.107 | -8.5905 | 2014-02-11 | 21772 | -10.2
8 | 2014-02-23 | 2869.348 | -1.419 | 2014-02-18 | 20357 | -1.6
9 | 2014-03-02 | 3075.27 | -10.3714 | 2014-02-27 | 21728 | -12.2
10 | 2014-03-09 | 2981.282 | -7.2286 | 2014-03-03 | 21642 | -12.1
11 | 2014-03-16 | 2821.492 | -1.5952 | 2014-03-13 | 20245 | -8
12 | 2014-03-23 | 2834.923 | -1.3905 | 2014-03-17 | 20120 | -4.5
13 | 2014-03-30 | 2824.759 | -1.1238 | 2014-03-26 | 20046 | -5.1
14 | 2014-04-06 | 2621.434 | 4.2762 | 2014-04-03 | 18027 | 3.4
15 | 2014-04-13 | 2520.922 | 10.0714 | 2014-04-07 | 18102 | 9.1
16 | 2014-04-20 | 2506.027 | 6.0381 | 2014-04-15 | 18552 | -0.9
17 | 2014-04-27 | 2474.661 | 8.7905 | 2014-04-22 | 17253 | 11.3
18 | 2014-05-04 | 2476.605 | 9.119 | 2014-04-30 | 17633 | 6.6
19 | 2014-05-11 | 2372.395 | 14.1714 | 2014-05-07 | 16515 | 13
20 | 2014-05-18 | 2395.651 | 13.8714 | 2014-05-13 | 16859 | 20.6
21 | 2014-05-25 | 2331.344 | 17.0905 | 2014-05-21 | 16532 | 19.6
22 | 2014-06-01 | 2471.538 | 19.6524 | 2014-05-27 | 18762 | 29.4
23 | 2014-06-08 | 2515.024 | 19.8333 | 2014-06-02 | 18848 | 29.1
24 | 2014-06-15 | 2543.584 | 19.8952 | 2014-06-12 | 18594 | 26.2
25 | 2014-06-22 | 2599.973 | 21.0667 | 2014-06-17 | 19826 | 31.2
26 | 2014-06-29 | 2819.858 | 23.1095 | 2014-06-24 | 19847 | 27.9
27 | 2014-07-06 | 2714.132 | 23.3429 | 2014-06-30 | 20852 | 30.3
28 | 2014-07-13 | 2669.169 | 22.2 | 2014-07-07 | 20006 | 28.4
29 | 2014-07-20 | 2552.327 | 19.6857 | 2014-07-14 | 18418 | 22.4
30 | 2014-07-27 | 2741.847 | 22.7857 | 2014-07-22 | 21250 | 29.8
31 | 2014-08-03 | 2568.17 | 20.5286 | 2014-08-01 | 18453 | 27
32 | 2014-08-10 | 2650.137 | 21.681 | 2014-08-06 | 18833 | 24.7
33 | 2014-08-17 | 2568.169 | 19.481 | 2014-08-11 | 19849 | 27.5
34 | 2014-08-24 | 2668.166 | 20.7238 | 2014-08-21 | 19519 | 25.7
35 | 2014-08-31 | 2737.966 | 22.9857 | 2014-08-26 | 21457 | 31.3
36 | 2014-09-07 | 2734.093 | 22.9905 | 2014-09-05 | 21341 | 31.4
37 | 2014-09-14 | 2509.656 | 15.7048 | 2014-09-10 | 18939 | 22.7
38 | 2014-09-21 | 2416.075 | 15.4762 | 2014-09-15 | 17138 | 17.8
39 | 2014-09-28 | 2449.553 | 17.6095 | 2014-09-25 | 17439 | 20.9
40 | 2014-10-05 | 2455.573 | 15.6 | 2014-09-29 | 18206 | 23.9
41 | 2014-10-12 | 2413.467 | 10.8429 | 2014-10-09 | 17405 | 13.9
42 | 2014-10-19 | 2395.899 | 13.6714 | 2014-10-14 | 17562 | 22.1
43 | 2014-10-26 | 2452.995 | 10.5667 | 2014-10-20 | 17679 | 11.8
44 | 2014-11-02 | 2516.429 | 6.4143 | 2014-10-30 | 17777 | 9.1
45 | 2014-11-09 | 2562.845 | 6.1619 | 2014-11-07 | 18215 | 9
46 | 2014-11-16 | 2648.011 | 4.2238 | 2014-11-13 | 19129 | 16.5
47 | 2014-11-23 | 2821.612 | -3.4048 | 2014-11-19 | 20091 | 0.8
48 | 2014-11-30 | 2775.392 | 2.7714 | 2014-11-28 | 19823 | 1.3
49 | 2014-12-07 | 3283.115 | -0.72381 | 2014-12-02 | 20813 | -1.2
50 | 2014-12-14 | 2859.799 | 0.39048 | 2014-12-11 | 20252 | -3.9
51 | 2014-12-21 | 2411.784 | 0.33333 | 2014-12-18 | 20068 | -0.7
52 | 2014-12-28 | 2822.78 | 4.4286 | 2014-12-22 | 19495 | 1.6
1 | 2015-01-04 | 2301.463 | -3.0095 | 2014-12-30 | 19294 | -3.4
2 | 2015-01-11 | 3057.961 | -10.5857 | 2015-01-07 | 21689 | -15.7
3 | 2015-01-18 | 3017.139 | -6.4905 | 2015-01-13 | 21134 | -11.6
4 | 2015-01-25 | 2937.356 | -5.0667 | 2015-01-20 | 20704 | -6.7
5 | 2015-02-01 | 3027.87 | -7.981 | 2015-01-27 | 20823 | -6.8
6 | 2015-02-08 | 3041.641 | -8.3238 | 2015-02-02 | 20807 | -11.3
7 | 2015-02-15 | 3084.421 | -11.6714 | 2015-02-12 | 21014 | -14.5
8 | 2015-02-22 | 3132.266 | -13.0905 | 2015-02-19 | 21474 | -15.8
9 | 2015-03-01 | 3090.03 | -12.0143 | 2015-02-23 | 21440 | -15.5
10 | 2015-03-08 | 2913.928 | -5.5048 | 2015-03-05 | 20934 | -9.6
11 | 2015-03-15 | 2638.4 | 3.0333 | 2015-03-09 | 18606 | 5.4
12 | 2015-03-22 | 2632.494 | 1.0476 | 2015-03-18 | 18457 | 2
13 | 2015-03-29 | 2715.982 | -1.5143 | 2015-03-23 | 19292 | -2.9
14 | 2015-04-05 | 2505.908 | 4.6714 | 2015-03-30 | 18059 | 6.9
15 | 2015-04-12 | 2545.891 | 6.8667 | 2015-04-08 | 18322 | 2.4
16 | 2015-04-19 | 2332.075 | 12.8905 | 2015-04-16 | 16601 | 14.9
17 | 2015-04-26 | 2442.08 | 6.4 | 2015-04-23 | 17598 | 2.8
18 | 2015-05-03 | 2313.268 | 14.7286 | 2015-04-27 | 16471 | 12.1
19 | 2015-05-10 | 2410.036 | 18.5333 | 2015-05-08 | 16839 | 24.1
20 | 2015-05-17 | 2348.964 | 15.181 | 2015-05-11 | 17104 | 19.2
21 | 2015-05-24 | 2299.844 | 16.1762 | 2015-05-18 | 16442 | 28.2
22 | 2015-05-31 | 2569.175 | 21.2905 | 2015-05-26 | 19339 | 28.8
23 | 2015-06-07 | 2363.66 | 15.8952 | 2015-06-05 | 17230 | 24.3
24 | 2015-06-14 | 2485.383 | 19.8905 | 2015-06-10 | 18133 | 27.6
25 | 2015-06-21 | 2552.342 | 20.7619 | 2015-06-15 | 18899 | 24.1
26 | 2015-06-28 | 2526.585 | 19.4143 | 2015-06-22 | 19328 | 25.5
27 | 2015-07-05 | 2378.004 | 19.6 | 2015-07-05 | 17258 | 25.6
28 | 2015-07-12 | 2668.985 | 22.2762 | 2015-07-06 | 19906 | 26.6
29 | 2015-07-19 | 2745.486 | 22.7905 | 2015-07-13 | 20698 | 28.1
30 | 2015-07-26 | 2782.495 | 23.7429 | 2015-07-20 | 20434 | 28
31 | 2015-08-02 | 2964.323 | 25.6143 | 2015-07-28 | 22508 | 32.5
32 | 2015-08-09 | 2540.375 | 21.081 | 2015-08-04 | 18181 | 25.8
33 | 2015-08-16 | 2730.578 | 22.8476 | 2015-08-16 | 20595 | 30.4
34 | 2015-08-23 | 2843.997 | 23.1333 | 2015-08-17 | 22396 | 32.1
35 | 2015-08-30 | 2541.425 | 19.3762 | 2015-08-30 | 18040 | 25.4
36 | 2015-09-06 | 3001.099 | 25.8 | 2015-09-02 | 21922 | 32.6
37 | 2015-09-13 | 2697.254 | 20.5619 | 2015-09-08 | 21842 | 28.7
38 | 2015-09-20 | 2580.759 | 20.8571 | 2015-09-17 | 20119 | 27.2
39 | 2015-09-27 | 2446.319 | 17.6476 | 2015-09-24 | 17875 | 22.6
40 | 2015-10-04 | 2421.31 | 13.7714 | 2015-09-28 | 18125 | 21.7
41 | 2015-10-11 | 2401.672 | 14.2333 | 2015-10-05 | 17363 | 14.2
42 | 2015-10-18 | 2381.522 | 9.8905 | 2015-10-15 | 16920 | 17.6
43 | 2015-10-25 | 2450.749 | 11.0286 | 2015-10-21 | 17269 | 10.6
44 | 2015-11-01 | 2485.082 | 8.6429 | 2015-10-26 | 17633 | 9.7
45 | 2015-11-08 | 2402.716 | 11.919 | 2015-11-03 | 17328 | 20.6
46 | 2015-11-15 | 2469.064 | 7.5571 | 2015-11-10 | 17850 | 9.2
47 | 2015-11-22 | 2481.201 | 6.7762 | 2015-11-17 | 17754 | 7.6
48 | 2015-11-29 | 2613.703 | 4.0429 | 2015-11-23 | 19042 | 1.9
49 | 2015-12-06 | 2254.946 | 4.0333 | 2015-11-30 | 19088 | 3
50 | 2015-12-13 | 2968.924 | 6.6667 | 2015-12-07 | 19002 | 5.4
51 | 2015-12-20 | 2633.978 | 3.8429 | 2015-12-16 | 18979 | 4.3
52 | 2015-12-27 | 2384.288 | 7.0238 | 2015-12-21 | 18443 | 6.6
53 | 2016-01-03 | 2531.649 | -0.48095 | 2016-01-03 | 18387 | 1.6
1 | 2016-01-10 | 2788.552 | -1.4333 | 2016-01-04 | 20719 | -11.8
2 | 2016-01-17 | 2880.036 | -4.2095 | 2016-01-11 | 20456 | -6.6
3 | 2016-01-24 | 2913.484 | -6.3286 | 2016-01-19 | 20616 | -4.3
4 | 2016-01-31 | 2737.29 | 1.0238 | 2016-01-29 | 19334 | -5.1
5 | 2016-02-07 | 2659.753 | 2.9048 | 2016-02-04 | 18732 | 2.9
6 | 2016-02-14 | 2928.908 | -8.2524 | 2016-02-11 | 20638 | -10
7 | 2016-02-21 | 2773.267 | -0.43333 | 2016-02-17 | 19976 | -1.4
8 | 2016-02-28 | 2731.77 | 0.31905 | 2016-02-24 | 19513 | 1.7
9 | 2016-03-06 | 2774.538 | -3.5571 | 2016-03-01 | 19933 | -7.9
10 | 2016-03-13 | 2473.733 | 8.8381 | 2016-03-07 | 17751 | 11.5
11 | 2016-03-20 | 2492.021 | 4.8952 | 2016-03-14 | 17209 | 8.7
12 | 2016-03-27 | 2515.03 | 1.9524 | 2016-03-24 | 18071 | -0.2
13 | 2016-04-03 | 2481.273 | 5.0333 | 2016-03-29 | 17370 | 7.2
14 | 2016-04-10 | 2606.917 | -0.86667 | 2016-04-04 | 18021 | -2.4
15 | 2016-04-17 | 2425.388 | 8.0048 | 2016-04-12 | 17669 | 6.7
16 | 2016-04-24 | 2305.512 | 11.7 | 2016-04-18 | 16356 | 22.9
17 | 2016-05-01 | 2362.348 | 7.1381 | 2016-04-25 | 16796 | 7.4
18 | 2016-05-08 | 2270.087 | 12 | 2016-05-02 | 16020 | 12
19 | 2016-05-15 | 2270.723 | 12.219 | 2016-05-12 | 15980 | 20.5
20 | 2016-05-22 | 2256.595 | 14.8667 | 2016-05-19 | 15942 | 19.7
21 | 2016-05-29 | 2592.606 | 23.9762 | 2016-05-27 | 19637 | 28.9
22 | 2016-06-05 | 2599.792 | 21.6619 | 2016-05-30 | 19852 | 27.2
23 | 2016-06-12 | 2375.761 | 17.9857 | 2016-06-11 | 17525 | 30.2
24 | 2016-06-19 | 2588.618 | 21.9857 | 2016-06-19 | 20020 | 32.1
25 | 2016-06-26 | 2743.584 | 23.8762 | 2016-06-20 | 21673 | 34
26 | 2016-07-03 | 2563.388 | 22.3667 | 2016-06-27 | 21680 | 32.5
27 | 2016-07-10 | 2862.87 | 25.3 | 2016-07-07 | 21388 | 30.9
28 | 2016-07-17 | 2832.049 | 24.7 | 2016-07-13 | 22709 | 35
29 | 2016-07-24 | 2927.854 | 26.1476 | 2016-07-22 | 22068 | 35.1
30 | 2016-07-31 | 2899.923 | 25.7333 | 2016-07-27 | 21707 | 33.7
31 | 2016-08-07 | 2944.088 | 25.9571 | 2016-08-04 | 22364 | 31.9
32 | 2016-08-14 | 3104.654 | 27.3571 | 2016-08-10 | 23128 | 34.8
33 | 2016-08-21 | 2925.272 | 24.2952 | 2016-08-19 | 21654 | 29.3
34 | 2016-08-28 | 2849.378 | 24.3524 | 2016-08-25 | 21510 | 29.7
35 | 2016-09-04 | 2647.95 | 21.9714 | 2016-08-30 | 21380 | 30.1
36 | 2016-09-11 | 2875.792 | 25.2 | 2016-09-07 | 23106 | 34.5
37 | 2016-09-18 | 2523.08 | 20.2476 | 2016-09-13 | 18966 | 27.8
38 | 2016-09-25 | 2555.66 | 19.9476 | 2016-09-19 | 19615 | 25.6
39 | 2016-10-02 | 2370.988 | 16.3238 | 2016-09-27 | 16876 | 21.8
40 | 2016-10-09 | 2361.984 | 16.3762 | 2016-10-06 | 17376 | 23
41 | 2016-10-16 | 2300.832 | 13.8333 | 2016-10-11 | 16802 | 16.5
42 | 2016-10-23 | 2378.094 | 13.9857 | 2016-10-18 | 17360 | 25.2
43 | 2016-10-30 | 2466.419 | 7.2143 | 2016-10-27 | 18018 | 5.2
44 | 2016-11-06 | 2405.64 | 10.1714 | 2016-11-02 | 17131 | 18
45 | 2016-11-13 | 2394.658 | 7.9476 | 2016-11-08 | 17349 | 15.8
46 | 2016-11-20 | 2464.404 | 7.9143 | 2016-11-20 | 17779 | 1.4
47 | 2016-11-27 | 2658.614 | 2.5286 | 2016-11-23 | 19203 | 0.2
48 | 2016-12-04 | 2564.837 | 5.7238 | 2016-11-28 | 18210 | 7
49 | 2016-12-10 | 2332.178 | -0.48095 | 2016-12-09 | 19264 | -1.4
50 | 2016-12-18 | 2873.365 | -5.081 | 2016-12-15 | 20657 | -8.1
51 | 2016-12-25 | 3496.243 | -1.5857 | 2016-12-19 | 20592 | -7.8
52 | 2017-01-01 | 2194.83 | 0.15714 | 2016-12-28 | 17992 | -1.8
1 | 2017-01-08 | 2800.458 | -5.0571 | 2017-01-05 | 19869 | -6.6
2 | 2017-01-15 | 2791.668 | -1.5571 | 2017-01-09 | 20192 | -3.3
3 | 2017-01-22 | 2683.189 | 2.3524 | 2017-01-17 | 19118 | 1.7
4 | 2017-01-29 | 2682.02 | 0.59524 | 2017-01-24 | 18640 | 1.2
5 | 2017-02-05 | 2799.958 | -3.9333 | 2017-01-30 | 19704 | -4.9
6 | 2017-02-12 | 2791.09 | -2.3667 | 2017-02-07 | 19584 | -1.1
7 | 2017-02-19 | 2624.133 | 0.45714 | 2017-02-16 | 19189 | -3.7
8 | 2017-02-26 | 2472.737 | 4.5333 | 2017-02-21 | 17837 | 5.5
9 | 2017-03-05 | 2635.347 | -0.2381 | 2017-03-03 | 19004 | -5.6
10 | 2017-03-12 | 2648.322 | -0.27619 | 2017-03-10 | 18977 | -4.6
11 | 2017-03-19 | 2689.337 | -2.681 | 2017-03-13 | 19109 | -6.1
12 | 2017-03-26 | 2570.353 | 2.8857 | 2017-03-22 | 18574 | -2.5
13 | 2017-04-02 | 2479.132 | 6.7571 | 2017-03-30 | 17510 | 2.9
14 | 2017-04-09 | 2395.597 | 8.2048 | 2017-04-06 | 17281 | 7.3
15 | 2017-04-16 | 2228.476 | 13.0762 | 2017-04-12 | 16506 | 7.7
16 | 2017-04-23 | 2301.158 | 10.0524 | 2017-04-20 | 16381 | 5.4
17 | 2017-04-30 | 2255.022 | 11.581 | 2017-04-25 | 15935 | 9.3
18 | 2017-05-07 | 2331.499 | 8.681 | 2017-05-04 | 16227 | 10
19 | 2017-05-14 | 2283.432 | 10.1619 | 2017-05-08 | 16078 | 11.1
20 | 2017-05-21 | 2275.55 | 16.3476 | 2017-05-18 | 17704 | 29.6
21 | 2017-05-28 | 2250.356 | 16.0667 | 2017-05-25 | 15950 | 11.9
22 | 2017-06-04 | 2276.16 | 17.7857 | 2017-05-29 | 16317 | 25.1
23 | 2017-06-11 | 2391.17 | 19.9714 | 2017-06-11 | 18926 | 31.6
24 | 2017-06-18 | 2710.523 | 23.5667 | 2017-06-12 | 21165 | 32.4
25 | 2017-06-25 | 2514.885 | 20.7524 | 2017-06-19 | 18783 | 25.8
26 | 2017-07-02 | 2429.473 | 21.2333 | 2017-06-30 | 18253 | 27.9
27 | 2017-07-09 | 2564.696 | 22.919 | 2017-07-06 | 20312 | 29.6
28 | 2017-07-16 | 2641.147 | 22.4524 | 2017-07-11 | 20191 | 28.9
29 | 2017-07-23 | 2751.121 | 23.7905 | 2017-07-19 | 20580 | 31.5
30 | 2017-07-30 | 2540.604 | 21.8524 | 2017-07-27 | 19098 | 25.8
31 | 2017-08-06 | 2680.86 | 22.7905 | 2017-07-31 | 20184 | 30.8
32 | 2017-08-13 | 2550.852 | 22.0524 | 2017-08-09 | 19389 | 28.7
33 | 2017-08-20 | 2628.866 | 22.0619 | 2017-08-15 | 19198 | 27.2
34 | 2017-08-27 | 2482.693 | 19.8762 | 2017-08-21 | 20313 | 30
35 | 2017-09-03 | 2338.323 | 17.7238 | 2017-08-30 | 17703 | 23.9
36 | 2017-09-10 | 2247.089 | 16.6667 | 2017-09-05 | 16449 | 21
37 | 2017-09-17 | 2489.987 | 21.0095 | 2017-09-14 | 18415 | 27
38 | 2017-09-24 | 2771.142 | 24.2905 | 2017-09-24 | 20394 | 33.3
39 | 2017-10-01 | 2574.485 | 18.5667 | 2017-09-25 | 21682 | 31.3
40 | 2017-10-08 | 2374.265 | 19.4905 | 2017-10-04 | 17491 | 26.5
41 | 2017-10-15 | 2326.158 | 15.8048 | 2017-10-10 | 16620 | 22.9
42 | 2017-10-22 | 2276.504 | 15.0333 | 2017-10-16 | 16750 | 10.1
43 | 2017-10-29 | 2351.981 | 10.3095 | 2017-10-26 | 16698 | 10.6
44 | 2017-11-05 | 2448.709 | 8.081 | 2017-11-01 | 17664 | 6.7
45 | 2017-11-12 | 2573.358 | 2.3333 | 2017-11-10 | 18731 | -4
46 | 2017-11-19 | 2593.993 | 4.0905 | 2017-11-13 | 18616 | 5.3
47 | 2017-11-26 | 2582.342 | 4.1286 | 2017-11-22 | 18924 | 0.1
48 | 2017-12-03 | 2945.44 | 4.6762 | 2017-11-27 | 18998 | 3
49 | 2017-12-10 | 2308.909 | 1.1714 | 2017-12-07 | 19148 | 0.1
50 | 2017-12-17 | 3356.972 | -7.419 | 2017-12-13 | 20293 | -7.5
51 | 2017-12-24 | 2791.103 | -1.4714 | 2017-12-21 | 19627 | -2.9
52 | 2017-12-31 | 2472.533 | -12.5476 | 2017-12-28 | 20010 | -12.8
1 | 2018-01-07 | 3045.502 | -13.0476 | 2018-01-05 | 20747 | -15.2
2 | 2018-01-14 | 2841.975 | -1.9143 | 2018-01-14 | 19921 | -6.7
3 | 2018-01-21 | 2857.148 | -3.4571 | 2018-01-15 | 20175 | -7.3
4 | 2018-01-28 | 2752.903 | 0.21905 | 2018-01-24 | 19844 | -5.3
5 | 2018-02-04 | 2871.627 | -5.0286 | 2018-01-30 | 20211 | -8.3
6 | 2018-02-11 | 2928.324 | -6.9 | 2018-02-07 | 19913 | -5.1
7 | 2018-02-18 | 2730.743 | -0.79524 | 2018-02-13 | 19555 | -4.1
8 | 2018-02-25 | 2622.584 | 4.1095 | 2018-02-22 | 18620 | 1.4
9 | 2018-03-04 | 2536.83 | 3.9667 | 2018-02-26 | 17795 | 7
10 | 2018-03-11 | 2644.177 | -0.085714 | 2018-03-06 | 18393 | 0.2
11 | 2018-03-18 | 2611.579 | -0.17143 | 2018-03-12 | 18079 | -0.3
12 | 2018-03-25 | 2568.737 | -0.24286 | 2018-03-19 | 18015 | -0.1
13 | 2018-04-01 | 2458.085 | 3.9333 | 2018-03-27 | 17354 | 3
14 | 2018-04-08 | 2573.814 | 0.69048 | 2018-04-04 | 17882 | 2.4
15 | 2018-04-15 | 2582.041 | 2.1762 | 2018-04-09 | 17555 | 2.9
16 | 2018-04-22 | 2482.217 | 4.2286 | 2018-04-17 | 17480 | 0.7
17 | 2018-04-29 | 2319.02 | 9.6381 | 2018-04-25 | 16167 | 11
18 | 2018-05-06 | 2239.906 | 17.6238 | 2018-05-02 | 16086 | 27.5
19 | 2018-05-13 | 2234.572 | 13.9381 | 2018-05-08 | 15706 | 18.5
20 | 2018-05-20 | 2255.281 | 16.8667 | 2018-05-14 | 15980 | 24.1
21 | 2018-05-27 | 2375.999 | 20.5714 | 2018-05-25 | 17788 | 30.2
22 | 2018-06-03 | 2694.117 | 23.0476 | 2018-05-28 | 20394 | 30.7
23 | 2018-06-10 | 2332.158 | 17.3524 | 2018-06-08 | 16765 | 21.9
24 | 2018-06-17 | 2570.35 | 22.3571 | 2018-06-17 | 20161 | 31.3
25 | 2018-06-24 | 2589.977 | 20.6095 | 2018-06-18 | 20992 | 30.2
26 | 2018-07-01 | 2799.84 | 24.5 | 2018-06-29 | 21037 | 31
27 | 2018-07-08 | 2918.27 | 25.5048 | 2018-07-05 | 23374 | 33.2
28 | 2018-07-15 | 2959.067 | 25.5905 | 2018-07-15 | 21510 | 29.9
29 | 2018-07-22 | 2806.574 | 23.5857 | 2018-07-16 | 21455 | 31.5
30 | 2018-07-29 | 2804.722 | 23.5524 | 2018-07-24 | 21545 | 29.5
31 | 2018-08-05 | 2903.656 | 25.219 | 2018-08-03 | 21028 | 28.5
32 | 2018-08-12 | 2886.233 | 24.3524 | 2018-08-07 | 21190 | 27.5
33 | 2018-08-19 | 2947.795 | 24.6095 | 2018-08-15 | 21456 | 30.9
34 | 2018-08-26 | 2701.424 | 22.6238 | 2018-08-20 | 20142 | 25
35 | 2018-09-02 | 2867.372 | 23.8286 | 2018-08-28 | 22175 | 31.7
36 | 2018-09-09 | 2762.349 | 22.0048 | 2018-09-05 | 23131 | 33.9
37 | 2018-09-16 | 2678.651 | 21.0952 | 2018-09-16 | 20871 | 28.3
38 | 2018-09-23 | 2579.775 | 19.4524 | 2018-09-17 | 21233 | 26.3
39 | 2018-09-30 | 2380.053 | 15.619 | 2018-09-25 | 17419 | 20.4
40 | 2018-10-07 | 2394.01 | 12.7381 | 2018-10-02 | 16841 | 12.9
41 | 2018-10-14 | 2397.565 | 14.7 | 2018-10-09 | 18640 | 28.6
42 | 2018-10-21 | 2409.557 | 7.7714 | 2018-10-17 | 17040 | 8.5
43 | 2018-10-28 | 2514.239 | 5.3143 | 2018-10-24 | 17481 | 5.2
44 | 2018-11-04 | 2501.666 | 6.3857 | 2018-10-29 | 17267 | 8.5
45 | 2018-11-11 | 2555.529 | 5.1952 | 2018-11-09 | 18209 | 2.6
46 | 2018-11-18 | 2700.142 | 0.41905 | 2018-11-14 | 19232 | 0.3
47 | 2018-11-25 | 2739.306 | -0.68095 | 2018-11-22 | 20048 | -6.6
48 | 2018-12-02 | 2713.598 | 2.5476 | 2018-11-27 | 19248 | 1.2
49 | 2018-12-07 | 2019.62 | -1.8905 | 2018-12-07 | 19686 | -4
50 | 2018-12-16 | 3213.188 | 1.019 | 2018-12-11 | 19718 | -1.4
51 | 2018-12-23 | 2723.873 | 1.019 | 2018-12-18 | 19450 | 0.2
52 | 2018-12-30 | 2915.267 | 0.34286 | 2018-12-27 | 18108 | -0.2
1 | 2019-01-06 | 2616.032 | 0.071429 | 2019-01-02 | 19580 | -3.9
2 | 2019-01-13 | 2826.392 | -4.2524 | 2019-01-10 | 19872 | -5.1
3 | 2019-01-20 | 2947.535 | -6.981 | 2019-01-20 | 20841 | -14.5
4 | 2019-01-27 | 2983.872 | -7.0667 | 2019-01-21 | 21356 | -11.8
5 | 2019-02-03 | 3039.29 | -9.4762 | 2019-01-31 | 21174 | -14.6
6 | 2019-02-10 | 2825.025 | -1.5571 | 2019-02-06 | 19739 | -1.1
7 | 2019-02-17 | 2825.059 | -3.4714 | 2019-02-12 | 20043 | -1.2
8 | 2019-02-24 | 2768.176 | -2.0905 | 2019-02-19 | 19796 | -4.4
9 | 2019-03-03 | 2863.896 | -6.5167 | 2019-02-27 | 20436 | -7.7
10 | 2019-03-10 | 2833.518 | -6.8929 | 2019-03-05 | 20176 | -9
11 | 2019-03-17 | 2603.892 | 1.8333 | 2019-03-11 | 18103 | 2
12 | 2019-03-24 | 2559.903 | 3.1619 | 2019-03-18 | 18023 | 2.6
13 | 2019-03-31 | 2530.669 | 3.3833 | 2019-03-26 | 17633 | 3.6
14 | 2019-04-07 | 2474.168 | 5.1238 | 2019-04-01 | 17516 | 2.8
15 | 2019-04-14 | 2432.225 | 7.019 | 2019-04-11 | 17180 | 1.3
16 | 2019-04-21 | 2348.088 | 8.5762 | 2019-04-15 | 16614 | 8.3
17 | 2019-04-28 | 2332.199 | 9.1143 | 2019-04-24 | 16068 | 12.8
18 | 2019-05-05 | 2398.814 | 8.2857 | 2019-04-29 | 16946 | 6.9
19 | 2019-05-12 | 2293.824 | 11.0429 | 2019-05-09 | 15930 | 14.4
20 | 2019-05-19 | 2311.692 | 12.8381 | 2019-05-13 | 16416 | 7.2
21 | 2019-05-26 | 2263.491 | 16.2048 | 2019-05-22 | 15851 | 15.1
22 | 2019-06-02 | 2321.033 | 15.5857 | 2019-05-27 | 16051 | 22.5
23 | 2019-06-09 | 2325.469 | 17.6571 | 2019-06-07 | 16394 | 25.8
24 | 2019-06-16 | 2313.68 | 17.2286 | 2019-06-10 | 16208 | 18.4
25 | 2019-06-23 | 2433.787 | 20.3857 | 2019-06-19 | 17956 | 24.8
26 | 2019-06-30 | 2699.016 | 23.6095 | 2019-06-27 | 20178 | 28.9
27 | 2019-07-07 | 2873.591 | 24.8952 | 2019-07-05 | 21727 | 30.2
28 | 2019-07-14 | 2776.132 | 23.5 | 2019-07-10 | 21007 | 28.9
29 | 2019-07-21 | 3032.724 | 25.9286 | 2019-07-20 | 21636 | 32.4
30 | 2019-07-28 | 2840.069 | 23.9476 | 2019-07-26 | 21010 | 29.1
31 | 2019-08-04 | 2836.533 | 24.0619 | 2019-07-29 | 21614 | 31.4
32 | 2019-08-11 | 2687.182 | 23.3524 | 2019-08-07 | 20920 | 27.7
33 | 2019-08-18 | 2769.827 | 23.0143 | 2019-08-13 | 21061 | 28.1
34 | 2019-08-25 | 2679.421 | 21.9238 | 2019-08-21 | 21376 | 30.2
35 | 2019-09-01 | 2505.522 | 20.3524 | 2019-08-28 | 18637 | 26.9
36 | 2019-09-08 | 2386.035 | 18.1714 | 2019-09-03 | 17581 | 22
37 | 2019-09-15 | 2435.541 | 18.5333 | 2019-09-11 | 19703 | 28.6
38 | 2019-09-22 | 2476.362 | 20.481 | 2019-09-22 | 18758 | 30.7
39 | 2019-09-29 | 2406.897 | 18.4524 | 2019-09-23 | 17942 | 24.3
40 | 2019-10-06 | 2374.288 | 14.5905 | 2019-10-01 | 18222 | 31.2
41 | 2019-10-13 | 2286.694 | 13.2667 | 2019-10-07 | 16422 | 17.7
42 | 2019-10-20 | 2332.984 | 9.5905 | 2019-10-17 | 16740 | 8.5
43 | 2019-10-27 | 2347.65 | 11.1619 | 2019-10-24 | 16476 | 13.4
44 | 2019-11-03 | 2445.165 | 7.4762 | 2019-11-01 | 17017 | 4.6
45 | 2019-11-10 | 2561.37 | 3.1095 | 2019-11-07 | 18253 | 2.4
46 | 2019-11-17 | 2777.214 | -3.3333 | 2019-11-13 | 19534 | -4.1
47 | 2019-11-24 | 2647.337 | 2.9548 | 2019-11-18 | 19044 | 2.1
48 | 2019-12-01 | 2669.441 | 2.2167 | 2019-12-01 | 19107 | -1.3
49 | 2019-12-08 | 2792.114 | -0.61905 | 2019-12-02 | 19584 | -1.1
50 | 2019-12-15 | 2793.234 | 0.02381 | 2019-12-11 | 20228 | -3
51 | 2019-12-22 | 3251.249 | -3.519 | 2019-12-19 | 20823 | -7.8
52 | 2019-12-29 | 2108.993 | 2.5952 | 2019-12-23 | 17518 | 8.6
1 | 2020-01-05 | 2527.453 | 2.1143 | 2020-01-05 | 17946 | 0.9
2 | 2020-01-12 | 2767.482 | 0.07619 | 2020-01-08 | 19759 | -4.5
3 | 2020-01-19 | 2856.195 | -2.1476 | 2020-01-17 | 19989 | -8.5
4 | 2020-01-26 | 2801.928 | -1.3429 | 2020-01-20 | 19982 | -5.3
5 | 2020-02-02 | 2789.92 | -1.3857 | 2020-01-29 | 19370 | -2.9
6 | 2020-02-09 | 2806.795 | -3.2333 | 2020-02-06 | 19257 | -3.6
7 | 2020-02-16 | 2782.415 | -2.7 | 2020-02-14 | 19813 | -10.4
8 | 2020-02-23 | 2664.318 | -0.86667 | 2020-02-20 | 19663 | -4.7
9 | 2020-03-01 | 2716.574 | -1.5714 | 2020-02-27 | 19116 | -3.8
10 | 2020-03-08 | 2593.923 | 3.1667 | 2020-03-03 | 18046 | 3.8
11 | 2020-03-15 | 2517.192 | 4.9238 | 2020-03-11 | 17662 | 3.4
12 | 2020-03-22 | 2525.756 | 2.5286 | 2020-03-16 | 17414 | 3.9
13 | 2020-03-29 | 2381.873 | 6.3619 | 2020-03-23 | 16935 | 3.5
14 | 2020-04-05 | 2235.936 | 7.5476 | 2020-03-30 | 15763 | 8
15 | 2020-04-12 | 2142.126 | 7.8143 | 2020-04-07 | 14803 | 13.6
16 | 2020-04-19 | 2226.22 | 4.5476 | 2020-04-15 | 15450 | 4.4
17 | 2020-04-26 | 2186.118 | 5.4238 | 2020-04-21 | 15334 | 3.6
18 | 2020-05-03 | 2074.461 | 12.119 | 2020-04-30 | 14475 | 13.2
19 | 2020-05-10 | 2145.501 | 6.1286 | 2020-05-08 | 14730 | 4.8
20 | 2020-05-17 | 2135.825 | 9.4571 | 2020-05-14 | 14954 | 12.3
21 | 2020-05-24 | 2090.504 | 17.2714 | 2020-05-24 | 15545 | 25.7
22 | 2020-05-31 | 2479.051 | 20.7524 | 2020-05-26 | 20582 | 30.6
23 | 2020-06-07 | 2371.542 | 21.3762 | 2020-06-05 | 18973 | 27.6
24 | 2020-06-14 | 2372.026 | 19.4714 | 2020-06-10 | 20580 | 31.6
25 | 2020-06-21 | 2628.362 | 22.7762 | 2020-06-20 | 20024 | 30.4
26 | 2020-06-28 | 2645.033 | 23.619 | 2020-06-22 | 20415 | 29.7
27 | 2020-07-05 | 2942.976 | 27.2571 | 2020-07-02 | 22589 | 34.6
28 | 2020-07-12 | 3181.686 | 27.4905 | 2020-07-09 | 24497 | 34
29 | 2020-07-19 | 2916.228 | 25.219 | 2020-07-17 | 22195 | 30.6
30 | 2020-07-26 | 2890.849 | 24.7905 | 2020-07-26 | 22648 | 33.3
31 | 2020-08-02 | 2948.168 | 25.7048 | 2020-07-27 | 23901 | 31.3
32 | 2020-08-09 | 2606.352 | 22.0048 | 2020-08-09 | 20521 | 30.4
33 | 2020-08-16 | 2967.735 | 25.181 | 2020-08-10 | 23745 | 31.9
34 | 2020-08-23 | 2684.076 | 22.9286 | 2020-08-23 | 21353 | 31.3
35 | 2020-08-30 | 2730.506 | 22.7714 | 2020-08-24 | 23357 | 32.4
36 | 2020-09-06 | 2516.733 | 20.7857 | 2020-09-01 | 20341 | 27.4
37 | 2020-09-13 | 2345.377 | 17.7429 | 2020-09-09 | 16595 | 18.2
38 | 2020-09-20 | 2256.233 | 14.3762 | 2020-09-16 | 16056 | 24.8
39 | 2020-09-27 | 2359.117 | 19.3476 | 2020-09-24 | 16954 | 23.8
40 | 2020-10-04 | 2343.523 | 13.8238 | 2020-09-28 | 18076 | 25.9
41 | 2020-10-11 | 2269.56 | 13.3476 | 2020-10-08 | 16055 | 16
42 | 2020-10-18 | 2268.958 | 12.0095 | 2020-10-15 | 16376 | 11.9
43 | 2020-10-25 | 2387.319 | 10.081 | 2020-10-19 | 16946 | 8
44 | 2020-11-01 | 2495.502 | 5.1714 | 2020-10-27 | 17628 | 7
45 | 2020-11-08 | 2379.319 | 12.1667 | 2020-11-02 | 18169 | 4.2
46 | 2020-11-15 | 2387.329 | 10.2643 | 2020-11-13 | 17331 | 8.7
47 | 2020-11-22 | 2545.051 | 4.6367 | 2020-11-18 | 18958 | 0.2
48 | 2020-11-29 | 2573.636 | 4.75 | 2020-11-24 | 19172 | 0.1
49 | 2020-12-06 | 2264.397 | 0.91905 | 2020-12-01 | 18959 | -0.5
50 | 2020-12-13 | 3079.802 | 2.1429 | 2020-12-07 | 19403 | 0.9
51 | 2020-12-20 | 2811.958 | -2.3 | 2020-12-16 | 20675 | -6.8
52 | 2020-12-27 | 2618.5 | 0.96667 | 2020-12-22 | 19042 | 2.6
53 | 2021-01-03 | 2586.452 | 0.17143 | 2020-12-29 | 19053 | -1.8
1 | 2021-01-10 | 2748.677 | -1.0857 | 2021-01-08 | 19296 | -3.6
2 | 2021-01-17 | 2698.095 | 1.0238 | 2021-01-12 | 19427 | -1.6
3 | 2021-01-24 | 2787.687 | -2.8857 | 2021-01-20 | 19515 | -4.5
4 | 2021-01-31 | 2875.028 | -5.7286 | 2021-01-28 | 20154 | -8.4
5 | 2021-02-07 | 2822.533 | -4.7 | 2021-02-01 | 19818 | -4
6 | 2021-02-14 | 2958.496 | -8.4952 | 2021-02-08 | 20361 | -6.9
7 | 2021-02-21 | 2869.063 | -5.9714 | 2021-02-16 | 20221 | -7.1
8 | 2021-02-28 | 2677.562 | 1.9429 | 2021-02-22 | 18774 | 2.8
9 | 2021-03-07 | 2723.977 | -2.6905 | 2021-03-01 | 19485 | -0.8
10 | 2021-03-14 | 2516.079 | 5.6762 | 2021-03-08 | 18026 | 9.4
11 | 2021-03-21 | 2529.233 | 3.7143 | 2021-03-15 | 17940 | -1.4
12 | 2021-03-28 | 2386.575 | 9.9524 | 2021-03-26 | 16268 | 9.6
13 | 2021-04-04 | 2365.144 | 5.6571 | 2021-04-01 | 16767 | 1.8
14 | 2021-04-11 | 2231.181 | 13.7524 | 2021-04-05 | 15668 | 12.8
15 | 2021-04-18 | 2306.786 | 8.981 | 2021-04-15 | 15802 | 8
16 | 2021-04-25 | 2326.647 | 7.1857 | 2021-04-20 | 16402 | 4.8
17 | 2021-05-02 | 2279.233 | 9.8524 | 2021-04-29 | 15646 | 10.5
18 | 2021-05-09 | 2272.663 | 9.6667 | 2021-05-03 | 15827 | 12.4
19 | 2021-05-16 | 2202.781 | 13.3952 | 2021-05-11 | 15447 | 9.5
20 | 2021-05-23 | 2473.753 | 22.5476 | 2021-05-21 | 19259 | 31.5
21 | 2021-05-30 | 2291.647 | 15.7381 | 2021-05-25 | 19291 | 31.6
22 | 2021-06-06 | 2495.72 | 22.7 | 2021-06-06 | 20677 | 33.5
23 | 2021-06-13 | 2787.64 | 23.981 | 2021-06-07 | 21207 | 31.1
24 | 2021-06-20 | 2453.821 | 20.6667 | 2021-06-20 | 18486 | 26.1
25 | 2021-06-27 | 2575.032 | 22.3714 | 2021-06-27 | 20656 | 30.7
26 | 2021-07-04 | 2714.895 | 23.6476 | 2021-06-28 | 22193 | 31.6
27 | 2021-07-11 | 2618.1 | 21.4429 | 2021-07-06 | 21748 | 31.7
28 | 2021-07-18 | 2759.419 | 23.5571 | 2021-07-14 | 21487 | 29.2
29 | 2021-07-25 | 2705.506 | 22.7714 | 2021-07-19 | 20895 | 28.9
30 | 2021-08-01 | 2564.649 | 21.0333 | 2021-07-26 | 20858 | 30.1
31 | 2021-08-08 | 2701.63 | 23.0857 | 2021-08-05 | 20993 | 27.3
32 | 2021-08-15 | 2947.49 | 25.2476 | 2021-08-09 | 22335 | 30.6
33 | 2021-08-22 | 3002.528 | 25.2429 | 2021-08-19 | 21877 | 30.8
34 | 2021-08-29 | 3137.955 | 26.6333 | 2021-08-24 | 22909 | 33.1
35 | 2021-09-05 | 2602.69 | 21.081 | 2021-08-30 | 21570 | 28.7
36 | 2021-09-12 | 2451.704 | 20.3714 | 2021-09-07 | 18560 | 25.5
37 | 2021-09-19 | 2487.729 | 20.0381 | 2021-09-17 | 18786 | 26
38 | 2021-09-26 | 2359.527 | 16.5143 | 2021-09-21 | 17846 | 24.4
39 | 2021-10-03 | 2347.134 | 16.8976 | 2021-09-27 | 16826 | 24.2
40 | 2021-10-10 | 2423.924 | 17.619 | 2021-10-07 | 17039 | 19.8
41 | 2021-10-17 | 2367.858 | 17.0571 | 2021-10-12 | 17270 | 21.95
42 | 2021-10-24 | 2344.856 | 11.6095 | 2021-10-18 | 16337 | 13.8
43 | 2021-10-31 | 2400.534 | 9.4414 | 2021-10-25 | 16946 | 8.25
44 | 2021-11-07 | 2460.598 | 6.1143 | 2021-11-04 | 17537 | 9
45 | 2021-11-14 | 2451.66 | 8.4762 | 2021-11-14 | 17628 | 4.7
46 | 2021-11-21 | 2567.212 | 5.0238 | 2021-11-16 | 18445 | 5.5
47 | 2021-11-28 | 2679.479 | 1.0571 | 2021-11-23 | 18744 | 3.3
48 | 2021-12-05 | 2748.075 | 1.5714 | 2021-11-29 | 19612 | 0.15
49 | 2021-12-11 | 2859.142 | 1.7429 | 2021-12-08 | 20443 | -2
50 | 2021-12-19 | 2672.947 | 3.8381 | 2021-12-19 | 19133 | -3.4
51 | 2021-12-26 | 2272.806 | 0.59524 | 2021-12-22 | 19457 | -0.7
52 | 2022-01-02 | 2988.475 | 0.20476 | 2022-01-02 | 18986 | -6.3
1 | 2022-01-09 | 2867.241 | -3.8857 | 2022-01-07 | 20239 | -7
2 | 2022-01-16 | 3020.725 | -7.6524 | 2022-01-11 | 21420 | -10
3 | 2022-01-23 | 3009.042 | -7.9667 | 2022-01-20 | 21166 | -12.1
4 | 2022-01-30 | 3094.318 | -10.4095 | 2022-01-24 | 21146 | -6.1
5 | 2022-02-06 | 2960.041 | -4.6905 | 2022-02-04 | 20513 | -10.6
6 | 2022-02-13 | 2832.569 | -2.0286 | 2022-02-13 | 20058 | -9.5
7 | 2022-02-20 | 2885.157 | -3.5571 | 2022-02-14 | 20783 | -9.8
8 | 2022-02-27 | 2837.291 | -3.2381 | 2022-02-23 | 19978 | -4.8
9 | 2022-03-06 | 2781.134 | -1.0857 | 2022-02-28 | 19972 | -5.9
10 | 2022-03-13 | 2756.58 | -1.1571 | 2022-03-07 | 18836 | 1
11 | 2022-03-20 | 2567.324 | 5.881 | 2022-03-15 | 17886 | 0.7
12 | 2022-03-27 | 2584.788 | 3.4905 | 2022-03-23 | 17862 | 3.3
13 | 2022-04-03 | 2631.049 | 1.4714 | 2022-03-28 | 18833 | -5.4
14 | 2022-04-10 | 2445.197 | 7.2524 | 2022-04-04 | 16901 | 7.9
15 | 2022-04-17 | 2301.483 | 9.0905 | 2022-04-11 | 16157 | 12.1
16 | 2022-04-24 | 2395.123 | 7.9476 | 2022-04-18 | 16992 | 6.6
17 | 2022-05-01 | 2357.543 | 8.0619 | 2022-04-27 | 16727 | 3.5
18 | 2022-05-08 | 2288.564 | 11.7905 | 2022-05-03 | 16193 | 12.1
19 | 2022-05-15 | 2420.061 | 19.7 | 2022-05-15 | 18286 | 28.9
20 | 2022-05-22 | 2336.128 | 16.7381 | 2022-05-20 | 16239 | 23.6
21 | 2022-05-29 | 2332.369 | 18.0952 | 2022-05-26 | 17195 | 26.6
22 | 2022-06-05 | 2537.915 | 21.119 | 2022-05-31 | 21305 | 32.2
23 | 2022-06-12 | 2378.093 | 18.9286 | 2022-06-08 | 16558 | 22.2
24 | 2022-06-19 | 2555.752 | 21.0762 | 2022-06-16 | 21211 | 32.2
25 | 2022-06-26 | 2850.099 | 25.3667 | 2022-06-22 | 21826 | 34.6
26 | 2022-07-03 | 2545.54 | 21.8905 | 2022-06-30 | 19242 | 25.7
27 | 2022-07-10 | 2636.564 | 22.2286 | 2022-07-07 | 19479 | 25
28 | 2022-07-17 | 2778.325 | 23.5238 | 2022-07-11 | 20476 | 30.8
29 | 2022-07-24 | 3097.347 | 27.8333 | 2022-07-19 | 22713 | 34.2
30 | 2022-07-31 | 2766.036 | 22.7381 | 2022-07-28 | 20533 | 28.7
31 | 2022-08-07 | 2984.792 | 25.8476 | 2022-08-06 | 21622 | 31.1
32 | 2022-08-14 | 2741.31 | 22.4857 | 2022-08-08 | 21426 | 30.9
33 | 2022-08-21 | 2837.659 | 23.4476 | 2022-08-18 | 20733 | 27.4
34 | 2022-08-28 | 2803.392 | 22.6286 | 2022-08-24 | 21399 | 28.7
35 | 2022-09-04 | 2768.199 | 22.619 | 2022-08-29 | 21697 | 30.5
36 | 2022-09-11 | 2631.655 | 21.2905 | 2022-09-09 | 19909 | 26.5
37 | 2022-09-18 | 2530.077 | 19.6905 | 2022-09-12 | 18941 | 23.7
38 | 2022-09-25 | 2440.529 | 17.8238 | 2022-09-19 | 18808 | 27.5
39 | 2022-10-02 | 2329.524 | 13.3095 | 2022-09-27 | 16395 | 16.5
40 | 2022-10-09 | 2357.445 | 12.8333 | 2022-10-05 | 16565 | 21.6
41 | 2022-10-16 | 2313.652 | 13.2667 | 2022-10-13 | 16252 | 14.8
42 | 2022-10-23 | 2388.92 | 9.681 | 2022-10-20 | 16960 | 6.8
43 | 2022-10-30 | 2366.94 | 10.3714 | 2022-10-27 | 16629 | 9.9
44 | 2022-11-06 | 2383.733 | 13.8714 | 2022-11-02 | 16690 | 14.1
45 | 2022-11-13 | 2451.794 | 8.7333 | 2022-11-08 | 17636 | 9.1
46 | 2022-11-20 | 2743.599 | -0.90476 | 2022-11-20 | 19100 | -3.6
47 | 2022-11-27 | 2668.657 | 4.4095 | 2022-11-21 | 19219 | 7.2
48 | 2022-12-04 | 2720.887 | 2.5619 | 2022-12-01 | 19285 | 1.4
49 | 2022-12-11 | 2390.011 | 1.8667 | 2022-12-09 | 19209 | 0.5
50 | 2022-12-18 | 2877.925 | -1.3429 | 2022-12-12 | 20246 | -2
51 | 2022-12-24 | 2498.242 | -3.5286 | 2022-12-19 | 19892 | 0.8
52 | 2023-01-01 | 3352.878 | 3.9429 | 2022-12-27 | 18647 | -2.7
1 | 2023-01-08 | 2758.054 | 9.2381 | 2023-01-08 | 19145 | 10
2 | 2023-01-15 | 2902.869 | 7.1905 | 2023-01-11 | 19834 | 10
3 | 2023-01-22 | 2848.659 | 7.9524 | 2023-01-19 | 19571 | 10
4 | 2023-01-29 | 2860.668 | 8.8571 | 2023-01-25 | 19602 | 5
5 | 2023-02-05 | 3028.967 | -2.8048 | 2023-02-03 | 21301 | -15.5
6 | 2023-02-12 | 2754.954 | 2.0381 | 2023-02-06 | 19595 | -1.7
7 | 2023-02-19 | 2695.121 | 2.6905 | 2023-02-17 | 19439 | -5
8 | 2023-02-26 | 2840.656 | -2.381 | 2023-02-23 | 20084 | -4.6
9 | 2023-03-05 | 2772.582 | 0.56667 | 2023-02-27 | 19616 | -1.3
10 | 2023-03-12 | 2715.289 | -0.8381 | 2023-03-10 | 18544 | -0.1
11 | 2023-03-19 | 2703.566 | 0.76667 | 2023-03-13 | 18389 | -0.4
12 | 2023-03-26 | 2614.795 | 4.5857 | 2023-03-24 | 17653 | 2.4
13 | 2023-04-02 | 2614.37 | 3.2333 | 2023-03-29 | 17965 | 8.3
14 | 2023-04-09 | 2451.281 | 6.4557 | 2023-04-05 | 17392 | 6.95
15 | 2023-04-16 | 2319.164 | 19.8643 | 2023-04-13 | 16537 | 28.95
16 | 2023-04-23 | 2410.193 | 7.6952 | 2023-04-18 | 16640 | 4.05
17 | 2023-04-30 | 2431.248 | 7.969 | 2023-04-24 | 16656 | 9.05
18 | 2023-05-07 | 2379.279 | 9.5762 | 2023-05-02 | 16484 | 6.5
19 | 2023-05-14 | 2309.979 | 17.3333 | 2023-05-12 | 16648 | 27
20 | 2023-05-21 | 2298.549 | 14.4571 | 2023-05-17 | 15971 | 11
21 | 2023-05-28 | 2277.446 | 15.9619 | 2023-05-28 | 16518 | 27.6
22 | 2023-06-04 | 2714.703 | 23.0333 | 2023-06-02 | 21527 | 31.6
23 | 2023-06-11 | 2434.275 | 18.8905 | 2023-06-05 | 17730 | 24.3
24 | 2023-06-18 | 2430.125 | 18.0333 | 2023-06-18 | 16916 | 24.3
25 | 2023-06-25 | 2777.778 | 22.5524 | 2023-06-21 | 20337 | 26.8
26 | 2023-07-02 | 2730.731 | 22.0952 | 2023-06-30 | 19792 | 25.2
27 | 2023-07-09 | 2919.107 | 24.15 | 2023-07-05 | 22682 | 30.95
28 | 2023-07-16 | 2786.581 | 22.7476 | 2023-07-10 | 21118 | 28.35
29 | 2023-07-23 | 2788.889 | 22.8048 | 2023-07-20 | 20656 | 27
30 | 2023-07-30 | 2930.606 | 24.1381 | 2023-07-27 | 21516 | 29
31 | 2023-08-06 | 2711.472 | 22.0286 | 2023-08-03 | 21295 | 29.1
32 | 2023-08-13 | 2738.292 | 22.9905 | 2023-08-09 | 21125 | 28.2
33 | 2023-08-20 | 2677.927 | 21.3571 | 2023-08-16 | 20821 | 26.8
34 | 2023-08-27 | 2651.031 | 20.1952 | 2023-08-21 | 19471 | 24
35 | 2023-09-03 | 2592.702 | 20.0905 | 2023-09-03 | 19526 | 31.1
36 | 2023-09-10 | 2918.15 | 23.681 | 2023-09-05 | 23559 | 32.1
37 | 2023-09-17 | 2488.632 | 18.1476 | 2023-09-11 | 18965 | 23
38 | 2023-09-24 | 2424.984 | 17.5857 | 2023-09-21 | 17280 | 21.9
39 | 2023-10-01 | 2475.184 | 18.5333 | 2023-10-01 | 17311 | 26.9
40 | 2023-10-08 | 2592.116 | 19.0714 | 2023-10-03 | 20766 | 30
41 | 2023-10-15 | 2404.223 | 10.6143 | 2023-10-10 | 16894 | 12.8
42 | 2023-10-22 | 2435.498 | 11.381 | 2023-10-16 | 16869 | 11.5
43 | 2023-10-29 | 2447.685 | 14.281 | 2023-10-23 | 17013 | 13.7
44 | 2023-11-05 | 2589.671 | 6.2857 | 2023-11-01 | 18170 | 4.4
45 | 2023-11-12 | 2661.355 | 5.2762 | 2023-11-08 | 19366 | 0.6
46 | 2023-11-19 | 2605.763 | 7.1476 | 2023-11-14 | 18301 | 9.1
47 | 2023-11-26 | 2779.011 | 2.1381 | 2023-11-20 | 19479 | 0.4
48 | 2023-12-03 | 2834.018 | 1.181 | 2023-11-28 | 20269 | -1.5
49 | 2023-12-10 | 2834.801 | 3.7381 | 2023-12-06 | 19991 | 0.2
50 | 2023-12-17 | 2375.44 | 3.3714 | 2023-12-13 | 19925 | 3
51 | 2023-12-24 | 3225.166 | 1.119 | 2023-12-19 | 19702 | -0.9
52 | 2023-12-31 | 2549.777 | 4.4571 | 2023-12-30 | 18241 | 0.2
1 | 2024-01-07 | 2849.764 | -1.4905 | 2024-01-04 | 20109 | -3.1
2 | 2024-01-14 | 2902.584 | 0.1381 | 2024-01-09 | 19874 | 2.2
3 | 2024-01-21 | 3119.757 | -8.9571 | 2024-01-15 | 21081 | -9
4 | 2024-01-28 | 2918.879 | 1.0667 | 2024-01-22 | 20456 | -1.2
5 | 2024-02-04 | 2831.597 | 1.5333 | 2024-01-30 | 19523 | 1.9
6 | 2024-02-11 | 2726.211 | 3.6762 | 2024-02-05 | 19112 | 3.1
7 | 2024-02-18 | 2880.556 | -1.9381 | 2024-02-16 | 19521 | -1
8 | 2024-02-25 | 2756.548 | 0.65714 | 2024-02-20 | 19025 | 3.2
9 | 2024-03-03 | 2696.804 | 4.4714 | 2024-02-29 | 19624 | -3
10 | 2024-03-10 | 2565.62 | 7.0524 | 2024-03-10 | 17541 | -0.6
11 | 2024-03-17 | 2534.182 | 7.4952 | 2024-03-11 | 17323 | 7.4
12 | 2024-03-24 | 2779.916 | -2.0095 | 2024-03-21 | 18902 | -1.8
13 | 2024-03-31 | 2532.722 | 5.8857 | 2024-03-27 | 17508 | 10.9
14 | 2024-04-07 | 2543.842 | 6.3429 | 2024-04-03 | 17947 | 6.1
15 | 2024-04-14 | 2412.129 | 11.3762 | 2024-04-11 | 16619 | 12.9
16 | 2024-04-21 | 2435.482 | 9.7095 | 2024-04-19 | 16584 | 14.9
17 | 2024-04-28 | 2396.297 | 10.1905 | 2024-04-25 | 16506 | 7.9
18 | 2024-05-05 | 2359.978 | 14.4286 | 2024-04-29 | 16329 | 9.9
19 | 2024-05-12 | 2327.749 | 14.3762 | 2024-05-08 | 15988 | 20
20 | 2024-05-19 | 2416.477 | 18.1333 | 2024-05-16 | 16619 | 20.9
21 | 2024-05-26 | 2591.702 | 21.6048 | 2024-05-22 | 20402 | 29.1
22 | 2024-06-02 | 2405.724 | 17.8048 | 2024-05-27 | 17291 | 24.2
23 | 2024-06-09 | 2598.025 | 19.8381 | 2024-06-04 | 20692 | 26.8
24 | 2024-06-16 | 2526.989 | 18.9429 | 2024-06-13 | 20220 | 30.1
25 | 2024-06-23 | 3110.749 | 25.1476 | 2024-06-19 | 23803 | 34.2
26 | 2024-06-30 | 2666.331 | 21.3905 | 2024-06-24 | 20982 | 28.1
27 | 2024-07-07 | 2847.757 | 23.4619 | 2024-07-05 | 21578 | 27.9
28 | 2024-07-14 | 3022.439 | 24.0048 | 2024-07-08 | 21979 | 29
29 | 2024-07-21 | 2875.998 | 23.0381 | 2024-07-15 | 21430 | 23.8
30 | 2024-07-28 | 2910.273 | 23.4857 | 2024-07-28 | 21710 | 28.2
31 | 2024-08-04 | 3254.234 | 26.4238 | 2024-07-31 | 23206 | 31.1
32 | 2024-08-11 | 2751.129 | 21.4048 | 2024-08-09 | 20784 | 27.2
33 | 2024-08-18 | 2901.005 | 22.8524 | 2024-08-15 | 21982 | 27.9
34 | 2024-08-25 | 2605.803 | 19.519 | 2024-08-25 | 20707 | 27.1
35 | 2024-09-01 | 2935.475 | 23.1095 | 2024-08-27 | 22503 | 31.1
36 | 2024-09-08 | 2504.95 | 17.9238 | 2024-09-05 | 19873 | 24.2
37 | 2024-09-15 | 2678.865 | 20.381 | 2024-09-15 | 20402 | 27.1
38 | 2024-09-22 | 2801.838 | 21.5381 | 2024-09-16 | 21643 | 28
39 | 2024-09-29 | 2595.066 | 20.181 | 2024-09-26 | 18357 | 24
40 | 2024-10-06 | 2493.17 | 17.5476 | 2024-09-30 | 18453 | 22.8
41 | 2024-10-13 | 2457.04 | 12.0524 | 2024-10-10 | 17159 | 14.2
42 | 2024-10-20 | 2448.06 | 10.6952 | 2024-10-16 | 17205 | 10.2
43 | 2024-10-27 | 2498.609 | 12.8571 | 2024-10-21 | 17209 | 26
44 | 2024-11-03 | 2540.856 | 11.4381 | 2024-10-28 | 17591 | 9.8
45 | 2024-11-10 | 2533.01 | 12.1333 | 2024-11-04 | 17812 | 14.1
46 | 2024-11-17 | 2641.032 | 7.1095 | 2024-11-14 | 18497 | 8.9
47 | 2024-11-24 | 2663.051 | 6.5429 | 2024-11-21 | 18481 | 5.1
48 | 2024-11-30 | 2406.491 | 1.4476 | 2024-12-01 | 19212 | 0.8
49 | 2024-12-08 | 3401.395 | -0.49048 | 2024-12-06 | 20421 | -2
50 | 2024-12-15 | 3408.632 | -0.40952 | 2024-12-12 | 20991 | -4.8
51 | 2024-12-22 | 2989.209 | -2.1143 | 2024-12-22 | 21016 | -10.5
52 | 2024-12-29 | 2783.16 | 1.2048 | 2024-12-23 | 20350 | -0.6
1 | 2025-01-05 | 2425.874 | -0.4 | 2025-01-05 | 20647 | -1
2 | 2025-01-12 | 3122.446 | -5.7095 | 2025-01-08 | 21504 | -6.6
3 | 2025-01-19 | 3073.46 | -3.7238 | 2025-01-16 | 21103 | -4.9
4 | 2025-01-26 | 3205.609 | -8.319 | 2025-01-22 | 22058 | -12
5 | 2025-02-02 | 3099.635 | -4.4762 | 2025-01-28 | 21092 | -5.1
6 | 2025-02-09 | 3112.475 | -3.5952 | 2025-02-05 | 20917 | -5.1
7 | 2025-02-16 | 3116.52 | -5.6286 | 2025-02-12 | 21115 | -6
8 | 2025-02-23 | 3096.877 | -7.2286 | 2025-02-19 | 21399 | -6.9
9 | 2025-03-02 | 2911.95 | -0.36667 | 2025-03-02 | 20232 | -5.3
10 | 2025-03-09 | 2836.548 | 1.5381 | 2025-03-03 | 19553 | 2.8
11 | 2025-03-16 | 2636.842 | 6.4333 | 2025-03-12 | 18720 | 0.9
12 | 2025-03-23 | 2626.909 | 5.7762 | 2025-03-17 | 18437 | 5.1
13 | 2025-03-30 | 2740.993 | 2.6714 | 2025-03-26 | 18565 | 3.8
14 | 2025-04-06 | 2616.332 | 5.5143 | 2025-04-02 | 19271 | 0.1
15 | 2025-04-13 | 2656.301 | 3.5143 | 2025-04-08 | 18508 | 1.1
16 | 2025-04-20 | 2463.399 | 9.6571 | 2025-04-16 | 17570 | 5.8
17 | 2025-04-27 | 2431.357 | 12.9714 | 2025-04-23 | 16501 | 15
18 | 2025-05-04 | 2422.202 | 12.2143 | 2025-05-01 | 16635 | 9.1
19 | 2025-05-11 | 2401.107 | 14.1952 | 2025-05-07 | 16320 | 23
20 | 2025-05-18 | 2500.327 | 18.5476 | 2025-05-16 | 18190 | 27.1
21 | 2025-05-25 | 2409.852 | 10.9952 | 2025-05-22 | 16664 | 10.8
22 | 2025-06-01 | 2412.068 | 15.2714 | 2025-05-28 | 16694 | 15.8
23 | 2025-06-08 | 2536.713 | 20.9333 | 2025-06-04 | 19623 | 31
24 | 2025-06-15 | 2531.677 | 19.9048 | 2025-06-11 | 18815 | 28
25 | 2025-06-22 | 2906.411 | 23.4048 | 2025-06-22 | 23182 | 34.8
26 | 2025-06-29 | 3142.408 | 25.1905 | 2025-06-24 | 24775 | 34.9
27 | 2025-07-06 | 3012.732 | 25.3048 | 2025-07-06 | 22563 | 34.2
28 | 2025-07-13 | 3222.327 | 26.0905 | 2025-07-12 | 22876 | 33.9
29 | 2025-07-20 | 3088.335 | 24.581 | 2025-07-16 | 23555 | 32.2
30 | 2025-07-27 | 3108.112 | 24.7048 | 2025-07-24 | 24399 | 33.2
31 | 2025-08-03 | 3042.594 | 24.8095 | 2025-07-28 | 24287 | 33
32 | 2025-08-10 | 3177.885 | 26.0238 | 2025-08-10 | 23996 | 32
33 | 2025-08-17 | 3311.213 | 26.2333 | 2025-08-11 | 24500 | 32.2
34 | 2025-08-24 | 2778.805 | 20.8857 | 2025-08-22 | 21032 | 26
35 | 2025-08-31 | 2507.418 | 17.1143 | 2025-08-25 | 17829 | 20.1
36 | 2025-09-07 | 2556.472 | 18.8238 | 2025-09-03 | 19590 | 26.8
37 | 2025-09-14 | 2598.283 | 19.419 | 2025-09-11 | 18587 | 24.9
38 | 2025-09-21 | 2652.341 | 19.8714 | 2025-09-18 | 19991 | 29.2
39 | 2025-09-28 | 2718.456 | 20.881 | 2025-09-23 | 19440 | 25
40 | 2025-10-05 | 2579.618 | 18.7238 | 2025-10-05 | 19379 | 26.9
41 | 2025-10-12 | 2545.678 | 14.9476 | 2025-10-06 | 20310 | 28
42 | 2025-10-19 | 2471.523 | 14.3762 | 2025-10-14 | 17088 | 21.2
43 | 2025-10-26 | 2571.18 | 9.4429 | 2025-10-23 | 17344 | 12.2
44 | 2025-11-02 | 2635.246 | 7.1714 | 2025-10-30 | 17825 | 7.9
45 | 2025-11-09 | 2719.497 | 6.3333 | 2025-11-09 | 19023 | -1.1
46 | 2025-11-16 | 2837.142 | 3.0476 | 2025-11-10 | 19827 | -2.9
47 | 2025-11-23 | 2844.141 | 3.9286 | 2025-11-17 | 19615 | 4.2
48 | 2025-11-30 | 2893.457 | 3.019 | 2025-11-27 | 19546 | 3
49 | 2025-12-07 | 3100.884 | -2.7762 | 2025-12-04 | 21541 | -4.9
50 | 2025-12-13 | 3648.047 | -5.1524 | 2025-12-08 | 21364 | -3.9
51 | 2025-12-21 | 3515.775 | -0.66667 | 2025-12-15 | 21321 | -4.8
52 | 2025-12-28 | 2119.727 | -1.6 | 2025-12-22 | 20284 | 3.2
1 | 2026-01-04 | 3046.55 | -5.1524 | 2026-01-04 | 20788 | -1.2
2 | 2026-01-11 | 3001.914 | 1.9048 | 2026-01-05 | 20994 | -0.1
3 | 2026-01-18 | 3110.401 | -2.7905 | 2026-01-15 | 21534 | -11
4 | 2026-01-25 | 3290.768 | -9.981 | 2026-01-25 | 22064 | -11
5 | 2026-02-01 | 3303.21 | -11.7571 | 2026-01-29 | 22022 | -12
6 | 2026-02-08 | 3258.679 | -9.3952 | 2026-02-08 | 21644 | -13.2
7 | 2026-02-15 | 3105.124 | -3.5476 | 2026-02-09 | 21821 | -8.1
8 | 2026-02-22 | 2957.738 | 0.87143 | 2026-02-18 | 20456 | -0.2
9 | 2026-03-01 | 3023.746 | -3.1238 | 2026-02-24 | 20716 | -4.2
10 | 2026-03-08 | 2890.173 | 2.481 | 2026-03-02 | 20333 | -5.1
11 | 2026-03-15 | 2811.66 | 4.8 | 2026-03-13 | 19212 | 1.2
12 | 2026-03-22 | 2909.913 | 1.4952 | 2026-03-17 | 20162 | -4.3
13 | 2026-03-29 | 2811.066 | 1.9667 | 2026-03-23 | 19045 | 2.2
14 | 2026-04-05 | 2632.186 | 8.681 | 2026-04-02 | 18042 | 3
15 | 2026-04-12 | 2680.52 | 5.0095 | 2026-04-07 | 18502 | 0.8
16 | 2026-04-19 | 2562.734 | 13.9571 | 2026-04-15 | 17354 | 18.9
17 | 2026-04-26 | 2542.087 | 8.8143 | 2026-04-20 | 17740 | 4.2
18 | 2026-05-03 | 2549.338 | 9.6048 | 2026-04-29 | 17203 | 9.8
19 | 2026-05-10 | 2492.546 | 11.5286 | 2026-05-05 | 17069 | 16.1
20 | 2026-05-17 | 2503.018 | 12.8381 | 2026-05-13 | 16991 | 13.9
21 | 2026-05-24 | 2558.967 | 15.881 | 2026-05-19 | 21046 | 30.1
22 | 2026-05-31 | 2551.364 | 19.4667 | 2026-05-26 | 19199 | 27.2
23 | 2026-06-07 | 2723.385 | 22.0524 | 2026-06-05 | 20602 | 30.8
24 | 2026-06-14 | 2982.273 | 22.8619 | 2026-06-11 | 22343 | 30.9
25 | 2026-06-21 | 2572.843 | 18.8619 | 2026-06-17 | 17820 | 22.1
26 | 2026-06-28 | 2751.215 | 20.4476 | 2026-06-28 | 20868 | 27.5
27 | 2026-07-05 | 3330.282 | 27.719 | 2026-07-02 | 24699 | 34
28 | 2026-07-12 | 3187.782 | 24.2238 | 2026-07-08 | 23449 | 28.9
29 | 2026-07-19 | 3217.668 | 25.5667 | 2026-07-14 | 25605 | 36.2
30 | 2026-07-26 | 2866.29 | 21.5762 | 2026-07-26 | 21281 | 27
31 | 2026-08-02 | 3108.281 | 24.0429 | 2026-07-31 | 23386 | 29.9
32 | 2026-08-09 | 3099.364 | 24.1286 | 2026-08-05 | 23016 | 28.9
33 | 2026-08-16 | 3091.113 | 23.8286 | 2026-08-10 | 22908 | 29.3
34 | 2026-08-23 | 2915.976 | 21.7143 | 2026-08-17 | 22093 | 26
35 | 2026-08-30 | 2802.544 | 20.9238 | 2026-08-27 | 20889 | 26.2
Back to main menu

## Table 1.4.2
Back to main menu
Table 1.4.2: Monthly Weather and Demand History
Month | Energy Demand (GWh) | Reported Embedded Generation (GWh) | Peak Demand (MW) | Average Hour (MW) | Minimum Hour (MW) | 90th Percentile (MW) | # of Hours Above 20,000MW (hrs) | Average Temperature (°C) | Weather Corrected Energy (GWh) | Forecasted Energy (GWh) | Energy Forecast MAPE | Peak Temperature (°C) | Weather Corrected Peak (MW) | Forecasted Peak (MW) | Peak Forecast MAPE
2002-05-31 | 11874.901 |  | 20068 | 15960.8884 | 12092 | 18344.4 | 1 | 12.4667 | 11661.943 | 11525.8367 | 1.167% | 27.9 | 20244.5263 | 19777 | 2.309%
2002-06-30 | 12185.238 |  | 23578 | 16923.9417 | 11537 | 20698 | 97 | 20.19 | 12055.7597 | 11830.544 | 1.868% | 30.7 | 23272.9209 | 21897 | 5.912%
2002-07-31 | 14033.343 |  | 25226 | 18862.0202 | 12348 | 23309.7 | 261 | 25.514 | 13532.3366 | 12956.0938 | 4.258% | 34.7 | 23653.7174 | 23007.2548 | 2.733%
2002-08-31 | 13748.878 |  | 25414 | 18479.6747 | 13077 | 22694.7 | 207 | 23.8785 | 13322.4613 | 12822.9862 | 3.749% | 33.4 | 24272.2514 | 22720.1818 | 6.394%
2002-09-30 | 12593.138 |  | 25062 | 17490.4694 | 12409 | 20801 | 114 | 21.43 | 12144.4221 | 11393.0328 | 6.187% | 33.5 | 21739.209 | 21099.9455 | 2.941%
2002-10-31 | 12397.839 |  | 21216 | 16663.7621 | 12244 | 19077.2 | 25 | 9.8516 | 12155.0684 | 12042.8325 | 0.9234% | 28.8 | 19901.5621 | 20319.2849 | 2.099%
2002-11-30 | 12655.667 |  | 21862 | 17577.3153 | 12709 | 20027.2 | 75 | 3.7489 | 12836.1101 | 12370.454 | 3.628% | 0.1 | 22314.4629 | 22421.8556 | 0.4813%
2002-12-31 | 13483.864 |  | 23334 | 18070.6062 | 13057 | 21021.7 | 197 | -1.2538 | 13500.9659 | 13362.8148 | 1.023% | -1.2 | 23550.9979 | 23522.7043 | 0.1201%
2003-01-31 | 14486.674 |  | 24158 | 19471.336 | 13236 | 22223.4 | 346 | -7.272 | 14211.1695 | 13919.5093 | 2.052% | -13.4 | 23893.0266 | 23850.0397 | 0.1799%
2003-02-28 | 13122.529 |  | 23469 | 19527.5729 | 14523 | 21982.3 | 315 | -6.0738 | 12808.0447 | 12426.863 | 2.976% | -10 | 22949.8962 | 23272.5444 | 1.406%
2003-03-31 | 13414.004 |  | 23117 | 18029.5753 | 13289 | 20781.2 | 142 | 0.44409 | 13159.4331 | 12901.8683 | 1.957% | -14.3 | 21751.8023 | 22090.2796 | 1.556%
2003-04-30 | 12097.332 |  | 21010 | 16801.85 | 12290 | 19540.6 | 53 | 6.7444 | 12069.9486 | 11760.2993 | 2.565% | -1.8 | 20846.9119 | 19850.9002 | 4.778%
2003-05-31 | 11627.445 |  | 18741 | 15628.2863 | 11604 | 17985.6 | 0 | 13.2559 | 11741.5567 | 11691.2195 | 0.4287% | 13.1 | 19844.7318 | 19853.0281 | 0.04181%
2003-06-30 | 11884.956 |  | 24753 | 16506.8833 | 11821 | 19404.9 | 58 | 19.6744 | 11841.7488 | 12214.3634 | 3.147% | 33.3 | 23523.3557 | 22798.6336 | 3.081%
2003-07-31 | 12897.586 |  | 23175 | 17335.4651 | 11957 | 20680.5 | 139 | 22.7849 | 12968.9604 | 13433.0128 | 3.578% | 31.3 | 23762.5491 | 23684.1903 | 0.3298%
2003-08-31 | 12514.308 |  | 23891 | 16820.3065 | 2270 | 21000.8 | 144 | 22.5495 | 12171.8874 | 13155.7383 | 8.083% | 31 | 23561.0011 | 23347.1957 | 0.9075%
2003-09-30 | 11794.469 |  | 20700 | 16381.2069 | 11802 | 19023.3 | 14 | 18.04 | 11779.2706 | 11789.027 | 0.08283% | 26.8 | 20307.2007 | 21599.7344 | 6.365%
2003-10-31 | 12159.932 |  | 20408 | 16343.9946 | 11941 | 18583.6 | 4 | 9.9935 | 12134.778 | 12368.2786 | 1.924% | 9.7 | 21259.1741 | 20666.6154 | 2.787%
2003-11-30 | 12389.858 |  | 21584 | 17208.1361 | 12724 | 19670.3 | 54 | 5.4578 | 12865.0242 | 12585.1188 | 2.176% | 13.4 | 22716.1034 | 22681.1697 | 0.1538%
2003-12-31 | 13327.663 |  | 22798 | 17779.9919 | 12550 | 20959.3 | 165 | 0.45591 | 13534.0494 | 13768.4138 | 1.732% | -5.6 | 23431.3362 | 23858.3895 | 1.823%
2004-01-31 | 14767.413 |  | 24937 | 19848.6734 | 13219 | 22977 | 399 | -8.5817 | 14323.0642 | 14191.7421 | 0.9169% | -19.7 | 24408.7438 | 24078.4061 | 1.353%
2004-02-29 | 13088.075 |  | 22608 | 18804.7055 | 14243 | 21145.5 | 249 | -2.554 | 13173.0548 | 13033.9545 | 1.056% | -3.9 | 23057.4279 | 23556.2598 | 2.163%
2004-03-31 | 13224.641 |  | 21634 | 17775.0551 | 13238 | 20123.3 | 84 | 2.9398 | 13203.0654 | 13279.366 | 0.5779% | -3.1 | 21870.1159 | 22452.4608 | 2.663%
2004-04-30 | 11792.132 |  | 19911 | 16377.9611 | 12427 | 18638.3 | 0 | 7.9389 | 11874.9664 | 11891.0349 | 0.1353% | 3.2 | 20525.8394 | 19942.5254 | 2.842%
2004-05-31 | 11835.269 |  | 20327 | 15907.6196 | 11983 | 18401.3 | 4 | 14.3634 | 11790.5055 | 11844.4455 | 0.4575% | 27.3 | 20053.0994 | 20166.6217 | 0.5661%
2004-06-30 | 12045.885 |  | 23163 | 16730.3958 | 12059 | 19989.2 | 72 | 18.8211 | 12217.9222 | 12553.0052 | 2.743% | 31.3 | 23163 | 23585.4466 | 1.824%
2004-07-31 | 12769.985 |  | 23976 | 17163.9583 | 12385 | 20583.8 | 94 | 21.7398 | 12930.3649 | 13366.3211 | 3.372% | 30.1 | 24618.2502 | 23677.3092 | 3.822%
2004-08-31 | 12746.297 |  | 23159 | 17132.1183 | 12223 | 20350.3 | 97 | 20.7581 | 12964.5229 | 13300.7716 | 2.594% | 28.6 | 23229.7881 | 23298.2624 | 0.2948%
2004-09-30 | 12369.687 |  | 21911 | 17180.1208 | 12285 | 20296.4 | 102 | 19.7733 | 12205.4933 | 11892.6387 | 2.563% | 25.8 | 20958.8749 | 21881.4147 | 4.402%
2004-10-31 | 12215.166 |  | 19829 | 16418.2339 | 12343 | 18770.5 | 0 | 11.7656 | 12456.5009 | 12357.6295 | 0.7937% | 8.8 | 20925.8279 | 21212.056 | 1.368%
2004-11-30 | 12601.008 |  | 22066 | 17501.4 | 12969 | 19980.6 | 71 | 5.8989 | 13148.5344 | 12864.0567 | 2.164% | 5 | 23333.9595 | 22748.6257 | 2.509%
2004-12-31 | 13981.717 |  | 24979 | 18705.2554 | 14169 | 21867.1 | 261 | -2.0914 | 13836.9923 | 13651.944 | 1.337% | -12.3 | 24073.4484 | 23404.0469 | 2.781%
2005-01-31 | 14619.18 |  | 24362 | 19649.4355 | 13545 | 22555.1 | 356 | -6.0849 | 14521.4247 | 14269.3901 | 1.736% | -14.5 | 24173.3301 | 23890.98 | 1.168%
2005-02-28 | 12731.835 |  | 22322 | 18946.183 | 14854 | 21241.5 | 249 | -2.7 | 12865.7476 | 12795.0929 | 0.5492% | -3.9 | 22791.1102 | 23507.03 | 3.141%
2005-03-31 | 13494.28 |  | 22724 | 18137.4731 | 13959 | 20632.1 | 143 | -0.29892 | 13288.2099 | 13401.8026 | 0.8548% | -8.5 | 22667.3301 | 22370.34 | 1.31%
2005-04-30 | 11827.861 |  | 19343 | 16427.5847 | 12279 | 18455.1 | 0 | 9.0533 | 12209.0045 | 12063.7878 | 1.189% | 10.9 | 20931.6333 | 20760.1 | 0.8195%
2005-05-31 | 11744.825 |  | 19007 | 15786.0551 | 11950 | 18139.5 | 0 | 13.2495 | 11734.2216 | 11928.3062 | 1.654% | 22.3 | 18687.7703 | 20306.03 | 8.659%
2005-06-30 | 13499.266 |  | 26157 | 18748.9806 | 12066 | 23349.8 | 260 | 23.7111 | 12679.5247 | 12284.376 | 3.116% | 31.6 | 24410.9107 | 23402.64 | 4.13%
2005-07-31 | 14094.375 |  | 26160 | 18944.0524 | 12109 | 23810.9 | 277 | 25.2505 | 13572.7661 | 13233.9731 | 2.496% | 34.6 | 25823.1716 | 23820.5 | 7.755%
2005-08-31 | 14031.29 |  | 25816 | 18859.2608 | 13487 | 22804.3 | 274 | 23.672 | 13565.2965 | 13465.8968 | 0.7327% | 32.9 | 24779.5218 | 23372.48 | 5.678%
2005-09-30 | 12552.618 |  | 23914 | 17434.1917 | 12541 | 20722.2 | 140 | 20.12 | 12367.9416 | 12151.9814 | 1.746% | 30.1 | 21719.6272 | 22078.34 | 1.652%
2005-10-31 | 12187.328 |  | 20752 | 16380.8172 | 12112 | 18944.1 | 22 | 11.9323 | 12126.6613 | 12472.8188 | 2.855% | 25.8 | 21108.1878 | 20922.81 | 0.8782%
2005-11-30 | 12440.55 |  | 22564 | 17278.5417 | 12548 | 20020.1 | 74 | 5.5967 | 12682.2654 | 12867.08 | 1.457% | -6.3 | 22614.2615 | 22937.6 | 1.43%
2005-12-31 | 13745.639 |  | 23766 | 18422.0914 | 12673 | 21484.9 | 250 | -2.7237 | 13620.1354 | 13796.3409 | 1.294% | -4.8 | 24097.0219 | 23641.84 | 1.889%
2006-01-31 | 13596.17 |  | 23052 | 18274.4207 | 13644 | 20907.3 | 189 | 0.7957 | 14274.4358 | 14424.4515 | 1.051% | -5 | 24238.2139 | 24284.96 | 0.1929%
2006-02-28 | 12568.25 | 196.7766 | 22321 | 18702.753 | 14051 | 20957.7 | 220 | -3.0024 | 12600.0722 | 12948.2914 | 2.764% | -0.9 | 22387.273 | 23800.5 | 6.313%
2006-03-31 | 13199.998 | 174.9678 | 21772 | 17741.9341 | 13274 | 20091.1 | 83 | 2.3215 | 13175.0216 | 13634.8299 | 3.49% | -2.2 | 22053.7104 | 22821.37 | 3.481%
2006-04-30 | 11512.852 | 209.6124 | 19582 | 15990.0722 | 12020 | 18469.4 | 0 | 9.45 | 11956.204 | 12047.9755 | 0.7676% | 3.7 | 20333.283 | 20910.04 | 2.837%
2006-05-31 | 11927.478 | 182.5572 | 24857 | 16031.5565 | 11812 | 18116.3 | 42 | 15.6548 | 11823.8872 | 12279.9916 | 3.857% | 32.8 | 21889.4457 | 21678.33 | 0.9645%
2006-06-30 | 12541.936 | 156.8548 | 23349 | 17419.3556 | 11957 | 20688.4 | 143 | 20.8756 | 12477.8857 | 12623.9122 | 1.17% | 30.6 | 23612.7463 | 23998.72 | 1.635%
2006-07-31 | 13853.619 | 105.9768 | 26092 | 18620.4556 | 12470 | 22948.8 | 269 | 24.6108 | 13347.7145 | 13679.2646 | 2.484% | 33.6 | 25257.3418 | 25397.46 | 0.5548%
2006-08-31 | 13308.1 | 102.0594 | 27005 | 17887.2312 | 12545 | 21104.2 | 172 | 22.2785 | 13263.4984 | 13630.8008 | 2.769% | 36.4 | 23880.5188 | 24805.29 | 3.872%
2006-09-30 | 11521.035 | 75.3164 | 19976 | 16001.4375 | 11796 | 18524.1 | 0 | 16.6411 | 11661.5416 | 12254.9406 | 5.089% | 28 | 21526.7648 | 23566.96 | 9.477%
2006-10-31 | 11962.307 | 112.2613 | 19590 | 16078.3696 | 11621 | 18409.9 | 0 | 9.7226 | 11803.3843 | 12521.8009 | 6.087% | 13.5 | 20459.0154 | 21498.15 | 5.079%
2006-11-30 | 12178.739 | 217.4506 | 21267 | 16914.9153 | 12720 | 19351.1 | 30 | 5.9711 | 12633.6484 | 12892.685 | 2.05% | 1.5 | 22968.2115 | 23080.82 | 0.4903%
2006-12-31 | 12884.176 | 213.476 | 22941 | 18010.0014 | 12246 | 20322.4 | 107 | 2.4269 | 13331.6936 | 13800.6488 | 3.518% | -5.5 | 23625.9393 | 24123.74 | 2.107%
2007-01-31 | 13758.097 | 206.1901 | 23537 | 17914.1888 | 12941 | 21448 | 243 | -2.2806 | 14060.0462 | 14347.6006 | 2.045% | -13.1 | 23776.8339 | 24407.33 | 2.652%
2007-02-28 | 13037.578 | 188.1128 | 23935 | 19401.1577 | 14894 | 21908 | 280 | -7.169 | 12657.9939 | 12799.7079 | 1.12% | -14 | 23053.0639 | 23805.23 | 3.263%
2007-03-31 | 13192.72 | 130.1285 | 22969 | 17732.1519 | 13331 | 20433.1 | 121 | 1.6097 | 13158.0262 | 13334.4268 | 1.341% | -12.5 | 22680.4017 | 22410.89 | 1.188%
2007-04-30 | 11827.647 | 154.9039 | 20016 | 16427.2875 | 11819 | 18975.2 | 1 | 7.2678 | 11883.5165 | 11833.3207 | 0.4224% | 4.1 | 21218.7001 | 20306.68 | 4.298%
2007-05-31 | 11818.634 | 186.5976 | 21490 | 15885.2608 | 11814 | 18653.5 | 33 | 15.9075 | 11715.6686 | 11997.9552 | 2.409% | 27.5 | 18881.5106 | 20882.55 | 10.6%
2007-06-30 | 12692.547 | 117.2711 | 25737 | 17628.5375 | 11699 | 21772.7 | 166 | 22.0044 | 12370.1039 | 12397.7724 | 0.2237% | 34.2 | 24968.2328 | 24501.25 | 1.87%
2007-07-31 | 12840.811 | 117.543 | 24561 | 17259.1546 | 11710 | 21065 | 133 | 22.6237 | 13020.6286 | 13470.8252 | 3.458% | 32.6 | 24937.0822 | 25524.57 | 2.356%
2007-08-31 | 13454.57 | 94.9993 | 25584 | 18084.0995 | 12293 | 22075.9 | 206 | 23.614 | 13116.9687 | 13368.0197 | 1.914% | 34.5 | 24566.9071 | 24734.55 | 0.6824%
2007-09-30 | 11916.219 | 59.8788 | 24046 | 16550.3042 | 11867 | 19637 | 51 | 19.5556 | 11730.0385 | 11853.5568 | 1.053% | 32.9 | 20976.0219 | 22636.33 | 7.915%
2007-10-31 | 11908.105 | 93.128 | 19233 | 16005.5175 | 11788 | 18411.2 | 0 | 15.0344 | 12052.1085 | 12419.5501 | 3.049% | 24.3 | 19607.6114 | 21554.34 | 9.928%
2007-11-30 | 12350.431 | 133.6983 | 21814 | 17153.3764 | 12371 | 19847.5 | 60 | 3.4744 | 12534.9107 | 12719.7604 | 1.475% | -0.3 | 22401.7023 | 22807.03 | 1.809%
2007-12-31 | 13407.761 | 151.2253 | 22935 | 17932.1102 | 13146 | 20760.6 | 189 | -1.8172 | 13302.9248 | 13588.2725 | 2.145% | -3.4 | 23142.7472 | 24122.74 | 4.235%
2008-01-31 | 13609.986 | 192.7611 | 22782 | 18292.9919 | 13556 | 20970.1 | 196 | -1.6978 | 13996.4363 | 13978.7473 | 0.1264% | -8 | 23324.016 | 23839.9286 | 2.212%
2008-02-29 | 12896.823 | 182.6809 | 23054 | 18529.9167 | 14295 | 21007 | 204 | -4.3287 | 12775.3563 | 12968.8203 | 1.514% | -9.3 | 22662.4184 | 23331.2989 | 2.951%
2008-03-31 | 13003.771 | 195.6356 | 20990 | 17478.1868 | 13902 | 19568.2 | 31 | -0.62903 | 12635.3784 | 12970.3688 | 2.651% | -1.6 | 21209.0269 | 21883.6734 | 3.181%
2008-04-30 | 11520.396 | 175.7789 | 19512 | 16000.55 | 11571 | 18116.5 | 0 | 10.6456 | 11872.3822 | 11698.943 | 1.461% | 14.1 | 21077.4953 | 20048.0315 | 4.884%
2008-05-31 | 11407.14 | 182.8544 | 18650 | 15332.1774 | 11465 | 17575.7 | 0 | 12.972 | 11443.4889 | 11735.9553 | 2.556% | 26.9 | 20139.9842 | 20210.7676 | 0.3515%
2008-06-30 | 12189.13 | 160.4473 | 24195 | 16929.3472 | 11764 | 20433.6 | 101 | 20.7033 | 11982.089 | 12103.6774 | 1.015% | 33.1 | 23724.3431 | 23892.0192 | 0.7068%
2008-07-31 | 13155.66 | 136.1417 | 23787 | 17682.3387 | 12035 | 21319.6 | 176 | 22.9054 | 13123.8184 | 13161.835 | 0.2897% | 30 | 24987.592 | 25231.8939 | 0.9777%
2008-08-31 | 12548.525 | 152.1998 | 22707 | 16866.297 | 11986 | 19786.9 | 65 | 20.6624 | 12703.1866 | 12926.0971 | 1.755% | 26.1 | 23579.6573 | 24477.7753 | 3.809%
2008-09-30 | 11793.462 | 123.1236 | 22975 | 16379.8083 | 12061 | 18964.3 | 41 | 18.1289 | 11692.7164 | 11529.5318 | 1.396% | 30.3 | 21404.2678 | 22290.904 | 4.142%
2008-10-31 | 11634.137 | 132.3682 | 19366 | 15637.2809 | 11450 | 17924.4 | 0 | 10.0656 | 11691.8059 | 12044.3073 | 3.015% | 4.8 | 19511.6562 | 20907.5479 | 7.154%
2008-11-30 | 11828.99 | 145.2536 | 21279 | 16429.1528 | 11881 | 19036.5 | 24 | 3.7756 | 12095.7719 | 12262.6183 | 1.379% | 3.8 | 22489.0231 | 22119.6095 | 1.643%
2008-12-31 | 13087.707 | 170.3211 | 22541 | 17555.7755 | 11992 | 20509.2 | 121 | -2.4763 | 12907.8943 | 13264.4707 | 2.762% | -3.7 | 22164.6447 | 23154.6001 | 4.466%
2009-01-31 | 13730.291 | 169.634 | 22983 | 18454.6922 | 13872 | 21036.7 | 199.392 | -7.6344 | 13535.4467 | 13686.8304 | 1.118% | -11.3 | 22667.0788 | 23813.0998 | 5.056%
2009-02-28 | 11697.974 | 165.2381 | 22110 | 17407.6994 | 13312 | 19675.5 | 47.712 | -2.5405 | 11749.4678 | 12296.9476 | 4.66% | -13.1 | 21808.7203 | 23220.5185 | 6.474%
2009-03-31 | 12166.882 | 173.3939 | 21466 | 16353.336 | 11855 | 18906.8 | 20.832 | 2.143 | 12165.27 | 12746.6818 | 4.779% | -9.6 | 20868.6368 | 21914.9455 | 5.014%
2009-04-30 | 10746.635 | 180.7399 | 18744 | 14925.8819 | 10790 | 17106.2 | 0 | 8.7178 | 10901.2606 | 11354.7401 | 4.16% | -0.5 | 20344.9145 | 20074.7226 | 1.328%
2009-05-31 | 10504.201 | 197.5122 | 17560 | 14118.5497 | 10794 | 16433.1 | 0 | 14.7226 | 10536.0659 | 11416.2719 | 8.354% | 28.6 | 18785.4908 | 20357.5736 | 8.369%
2009-06-30 | 10884.323 | 147.3338 | 22540 | 15117.1153 | 10678 | 17997.5 | 34.56 | 18.4178 | 11161.8895 | 11587.9581 | 3.817% | 30.7 | 23485.0159 | 23172.7205 | 1.33%
2009-07-31 | 11315.411 | 141.1481 | 20011 | 15208.8858 | 10786 | 18132.3 | 0.744 | 20.3344 | 12091.706 | 12626.1861 | 4.42% | 27.4 | 22352.287 | 24350.6569 | 8.94%
2009-08-31 | 12225.812 | 143.9902 | 24380 | 16432.543 | 11040 | 20682.7 | 122.016 | 21.8935 | 12113.2789 | 12370.0057 | 2.119% | 31.2 | 24120.5582 | 23669.6928 | 1.869%
2009-09-30 | 10931.831 | 112.68 | 19731 | 15183.0986 | 10890 | 18072.2 | 0 | 17.9767 | 10838.0625 | 10978.4771 | 1.296% | 25.1 | 19977.6676 | 21055.1421 | 5.393%
2009-10-31 | 11181.875 | 146.4268 | 18420 | 15029.4019 | 11295 | 17250.6 | 0 | 9.3043 | 11214.1928 | 11567.95 | 3.155% | 4.1 | 19464.8512 | 20214.6873 | 3.852%
2009-11-30 | 11112.909 | 186.1543 | 19710 | 15434.5958 | 11333 | 17812.7 | 0 | 6.9422 | 11605.7866 | 11858.5268 | 2.178% | 3.7 | 21501.2294 | 21361.9788 | 0.6476%
2009-12-31 | 12688.573 | 197.3074 | 21831 | 17054.5336 | 12293 | 19724.4 | 55.8 | -1.4763 | 12677.5761 | 12693.1919 | 0.1232% | -6.7 | 21730.9099 | 21919.3561 | 0.8672%
2010-01-31 | 13145.438 | 206.3791 | 22045 | 17668.5995 | 13075 | 20120.3 | 84.072 | -4.2796 | 13227.8161 | 13097.6605 | 0.984% | -7.3 | 22297.8804 | 22717.3216 | 1.881%
2010-02-28 | 11751.752 | 175.9426 | 21367 | 17487.7262 | 13243 | 19687.6 | 45.696 | -2.644 | 11777.6488 | 11804.099 | 0.2246% | -3.6 | 22020.4448 | 22459.742 | 1.995%
2010-03-31 | 11686.054 | 96.5068 | 19393 | 15707.0618 | 11951 | 17744.6 | 0 | 5.5548 | 12010.9613 | 12430.8985 | 3.496% | 2 | 21346.0734 | 21309.448 | 0.1716%
2010-04-30 | 10474.752 | 174.4465 | 17398 | 14548.2667 | 10618 | 16556.5 | 0 | 11.8533 | 10898.0905 | 10857.612 | 0.3714% | 3.6 | 19258.6821 | 18770.6298 | 2.534%
2010-05-31 | 11368.031 | 153.2328 | 22904 | 15279.6116 | 10914 | 18075.7 | 43.896 | 17.0323 | 10951.2917 | 10814.7613 | 1.247% | 31.4 | 21295.2011 | 18843.502 | 11.51%
2010-06-30 | 11555.961 | 145.4928 | 21527 | 16049.9458 | 11506 | 19165.4 | 43.92 | 20.2422 | 11538.1526 | 11411.3572 | 1.099% | 28.3 | 22474.9206 | 22550.9548 | 0.3383%
2010-07-31 | 13307.242 | 172.6285 | 25075 | 17886.078 | 11400 | 22219.6 | 223.944 | 24.5226 | 12903.2908 | 12442.4622 | 3.571% | 33.3 | 24049.6327 | 23498.3733 | 2.292%
2010-08-31 | 12921.565 | 148.0201 | 24917 | 17367.6949 | 11813 | 21949.3 | 154.752 | 23.5247 | 12462.2289 | 12301.8326 | 1.287% | 32.9 | 24202.4847 | 22972.5225 | 5.082%
2010-09-30 | 11049.081 | 177.8492 | 24444 | 15345.9458 | 11124 | 17783.9 | 34.56 | 17.6822 | 10949.8132 | 11055.5026 | 0.9652% | 32.4 | 21702.065 | 21442.7835 | 1.195%
2010-10-31 | 10929.335 | 220.7635 | 17704 | 14689.9664 | 10816 | 16634.7 | 0 | 11.3839 | 10983.9114 | 11228.8238 | 2.23% | 11.4 | 19199.6083 | 18855.0679 | 1.795%
2010-11-30 | 11303.778 | 237.219 | 19970 | 15699.6917 | 11584 | 17896.8 | 0 | 5.0711 | 11457.171 | 11620.4239 | 1.425% | 4.2 | 20712.8718 | 20717.7815 | 0.0237%
2010-12-31 | 12694.155 | 264.8843 | 22114 | 17062.0363 | 12614 | 19769 | 55.8 | -3.1946 | 12581.1214 | 12708.2117 | 1.01% | -11.6 | 21966.6139 | 21580.6272 | 1.757%
2011-01-31 | 13301.687 | 252.0926 | 22733 | 17878.6116 | 11835 | 20361.5 | 113.832 | -6.0312 | 13237.9305 | 13343.9086 | 0.8006% | -9 | 22876.7298 | 22270.5192 | 2.65%
2011-02-28 | 11775.464 | 233.9528 | 21871 | 17523.0119 | 13358 | 19879.6 | 53.088 | -4.0107 | 11710.5829 | 11979.6008 | 2.297% | -7.7 | 21660.2043 | 21982.186 | 1.487%
2011-03-31 | 12352.443 | 266.6101 | 20667 | 16602.746 | 12736 | 18528.7 | 8.184 | 0.46559 | 12318.7834 | 12467.2468 | 1.205% | -4.3 | 21179.9192 | 20550.1632 | 2.973%
2011-04-30 | 10789.012 | 282.9928 | 17945 | 14984.7389 | 11276 | 17112.6 | 0 | 7.8011 | 11022.5512 | 10965.5571 | 0.5171% | 5.2 | 19571.3477 | 18195.8466 | 7.028%
2011-05-31 | 10781.74 | 261.12 | 20847 | 14491.586 | 10799 | 16552 | 8.928 | 15.1258 | 10594.0641 | 10934.6882 | 3.215% | 29.3 | 18742.8072 | 18515.1791 | 1.214%
2011-06-30 | 11238.277 | 218.9465 | 22765 | 15608.7181 | 10890 | 18748.6 | 18 | 20.4978 | 11253.6631 | 11593.1744 | 3.017% | 33.3 | 22294.084 | 23107.108 | 3.647%
2011-07-31 | 13298.189 | 200.5274 | 25450 | 17873.9099 | 11529 | 21827.5 | 190.464 | 25.7946 | 12809.1348 | 12517.8651 | 2.274% | 37.5 | 23631.2692 | 23538.8355 | 0.3911%
2011-08-31 | 12531.706 | 189.0822 | 22051 | 16843.6909 | 12205 | 20167.4 | 84.072 | 23.0892 | 12292.4814 | 12538.1515 | 1.999% | 31.3 | 22208.747 | 23196.6756 | 4.448%
2011-09-30 | 11144.546 | 169.0598 | 21552 | 15478.5361 | 11300 | 18071.9 | 23.76 | 18.6522 | 11031.1087 | 10964.8288 | 0.6008% | 28.3 | 21317.1824 | 21238.6927 | 0.3682%
2011-10-31 | 11012.737 | 211.1046 | 18234 | 14802.0659 | 11124 | 16971.2 | 0 | 11.6097 | 10973.2195 | 11154.7901 | 1.655% | 4.7 | 18168.0995 | 18437.0481 | 1.48%
2011-11-30 | 11116.536 | 267.3446 | 19673 | 15439.6333 | 11284 | 17789 | 0 | 7.6078 | 11452.4357 | 11622.5291 | 1.485% | 5.6 | 21347.2844 | 20747.3335 | 2.81%
2011-12-31 | 12121.895 | 278.8385 | 20204 | 16292.8696 | 11974 | 18901.5 | 4.464 | 1.3043 | 12314.3757 | 12864.6619 | 4.469% | -1.3 | 20772.1165 | 21942.4375 | 5.634%
2012-01-31 | 12715.234 | 290.1431 | 21847 | 17090.3683 | 12439 | 19422.5 | 31.248 | -0.83763 | 12932.2873 | 13280.0235 | 2.689% | -14.3 | 22084.7322 | 22160.0997 | 0.3413%
2012-02-29 | 11610.18 | 259.7219 | 19956 | 16681.2931 | 13228 | 18709 | 0 | 0.41839 | 11380.2015 | 12202.5791 | 7.226% | 1.3 | 20756.8677 | 21813.8691 | 5.092%
2012-03-31 | 11487.527 | 304.436 | 20332 | 15440.2245 | 11250 | 17580.1 | 2.232 | 7.8925 | 11726.1779 | 12264.8125 | 4.593% | -2.8 | 20595.0545 | 20708.9072 | 0.5528%
2012-04-30 | 10641.371 | 287.2476 | 17874 | 14779.6819 | 11248 | 16598.3 | 0 | 8.6278 | 10883.4994 | 10866.5786 | 0.1555% | 4.1 | 19830.1533 | 18745.092 | 5.472%
2012-05-31 | 11136.995 | 273.7978 | 21106 | 14969.0793 | 10998 | 17581 | 13.392 | 18.0011 | 10838.5019 | 10943.6824 | 0.9704% | 28.6 | 19736.9901 | 19038.2309 | 3.54%
2012-06-30 | 11800.326 | 280.2738 | 24107 | 16389.3417 | 11017 | 20405.4 | 93.6 | 21.7878 | 11511.081 | 11398.2442 | 0.9802% | 34.2 | 22832.4909 | 22569.1521 | 1.153%
2012-07-31 | 13456.845 | 224.7422 | 24636 | 18087.1573 | 12425 | 22075.1 | 212.04 | 25.5516 | 13057.6199 | 12319.3311 | 5.654% | 36.2 | 23630.2664 | 23298.1422 | 1.406%
2012-08-31 | 12632.817 | 218.4517 | 23188 | 16979.5927 | 11676 | 20667.4 | 109.368 | 22.9667 | 12373.2613 | 12419.0386 | 0.37% | 30.1 | 22726.501 | 22956.5741 | 1.012%
2012-09-30 | 11040.767 | 215.7734 | 21183 | 15334.3986 | 11012 | 18710.3 | 23.04 | 17.5778 | 10900.4102 | 10811.3017 | 0.8175% | 27.1 | 20370.1157 | 20506.0631 | 0.6674%
2012-10-31 | 11141.991 | 278.1392 | 18829 | 14975.7944 | 11436 | 16974.5 | 0 | 11.0935 | 11149.8822 | 11199.8353 | 0.448% | 4.3 | 18684.153 | 18345.9037 | 1.81%
2012-11-30 | 11487.169 | 271.2616 | 20144 | 15954.4014 | 11824 | 18349.8 | 2.16 | 4.2867 | 11663.449 | 11629.6439 | 0.2898% | -3.7 | 20258.2258 | 20571.5606 | 1.547%
2012-12-29 | 12156.557 | 285.1456 | 20382 | 17466.3175 | 12670 | 18764.9 | 9.672 | 1.4419 | 12306.8289 | 12612.0073 | 2.48% | -1 | 20910.8981 | 21693.287 | 3.742%
2013-01-31 | 12889.507 | 301.2556 | 22610 | 16274.6301 | 12270 | 20123.6 | 83.328 | -1.7989 | 13061.0693 | 13314.3055 | 1.939% | -11.6 | 22610 | 22013.997 | 2.636%
2013-02-28 | 11742.246 | 289.301 | 21426 | 17473.5804 | 13638 | 19632.9 | 38.976 | -3.6452 | 11668.8474 | 11819.7381 | 1.293% | -5.8 | 21333.0082 | 21773.6201 | 2.065%
2013-03-31 | 11958.319 | 350.9198 | 19825 | 16073.0094 | 11963 | 18101.1 | 0 | 0.98602 | 11869.9986 | 12283.0437 | 3.48% | -1.8 | 20784.4526 | 20634.9497 | 0.7193%
2013-04-30 | 10944.906 | 354.007 | 18854 | 15201.2583 | 11209 | 17185.7 | 0 | 6.9567 | 11090.2932 | 11018.1303 | 0.6507% | 2.3 | 19284.8182 | 18492.3312 | 4.109%
2013-05-31 | 10785.424 | 362.6957 | 20488 | 14496.5376 | 10765 | 16610.7 | 4.464 | 16.5247 | 10533.5712 | 10932.3105 | 3.785% | 29.9 | 18341.9804 | 19100.9692 | 4.138%
2013-06-30 | 11174.679 | 290.1226 | 22662 | 15520.3875 | 10816 | 18354.4 | 43.2 | 19.9844 | 11283.4325 | 11406.4319 | 1.09% | 31.6 | 22719.4401 | 22499.2459 | 0.9692%
2013-07-31 | 12722.707 | 357.4735 | 24927 | 17100.4126 | 11506 | 21288 | 122.76 | 23.2097 | 12736.3503 | 12479.5529 | 2.016% | 34.3 | 24352.1456 | 23212.9348 | 4.678%
2013-08-31 | 12100.351 | 398.7601 | 22833 | 16263.9126 | 11139 | 20243.4 | 84.816 | 22.1183 | 12084.9413 | 12227.7513 | 1.182% | 28.2 | 23255.371 | 22359.7987 | 3.851%
2013-09-30 | 10837.167 | 336.0942 | 22682 | 15051.6208 | 11003 | 17399.6 | 20.88 | 17.26 | 10767.0057 | 11015.3041 | 2.306% | 33.9 | 20422.3176 | 20513.3592 | 0.4458%
2013-10-31 | 11135.689 | 352.2154 | 18445 | 14967.3239 | 11018 | 17040.1 | 0 | 11.7849 | 11114.0467 | 11279.1846 | 1.486% | 6.6 | 18981.007 | 18388.3002 | 3.123%
2013-11-30 | 11640.948 | 422.4146 | 20615 | 16167.9833 | 11571 | 18660.2 | 8.64 | 2.53 | 11709.7788 | 11686.9287 | 0.1951% | -3.3 | 20034.8189 | 20326.4941 | 1.456%
2013-12-31 | 12702.006 | 329.2647 | 21964 | 17072.5887 | 12626 | 19937.2 | 66.216 | -3.5086 | 12528.9266 | 12699.9803 | 1.365% | -8.3 | 21184.5386 | 21395.0558 | 0.9937%
2014-01-31 | 13613.596 | 400.6012 | 22774 | 18297.8441 | 13381 | 20167.4 | 87.048 | -7.8516 | 13409.7767 | 13356.427 | 0.3978% | -17.4 | 22043.8439 | 22319.8106 | 1.252%
2014-02-28 | 12067.276 | 336.7994 | 21905 | 17957.256 | 13981 | 20340.8 | 109.536 | -7.1464 | 11812.9441 | 11748.3799 | 0.5466% | -12.2 | 21218.2216 | 20964.0592 | 1.198%
2014-03-31 | 12672.074 | 436.3629 | 21656 | 17032.3575 | 13296 | 18156.7 | 8.928 | -2.8688 | 12242.1563 | 12054.5719 | 1.532% | -12.1 | 20728.4579 | 19906 | 3.968%
2014-04-30 | 10836.804 | 477.6859 | 18557 | 15051.1167 | 11944 | 16454 | 0 | 7.3289 | 11038.5265 | 10731.1367 | 2.785% | -0.9 | 19249.9632 | 17649 | 8.317%
2014-05-31 | 10642.583 | 485.0087 | 18844 | 14304.547 | 10719 | 16623.2 | 0 | 15.3871 | 10546.4252 | 10790.2174 | 2.312% | 29.4 | 18750.4605 | 18964 | 1.139%
2014-06-30 | 11228.548 | 467.8886 | 20807 | 15595.2056 | 10723 | 17232.9 | 0 | 21.0889 | 11140.5499 | 11346.2756 | 1.847% | 30.3 | 20705.1957 | 22469.55 | 8.521%
2014-07-31 | 11717.444 | 448.354 | 21300 | 15749.2527 | 11321 | 19790.1 | 63.984 | 21.471 | 12324.9268 | 12360.0815 | 0.2852% | 29.8 | 22294.8035 | 22948.69 | 2.933%
2014-08-31 | 11718.183 | 386.2556 | 21363 | 15750.246 | 11362 | 19044 | 47.616 | 21.3172 | 11819.2371 | 11992.5131 | 1.466% | 31.3 | 21644.3547 | 21403.44 | 1.113%
2014-09-30 | 10836.546 | 423.8321 | 21123 | 15050.7583 | 11112 | 19853.4 | 61.2 | 17.9967 | 10671.4853 | 10579.5258 | 0.8617% | 31.4 | 19449.0766 | 19023.2704 | 2.189%
2014-10-31 | 10819.853 | 438.5968 | 17784 | 14542.8132 | 10769 | 16432.6 | 0 | 11.6849 | 10814.1957 | 11126.7565 | 2.89% | 9.1 | 18447.2196 | 18638.7361 | 1.038%
2014-11-30 | 11487.634 | 407.9288 | 20102 | 15955.0472 | 12082 | 17109.3 | 0 | 2.2756 | 11410.1121 | 11497.4835 | 0.7657% | 0.8 | 19923.2587 | 20302.34 | 1.903%
2014-12-31 | 12131.525 | 425.9567 | 20938 | 16305.8132 | 11398 | 17611.5 | 0 | 0.52366 | 12256.0958 | 12769.4956 | 4.189% | -1.2 | 21582.6701 | 21237.74 | 1.598%
2015-01-31 | 13119.979 | 462.7948 | 21814 | 17634.3804 | 13344 | 19048.7 | 26.784 | -6.6624 | 12937.1182 | 13068.9431 | 1.019% | -15.7 | 21503.4489 | 22293.59 | 3.674%
2015-02-28 | 12302.278 | 399.7277 | 21494 | 18306.9613 | 14588 | 18778.7 | 5.376 | -11.4369 | 11740.7311 | 11528.5197 | 1.807% | -15.8 | 19709.6284 | 21016.81 | 6.632%
2015-03-31 | 12044.976 | 495.7729 | 20827 | 16189.4839 | 12675 | 18117.4 | 5.208 | -0.59892 | 11748.227 | 11856.8161 | 0.9243% | -9.6 | 20109.8817 | 19840.93 | 1.337%
2015-04-30 | 10404.962 | 653.4141 | 18462 | 14451.3361 | 10975 | 16390.3 | 0 | 8.6044 | 10624.618 | 10542.0267 | 0.7774% | 2.4 | 19362.8308 | 18121.2 | 6.412%
2015-05-31 | 10547.132 | 529.8747 | 19158 | 14176.2527 | 10657 | 16587.6 | 0 | 17.772 | 10231.5964 | 10635.9243 | 3.952% | 28.8 | 17881.7583 | 19370.33 | 8.325%
2015-06-30 | 10624.316 | 577.9038 | 19339 | 14755.9944 | 10804 | 17220.7 | 0 | 18.9767 | 10908.724 | 11410.2692 | 4.598% | 25.5 | 20554.6293 | 22276.64 | 8.378%
2015-07-31 | 12105.066 | 521.3404 | 22516 | 16270.25 | 11010 | 19756.8 | 61.752 | 23.0602 | 12273.6405 | 12174.2184 | 0.81% | 32.5 | 22638.5319 | 22888.49 | 1.104%
2015-08-31 | 11797.099 | 472.2223 | 22383 | 15856.3159 | 11414 | 19007.1 | 46.872 | 21.8011 | 11782.7212 | 11821.2763 | 0.3272% | 32.1 | 22383 | 21463.69 | 4.107%
2015-09-30 | 11361.901 | 503.8076 | 22063 | 15780.4181 | 10927 | 19812.8 | 61.92 | 20.7778 | 10718.9879 | 10512.648 | 1.925% | 32.6 | 19299.6325 | 18485 | 4.221%
2015-10-31 | 10687.264 | 497.6939 | 17667 | 14364.6022 | 10539 | 16384.2 | 0 | 10.829 | 10731.7474 | 11150.1256 | 3.899% | 13.1 | 18444.3181 | 18339 | 0.571%
2015-11-30 | 10681.592 | 477.3161 | 19239 | 14835.5444 | 11338 | 17157.4 | 0 | 7.5422 | 10867.5486 | 11595.0899 | 6.695% | 1.9 | 19631.9089 | 20306 | 3.434%
2015-12-31 | 11313.857 | 435.4307 | 19161 | 15206.797 | 10811 | 17642 | 0 | 4.8495 | 11784.7123 | 12611.2501 | 7.014% | 6.8 | 20418.0801 | 21160.04 | 3.634%
2016-01-31 | 12384.867 | 471.7938 | 20836 | 16646.3266 | 12116 | 19066 | 24.552 | -2.6 | 12523.599 | 12982.1466 | 3.661% | -11.8 | 21249.7402 | 22360.24 | 5.226%
2016-02-29 | 11471.763 | 474.1135 | 20766 | 16482.4181 | 12533 | 18707.5 | 4.872 | -1.2391 | 11502.97 | 11806.8997 | 2.642% | -10 | 20194.6163 | 20985.25 | 3.915%
2016-03-31 | 11302.963 | 530.5494 | 20063 | 15192.1546 | 11717 | 17387.3 | 0.744 | 3.6194 | 11445.7227 | 11758.7447 | 2.735% | -7.9 | 20324.618 | 20075.21 | 1.227%
2016-04-30 | 10409.92 | 661.3944 | 17821 | 14458.2222 | 11286 | 16583.2 | 0 | 5.97 | 10578.9099 | 10309.6515 | 2.545% | 0.6 | 18912.1728 | 17405.08 | 7.969%
2016-05-31 | 10470.808 | 665.3817 | 19885 | 14073.6667 | 10461 | 17171.1 | 0 | 15.9602 | 10115.8584 | 10530.0143 | 4.094% | 27.2 | 19707.6447 | 19235.65 | 2.395%
2016-06-30 | 11101.521 | 613.5199 | 21692 | 15418.7792 | 10596 | 18447.4 | 24.48 | 21.52 | 11141.3797 | 11378.6081 | 2.129% | 34 | 21568.912 | 22315.7305 | 3.462%
2016-07-31 | 12497.616 | 548.7117 | 22659 | 16797.871 | 10985 | 20860.1 | 143.592 | 25.0882 | 12345.0421 | 11896.1402 | 3.636% | 35 | 22288.7672 | 22599.9414 | 1.396%
2016-08-31 | 13113.359 | 534.2805 | 23100 | 17625.4825 | 12287 | 21278.8 | 183.768 | 25.4183 | 12295.9028 | 11771.834 | 4.262% | 34.8 | 22375.997 | 21440.3166 | 4.182%
2016-09-30 | 11072.26 | 523.2114 | 23213 | 15378.1389 | 10855 | 18825.3 | 42.48 | 20.6733 | 10659.2295 | 10401.8861 | 2.414% | 34.5 | 19712.7154 | 18289 | 7.222%
2016-10-31 | 10518.677 | 417.6305 | 18189 | 14138.0067 | 10663 | 16351 | 0 | 12.6344 | 10453.1463 | 10947.5325 | 4.73% | 5.2 | 18394.9922 | 18079 | 1.718%
2016-11-30 | 10697.637 | 418.8378 | 19369 | 14857.8292 | 11211 | 17154.5 | 0 | 7.5167 | 10913.6011 | 11524.026 | 5.593% | 0.2 | 19544.7667 | 20296 | 3.844%
2016-12-31 | 11978.041 | 435.9647 | 20688 | 16099.5175 | 11684 | 18666.1 | 10.416 | -1.129 | 11950.5536 | 12430.7427 | 4.018% | -8.1 | 20286.7849 | 20888 | 2.964%
2017-01-31 | 12108.005 | 463.9501 | 20372 | 16274.2003 | 12246 | 18425.1 | 2.232 | -1.1495 | 12369.7298 | 12818.8508 | 3.631% | -3.3 | 20965.9674 | 21913.73 | 4.52%
2017-02-28 | 10607.563 | 490.9519 | 19838 | 15785.064 | 11867 | 18064.6 | 0 | 0.47143 | 10787.4931 | 11294.713 | 4.702% | -1.1 | 20379.4501 | 20966.2287 | 2.879%
2017-03-31 | 11591.031 | 560.1987 | 19174 | 15579.3427 | 12158 | 17608.2 | 0 | 0.46667 | 11413.3465 | 11824.0632 | 3.599% | -8.1 | 18692.3503 | 20137.3 | 7.73%
2017-04-30 | 9788.616 | 594.6314 | 17349 | 13595.3 | 10167 | 15576.2 | 0 | 10.6278 | 10105.7565 | 10366.7129 | 2.582% | 7.3 | 18482.7844 | 17969.79 | 2.776%
2017-05-31 | 10153.182 | 619.1188 | 17738 | 13646.75 | 10249 | 15622.5 | 0 | 13.4538 | 10012.8427 | 10576.9018 | 5.633% | 29.6 | 18260.3078 | 19193.19 | 5.109%
2017-06-30 | 10657.08 | 578.0093 | 21168 | 14801.5 | 10518 | 17663.4 | 7.2 | 20.6422 | 10682.999 | 11159.3312 | 4.459% | 32.4 | 21144.8187 | 22454.87 | 6.196%
2017-07-31 | 11587.63 | 582.9578 | 20627 | 15574.7715 | 10806 | 19028.7 | 17.112 | 22.8473 | 11851.6211 | 11984.7355 | 1.123% | 31.5 | 22152.8524 | 22492.73 | 1.534%
2017-08-31 | 11350.012 | 559.5215 | 20158 | 15255.3925 | 10829 | 18577.9 | 5.208 | 21.228 | 11513.597 | 12105.5471 | 5.141% | 30 | 21323.3584 | 22376.43 | 4.939%
2017-09-30 | 10679.393 | 484.1858 | 21786 | 14832.4903 | 10487 | 18795.6 | 25.2 | 19.9789 | 10155.927 | 10494.2948 | 3.332% | 31.3 | 17821.4732 | 19490.21 | 9.364%
2017-10-31 | 10339.329 | 532.8493 | 17418 | 13896.9476 | 10534 | 15857.7 | 0 | 14.4925 | 10260.3837 | 10942.7953 | 6.651% | 26.5 | 17407.7858 | 18030.62 | 3.578%
2017-11-30 | 10955.909 | 497.8786 | 19115 | 15216.5403 | 11199 | 17381.1 | 0 | 4.6056 | 10946.7668 | 11371.7451 | 3.882% | 3 | 19195.4397 | 20230.97 | 5.395%
2017-12-31 | 12338.893 | 402.8257 | 20306 | 16584.5336 | 12093 | 18875.6 | 5.952 | -4.1731 | 12096.0133 | 12303.6865 | 1.717% | -4.1 | 21439.6493 | 20901.44 | 2.51%
2018-01-31 | 12700.826 | 533.4365 | 20906 | 17071.0027 | 12453 | 19337.8 | 14.88 | -4.6452 | 12679.8037 | 12685.9178 | 0.04822% | -15.2 | 20177.5339 | 21618.93 | 7.144%
2018-02-28 | 10951.065 | 496.4596 | 20076 | 16296.2277 | 12716 | 18608.6 | 1.344 | -0.70714 | 11081.1365 | 11074.1738 | 0.06283% | -8.2 | 20042.2165 | 20242.21 | 0.9979%
2018-03-31 | 11372.42 | 596.6609 | 18462 | 15285.5108 | 12158 | 17159.9 | 0 | 0.8828 | 11267.3415 | 11423.555 | 1.386% | 0.2 | 19330.8728 | 19551.97 | 1.144%
2018-04-30 | 10578.368 | 586.9588 | 18011 | 14692.1778 | 11497 | 16647.2 | 0 | 4.37 | 10586.2978 | 10157.8502 | 4.047% | 2.4 | 18107.9593 | 17669.81 | 2.42%
2018-05-31 | 10421.469 | 664.6636 | 20473 | 14007.3508 | 10541 | 16770.4 | 10.416 | 18.4376 | 10081.137 | 10289.6502 | 2.068% | 30.7 | 19262.1307 | 18817.47 | 2.308%
2018-06-30 | 10923.446 | 602.8769 | 21369 | 15171.4528 | 10698 | 18437.3 | 37.44 | 20.7522 | 10980.4534 | 10863.4062 | 1.066% | 30.2 | 20626.9619 | 21890.0001 | 6.123%
2018-07-31 | 12685.981 | 517.157 | 22909 | 17051.0497 | 11413 | 20705.3 | 140.616 | 24.6247 | 12483.776 | 11652.7714 | 6.657% | 33.2 | 22409.0792 | 22076.0001 | 1.486%
2018-08-31 | 12688.795 | 531.4383 | 21990 | 17054.832 | 11966 | 20622.8 | 120.528 | 24.1731 | 12040.5393 | 11685.5744 | 2.948% | 31.7 | 21385.6483 | 21946.0001 | 2.62%
2018-09-30 | 11147.31 | 480.938 | 23240 | 15482.375 | 10701 | 19596.5 | 56.88 | 19.9011 | 10579.1906 | 10189.9802 | 3.679% | 33.9 | 19505.5646 | 19019 | 2.494%
2018-10-31 | 10717.348 | 485.4689 | 18205 | 14405.0376 | 10847 | 16419.1 | 0 | 9.9258 | 10526.7735 | 10750.0648 | 2.121% | 26.1 | 17751.4152 | 17788 | 0.2061%
2018-11-30 | 11360.321 | 423.7495 | 20152 | 15778.2236 | 11765 | 17927.3 | 0.72 | 2.12 | 11184.9393 | 11170.7506 | 0.1269% | -6.6 | 19266.3918 | 19828 | 2.915%
2018-12-31 | 11938.614 | 407.6369 | 19891 | 16046.5242 | 12284 | 18215.4 | 0 | 0.47097 | 12019.553 | 12007.3958 | 0.1011% | -1.4 | 20375.1864 | 20503 | 0.6273%
2019-01-31 | 12777.216 | 463.966 | 21525 | 17173.6774 | 12291 | 19588.2 | 41.664 | -5.9118 | 12688.8389 | 12973.2132 | 2.241% | -11.8 | 21058.2817 | 21506 | 2.126%
2019-02-28 | 11291.744 | 455.9299 | 20500 | 16803.1905 | 13041 | 19051 | 8.736 | -3.4405 | 11212.4836 | 11162.2057 | 0.4484% | -10.1 | 20420.3692 | 20008 | 2.019%
2019-03-31 | 11658.678 | 588.34 | 20263 | 15670.2661 | 12210 | 17519 | 2.232 | -0.036022 | 11458.0531 | 11522.1982 | 0.5598% | -9 | 19573.6921 | 19457 | 0.5962%
2019-04-30 | 10264.505 | 597.1531 | 17645 | 14256.2569 | 11079 | 16133.5 | 0 | 7.3189 | 10432.2785 | 10252.9314 | 1.719% | 2.8 | 18796.3299 | 17548 | 6.641%
2019-05-31 | 10219.56 | 574.423 | 16784 | 13735.9677 | 10328 | 15586.7 | 0 | 13.0312 | 10218.7126 | 10412.0446 | 1.892% | 8.2 | 17977.0308 | 18663 | 3.816%
2019-06-30 | 10365.619 | 600.8034 | 20248 | 14396.6931 | 10564 | 17336.5 | 2.88 | 19.5056 | 10608.5215 | 10939.3571 | 3.119% | 28.9 | 21239.1838 | 21623 | 1.807%
2019-07-31 | 12792.766 | 606.5726 | 21791 | 17194.578 | 11565 | 20646.4 | 145.824 | 24.6344 | 12446.1887 | 11763.9974 | 5.481% | 31.4 | 21120.5208 | 22061 | 4.453%
2019-08-31 | 11825.052 | 555.2842 | 21354 | 15893.8871 | 11280 | 19305.9 | 40.92 | 22.4419 | 11798.5843 | 11598.2109 | 1.698% | 30.2 | 22490.4547 | 21200 | 5.738%
2019-09-30 | 10318.533 | 482.8673 | 19717 | 14331.2958 | 10477 | 16722 | 0 | 18.74 | 10167.6302 | 10564.4926 | 3.903% | 28.6 | 18958.9757 | 19469.84 | 2.695%
2019-10-31 | 10351.05 | 505.1513 | 18329 | 13912.7016 | 10739 | 15950.2 | 0 | 11.7903 | 10446.8836 | 10788.0047 | 3.265% | 31.2 | 18814.592 | 17559 | 6.674%
2019-11-30 | 11255.325 | 452.3729 | 19625 | 15632.3958 | 11711 | 17850 | 0 | 1.6178 | 11094.2081 | 11194.6524 | 0.9054% | -4.1 | 19001.8635 | 19597 | 3.132%
2019-12-31 | 11997.095 | 447.2177 | 20974 | 16125.1277 | 11787 | 18657.6 | 11.16 | -0.23333 | 12094.1802 | 12086.6766 | 0.06204% | -7.8 | 20974 | 20307 | 3.18%
2020-01-31 | 12178.575 | 426.7563 | 19928 | 16369.0524 | 12353 | 18557.8 | 0 | -0.75161 | 12460.9405 | 12859.4588 | 3.198% | -8.5 | 21137.8728 | 21185.0004 | 0.223%
2020-02-29 | 11239.82 | 490.212 | 19630 | 16149.1667 | 12683 | 18163 | 0 | -1.9977 | 11253.1814 | 11586.6754 | 2.964% | -10.4 | 19776.0281 | 19917.0004 | 0.7128%
2020-03-31 | 10989.389 | 585.8152 | 18183 | 14770.6841 | 11120 | 16702.6 | 0 | 4.1634 | 11058.3098 | 11522.322 | 4.196% | 5.4 | 19680.948 | 19377.0004 | 1.544%
2020-04-30 | 9282.854 | 642.7441 | 15350 | 12892.8528 | 10379 | 14231.4 | 0 | 7.01 | 9383.3554 | 10229.1483 | 9.014% | 4.4 | 16515.7848 | 17302.0004 | 4.76%
2020-05-31 | 9642.117 | 671.1773 | 20649 | 12959.8347 | 9831 | 15246.8 | 3.72 | 13.3968 | 9306.4436 | 9434.378 | 1.375% | 30.6 | 18761.2836 | 17426 | 7.117%
2020-06-30 | 10800.015 | 634.4604 | 21292 | 15000.0208 | 10340 | 18996.7 | 20.88 | 22.0667 | 10596.6512 | 10274.389 | 3.041% | 31.2 | 20741.8718 | 20034 | 3.413%
2020-07-31 | 13202.706 | 617.8423 | 24446 | 17745.5726 | 12154 | 21827.4 | 188.232 | 26.2043 | 12529.7172 | 11731.6936 | 6.369% | 34 | 24057.7367 | 22364.4404 | 7.038%
2020-08-31 | 12081.08 | 578.6123 | 23823 | 16238.0108 | 11221 | 20133.6 | 82.584 | 23.2366 | 12338.1938 | 11441.5908 | 7.267% | 31.9 | 25317.7535 | 21631.4406 | 14.56%
2020-09-30 | 10114.374 | 551.2872 | 20225 | 14047.7417 | 10834 | 16340.6 | 1.44 | 17.9378 | 10011.2355 | 10356.1124 | 3.445% | 27.4 | 19254.2062 | 20312.4408 | 5.496%
2020-10-31 | 10339.39 | 528.3272 | 17679 | 13897.0296 | 10645 | 16042.5 | 0 | 10.371 | 10349.5982 | 10040.7873 | 2.984% | 7 | 17587.3164 | 17039.9727 | 3.112%
2020-11-30 | 10529.032 | 524.2466 | 19147 | 14623.6556 | 10808 | 17008.6 | 0 | 7.763 | 10693.8532 | 10531.6058 | 1.517% | 0.1 | 19416.1975 | 18891.9134 | 2.7%
2020-12-31 | 11811.675 | 485.452 | 20738 | 15875.9073 | 12389 | 18200.4 | 3.72 | 0.31505 | 11932.8039 | 11815.0887 | 0.9865% | -6.8 | 20975.3455 | 19805.1651 | 5.579%
2021-01-31 | 12105.158 | 409.653 | 20150 | 16270.3737 | 12798 | 18344.9 | 1.488 | -1.9591 | 12307.6071 | 12539.1611 | 1.881% | -8.4 | 20951.6431 | 21176.0005 | 1.071%
2021-02-28 | 11233.123 | 456.7989 | 20318 | 16715.9568 | 13200 | 18799.9 | 3.36 | -4.306 | 11144.3783 | 11073.4765 | 0.6362% | -6.9 | 20175.4672 | 20760.0005 | 2.897%
2021-03-31 | 11101.706 | 690.6151 | 19344 | 14921.6478 | 11659 | 16933 | 0 | 4.6086 | 11249.5616 | 11497.7125 | 2.206% | -0.8 | 19868.2566 | 19384.0005 | 2.437%
2021-04-30 | 9781.57 | 596.9459 | 16644 | 13585.5139 | 10498 | 15264.1 | 0 | 8.98 | 10097.7166 | 10244.8035 | 1.457% | 4.8 | 17618.7846 | 17070.0009 | 3.115%
2021-05-31 | 10086.333 | 622.8177 | 19443 | 13556.8992 | 10782 | 15777.1 | 0 | 15.1602 | 9986.9371 | 10152.0681 | 1.653% | 31.6 | 18021.5172 | 18055.3342 | 0.1876%
2021-06-30 | 11262.474 | 611.5113 | 22258 | 15642.325 | 11304 | 19635.9 | 59.76 | 22.9889 | 10840.8856 | 10747.5852 | 0.8606% | 31.6 | 21528.4908 | 22162.0009 | 2.943%
2021-07-31 | 11636.443 | 611.3859 | 21655 | 15640.3804 | 11108 | 19487.8 | 49.848 | 22.2151 | 11970.9832 | 11806.5074 | 1.374% | 31.7 | 22251.4821 | 22413.0005 | 0.7259%
2021-08-31 | 12856.511 | 581.7597 | 22986 | 17280.2567 | 10853 | 21313.1 | 188.976 | 24.7634 | 12072.0791 | 11706.2663 | 3.03% | 33.1 | 21854.4728 | 22235.0005 | 1.741%
2021-09-30 | 10389.017 | 544.7746 | 18769 | 14429.1903 | 10426 | 16782 | 0 | 18.74 | 10401.3058 | 10472.6839 | 0.6862% | 26 | 18979.8917 | 21212.0005 | 11.76%
2021-10-31 | 10516.14 | 524.146 | 17312 | 14134.5968 | 10779 | 16116.7 | 0 | 14.3432 | 10429.4829 | 10365.0376 | 0.6179% | 21.95 | 17606.8602 | 17270.7147 | 1.909%
2021-11-30 | 10956.602 | 515.9736 | 19644 | 15217.5028 | 11605 | 17496.4 | 0 | 4.74 | 11017.3258 | 10886.7659 | 1.185% | 0.15 | 19684.7166 | 19227.38 | 2.323%
2021-12-31 | 11969.602 | 476.8031 | 20455 | 16088.1747 | 12517 | 18342.8 | 2.976 | 2.0215 | 12185.9418 | 11984.4925 | 1.653% | -2.3 | 21331.5579 | 20088.8968 | 5.825%
2022-01-31 | 13085.388 | 489.3876 | 21349 | 17587.8871 | 12491 | 19796.7 | 55.056 | -7.0054 | 12928.5532 | 12536.9576 | 3.029% | -12.1 | 21334.1018 | 20983.6671 | 1.643%
2022-02-28 | 11487.734 | 515.5153 | 20918 | 17094.8423 | 13761 | 19171.3 | 14.112 | -3.5488 | 11400.5165 | 11208.712 | 1.682% | -9.8 | 20782.3287 | 20446.0004 | 1.618%
2022-03-31 | 11816.835 | 611.8729 | 19763 | 15882.8427 | 12285 | 17932.4 | 0 | 1.929 | 11793.6956 | 11617.5125 | 1.494% | -5.2 | 19941.2707 | 19401.3338 | 2.708%
2022-04-30 | 10265.047 | 646.6282 | 17256 | 14257.0097 | 11430 | 16016.1 | 0 | 7.5244 | 10311.1592 | 10239.112 | 0.6987% | 6.6 | 17752.3935 | 17251.0005 | 2.824%
2022-05-31 | 10469.914 | 677.424 | 21292 | 14072.4651 | 10485 | 16297 | 8.928 | 17.0151 | 10137.6947 | 10372.2878 | 2.314% | 32.2 | 20136.0014 | 18269.0005 | 9.272%
2022-06-30 | 10929.858 | 654.792 | 21954 | 15180.3583 | 10627 | 18994.9 | 43.2 | 21.0744 | 11002.2267 | 10967.9836 | 0.3112% | 34.6 | 22101.7092 | 22161.0005 | 0.2683%
2022-07-31 | 12343.623 | 588.0453 | 22607 | 16590.8911 | 11449 | 20039.3 | 77.376 | 24.086 | 12411.016 | 11893.9057 | 4.167% | 34.2 | 22484.9516 | 22542.0005 | 0.2537%
2022-08-31 | 12624.254 | 603.8346 | 21871 | 16968.0833 | 11830 | 20450 | 99.696 | 23.6763 | 11998.9314 | 12028.3221 | 0.2449% | 30.5 | 23477.9346 | 22430.0005 | 4.463%
2022-09-30 | 10814.096 | 493.97 | 20350 | 15019.5778 | 11082 | 17965.3 | 2.88 | 18.7344 | 10678.4907 | 10551.0851 | 1.193% | 29.2 | 20446.2276 | 21489.0005 | 5.1%
2022-10-31 | 10384.167 | 567.3429 | 17294 | 13957.2137 | 10820 | 15961.1 | 0 | 11.6301 | 10447.0825 | 10603.0084 | 1.493% | 8.9 | 17724.6236 | 17559.0005 | 0.9344%
2022-11-30 | 11044.181 | 489.5672 | 19441 | 15339.1403 | 10931 | 17734 | 0 | 6.0933 | 11128.3255 | 11151.0711 | 0.2044% | -3.6 | 19389.6575 | 19812.0005 | 2.178%
2022-12-31 | 12273.23 | 460.9624 | 20173 | 16496.2769 | 12417 | 18629 | 2.232 | 0.16129 | 12412.7534 | 12191.9609 | 1.779% | 0.8 | 20584.5241 | 20241.0005 | 1.669%
2023-01-31 | 12519.712 | 376.932 | 20486 | 16827.5699 | 12603 | 18821.9 | 4.464 | 8.3011 | 13052.768 | 12663.6554 | 2.981% | 8 | 21435.1399 | 21170.3338 | 1.235%
2023-02-28 | 11225.17 | 505.7145 | 21388 | 16704.122 | 12990 | 19014 | 10.08 | -0.72976 | 11325.8235 | 11375.0622 | 0.4347% | -15.5 | 20433.0112 | 20892.3338 | 2.248%
2023-03-31 | 11846.269 | 623.4296 | 18811 | 15922.4046 | 12940 | 17656 | 0 | 1.6882 | 11814.7494 | 11846.6528 | 0.27% | -0.1 | 19000.8853 | 19701.0485 | 3.685%
2023-04-30 | 10271.638 | 587.4763 | 17547 | 14266.1639 | 11117 | 15920.1 | 0 | 10.0774 | 10374.8437 | 10349.2653 | 0.2465% | 5.4 | 19103.3719 | 17785.9996 | 6.896%
2023-05-31 | 10356.75 | 675.0171 | 20787 | 13920.3629 | 10859 | 15783.1 | 5.208 | 15.1742 | 10473.6584 | 10418.8057 | 0.5237% | 29.9 | 18001.5877 | 18869.9996 | 4.824%
2023-06-30 | 11119.814 | 599.2129 | 21463 | 15444.1861 | 11438 | 18666.1 | 23.04 | 20.5444 | 11230.6805 | 10652.496 | 5.148% | 31.6 | 22417.4764 | 21884.9996 | 2.375%
2023-07-31 | 12507.785 | 591.493 | 22686 | 16811.539 | 11987 | 20318.4 | 102.672 | 23.3629 | 12455.0186 | 11858.9002 | 4.786% | 30.95 | 23368.3724 | 22445.9996 | 3.947%
2023-08-31 | 11828.62 | 564.0255 | 21364 | 15898.6828 | 11629 | 18779.7 | 17.856 | 21.272 | 12005.3253 | 12249.9171 | 2.037% | 29.1 | 21865.1956 | 22396.9996 | 2.432%
2023-09-30 | 10997.556 | 494.2157 | 23713 | 15274.3833 | 11402 | 18088.3 | 43.92 | 19.6733 | 10685.1004 | 10718.9739 | 0.317% | 32.1 | 21317.3942 | 21479.9996 | 0.7628%
2023-10-31 | 10932.34 | 461.1476 | 20849 | 14694.0054 | 11260 | 16853.6 | 5.952 | 13.4688 | 10757.1302 | 10593.967 | 1.517% | 30 | 19208.5675 | 17668.0452 | 8.02%
2023-11-30 | 11456.562 | 454.778 | 20579 | 15911.8917 | 12555 | 18103 | 2.88 | 4.66 | 11478.5016 | 11007.299 | 4.105% | -1.5 | 20453.2108 | 19742.0453 | 3.477%
2023-12-31 | 12065.5 | 427.7837 | 20004 | 16217.0699 | 12029 | 18506.6 | 0.744 | 3.0699 | 12384.2261 | 12018.94 | 2.95% | 3 | 21211.1571 | 20346.0453 | 4.079%
2024-01-31 | 13036.084 | 436.2955 | 21081 | 17521.6183 | 13750 | 19526.1 | 26.04 | -1.8882 | 13208.8176 | 12929.406 | 2.115% | -9 | 21405.4347 | 21418.2553 | 0.05989%
2024-02-29 | 11516.766 | 515.0876 | 19624 | 16547.0776 | 12975 | 18418 | 0 | 1.231 | 11729.9509 | 11956.6273 | 1.932% | -3 | 20022.691 | 20987.7553 | 4.82%
2024-03-31 | 11542.29 | 590.9683 | 18902 | 15513.8306 | 12598 | 17286.8 | 0 | 4.7065 | 11632.2959 | 11836.2413 | 1.753% | -1.8 | 18939.8337 | 19645.2454 | 3.724%
2024-04-30 | 10489.417 | 651.5238 | 17947 | 14568.6347 | 11368 | 16245.8 | 0 | 9.56 | 10650.6806 | 10616.6408 | 0.3196% | 6.1 | 18586.0743 | 17839.6154 | 4.016%
2024-05-31 | 10735.152 | 649.7686 | 20402 | 14428.9677 | 11280 | 16339.7 | 6.696 | 17.5914 | 10640.585 | 10660.6544 | 0.1886% | 29.1 | 19498.7984 | 19148.7554 | 1.795%
2024-06-30 | 11566.905 | 625.1741 | 23803 | 16065.1458 | 11298 | 19934.3 | 69.84 | 21.0956 | 11334.1111 | 10892.6773 | 3.895% | 34.2 | 22585.2284 | 22502.1655 | 0.3678%
2024-07-31 | 13072.592 | 622.0428 | 23206 | 17570.6882 | 11159 | 21098.8 | 184.512 | 23.7667 | 12956.8035 | 12334.9116 | 4.8% | 31.1 | 23182.1746 | 22729.3704 | 1.953%
2024-08-31 | 12666.051 | 541.4969 | 23110 | 17024.2621 | 12063 | 20495.1 | 113.832 | 22.3538 | 12419.372 | 12432.5962 | 0.1065% | 29.1 | 22518.533 | 22592.9271 | 0.3304%
2024-09-30 | 11321.751 | 509.8347 | 21643 | 15724.6542 | 11633 | 18533 | 14.4 | 20.0589 | 10932.1478 | 11042.347 | 1.008% | 28 | 21462.7165 | 21998.022 | 2.494%
2024-10-31 | 10992.867 | 533.6771 | 18117 | 14775.3589 | 11730 | 16621.4 | 0 | 13.2301 | 11048.6213 | 11073.6096 | 0.2262% | 21.2 | 18603.2901 | 17976.8176 | 3.368%
2024-11-30 | 11312.89 | 458.6703 | 19212 | 15712.3472 | 12378 | 17631.1 | 0 | 7.1389 | 11494.5336 | 11500.099 | 0.04842% | 5.8 | 19942.2233 | 20217.9361 | 1.383%
2024-12-31 | 12959.601 | 445.067 | 21016 | 17418.8185 | 13155 | 19552.8 | 34.968 | -0.25484 | 13046.7703 | 12626.6472 | 3.22% | -10.5 | 21342.8087 | 21036.6297 | 1.435%
2025-01-31 | 13668.714 | 511.7658 | 22058 | 18371.9274 | 13626 | 20564 | 148.056 | -4.7839 | 13661.657 | 13253.9945 | 2.984% | -12 | 22379.5336 | 21835.8361 | 2.429%
2025-02-28 | 12278.547 | 424.9022 | 21399 | 16503.4234 | 14670 | 20182.3 | 96.096 | -4.2048 | 12130.7045 | 11671.9004 | 3.782% | -6.9 | 21116.0479 | 21259.4124 | 0.6789%
2025-03-31 | 12057.659 | 627.9253 | 20232 | 16206.5309 | 12515 | 18017.4 | 2.232 | 3.3323 | 12091.2745 | 12058.4394 | 0.2716% | -5.3 | 19614.4739 | 20000.0174 | 1.966%
2025-04-30 | 10837.309 | 643.6038 | 19271 | 14566.2755 | 11805 | 16902.1 | 0 | 8.5978 | 10891.1786 | 10619.601 | 2.494% | 0.1 | 19246.3001 | 18154.8411 | 5.671%
2025-05-31 | 10784.244 | 639.538 | 18190 | 14494.9516 | 11648 | 16270.8 | 0 | 14.3613 | 10886.6628 | 10649.1943 | 2.181% | 27.1 | 18891.1849 | 19064.5516 | 0.9177%
2025-06-30 | 11845.624 | 633.9965 | 24775 | 15921.5376 | 11639 | 20141.9 | 77.04 | 22.01 | 11544.6629 | 11223.7937 | 2.779% | 34.9 | 22678.4237 | 22279.0506 | 1.761%
2025-07-31 | 13905.926 | 604.4885 | 24399 | 18690.7608 | 12762 | 22537.1 | 279 | 25.4108 | 13471.3387 | 12424.9641 | 7.767% | 33.2 | 23249.8525 | 23168.1551 | 0.3514%
2025-08-31 | 12930.485 | 545.7734 | 24500 | 17379.6841 | 12184 | 22130.4 | 155.496 | 22.5892 | 12734.6294 | 12363.8608 | 2.911% | 32.2 | 23530.1953 | 22782.3554 | 3.178%
2025-09-30 | 11276.887 | 458.924 | 19991 | 15157.1062 | 12093 | 18262.3 | 0 | 19.7033 | 11125.7506 | 11069.0052 | 0.51% | 29.2 | 21192.8937 | 21288.0486 | 0.449%
2025-10-31 | 11319.417 | 481.3716 | 20310 | 15214.2702 | 11805 | 17125.2 | 1.488 | 12.943 | 11323.7934 | 11076.979 | 2.18% | 28 | 18572.3296 | 18320.7967 | 1.354%
2025-11-30 | 12026.73 | 415.8447 | 19827 | 16164.9597 | 13242 | 18499.4 | 0 | 4.2522 | 12004.1764 | 11562.3458 | 3.681% | -2.9 | 19963.3073 | 20153.1936 | 0.9512%
2025-12-31 | 13676.513 | 407.8892 | 21541 | 18382.4099 | 14548 | 20160.6 | 97.464 | -2.686 | 13529.2595 | 12900.8568 | 4.645% | -4.9 | 21487.8851 | 21447.1157 | 0.1897%
2026-01-31 | 14011.783 | 477.182 | 22064 | 18833.0417 | 14781 | 20879.6 | 220.224 | -5.5957 | 13936.0376 | 13826.1993 | 0.7882% | -11 | 22160.5721 | 22550.57 | 1.76%
2026-02-28 | 12373.552 | 436.1314 | 21821 | 16631.1183 | 14595 | 20375.4 | 110.88 | -3.8238 | 12322.8763 | 12168.7162 | 1.251% | -8.1 | 21428.1773 | 21686.2 | 1.204%
2026-03-31 | 12605.429 | 598.5443 | 20333 | 16942.7809 | 13270 | 18781.8 | 5.952 | 3.1204 | 12592.449 | 12554.0826 | 0.3047% | -5.1 | 19889.5794 | 20412.11 | 2.627%
2026-04-30 | 11126.138 | 602.9352 | 18502 | 14954.4866 | 12484 | 17173.6 | 0 | 9.0556 | 11195.2801 | 10995.8665 | 1.781% | 0.8 | 19288.6539 | 18337.2522 | 4.932%
2026-05-31 | 11184.72 | 651.7871 | 21046 | 15033.2258 | 11945 | 16593.3 | 3.72 | 14.1581 | 11155.5649 | 11100.8529 | 0.4904% | 30.1 | 19401.3919 | 19510.8225 | 0.564%
2026-06-30 | 11967.926 | 653.2155 | 23494 | 16085.922 | 12513 | 20025.2 | 72.72 | 21.4244 | 11932.5336 | 11828.0828 | 0.8753% | 34.2 | 23371.3311 | 23042.9438 | 1.405%
2026-07-31 | 13920.584 | 592.5681 | 25605 | 18710.4624 | 13184 | 22393.8 | 248.496 | 24.5849 | 13701.3716 | 12841.511 | 6.276% | 36.2 | 24298.8266 | 23592.6172 | 2.906%
2026-08-31 | 13180.451 | 545 | 23016 | 17715.6599 | 13012 | 21056.2 | 161.448 | 22.6204 | 13018.1365 | 12548.2185 | 3.61% | 28.9 | 23142.9682 | 22878.6943 | 1.142%
Back to main menu

## Table 1.4.3
Back to main menu
Table 1.4.3: Monthly Consumption by Market Participant Type
| Monthly Energy Demand (GWh) |  |  |  |  | Monthly Peak Demand (MW)
Month | Energy Demand | LDC Consumption | Wholesale Consumption | Generator Consumption | Losses | Peak Demand | LDC Consumption | Wholesale Consumption | Generator Consumption | Losses
2002-05-31 | 11874.901 | 9466.601 | 2081.739 | 140.146 | 186.415 | 20068 | 16707.96 | 2841.338 | 157.638 | 361.064
2002-06-30 | 12185.238 | 9864.032 | 2012.067 | 134.504 | 174.635 | 23578 | 20428.91 | 2643.003 | 137.661 | 368.426
2002-07-31 | 14033.343 | 11576.297 | 2018.911 | 150.335 | 287.8 | 25226 | 22063.8 | 2415.473 | 134.548 | 612.179
2002-08-31 | 13748.878 | 11167.443 | 2096.774 | 176.548 | 308.113 | 25414 | 21694.54 | 2594.581 | 196.459 | 928.42
2002-09-30 | 12593.138 | 10114.337 | 2050.509 | 142.07 | 286.222 | 25062 | 21577.29 | 2561.387 | 144.599 | 778.724
2002-10-31 | 12397.839 | 9862.483 | 2137.213 | 149.407 | 248.736 | 21216 | 17642.04 | 2820.526 | 141.773 | 611.661
2002-11-30 | 12655.667 | 10127.444 | 2112.743 | 143.845 | 271.635 | 21862 | 18381.47 | 2755.733 | 168.79 | 556.007
2002-12-31 | 13483.864 | 11037.036 | 2023.317 | 170.222 | 253.289 | 23334 | 19815.43 | 2740.625 | 146.763 | 631.182
2003-01-31 | 14486.674 | 11888.726 | 2187.64 | 167.688 | 242.62 | 24158 | 20778.8 | 2817.494 | 154.589 | 407.117
2003-02-28 | 13122.529 | 10715.513 | 1981.331 | 156.006 | 269.679 | 23469 | 20024.81 | 2805.901 | 215.791 | 422.498
2003-03-31 | 13414.004 | 10768.113 | 2192.28 | 167.167 | 286.444 | 23117 | 19689.78 | 2885.733 | 187.437 | 354.05
2003-04-30 | 12097.332 | 9624.429 | 2088.532 | 161.837 | 222.534 | 21010 | 17771.1 | 2657.654 | 196.626 | 384.62
2003-05-31 | 11627.445 | 9165.532 | 2114.832 | 143.984 | 203.097 | 18741 | 15387.78 | 2817.187 | 186.956 | 349.077
2003-06-30 | 11884.956 | 9582.859 | 1921.764 | 167.923 | 212.41 | 24753 | 21586.53 | 2263.442 | 188.539 | 714.489
2003-07-31 | 12897.586 | 10664.835 | 1835.72 | 158.334 | 238.697 | 23175 | 20435.12 | 2212.712 | 162.441 | 364.727
2003-08-31 | 12514.308 | 10340.948 | 1783.823 | 170.359 | 219.178 | 23891 | 20915.12 | 2358.598 | 184.046 | 433.236
2003-09-30 | 11794.469 | 9431.235 | 1977.11 | 167.921 | 218.203 | 20700 | 17454.71 | 2612.308 | 163.716 | 469.266
2003-10-31 | 12159.932 | 9686.179 | 2067.456 | 198.093 | 208.204 | 20408 | 16887.17 | 2775.37 | 298.908 | 446.552
2003-11-30 | 12389.858 | 9948.111 | 2036.796 | 175.8 | 229.151 | 21584 | 17991.12 | 2782.01 | 190.243 | 620.627
2003-12-31 | 13327.663 | 10932.665 | 1969.767 | 183.865 | 241.366 | 22798 | 19265.16 | 2834.078 | 176.349 | 522.413
2004-01-31 | 14767.413 | 12198.477 | 2104.447 | 198.64 | 265.849 | 24937 | 21481.3 | 2721.368 | 264.033 | 470.299
2004-02-29 | 13088.075 | 10672.632 | 1970.306 | 177.544 | 267.593 | 22608 | 19037.09 | 2699.003 | 255.4771 | 616.4299
2004-03-31 | 13224.641 | 10655.46 | 2122.051 | 169.56 | 277.57 | 21634 | 18016.84 | 2626.161 | 277.468 | 713.531
2004-04-30 | 11792.132 | 9440.718 | 1965.52 | 135.051 | 250.843 | 19911 | 16643.61 | 2707.734 | 178.464 | 381.192
2004-05-31 | 11835.269 | 9342.564 | 2043.903 | 155.45 | 293.352 | 20327 | 17063.54 | 2516.653 | 165.742 | 581.065
2004-06-30 | 12045.885 | 9547.152 | 2052.914 | 164.35 | 281.469 | 23163 | 19707.77 | 2663.11 | 157.95 | 634.17
2004-07-31 | 12769.985 | 10306.992 | 1967.079 | 177.05 | 318.864 | 23976 | 20506.23 | 2491.816 | 166.45 | 811.504
2004-08-31 | 12746.297 | 10241.325 | 2047.405 | 178.064 | 279.503 | 23159 | 19644.67 | 2631.637 | 186.377 | 696.316
2004-09-30 | 12369.687 | 9861.224 | 2065.015 | 156.763 | 286.685 | 21911 | 18334.65 | 2713.43 | 146.421 | 716.499
2004-10-31 | 12215.166 | 9633.603 | 2153.798 | 167.2 | 260.565 | 19829 | 16245.53 | 2899.387 | 159.471 | 524.612
2004-11-30 | 12601.008 | 10046.497 | 2070.218 | 187.926 | 296.367 | 22066 | 18138.28 | 2941.28 | 297.978 | 688.462
2004-12-31 | 13981.717 | 11434.513 | 2017.175 | 194.386 | 335.643 | 24979 | 21447.05 | 2662.278 | 196.875 | 672.797
2005-01-31 | 14619.18 | 12016.966 | 2090.334 | 198.56 | 313.32 | 24362 | 21030.26 | 2558.497 | 208.777 | 564.466
2005-02-28 | 12731.835 | 10393.346 | 1913.32 | 153.437 | 271.732 | 22322 | 18828.79 | 2715.305 | 226.273 | 551.632
2005-03-31 | 13494.28 | 10952.794 | 2055.749 | 195.636 | 290.101 | 22724 | 19266.54 | 2706.327 | 202.516 | 548.617
2005-04-30 | 11827.861 | 9388.13 | 1980.341 | 188.9 | 270.49 | 19343 | 15820.59 | 2789.575 | 261.253 | 471.582
2005-05-31 | 11744.825 | 9333.369 | 1989.317 | 174.521 | 247.618 | 19007 | 15617.54 | 2700.374 | 152.414 | 536.672
2005-06-30 | 13499.266 | 11095.068 | 1907.147 | 169.877 | 327.174 | 26157 | 22535.89 | 2563.391 | 200.283 | 857.436
2005-07-31 | 14094.375 | 11641.796 | 1878.941 | 191.549 | 382.089 | 26160 | 22580.23 | 2333.553 | 242.33 | 1003.887
2005-08-31 | 14031.29 | 11407.667 | 2030.291 | 207.892 | 385.44 | 25816 | 22243.61 | 2430.247 | 216.422 | 925.721
2005-09-30 | 12552.618 | 10024.722 | 1983.19 | 197.067 | 347.639 | 23914 | 20335.88 | 2512.888 | 216.241 | 848.991
2005-10-31 | 12187.328 | 9837.039 | 1904.417 | 177.228 | 268.644 | 20752 | 17598.01 | 2427.417 | 178.481 | 548.092
2005-11-30 | 12440.55 | 10179.434 | 1831.654 | 164.858 | 264.604 | 22564 | 19415.04 | 2459.517 | 173.174 | 516.269
2005-12-31 | 13745.639 | 11400.567 | 1858.136 | 196.651 | 290.285 | 23766 | 20461.34 | 2428.282 | 252.777 | 623.601
2006-01-31 | 13596.17 | 11188.909 | 1905.583 | 187.931 | 313.747 | 23052 | 19542.59 | 2540.335 | 211.234 | 757.841
2006-02-28 | 12568.25 | 10421.74 | 1719.011 | 163.583 | 263.916 | 22321 | 18801.15 | 2538.497 | 239.103 | 742.25
2006-03-31 | 13199.998 | 10803.314 | 1939.387 | 173.782 | 283.515 | 21772 | 18543.05 | 2487.994 | 178.339 | 562.617
2006-04-30 | 11512.852 | 9215.929 | 1861.338 | 153.612 | 281.973 | 19582 | 16298.82 | 2556.562 | 160.219 | 566.399
2006-05-31 | 11927.478 | 9647.028 | 1867.851 | 176.75 | 235.849 | 24857 | 21656.22 | 2407.501 | 238.276 | 555.003
2006-06-30 | 12541.936 | 10215.528 | 1875.843 | 193.439 | 257.126 | 23349 | 20111.81 | 2383.145 | 176.614 | 677.431
2006-07-31 | 13853.619 | 11539.169 | 1830.002 | 187.291 | 297.157 | 26092 | 22600.56 | 2398.848 | 185.769 | 906.823
2006-08-31 | 13308.1 | 10969.255 | 1903.683 | 161.696 | 273.466 | 27005 | 23709.23 | 2399.945 | 170.879 | 724.946
2006-09-30 | 11521.035 | 9386.092 | 1789.232 | 159.352 | 186.359 | 19976 | 16932.17 | 2457.453 | 175.436 | 410.941
2006-10-31 | 11962.307 | 9829.599 | 1745.321 | 150.308 | 237.079 | 19590 | 16650.66 | 2371.199 | 188.448 | 379.693
2006-11-30 | 12178.739 | 10018.7 | 1734.991 | 163.953 | 261.095 | 21267 | 18187.39 | 2295.35 | 204.2 | 580.06
2006-12-31 | 12884.176 | 10733.116 | 1708.01 | 162.411 | 280.639 | 22941 | 19873.93 | 2164.479 | 207.483 | 695.108
2007-01-31 | 13758.097 | 11458.472 | 1823.005 | 161.93 | 314.69 | 23537 | 20372.37 | 2394.209 | 185.55 | 584.871
2007-02-28 | 13037.578 | 11013.358 | 1619.551 | 142.892 | 261.777 | 23935 | 20829.21 | 2384.199 | 165.209 | 556.382
2007-03-31 | 13192.72 | 10931.852 | 1833.514 | 178.988 | 248.366 | 22969 | 19865.96 | 2417.187 | 260.159 | 425.694
2007-04-30 | 11827.647 | 9668.557 | 1776.836 | 165.698 | 216.556 | 20016 | 16660.53 | 2684.113 | 161.312 | 510.045
2007-05-31 | 11818.634 | 9589.524 | 1804.081 | 202.45 | 222.579 | 21490 | 18256.83 | 2306.318 | 236.902 | 689.95
2007-06-30 | 12692.547 | 10502.573 | 1730.187 | 186.088 | 273.699 | 25737 | 22461.02 | 2385.343 | 177.232 | 713.405
2007-07-31 | 12840.811 | 10640.371 | 1719.629 | 188.169 | 292.642 | 24561 | 21500.94 | 2264.306 | 200.085 | 595.669
2007-08-31 | 13454.57 | 11202.657 | 1742.24 | 199.774 | 309.899 | 25584 | 22471.59 | 2135.841 | 233.451 | 743.118
2007-09-30 | 11916.219 | 9815.422 | 1676.489 | 184.25 | 240.058 | 24046 | 20805.99 | 2324.986 | 195.763 | 719.261
2007-10-31 | 11908.105 | 9825.783 | 1715.497 | 148.482 | 218.343 | 19233 | 16516.44 | 2203.376 | 131.916 | 381.268
2007-11-30 | 12350.431 | 10287.772 | 1677.403 | 169.532 | 215.724 | 21814 | 19071.32 | 2102.755 | 159.15 | 480.775
2007-12-31 | 13407.761 | 11284.385 | 1674.218 | 171.179 | 277.979 | 22935 | 19842.07 | 2253.562 | 206.111 | 633.257
2008-01-31 | 13609.986 | 11443.712 | 1728.704 | 166.817 | 270.753 | 22782 | 19743.18 | 2259.941 | 188.114 | 590.765
2008-02-29 | 12896.823 | 10838.401 | 1633.662 | 147.825 | 276.935 | 23054 | 19969.28 | 2349.389 | 165.128 | 570.203
2008-03-31 | 13003.771 | 10838.211 | 1720.417 | 173.083 | 272.06 | 20990 | 17994.66 | 2205.371 | 217.193 | 572.776
2008-04-30 | 11520.396 | 9367.341 | 1699.281 | 151.486 | 302.288 | 19512 | 16522.2 | 2326.748 | 194.598 | 468.454
2008-05-31 | 11407.14 | 9211.31 | 1732.848 | 162.026 | 300.956 | 18650 | 15591.79 | 2431.522 | 170.796 | 455.892
2008-06-30 | 12189.13 | 9970.632 | 1736.46 | 170.098 | 311.94 | 24195 | 21012.33 | 2343.515 | 181.583 | 657.572
2008-07-31 | 13155.66 | 10881.08 | 1770.797 | 177.722 | 326.061 | 23787 | 20810.26 | 2200.689 | 153.239 | 622.812
2008-08-31 | 12548.525 | 10286.646 | 1787.408 | 173.04 | 301.431 | 22707 | 19448.08 | 2289.167 | 231.554 | 738.199
2008-09-30 | 11793.462 | 9611.373 | 1755.254 | 170.494 | 256.341 | 22975 | 20077.14 | 2198.497 | 161.722 | 537.641
2008-10-31 | 11634.137 | 9611.594 | 1645.026 | 164.976 | 212.541 | 19366 | 16642.02 | 2071.701 | 179.135 | 473.144
2008-11-30 | 11828.99 | 9989.561 | 1418.322 | 179.317 | 241.79 | 21279 | 18309.22 | 1826.499 | 227.767 | 915.514
2008-12-31 | 13087.707 | 11170.594 | 1413.875 | 191.224 | 312.014 | 22541 | 19782.98 | 1874.284 | 198.588 | 685.148
2009-01-31 | 13730.291 | 11751.74 | 1506.224 | 184.672 | 287.655 | 22983 | 19479.27 | 1824.502 | 239.3108 | 1439.9172
2009-02-28 | 11697.974 | 10037.791 | 1242.672 | 159.759 | 257.752 | 22110 | 18884.05 | 1763.431 | 255.6966 | 1206.8224
2009-03-31 | 12166.882 | 10357.06 | 1375.926 | 158.075 | 275.821 | 21466 | 16832.38 | 1780.814 | 221.7559 | 2631.0501
2009-04-30 | 10746.635 | 9088.459 | 1224.828 | 201.2 | 232.148 | 18744 | 15030.25 | 1775.23 | 295.5305 | 1642.9895
2009-05-31 | 10504.201 | 8780.168 | 1251.811 | 206.235 | 265.987 | 17560 | 20038.81 | 1886.091 | 227.77 | -4592.671
2009-06-30 | 10884.323 | 9216.895 | 1206.297 | 188.948 | 272.183 | 22540 | 19081.86 | 1829.943 | 141.6956 | 1486.5014
2009-07-31 | 11315.411 | 9620.536 | 1210.339 | 221.321 | 263.215 | 20011 | 22713.48 | 1581.902 | 158.5048 | -4442.8868
2009-08-31 | 12225.812 | 10434.537 | 1301.835 | 211.757 | 277.683 | 24380 | 22057.34 | 1746.493 | 229.3842 | 346.7828
2009-09-30 | 10931.831 | 9277.913 | 1239.615 | 177.855 | 236.448 | 19731 | 21922.34 | 1687.679 | 239.7521 | -4118.7711
2009-10-31 | 11181.875 | 9508.079 | 1259.913 | 179.112 | 234.771 | 18420 | 15363.31 | 1932.541 | 233.1459 | 891.0031
2009-11-30 | 11112.909 | 9475.052 | 1262.265 | 173.551 | 202.041 | 19710 | 17340.45 | 1920.156 | 233.9333 | 215.4607
2009-12-31 | 12688.573 | 10946.598 | 1225.323 | 204.103 | 312.549 | 21831 | 19729.84 | 1749.27 | 252.1934 | 99.6966
2010-01-31 | 13145.438 | 11330.024 | 1308.6 | 224.973 | 281.841 | 22045 | 19479.27 | 1824.502 | 239.3108 | 501.9172
2010-02-28 | 11751.752 | 10068.441 | 1247.677 | 172.272 | 263.362 | 21367 | 18884.05 | 1763.431 | 255.6966 | 463.8224
2010-03-31 | 11686.054 | 9927.551 | 1346.685 | 178.911 | 232.907 | 19393 | 16832.38 | 1780.814 | 221.7559 | 558.0501
2010-04-30 | 10474.752 | 8748.214 | 1305.947 | 201.493 | 219.098 | 17398 | 15030.25 | 1775.23 | 295.5305 | 296.9895
2010-05-31 | 11368.031 | 9536.118 | 1350.434 | 184.847 | 296.632 | 22904 | 20038.81 | 1886.091 | 227.77 | 751.329
2010-06-30 | 11555.961 | 9797.61 | 1334.971 | 175.296 | 248.084 | 21527 | 19081.86 | 1829.943 | 141.6956 | 473.5014
2010-07-31 | 13307.242 | 11457.602 | 1358.685 | 196.219 | 294.736 | 25075 | 22713.48 | 1581.902 | 158.5048 | 621.1132
2010-08-31 | 12921.565 | 11046.524 | 1379.923 | 227.005 | 268.113 | 24917 | 22057.34 | 1746.493 | 229.3842 | 883.7828
2010-09-30 | 11049.081 | 9272.091 | 1363.8 | 223.294 | 189.896 | 24444 | 21922.34 | 1687.679 | 239.7521 | 594.2289
2010-10-31 | 10929.335 | 9166.553 | 1415.512 | 194.924 | 152.346 | 17704 | 15363.31 | 1932.541 | 233.1459 | 175.0031
2010-11-30 | 11303.778 | 9631.649 | 1343.104 | 197.012 | 132.013 | 19970 | 17340.45 | 1920.156 | 233.9333 | 475.4607
2010-12-31 | 12694.155 | 10967.855 | 1333.472 | 213.793 | 179.035 | 22114 | 19729.84 | 1749.27 | 252.1934 | 382.6966
2011-01-31 | 13301.687 | 11430.562 | 1397.349 | 228.348 | 245.428 | 22733 | 19938.47 | 1797.701 | 258.0538 | 738.7752
2011-02-28 | 11775.464 | 10128.289 | 1258.023 | 199.187 | 189.965 | 21871 | 19081.88 | 1931.922 | 277.2781 | 579.9199
2011-03-31 | 12352.443 | 10487.541 | 1406.471 | 201.955 | 256.476 | 20667 | 17995.89 | 1925.285 | 237.1581 | 508.6669
2011-04-30 | 10789.012 | 9101.443 | 1313.581 | 194.8 | 179.188 | 17945 | 15411.63 | 1836.07 | 292.9127 | 404.3873
2011-05-31 | 10781.74 | 9046.905 | 1316.588 | 204.821 | 213.426 | 20847 | 18580.71 | 1504.528 | 253.6881 | 508.0739
2011-06-30 | 11238.277 | 9544.739 | 1219.471 | 194.518 | 279.549 | 22765 | 20342.47 | 1415.288 | 252.5383 | 754.7037
2011-07-31 | 13298.189 | 11448.888 | 1312.715 | 207.837 | 328.749 | 25450 | 23322.88 | 1198.084 | 203.9427 | 725.0933
2011-08-31 | 12531.706 | 10718.286 | 1371.117 | 191.542 | 250.761 | 22051 | 19562.88 | 1720.727 | 249.3743 | 518.0187
2011-09-30 | 11144.546 | 9376.834 | 1367.366 | 174.416 | 225.93 | 21552 | 19043.84 | 1747.319 | 185.7929 | 575.0481
2011-10-31 | 11012.737 | 9287.2 | 1366.261 | 151.445 | 207.831 | 18234 | 15871.5 | 1827.09 | 177.9033 | 357.5067
2011-11-30 | 11116.536 | 9428.401 | 1307.621 | 148.173 | 232.341 | 19673 | 17154.6 | 1837.406 | 218.8018 | 462.1922
2011-12-31 | 12121.895 | 10412.869 | 1295.596 | 184.83 | 228.6 | 20204 | 17925.51 | 1726.402 | 223.1266 | 328.9614
2012-01-31 | 12715.234 | 10948.174 | 1362.721 | 185.799 | 218.54 | 21847 | 19150.62 | 1791.478 | 308.8587 | 596.0433
2012-02-29 | 11610.18 | 9922.71 | 1283.368 | 163.061 | 241.041 | 19956 | 17273.85 | 1856.136 | 237.3638 | 588.6502
2012-03-31 | 11487.527 | 9660.31 | 1405.691 | 196.881 | 224.645 | 20332 | 17720.09 | 1987.229 | 260.8596 | 363.8214
2012-04-30 | 10641.371 | 8873.913 | 1365.573 | 191.349 | 210.536 | 17874 | 15231.22 | 1915.3 | 237.3826 | 490.0974
2012-05-31 | 11136.995 | 9304.02 | 1413.625 | 203.936 | 215.414 | 21106 | 18637.39 | 1687.272 | 242.2982 | 539.0398
2012-06-30 | 11800.326 | 10038.614 | 1338.673 | 178.791 | 244.248 | 24107 | 21813.12 | 1275.996 | 181.9566 | 835.9274
2012-07-31 | 13456.845 | 11552.619 | 1422.06 | 191.485 | 290.681 | 24636 | 22490.51 | 1276.191 | 198.1912 | 671.1078
2012-08-31 | 12632.817 | 10729.711 | 1428.622 | 212.649 | 261.835 | 23188 | 20435.58 | 1870.187 | 259.9366 | 622.2964
2012-09-30 | 11040.767 | 9271.502 | 1330.396 | 211.341 | 227.528 | 21183 | 18728.86 | 1751.122 | 241.4408 | 461.5772
2012-10-31 | 11141.991 | 9297.822 | 1426.415 | 176.549 | 241.205 | 18829 | 16008.33 | 2069.298 | 235.9358 | 515.4362
2012-11-30 | 11487.169 | 9711.027 | 1408.816 | 158.8 | 208.526 | 20144 | 17569.58 | 1922.144 | 212.0993 | 440.1767
2012-12-29 | 12156.557 | 10354.012 | 1377.79 | 173.831 | 250.924 | 20382 | 18041.85 | 1839.009 | 197.6117 | 303.5293
2013-01-31 | 12889.507 | 11003.972 | 1469.787 | 173.53 | 242.218 | 22610 | 19640.28 | 2147.084 | 197.0555 | 625.5805
2013-02-28 | 11742.246 | 9983.339 | 1377.594 | 153.907 | 227.406 | 21426 | 18759.8 | 2044.78 | 262.5673 | 358.8527
2013-03-31 | 11958.319 | 10134.187 | 1438.761 | 184.656 | 200.715 | 19825 | 17448.6 | 1936.126 | 222.6267 | 217.6473
2013-04-30 | 10944.906 | 9160.548 | 1366.503 | 212.478 | 205.377 | 18854 | 16176.39 | 2065.198 | 293.6076 | 318.8044
2013-05-31 | 10785.424 | 8990.721 | 1394.035 | 183.639 | 217.029 | 20488 | 18010.02 | 1884.409 | 199.7068 | 393.8642
2013-06-30 | 11174.679 | 9355.295 | 1365.081 | 163.498 | 290.805 | 22662 | 20486.94 | 1445.578 | 196.7334 | 532.7486
2013-07-31 | 12722.707 | 10867.174 | 1383.961 | 174.841 | 296.731 | 24927 | 22682.78 | 1267.167 | 241.1029 | 735.9501
2013-08-31 | 12100.351 | 10221.728 | 1420.874 | 179.937 | 277.812 | 22833 | 20219.6 | 1889.837 | 209.7228 | 513.8402
2013-09-30 | 10837.167 | 9076.722 | 1392.777 | 156.459 | 211.209 | 22682 | 20068.89 | 1821.304 | 205.8435 | 585.9625
2013-10-31 | 11135.689 | 9198.19 | 1502.292 | 176.758 | 258.449 | 18445 | 15816.3 | 2025.741 | 254.2856 | 348.6734
2013-11-30 | 11640.948 | 9790.636 | 1461.583 | 148.408 | 240.321 | 20615 | 18030.36 | 1922.273 | 267.9082 | 394.4588
2013-12-31 | 12702.006 | 10912.622 | 1447.614 | 188.083 | 153.687 | 21964 | 19570.07 | 2142.251 | 274.6158 | -22.9368
2014-01-31 | 13613.596 | 11658.477 | 1476.947 | 190.578 | 287.594 | 22774 | 20229.64 | 1760.07 | 276.9846 | 507.3054
2014-02-28 | 12067.276 | 10225.218 | 1395.693 | 206.555 | 239.81 | 21905 | 18798.24 | 2082.484 | 434.6011 | 589.6749
2014-03-31 | 12672.074 | 10666.474 | 1546.683 | 198.863 | 260.054 | 21656 | 18943.11 | 1956.483 | 351.4494 | 404.9576
2014-04-30 | 10836.804 | 8962.645 | 1460.568 | 212.109 | 201.482 | 18557 | 15838.52 | 2088.889 | 359.4376 | 270.1534
2014-05-31 | 10642.583 | 8790.577 | 1448.055 | 189.754 | 214.197 | 18844 | 16340.76 | 1952.935 | 239.5254 | 310.7796
2014-06-30 | 11228.548 | 9412.544 | 1454.421 | 166.33 | 195.253 | 20807 | 18622.91 | 1656.722 | 247.2939 | 280.0741
2014-07-31 | 11717.444 | 9845.802 | 1478.577 | 165.739 | 227.326 | 21300 | 19331.84 | 1234.529 | 223.8554 | 509.7756
2014-08-31 | 11718.183 | 9805.466 | 1488.258 | 173.903 | 250.556 | 21363 | 19501.8 | 1280.928 | 252.222 | 328.05
2014-09-30 | 10836.546 | 9080.103 | 1437.045 | 139.093 | 180.305 | 21123 | 19361.88 | 1344.12 | 216.4065 | 200.5935
2014-10-31 | 10819.853 | 9041.876 | 1446.698 | 151.093 | 180.186 | 17784 | 15264.16 | 1959.928 | 218.3104 | 341.6016
2014-11-30 | 11487.634 | 9707.192 | 1437.231 | 142.519 | 200.692 | 20102 | 17733.74 | 1806.566 | 246.3103 | 315.3837
2014-12-31 | 12131.525 | 10359.109 | 1425.828 | 154.903 | 191.685 | 20938 | 18328.41 | 1917.17 | 241.7382 | 450.6818
2015-01-31 | 13119.979 | 11250.337 | 1432.84 | 164.562 | 272.24 | 21814 | 19647.04 | 1319.941 | 240.0045 | 607.0145
2015-02-28 | 12302.278 | 10600.396 | 1335.858 | 142.772 | 223.252 | 21494 | 19379.05 | 1447.463 | 235.947 | 431.54
2015-03-31 | 12044.976 | 10212.786 | 1453.153 | 161.032 | 218.005 | 20827 | 18298.38 | 1955.219 | 289.3311 | 284.0699
2015-04-30 | 10404.962 | 8679.37 | 1405.231 | 151.615 | 168.746 | 18462 | 15708.66 | 1925.434 | 271.1328 | 556.7732
2015-05-31 | 10547.132 | 8798.507 | 1412.842 | 170.524 | 165.259 | 19158 | 16907.98 | 1888.851 | 228.6186 | 132.5504
2015-06-30 | 10624.316 | 8942.283 | 1351.048 | 148.015 | 182.97 | 19339 | 16892.13 | 1861.715 | 253.0514 | 332.1036
2015-07-31 | 12105.066 | 10312.467 | 1395.071 | 169.088 | 228.44 | 22516 | 20656.56 | 1189.704 | 228.4097 | 441.3263
2015-08-31 | 11797.099 | 9965.934 | 1418.277 | 166.564 | 246.324 | 22383 | 20498.96 | 1201.994 | 203.3686 | 478.6774
2015-09-30 | 11361.901 | 9625.828 | 1369.332 | 184.574 | 182.167 | 22063 | 19973.68 | 1257.934 | 211.4512 | 619.9348
2015-10-31 | 10687.264 | 8878.974 | 1453.202 | 194.589 | 160.499 | 17667 | 15013.54 | 1992.14 | 298.4092 | 362.9108
2015-11-30 | 10681.592 | 8963.684 | 1381.098 | 147.434 | 189.376 | 19239 | 16530.39 | 1927.785 | 302.168 | 478.657
2015-12-31 | 11313.857 | 9546.732 | 1393.262 | 167.618 | 206.245 | 19161 | 16555.58 | 1828.622 | 286.6657 | 490.1323
2016-01-31 | 12384.867 | 10508.333 | 1440.227 | 155.238 | 281.069 | 20836 | 18202.71 | 1838.962 | 317.9757 | 476.3523
2016-02-29 | 11471.763 | 9726.471 | 1372.476 | 150.337 | 222.479 | 20766 | 18094.22 | 1993.201 | 286.9147 | 391.6643
2016-03-31 | 11302.963 | 9496.261 | 1451.793 | 148.34 | 206.569 | 20063 | 17468.06 | 1861.963 | 293.4842 | 439.4928
2016-04-30 | 10409.92 | 8680.447 | 1436.773 | 153.646 | 139.054 | 17821 | 15610.16 | 1907.108 | 284.1523 | 19.5797
2016-05-31 | 10470.808 | 8757.947 | 1400.24 | 152.605 | 160.016 | 19885 | 17239.79 | 1934.375 | 353.4562 | 357.3788
2016-06-30 | 11101.521 | 9374.678 | 1386.493 | 146.615 | 193.735 | 21692 | 19702.23 | 1369.924 | 204.5618 | 415.2842
2016-07-31 | 12497.616 | 10733.656 | 1374.658 | 138.773 | 250.529 | 22659 | 20955.64 | 1104.207 | 161.3168 | 437.8362
2016-08-31 | 13113.359 | 11248.853 | 1404.99 | 164.839 | 294.677 | 23100 | 21332.92 | 1122.548 | 195.706 | 448.826
2016-09-30 | 11072.26 | 9296.858 | 1377.715 | 140.375 | 257.312 | 23213 | 21260.85 | 1152.819 | 142.8112 | 656.5198
2016-10-31 | 10518.677 | 8755.244 | 1410.365 | 158.328 | 194.74 | 18189 | 15451.67 | 1927.67 | 270.9776 | 538.6824
2016-11-30 | 10697.637 | 8920.356 | 1404.427 | 165.552 | 207.302 | 19369 | 16599.65 | 2002.135 | 266.5365 | 500.6785
2016-12-31 | 11978.041 | 10093.776 | 1403.94 | 191.718 | 288.607 | 20688 | 18146.04 | 1877.911 | 358.1404 | 305.9086
2017-01-31 | 12108.005 | 10235.721 | 1426.113 | 167.231 | 278.94 | 20372 | 17605.02 | 1903.952 | 284.0204 | 579.0076
2017-02-28 | 10607.563 | 8932.522 | 1327.331 | 157.939 | 189.771 | 19838 | 16763.11 | 2026.818 | 334.4528 | 713.6192
2017-03-31 | 11591.031 | 9770.579 | 1477.122 | 159.279 | 184.051 | 19174 | 16538.62 | 2020.879 | 270.5038 | 343.9972
2017-04-30 | 9788.616 | 8175.766 | 1362.45 | 157.307 | 93.093 | 17349 | 14585.55 | 2041.365 | 287.8311 | 434.2539
2017-05-31 | 10153.182 | 8442.449 | 1391.732 | 178.48 | 140.521 | 17738 | 15261.02 | 1979.705 | 284.9445 | 212.3305
2017-06-30 | 10657.08 | 8977.237 | 1340.846 | 158.409 | 180.588 | 21168 | 18975.18 | 1556.569 | 230.3528 | 405.8982
2017-07-31 | 11587.63 | 9826.461 | 1377.59 | 151.2 | 232.379 | 20627 | 18563.72 | 1412.149 | 207.7732 | 443.3578
2017-08-31 | 11350.012 | 9622.113 | 1359.22 | 157.201 | 211.478 | 20158 | 18606.52 | 1077.556 | 200.8482 | 273.0758
2017-09-30 | 10679.393 | 9122.15 | 1230.396 | 145.584 | 181.263 | 21786 | 20018.32 | 1007.671 | 215.3174 | 544.6916
2017-10-31 | 10339.329 | 8601.176 | 1426.975 | 139.553 | 171.625 | 17418 | 15048.39 | 1943.664 | 223.0329 | 202.9131
2017-11-30 | 10955.909 | 9213.777 | 1408.105 | 157.772 | 176.255 | 19115 | 16384.24 | 2051.185 | 276.3474 | 403.2276
2017-12-31 | 12338.893 | 10436.662 | 1408.63 | 196.667 | 296.934 | 20306 | 17882.19 | 1752.098 | 348.8256 | 322.8864
2018-01-31 | 12700.826 | 10882.596 | 1418.086 | 184.612 | 215.532 | 20906 | 18729.15 | 1274.496 | 374.7405 | 527.6135
2018-02-28 | 10951.065 | 9286.31 | 1323.263 | 160.19 | 181.302 | 20076 | 17391.54 | 1864.722 | 311.1241 | 508.6139
2018-03-31 | 11372.42 | 9566.427 | 1481.01 | 151.405 | 173.578 | 18462 | 15935.17 | 1911.541 | 271.1181 | 344.1709
2018-04-30 | 10578.368 | 8906.101 | 1368.878 | 139.08 | 164.309 | 18011 | 15475.92 | 1864.188 | 260.0555 | 410.8365
2018-05-31 | 10421.469 | 8725.155 | 1401.01 | 144.713 | 150.591 | 20473 | 18194.47 | 1599.295 | 211.7844 | 467.4506
2018-06-30 | 10923.446 | 9205.996 | 1373.762 | 146.9 | 196.788 | 21369 | 19090.62 | 1289.531 | 204.4922 | 784.3568
2018-07-31 | 12685.981 | 10951.054 | 1361.765 | 156.277 | 216.885 | 22909 | 21057.29 | 1149.358 | 275.492 | 426.86
2018-08-31 | 12688.795 | 10901.079 | 1390.079 | 149.133 | 248.504 | 21990 | 20345.65 | 1147.967 | 182.3349 | 314.0481
2018-09-30 | 11147.31 | 9441.469 | 1367.583 | 123.823 | 214.435 | 23240 | 21307.89 | 1121.28 | 169.2054 | 641.6246
2018-10-31 | 10717.348 | 9029.399 | 1440.57 | 138.254 | 109.125 | 18205 | 16055.12 | 1996.924 | 203.89 | -50.934
2018-11-30 | 11360.321 | 9612.505 | 1412.934 | 141.553 | 193.329 | 20152 | 17440.76 | 1925.193 | 292.2894 | 493.7576
2018-12-31 | 11938.614 | 10066.572 | 1439.964 | 165.292 | 266.786 | 19891 | 17186.14 | 1853.428 | 293.5 | 557.932
2019-01-31 | 12777.216 | 10984.339 | 1424.631 | 157.579 | 210.667 | 21525 | 18834.82 | 1824.973 | 233.4161 | 631.7909
2019-02-28 | 11291.744 | 9679.029 | 1303.065 | 132.852 | 176.798 | 20500 | 17986.65 | 1882.421 | 243.2612 | 387.6678
2019-03-31 | 11658.678 | 9872.263 | 1444.563 | 151.489 | 190.363 | 20263 | 17522.65 | 2049.826 | 239.7963 | 450.7277
2019-04-30 | 10264.505 | 8608.974 | 1338.349 | 170.596 | 146.586 | 17645 | 14956.61 | 2012.241 | 273.7595 | 402.3895
2019-05-31 | 10219.56 | 8467.021 | 1405.277 | 177.012 | 170.25 | 16784 | 14068.65 | 1848.762 | 312.4022 | 554.1858
2019-06-30 | 10365.619 | 8681.844 | 1388.098 | 145.5 | 150.177 | 20248 | 18015.36 | 1545.989 | 210.2323 | 476.4187
2019-07-31 | 12792.766 | 11052.777 | 1356.389 | 147.863 | 235.737 | 21791 | 20077.9 | 1055.989 | 181.1607 | 475.9503
2019-08-31 | 11825.052 | 10103.635 | 1379.382 | 141.201 | 200.834 | 21354 | 19286.97 | 1418.286 | 163.5032 | 485.2408
2019-09-30 | 10318.533 | 8735.445 | 1286.871 | 129.154 | 167.063 | 19717 | 17232.99 | 1865.817 | 179.2536 | 438.9394
2019-10-31 | 10351.05 | 8695.342 | 1377.19 | 133.423 | 145.095 | 18329 | 15858.72 | 1799.031 | 169.3067 | 501.9423
2019-11-30 | 11255.325 | 9566.229 | 1344.964 | 144.138 | 199.994 | 19625 | 17204.45 | 1869.312 | 264.8378 | 286.4002
2019-12-31 | 11997.095 | 10167.965 | 1390.827 | 185.248 | 253.055 | 20974 | 18132.44 | 1886.516 | 329.041 | 626.003
2020-01-31 | 12178.575 | 10383.457 | 1421.435 | 154.804 | 218.879 | 19928 | 17248.55 | 2038.156 | 255.5653 | 385.7287
2020-02-29 | 11239.82 | 9622.815 | 1333.64 | 130.239 | 153.126 | 19630 | 17209.54 | 1932.968 | 256.8344 | 230.6576
2020-03-31 | 10989.389 | 9283.197 | 1393.918 | 146.703 | 165.571 | 18183 | 15475.37 | 1969.849 | 270.2771 | 467.5039
2020-04-30 | 9282.854 | 7848.11 | 1153.337 | 156.852 | 124.555 | 15350 | 13280.69 | 1582.584 | 267.4529 | 219.2731
2020-05-31 | 9642.117 | 8168.463 | 1164.589 | 179.62 | 129.445 | 20649 | 18503.86 | 1386.916 | 269.737 | 488.487
2020-06-30 | 10800.015 | 9266.452 | 1204.421 | 158.555 | 170.587 | 21292 | 19034.88 | 1670.309 | 214.578 | 372.233
2020-07-31 | 13202.706 | 11611.332 | 1217.734 | 133.797 | 239.843 | 24446 | 22412.78 | 1343.705 | 211.87 | 477.645
2020-08-31 | 12081.08 | 10404.924 | 1293.469 | 146.854 | 235.833 | 23823 | 21283.78 | 1752.135 | 160.3762 | 626.7088
2020-09-30 | 10114.374 | 8539.376 | 1272.232 | 155.933 | 146.833 | 20225 | 17908.17 | 1726.147 | 208.4155 | 382.2675
2020-10-31 | 10339.39 | 8709.182 | 1346.746 | 136.399 | 147.063 | 17679 | 15258.76 | 1701.44 | 205.3914 | 513.4086
2020-11-30 | 10529.032 | 8952.778 | 1298.175 | 117.956 | 160.123 | 19147 | 16766.96 | 1779.029 | 198.332 | 402.679
2020-12-31 | 11811.675 | 10133.006 | 1324.33 | 159.628 | 194.711 | 20738 | 18149.66 | 1713.527 | 257.8595 | 616.9535
2021-01-31 | 12105.158 | 10361.393 | 1380.422 | 146.481 | 216.862 | 20150 | 17617.05 | 1904.916 | 201.7136 | 426.3204
2021-02-28 | 11233.123 | 9628.043 | 1286.376 | 128.04 | 190.664 | 20318 | 17713.35 | 1954.603 | 223.5765 | 426.4705
2021-03-31 | 11101.706 | 9383.05 | 1403.012 | 168.316 | 147.328 | 19344 | 16809.63 | 2016.47 | 209.1617 | 308.7383
2021-04-30 | 9781.57 | 8232.163 | 1334.867 | 145.429 | 69.111 | 16644 | 14263.1 | 1961.507 | 260.3496 | 159.0434
2021-05-31 | 10086.333 | 8498.898 | 1381.951 | 153.836 | 51.648 | 19443 | 17017.05 | 1789.111 | 185.9648 | 450.8742
2021-06-30 | 11262.474 | 9735.938 | 1259.332 | 132.576 | 134.628 | 22258 | 20483.21 | 1053.779 | 173.4785 | 547.5325
2021-07-31 | 11636.443 | 10067.983 | 1281.389 | 140.02 | 147.051 | 21655 | 20129.06 | 1024.867 | 174.991 | 326.082
2021-08-31 | 12856.511 | 11257.223 | 1276.353 | 145.534 | 177.401 | 22986 | 21152.87 | 1128.732 | 185.5447 | 518.8533
2021-09-30 | 10389.017 | 8816.858 | 1282.526 | 133.464 | 156.169 | 18769 | 16537.54 | 1688.898 | 169.64 | 372.922
2021-10-31 | 10516.14 | 8812.988 | 1349.298 | 146.187 | 207.667 | 17312 | 14836.55 | 1808.165 | 181.1434 | 486.1416
2021-11-30 | 10956.602 | 9289.843 | 1330.551 | 131.91 | 204.298 | 19644 | 17057.11 | 1886.821 | 179.7903 | 520.2787
2021-12-31 | 11969.602 | 10162.622 | 1393.558 | 150.401 | 263.021 | 20455 | 17758.36 | 1898.71 | 182.8977 | 615.0323
2022-01-31 | 13085.388 | 11309.713 | 1429.374 | 141.901 | 204.4 | 21349 | 18872.96 | 1818.319 | 192.0121 | 465.7089
2022-02-28 | 11487.734 | 9868.554 | 1279.543 | 139.57 | 200.067 | 20918 | 18284.47 | 1830.206 | 189.9149 | 613.4091
2022-03-31 | 11816.835 | 10021.983 | 1420.351 | 166.958 | 207.543 | 19763 | 17226.22 | 1876.425 | 246.9115 | 413.4435
2022-04-30 | 10265.047 | 8643.765 | 1301.591 | 139.261 | 180.43 | 17256 | 14635.63 | 1914.953 | 182.8324 | 522.5846
2022-05-31 | 10469.914 | 8743.427 | 1411.702 | 163.924 | 150.861 | 21292 | 19075.72 | 1585.076 | 182.1273 | 449.0767
2022-06-30 | 10929.858 | 9321.502 | 1299.146 | 148.831 | 160.379 | 21954 | 20047.8 | 1088.784 | 246.9046 | 570.5114
2022-07-31 | 12343.623 | 10601.099 | 1341.868 | 144.639 | 256.017 | 22607 | 21008.88 | 1021.468 | 156.3699 | 420.2821
2022-08-31 | 12624.254 | 10830.757 | 1351.532 | 144.462 | 297.503 | 21871 | 19879.56 | 1139.376 | 178.3511 | 673.7129
2022-09-30 | 10814.096 | 9116.212 | 1329.888 | 135.217 | 232.779 | 20350 | 17812.02 | 1857.612 | 220.7457 | 459.6223
2022-10-31 | 10384.167 | 8716.711 | 1336.906 | 114.553 | 215.997 | 17294 | 14671.49 | 1804.303 | 147.6571 | 670.5499
2022-11-30 | 11044.181 | 9332.357 | 1358.357 | 150.022 | 203.445 | 19441 | 16685.5 | 1963.331 | 221.7309 | 570.4381
2022-12-31 | 12273.23 | 10425.209 | 1423.836 | 177.746 | 246.439 | 20173 | 17611.79 | 1854.189 | 279.0826 | 427.9384
2023-01-31 | 12519.712 | 10663.9284 | 1442.7604 | 147.6643 | 265.3589 | 20486 | 17788.22 | 1880.245 | 189.9117 | 627.6233
2023-02-28 | 11225.17 | 9600.1488 | 1293.0651 | 135.588 | 196.3681 | 21388 | 18906.97 | 1669.987 | 182.8198 | 628.2232
2023-03-31 | 11846.269 | 10020.4543 | 1460.0804 | 185.4365 | 180.2977 | 18811 | 16110.98 | 1876.802 | 245.219 | 577.999
2023-04-30 | 10271.638 | 8627.354 | 1342.3702 | 129.821 | 172.0928 | 17547 | 14996.01 | 1623.887 | 195.8285 | 731.2745
2023-05-31 | 10356.75 | 8683.1386 | 1389.07 | 150.1265 | 134.4149 | 20787 | 18609.24 | 1622.633 | 190.6279 | 364.4991
2023-06-30 | 11119.814 | 9405.7355 | 1361.0294 | 177.7235 | 175.3256 | 21463 | 19512.09 | 1275.405 | 235.6532 | 439.8518
2023-07-31 | 12507.785 | 10774.2868 | 1327.9647 | 198.4082 | 207.1253 | 22686 | 20840.57 | 904.1759 | 297.5355 | 643.7186
2023-08-31 | 11828.62 | 10023.4866 | 1395.9442 | 179.0739 | 230.1152 | 21364 | 19051.29 | 1542.652 | 220.7961 | 549.2619
2023-09-30 | 10997.556 | 9302.3516 | 1313.7649 | 153.072 | 228.3675 | 23713 | 21787.11 | 917.0429 | 198.5693 | 810.2778
2023-10-31 | 10932.34 | 9206.3755 | 1385.768 | 125.7878 | 214.4087 | 20849 | 18263.33 | 1804.525 | 147.9438 | 633.2012
2023-11-30 | 11456.562 | 9679.0271 | 1398.5566 | 132.3457 | 246.6327 | 20579 | 17750.2 | 1866.194 | 194.518 | 768.088
2023-12-31 | 12065.5 | 10241.9514 | 1447.2337 | 146.7123 | 229.6026 | 20004 | 17492.49 | 1921.522 | 198.1631 | 391.8249
2024-01-31 | 13036.084 | 11101.9147 | 1422.9814 | 144.7408 | 366.4471 | 21081 | 18633 | 1745 | 183 | 520
2024-02-29 | 11516.766 | 9706.5825 | 1363.2675 | 141.9094 | 305.0065 | 19624 | 17059 | 1856 | 158 | 551
2024-03-31 | 11542.29 | 9662.1438 | 1438.1805 | 143.1947 | 298.7711 | 18902 | 16343 | 1919 | 176 | 464
2024-04-30 | 10489.417 | 8729.9908 | 1352.5453 | 150.6011 | 256.2799 | 17947 | 15250 | 1833 | 219 | 645
2024-05-31 | 10735.152 | 8909.3306 | 1386.8118 | 153.3365 | 285.6731 | 20402 | 17955 | 1893 | 137 | 417
2024-06-30 | 11566.905 | 9793.673 | 1359.5387 | 146.7093 | 266.984 | 23803 | 21929 | 1044 | 137 | 693
2024-07-31 | 13072.592 | 11226.7543 | 1335.3985 | 156.2716 | 354.1676 | 23206 | 21321 | 1003 | 155 | 727
2024-08-31 | 12666.051 | 10757.7104 | 1389.3925 | 161.2831 | 357.6651 | 23110 | 21255 | 995 | 149 | 711
2024-09-30 | 11321.751 | 9503.6166 | 1328.4107 | 153.2011 | 336.5227 | 21643 | 18979 | 1901 | 147 | 616
2024-10-31 | 10992.867 | 9093.9808 | 1422.713 | 180.5173 | 295.6559 | 18117 | 15554 | 1936 | 161 | 466
2024-11-30 | 11312.89 | 9431.1455 | 1419.4526 | 169.3741 | 292.9179 | 19212 | 16505 | 1973 | 175 | 559
2024-12-31 | 12959.601 | 10870.5701 | 1482.7244 | 147.4629 | 458.8435 | 21016 | 18161 | 1987 | 146 | 722
2025-01-31 | 13668.714 | 11640.674 | 1492.7451 | 125.8563 | 409.4386 | 22058 | 19455.51 | 1697.669 | 126.296 | 778.525
2025-02-28 | 12278.547 | 10423.565 | 1347.7547 | 150.2559 | 356.9713 | 21399 | 18634.07 | 1887.744 | 218.4029 | 658.7831
2025-03-31 | 12057.659 | 10104.3239 | 1508.986 | 134.0913 | 310.2578 | 20232 | 17493 | 1979.753 | 136.018 | 623.229
2025-04-30 | 10837.309 | 8985.7009 | 1425.0625 | 120.9368 | 305.6088 | 19271 | 16501.89 | 1894.611 | 135.812 | 738.687
2025-05-31 | 10784.244 | 8828.1414 | 1519.7494 | 135.5994 | 300.7538 | 18190 | 15481.69 | 2102.413 | 146.2299 | 459.6671
2025-06-30 | 11845.624 | 10083.8169 | 1324.7326 | 141.1828 | 295.8917 | 24775 | 22897.3 | 1081.067 | 115.504 | 681.129
2025-07-31 | 13905.926 | 12037.1718 | 1324.2562 | 155.3669 | 389.131 | 24399 | 22476.48 | 1128.796 | 108.979 | 684.745
2025-08-31 | 12930.485 | 10968.0995 | 1432.9397 | 151.2097 | 378.2361 | 24500 | 22472.56 | 1115.856 | 113.448 | 798.136
2025-09-30 | 11276.887 | 9403.587 | 1395.6112 | 153.5059 | 324.1829 | 19991 | 17458.95 | 1835.465 | 136.7609 | 559.8241
2025-10-31 | 11319.417 | 9397.4939 | 1447.8928 | 142.6134 | 331.4169 | 20310 | 17632.92 | 2070.743 | 105.693 | 500.644
2025-11-30 | 12026.73 | 10055.8108 | 1426.7021 | 175.429 | 368.7881 | 19827 | 17341.62 | 1844.312 | 166.851 | 474.217
2025-12-31 | 13676.513 | 11575.4106 | 1419.8716 | 185.5533 | 495.6775 | 21541 | 18858.91 | 1805.179 | 174.4509 | 702.4601
2026-01-31 | 14011.783 | 11974.7559 | 1449.5323 | 164.6151 | 422.8797 | 22064 | 19398.696 | 1872.272 | 171.153 | 621.879
2026-02-28 | 12373.552 | 10534.3995 | 1295.0671 | 186.4308 | 357.6546 | 21821 | 19119.72 | 1920.975 | 160.136 | 620.169
2026-03-31 | 12605.429 | 10619.5205 | 1503.2649 | 190.3699 | 292.2737 | 20333 | 17633.654 | 2001.765 | 177.854 | 519.727
2026-04-30 | 11126.138 | 9246.822 | 1405.5256 | 189.7035 | 284.0869 | 18502 | 16088.619 | 1856.16 | 161.258 | 395.963
2026-05-31 | 11184.72 | 9216.0076 | 1433.3973 | 228.6576 | 306.6575 | 21046 | 18422.232 | 1906.711 | 245.397 | 471.66
2026-06-30 | 11967.926 | 10050.5195 | 1390.4898 | 212.5831 | 314.3336 | 23494 | 21520.081 | 1142.235 | 150.115 | 681.569
2026-07-31 | 13920.584 | 11915.0059 | 1371.5984 | 222.8443 | 411.1354 | 25605 | 23568.8961 | 1198.307 | 102.103 | 735.6939
2026-08-31 | 13180.451 | 11091.7553 | 1425.3136 | 270.992 | 392.3901 | 23016 | 20582.089 | 1590.716 | 186.72 | 656.475
Back to main menu

## Table 1.4.4
Back to main menu
Table 1.4.4: Economic Assumptions
Year | Ontario Employment |  | Ontario Housing Starts |  | Ontario Growth Index
| Thousands | Annual Growth (%) | Thousands | Annual Growth (%) | Index | Annual Growth (%)
2011 | 6647.6 |  | 67.801 |  | 1.0465
2012 | 6685.4083 | 0.56875 | 77.387 | 14.1384 | 1.0572 | 1.0192
2013 | 6790.8917 | 1.5778 | 61.076 | -21.0772 | 1.0715 | 1.3499
2014 | 6823.4 | 0.4787 | 58.587 | -4.0753 | 1.0797 | 0.76876
2015 | 6862.7417 | 0.57657 | 68.997 | 17.7684 | 1.0896 | 0.91341
2016 | 6934.525 | 1.046 | 74.748 | 8.3351 | 1.1026 | 1.1958
2017 | 7109.1917 | 2.5188 | 79.876 | 6.8604 | 1.1243 | 1.9702
2018 | 7240.425 | 1.846 | 79.076 | -1.0016 | 1.1425 | 1.6168
2019 | 7412.8583 | 2.3815 | 68.99 | -12.7548 | 1.1628 | 1.7793
2020 | 7043.45 | -4.9833 | 81.237 | 17.7518 | 1.1413 | -1.8483
2021 | 7404.8167 | 5.1305 | 100.425 | 23.6198 | 1.1802 | 3.4097
2022 | 7764.1 | 4.852 | 95.957 | -4.4491 | 1.2182 | 3.2167
2023 | 8006.1333 | 3.1173 | 89.726 | -6.4935 | 1.2461 | 2.2907
2024 | 8146.1417 | 1.7488 | 74.5 | -16.9694 | 1.2644 | 1.4665
2025 | 8226.9583 | 0.99209 | 65.281 | -12.3745 | 1.2771 | 1.0024
2026 (f) | 8261.448 | 0.41923 | 64.754 | -0.80728 | 1.2867 | 0.75556
2027 (f) | 8324.004 | 0.7572 | 65.958 | 1.8593 | 1.2987 | 0.92911
2028 (f) | 8385.8879 | 0.74344 | 74.595 | 13.0947 | 1.3115 | 0.9874
Back to main menu

## Table 1.4.5
Back to main menu
Table 1.4.5: Estimate of Contracted Embedded Generation Capacity (MW)
| Biogas | Cogeneration | Solar | Hydro | Wind | Total
2007-01-01 | 5 | 0.206 | 0 | 75.564 | 0 | 80.77
2007-02-01 | 5 | 0.206 | 0 | 75.564 | 0 | 80.77
2007-03-01 | 5.9073 | 0.206 | 0 | 75.564 | 0 | 81.6773
2007-04-01 | 10.625 | 0.206 | 0 | 75.564 | 0.342 | 86.737
2007-05-01 | 13.4363 | 0.206 | 0 | 75.564 | 5.3584 | 94.5647
2007-06-01 | 16.85 | 0.206 | 0 | 75.564 | 6.51 | 99.13
2007-07-01 | 16.85 | 0.206 | 0 | 298.4473 | 6.51 | 322.0133
2007-08-01 | 16.85 | 0.206 | 0.031266 | 341.553 | 6.51 | 365.1502
2007-09-01 | 16.994 | 0.206 | 0.05049 | 341.682 | 6.51 | 365.4425
2007-10-01 | 18.63 | 0.206 | 0.051666 | 341.682 | 6.631 | 367.2006
2007-11-01 | 19.129 | 0.206 | 0.061423 | 342.326 | 6.76 | 368.4824
2007-12-01 | 19.5748 | 0.206 | 0.14116 | 342.9565 | 6.76 | 369.6385
2008-01-01 | 20.192 | 0.206 | 0.21465 | 343.351 | 8.9955 | 372.9591
2008-02-01 | 20.2748 | 0.206 | 0.21761 | 343.351 | 16.66 | 380.7094
2008-03-01 | 20.292 | 1.7641 | 0.21992 | 343.351 | 22.7568 | 388.3838
2008-04-01 | 20.292 | 2.506 | 0.25272 | 343.351 | 25.66 | 392.0617
2008-05-01 | 20.292 | 2.506 | 0.29071 | 343.351 | 25.66 | 392.0997
2008-06-01 | 20.292 | 7.006 | 0.29071 | 343.351 | 38.2 | 409.1397
2008-07-01 | 20.292 | 7.506 | 0.29363 | 343.351 | 45.46 | 416.9026
2008-08-01 | 20.292 | 7.506 | 0.29739 | 343.351 | 45.46 | 416.9064
2008-09-01 | 20.292 | 7.506 | 0.30381 | 343.351 | 46.835 | 418.2878
2008-10-01 | 20.292 | 7.8705 | 0.32459 | 343.351 | 56.2648 | 428.1029
2008-11-01 | 21.572 | 18.806 | 0.32618 | 346.751 | 69.22 | 456.6752
2008-12-01 | 23.492 | 18.9189 | 3.2231 | 347.351 | 73.51 | 466.495
2009-01-01 | 23.492 | 22.306 | 11.5259 | 347.351 | 73.51 | 478.1849
2009-02-01 | 23.492 | 22.306 | 11.6487 | 347.351 | 73.51 | 478.3077
2009-03-01 | 23.492 | 22.306 | 11.6749 | 347.351 | 73.5487 | 478.3726
2009-04-01 | 23.5381 | 22.306 | 11.6767 | 347.351 | 74.11 | 478.9818
2009-05-01 | 23.838 | 22.306 | 11.6803 | 347.351 | 74.11 | 479.2853
2009-06-01 | 23.838 | 60.106 | 11.6803 | 347.351 | 74.11 | 517.0853
2009-07-01 | 23.838 | 85.306 | 11.6803 | 347.351 | 74.11 | 542.2853
2009-08-01 | 23.838 | 85.306 | 11.6803 | 347.351 | 74.11 | 542.2853
2009-09-01 | 23.838 | 85.306 | 12.6342 | 348.4843 | 74.11 | 544.3725
2009-10-01 | 23.838 | 85.306 | 21.2196 | 349.351 | 74.11 | 553.8246
2009-11-01 | 23.838 | 85.306 | 23.4542 | 349.351 | 74.11 | 556.0592
2009-12-01 | 23.838 | 85.306 | 33.0765 | 349.6091 | 87.5423 | 579.3718
2010-01-01 | 23.838 | 85.306 | 47.0949 | 360.451 | 104.9035 | 621.5935
2010-02-01 | 23.838 | 85.306 | 53.5913 | 360.973 | 120.71 | 644.4183
2010-03-01 | 23.838 | 85.306 | 53.5913 | 360.973 | 120.71 | 644.4183
2010-04-01 | 27.6624 | 85.306 | 53.5913 | 364.3463 | 120.71 | 651.616
2010-05-01 | 30.917 | 85.306 | 53.5913 | 365.573 | 142.7455 | 678.1328
2010-06-01 | 30.917 | 85.306 | 53.607 | 366.6886 | 160.31 | 696.8286
2010-07-01 | 32.2331 | 85.306 | 64.4924 | 367.1394 | 160.31 | 709.4809
2010-08-01 | 37.8164 | 85.306 | 103.6895 | 367.191 | 160.31 | 754.313
2010-09-01 | 42.9311 | 85.306 | 120.9962 | 367.881 | 160.31 | 777.4243
2010-10-01 | 43.164 | 85.306 | 129.8468 | 369.046 | 162.4132 | 789.7761
2010-11-01 | 43.164 | 85.306 | 149.9779 | 369.196 | 175.11 | 822.7539
2010-12-01 | 43.164 | 85.306 | 165.0208 | 369.796 | 186.9165 | 850.2033
2011-01-01 | 44.1163 | 85.306 | 193.1646 | 369.796 | 204.3358 | 896.7187
2011-02-01 | 44.804 | 85.306 | 207 | 369.796 | 221.11 | 928.016
2011-03-01 | 44.804 | 85.306 | 212.7987 | 369.796 | 221.11 | 933.8147
2011-04-01 | 44.804 | 85.306 | 221.202 | 369.796 | 221.11 | 942.218
2011-05-01 | 44.9008 | 85.306 | 224.2298 | 369.796 | 234.0132 | 958.2458
2011-06-01 | 44.904 | 85.306 | 227.8477 | 370.916 | 241.11 | 970.0837
2011-07-01 | 44.904 | 85.306 | 259.3137 | 370.916 | 241.11 | 1001.5497
2011-08-01 | 44.904 | 85.306 | 286.3255 | 370.916 | 241.11 | 1028.5615
2011-09-01 | 44.9289 | 85.306 | 314.495 | 370.916 | 241.11 | 1056.756
2011-10-01 | 45.278 | 85.306 | 321.9786 | 370.916 | 241.11 | 1064.5886
2011-11-01 | 45.303 | 85.306 | 327.0096 | 371.381 | 241.11 | 1070.1096
2011-12-01 | 45.6199 | 85.306 | 355.7744 | 371.381 | 241.11 | 1099.1913
2012-01-01 | 48.4134 | 85.306 | 374.3287 | 371.381 | 242.8519 | 1122.281
2012-02-01 | 48.515 | 85.306 | 380.4701 | 371.381 | 250.11 | 1135.7821
2012-03-01 | 48.515 | 85.306 | 437.6008 | 371.381 | 265.9616 | 1208.7644
2012-04-01 | 49.5174 | 85.306 | 458.7959 | 371.381 | 287.91 | 1252.9103
2012-05-01 | 50.0359 | 85.306 | 485.1125 | 371.381 | 293.3939 | 1285.2293
2012-06-01 | 51.1197 | 85.306 | 515.6181 | 371.381 | 297.91 | 1321.3348
2012-07-01 | 52.0384 | 85.306 | 521.0967 | 371.381 | 297.91 | 1327.7321
2012-08-01 | 52.9475 | 85.306 | 532.5016 | 371.631 | 297.91 | 1340.2962
2012-09-01 | 53.558 | 85.306 | 541.6338 | 371.631 | 301.51 | 1353.6388
2012-10-01 | 53.6709 | 85.306 | 552.0531 | 371.631 | 301.91 | 1364.571
2012-11-01 | 53.808 | 85.306 | 570.7029 | 371.631 | 301.91 | 1383.3579
2012-12-01 | 54.1467 | 85.306 | 582.401 | 371.631 | 310.8132 | 1404.2979
2013-01-01 | 55.3679 | 85.306 | 599.0215 | 371.631 | 327.8132 | 1439.1396
2013-02-01 | 58.753 | 85.306 | 642.2677 | 373.5953 | 334.91 | 1494.832
2013-03-01 | 58.753 | 85.306 | 701.5808 | 379.046 | 334.91 | 1559.5958
2013-04-01 | 59.002 | 85.306 | 737.2683 | 379.346 | 334.91 | 1595.8323
2013-05-01 | 60.4955 | 85.306 | 755.764 | 384.846 | 334.91 | 1621.3216
2013-06-01 | 61.9907 | 85.306 | 787.9376 | 390.746 | 334.91 | 1660.8903
2013-07-01 | 62.099 | 85.306 | 823.3897 | 394.1154 | 334.91 | 1699.82
2013-08-01 | 62.099 | 85.306 | 846.7295 | 398.196 | 334.91 | 1727.2405
2013-09-01 | 62.099 | 85.306 | 873.0577 | 398.196 | 334.91 | 1753.5687
2013-10-01 | 62.2925 | 85.306 | 897.06 | 403.1637 | 335.039 | 1782.8613
2013-11-01 | 62.349 | 85.306 | 906.6198 | 403.696 | 335.41 | 1793.3808
2013-12-01 | 62.349 | 85.306 | 945.3376 | 403.696 | 335.41 | 1832.0986
2014-01-01 | 62.59 | 85.306 | 984.8715 | 403.696 | 335.41 | 1871.8735
2014-02-01 | 66.847 | 85.306 | 1040.8206 | 403.696 | 339.91 | 1936.5796
2014-03-01 | 70.847 | 85.306 | 1117.9857 | 403.696 | 368.5068 | 2046.3415
2014-04-01 | 73.0335 | 85.306 | 1152.4978 | 403.696 | 371.41 | 2085.9433
2014-05-01 | 73.699 | 85.306 | 1178.084 | 403.696 | 371.41 | 2112.195
2014-06-01 | 73.699 | 85.306 | 1193.7326 | 403.696 | 373.41 | 2129.8436
2014-07-01 | 73.699 | 85.306 | 1214.1827 | 405.346 | 381.41 | 2159.9437
2014-08-01 | 73.7313 | 85.306 | 1266.963 | 405.346 | 386.9145 | 2218.2607
2014-09-01 | 73.949 | 85.306 | 1310.0845 | 405.346 | 395.89 | 2270.5755
2014-10-01 | 73.949 | 85.306 | 1389.8383 | 405.346 | 410.89 | 2365.3293
2014-11-01 | 73.949 | 85.306 | 1454.1719 | 405.346 | 415.6733 | 2434.4462
2014-12-01 | 73.949 | 85.306 | 1491.1889 | 405.346 | 425.24 | 2481.0299
2015-01-01 | 73.949 | 85.306 | 1516.7367 | 405.346 | 425.24 | 2506.5777
2015-02-01 | 73.949 | 85.306 | 1571.7349 | 405.346 | 425.24 | 2561.5759
2015-03-01 | 73.949 | 85.306 | 1616.4799 | 405.346 | 425.24 | 2606.3209
2015-04-01 | 74.099 | 85.306 | 1642.3296 | 405.346 | 425.24 | 2632.3206
2015-05-01 | 74.199 | 85.306 | 1659.5083 | 405.346 | 425.24 | 2649.5993
2015-06-01 | 85.4799 | 85.306 | 1682.2317 | 408.856 | 429.74 | 2691.6136
2015-07-01 | 92.6158 | 85.306 | 1705.1571 | 412.105 | 449.5303 | 2744.7143
2015-08-01 | 92.761 | 85.306 | 1726.3479 | 418.916 | 470.7045 | 2794.0354
2015-09-01 | 92.761 | 85.306 | 1754.6761 | 418.916 | 483.54 | 2835.1991
2015-10-01 | 99.9352 | 85.306 | 1778.6685 | 418.916 | 483.54 | 2866.3657
2015-11-01 | 106.879 | 87.7861 | 1806.2252 | 418.916 | 483.54 | 2903.3463
2015-12-01 | 107.796 | 89.222 | 1839.1469 | 420.4644 | 484.9948 | 2941.6242
2016-01-01 | 107.796 | 89.222 | 1850.7319 | 420.516 | 487.64 | 2955.9059
2016-02-01 | 107.796 | 89.222 | 1857.2838 | 420.516 | 489.0193 | 2963.8371
2016-03-01 | 107.796 | 89.222 | 1864.9679 | 420.516 | 497.64 | 2980.1419
2016-04-01 | 107.796 | 89.222 | 1871.5551 | 420.516 | 497.64 | 2986.7291
2016-05-01 | 107.796 | 89.222 | 1875.2243 | 420.516 | 512.4013 | 3005.1596
2016-06-01 | 107.796 | 89.222 | 1877.2384 | 420.516 | 515.24 | 3010.0124
2016-07-01 | 107.796 | 89.222 | 1882.7053 | 420.516 | 515.24 | 3015.4793
2016-08-01 | 107.9921 | 89.222 | 1891.9307 | 420.516 | 515.24 | 3024.9008
2016-09-01 | 108.176 | 89.222 | 1907.7185 | 420.516 | 521.39 | 3047.0225
2016-10-01 | 108.1841 | 89.222 | 1915.9616 | 420.516 | 542.3997 | 3076.2834
2016-11-01 | 108.426 | 89.222 | 1923.3447 | 420.516 | 553.89 | 3095.3987
2016-12-01 | 108.426 | 89.222 | 1931.2852 | 420.581 | 569.1094 | 3118.6235
2017-01-01 | 108.426 | 89.222 | 1935.8393 | 420.581 | 571.69 | 3125.7583
2017-02-01 | 108.426 | 89.222 | 1940.709 | 420.581 | 571.69 | 3130.628
2017-03-01 | 108.426 | 91.4546 | 1947.771 | 420.581 | 571.69 | 3139.9226
2017-04-01 | 108.426 | 93.067 | 1963.2503 | 420.581 | 578.6233 | 3163.9477
2017-05-01 | 108.426 | 93.3799 | 1976.6781 | 420.8568 | 579.9481 | 3179.2889
2017-06-01 | 108.426 | 96.3 | 1981.7666 | 421.8143 | 580.19 | 3188.4969
2017-07-01 | 108.426 | 96.3 | 1983.621 | 422.031 | 580.19 | 3190.568
2017-08-01 | 108.426 | 97.4472 | 1986.7569 | 422.031 | 580.19 | 3194.8511
2017-09-01 | 108.426 | 99.533 | 1992.5016 | 422.031 | 580.19 | 3202.6816
2017-10-01 | 108.426 | 99.533 | 1997.4386 | 422.031 | 580.19 | 3207.6186
2017-11-01 | 108.426 | 99.7908 | 2002.8191 | 422.031 | 587.7067 | 3220.7735
2017-12-01 | 108.426 | 102.111 | 2006.8166 | 422.031 | 590.44 | 3229.8246
2018-01-01 | 108.426 | 102.111 | 2012.8244 | 422.031 | 590.44 | 3235.8324
2018-02-01 | 108.426 | 102.111 | 2020.9207 | 422.031 | 590.44 | 3243.9287
2018-03-01 | 108.426 | 102.111 | 2028.9461 | 422.031 | 590.44 | 3251.9541
2018-04-01 | 108.6093 | 102.111 | 2033.4623 | 422.031 | 590.44 | 3256.6536
2018-05-01 | 108.676 | 102.111 | 2036.006 | 422.031 | 590.44 | 3259.264
2018-06-01 | 108.676 | 102.111 | 2042.1636 | 422.031 | 590.44 | 3265.4216
2018-07-01 | 108.9018 | 102.111 | 2049.1407 | 422.031 | 590.44 | 3272.6245
2018-08-01 | 109.426 | 102.111 | 2062.096 | 422.031 | 590.44 | 3286.104
2018-09-01 | 109.501 | 102.111 | 2069.698 | 422.031 | 590.44 | 3293.781
2018-10-01 | 109.676 | 102.111 | 2075.4269 | 422.031 | 590.44 | 3299.6849
2018-11-01 | 109.771 | 102.111 | 2076.0426 | 422.031 | 590.44 | 3300.3956
2018-12-01 | 110.026 | 102.111 | 2076.9038 | 422.031 | 590.44 | 3301.5118
2019-01-01 | 110.026 | 102.111 | 2099.1202 | 422.031 | 590.44 | 3323.7282
2019-02-01 | 110.026 | 102.111 | 2109.2438 | 422.031 | 590.44 | 3333.8518
2019-03-01 | 110.276 | 102.111 | 2116.0375 | 422.031 | 590.44 | 3340.8955
2019-04-01 | 110.276 | 103.563 | 2119.3182 | 422.031 | 590.44 | 3345.6282
2019-05-01 | 110.5099 | 104.091 | 2121.5007 | 422.031 | 590.44 | 3348.5725
2019-06-01 | 110.526 | 104.091 | 2122.9333 | 422.031 | 590.44 | 3350.0213
2019-07-01 | 110.526 | 104.091 | 2123.7894 | 422.031 | 590.44 | 3350.8774
2019-08-01 | 110.5502 | 104.091 | 2125.5157 | 422.031 | 590.44 | 3352.6279
2019-09-01 | 110.8843 | 105.183 | 2128.6008 | 422.031 | 590.44 | 3357.1391
2019-10-01 | 111.026 | 106.821 | 2129.6581 | 422.031 | 590.44 | 3359.9761
2019-11-01 | 111.026 | 106.821 | 2130.7874 | 422.031 | 590.44 | 3361.1054
2019-12-01 | 111.026 | 106.821 | 2130.9674 | 426.5471 | 590.44 | 3365.8016
2020-01-01 | 115.1631 | 106.821 | 2130.9674 | 427.031 | 590.44 | 3370.4225
2020-02-01 | 115.276 | 107.7101 | 2132.3836 | 427.031 | 590.44 | 3372.8407
2020-03-01 | 115.276 | 111.978 | 2134.0129 | 427.031 | 590.44 | 3378.7379
2020-04-01 | 115.276 | 111.978 | 2134.0129 | 427.031 | 590.44 | 3378.7379
2020-05-01 | 115.276 | 111.978 | 2134.0129 | 427.031 | 590.44 | 3378.7379
2020-06-01 | 115.276 | 124.7009 | 2134.1029 | 427.031 | 590.44 | 3391.5508
2020-07-01 | 115.276 | 139.765 | 2134.5529 | 427.031 | 590.44 | 3407.0649
2020-08-01 | 115.276 | 139.765 | 2134.5529 | 427.031 | 590.44 | 3407.0649
2020-09-01 | 115.276 | 139.765 | 2134.8553 | 427.031 | 590.44 | 3407.3673
2020-10-01 | 115.276 | 139.765 | 2137.3297 | 427.031 | 590.44 | 3409.8417
2020-11-01 | 115.276 | 139.765 | 2137.9364 | 428.281 | 590.44 | 3411.6984
2020-12-01 | 115.276 | 139.765 | 2138.6727 | 428.281 | 590.44 | 3412.4347
2021-01-01 | 115.276 | 139.765 | 2140.7676 | 428.281 | 590.44 | 3414.5296
2021-02-01 | 115.276 | 139.765 | 2141.0621 | 428.281 | 590.44 | 3414.8241
2021-03-01 | 115.276 | 139.765 | 2141.0621 | 428.281 | 590.44 | 3414.8241
2021-04-01 | 115.276 | 139.765 | 2141.0621 | 428.281 | 590.44 | 3414.8241
2021-05-01 | 115.276 | 139.765 | 2141.0621 | 428.281 | 590.44 | 3414.8241
2021-06-01 | 115.276 | 139.765 | 2141.0621 | 428.281 | 590.44 | 3414.8241
2021-07-01 | 115.276 | 139.765 | 2141.0621 | 428.281 | 590.44 | 3414.8241
2021-08-01 | 115.276 | 139.765 | 2141.0621 | 428.281 | 590.44 | 3414.8241
2021-09-01 | 115.276 | 139.765 | 2141.0621 | 428.281 | 590.44 | 3414.8241
2021-10-01 | 115.276 | 139.765 | 2141.0621 | 428.281 | 590.44 | 3414.8241
2021-11-01 | 115.276 | 139.765 | 2141.0621 | 428.281 | 590.44 | 3414.8241
2021-12-01 | 115.276 | 139.765 | 2141.0621 | 428.281 | 590.44 | 3414.8241
2022-01-01 | 115.276 | 139.765 | 2141.0621 | 428.281 | 590.44 | 3414.8241
2022-02-01 | 115.276 | 139.765 | 2141.0621 | 428.281 | 590.44 | 3414.8241
2022-03-01 | 115.276 | 139.765 | 2141.0621 | 428.281 | 590.44 | 3414.8241
2022-04-01 | 115.276 | 139.765 | 2141.0621 | 428.281 | 590.44 | 3414.8241
2022-05-01 | 115.276 | 139.765 | 2141.0621 | 428.281 | 590.44 | 3414.8241
2022-06-01 | 115.276 | 139.765 | 2141.0621 | 428.281 | 590.44 | 3414.8241
2022-07-01 | 115.276 | 139.765 | 2141.0621 | 428.281 | 590.44 | 3414.8241
2022-08-01 | 115.276 | 139.765 | 2141.0621 | 428.281 | 590.44 | 3414.8241
2022-09-01 | 115.276 | 139.765 | 2141.0621 | 428.281 | 590.44 | 3414.8241
2022-10-01 | 115.276 | 139.765 | 2141.0621 | 428.281 | 590.44 | 3414.8241
2022-11-01 | 115.276 | 139.765 | 2141.0621 | 428.281 | 590.44 | 3414.8241
2022-12-01 | 115.276 | 139.765 | 2141.0621 | 428.281 | 590.44 | 3414.8241
2023-01-01 | 115.276 | 139.765 | 2141.0621 | 428.281 | 590.44 | 3414.8241
2023-02-01 | 115.276 | 139.765 | 2141.0621 | 428.281 | 590.44 | 3414.8241
2023-03-01 | 115.276 | 139.765 | 2141.0621 | 428.281 | 590.44 | 3414.8241
2023-04-01 | 115.276 | 139.765 | 2141.0621 | 428.281 | 590.44 | 3414.8241
2023-05-01 | 115.276 | 139.765 | 2141.0621 | 428.281 | 590.44 | 3414.8241
2023-06-01 | 115.276 | 139.765 | 2141.0621 | 428.281 | 590.44 | 3414.8241
2023-07-01 | 115.276 | 139.765 | 2141.0621 | 428.281 | 590.44 | 3414.8241
2023-08-01 | 115.276 | 139.765 | 2141.0621 | 428.281 | 590.44 | 3414.8241
2023-09-01 | 115.276 | 139.765 | 2141.0621 | 428.281 | 590.44 | 3414.8241
2023-10-01 | 115.276 | 139.765 | 2141.0621 | 428.281 | 590.44 | 3414.8241
2023-11-01 | 115.276 | 139.765 | 2141.0621 | 428.281 | 590.44 | 3414.8241
2023-12-01 | 115.276 | 139.765 | 2141.0621 | 428.281 | 590.44 | 3414.8241
2024-01-01 | 115.276 | 139.765 | 2141.0621 | 428.281 | 590.44 | 3414.8241
2024-02-01 | 115.276 | 139.765 | 2141.0621 | 428.281 | 590.44 | 3414.8241
2024-03-01 | 115.276 | 139.765 | 2141.0621 | 428.281 | 590.44 | 3414.8241
2024-04-01 | 115.276 | 139.765 | 2141.0621 | 428.281 | 590.44 | 3414.8241
2024-05-01 | 115.276 | 139.765 | 2141.0621 | 428.281 | 590.44 | 3414.8241
2024-06-01 | 115.276 | 139.765 | 2141.0621 | 445.1637 | 590.44 | 3431.7068
2024-07-01 | 115.276 | 139.765 | 2141.0621 | 448.521 | 590.44 | 3435.0641
2024-08-01 | 115.276 | 139.765 | 2141.0621 | 448.521 | 590.44 | 3435.0641
2024-09-01 | 115.276 | 139.765 | 2141.0621 | 448.521 | 590.44 | 3435.0641
2024-10-01 | 115.276 | 139.765 | 2141.0621 | 449.0694 | 590.44 | 3435.6125
2024-11-01 | 115.276 | 139.765 | 2141.0621 | 449.521 | 590.44 | 3436.0641
2024-12-01 | 115.276 | 139.765 | 2141.0621 | 449.521 | 590.44 | 3436.0641
2025-01-01 | 115.276 | 139.765 | 2141.0621 | 449.521 | 590.44 | 3436.0641
2025-02-01 | 115.276 | 139.765 | 2141.0621 | 449.521 | 590.44 | 3436.0641
2025-03-01 | 115.276 | 139.765 | 2141.0621 | 449.521 | 590.44 | 3436.0641
2025-04-01 | 115.276 | 139.765 | 2141.0621 | 449.521 | 590.44 | 3436.0641
2025-05-01 | 115.276 | 139.765 | 2333.0447 | 449.521 | 590.44 | 3628.0467
2025-06-01 | 115.276 | 139.765 | 2333.0447 | 449.521 | 590.44 | 3628.0467
2025-07-01 | 115.276 | 139.765 | 2333.0447 | 449.521 | 590.44 | 3628.0467
2025-08-01 | 115.276 | 139.765 | 2333.0447 | 449.521 | 590.44 | 3628.0467
2025-09-01 | 115.276 | 139.765 | 2333.0447 | 449.521 | 590.44 | 3628.0467
2025-10-01 | 115.276 | 139.765 | 2333.0447 | 449.521 | 590.44 | 3628.0467
2025-11-01 | 115.276 | 139.765 | 2333.0447 | 449.521 | 590.44 | 3628.0467
2025-12-01 | 115.276 | 139.765 | 2333.0447 | 449.521 | 590.44 | 3628.0467
2026-01-01 | 115.276 | 139.765 | 2333.0447 | 449.521 | 590.44 | 3628.0467
2026-02-01 | 115.276 | 139.765 | 2333.0447 | 449.521 | 590.44 | 3628.0467
2026-03-01 | 115.276 | 139.765 | 2333.0447 | 449.521 | 590.44 | 3628.0467
2026-04-01 | 115.276 | 139.765 | 2333.0447 | 449.521 | 590.44 | 3628.0467
2026-05-01 | 115.276 | 139.765 | 2333.0447 | 449.521 | 590.44 | 3628.0467
2026-06-01 | 115.276 | 139.765 | 2333.0447 | 449.521 | 590.44 | 3628.0467
2026-07-01 | 115.276 | 139.765 | 2333.0447 | 449.521 | 590.44 | 3628.0467
2026-08-01 | 115.276 | 139.765 | 2333.0447 | 449.521 | 590.44 | 3628.0467
2026-09-01 | 115.276 | 139.765 | 2333.0447 | 449.521 | 590.44 | 3628.0467
2026-10-01 | 115.276 | 139.765 | 2333.0447 | 449.521 | 590.44 | 3628.0467
2026-11-01 | 115.276 | 139.765 | 2333.0447 | 449.521 | 590.44 | 3628.0467
2026-12-01 | 115.276 | 139.765 | 2333.0447 | 449.521 | 590.44 | 3628.0467
2027-01-01 | 115.276 | 139.765 | 2333.0447 | 449.521 | 590.44 | 3628.0467
2027-02-01 | 115.276 | 139.765 | 2333.0447 | 449.521 | 590.44 | 3628.0467
2027-03-01 | 115.276 | 139.765 | 2333.0447 | 449.521 | 590.44 | 3628.0467
2027-04-01 | 115.276 | 139.765 | 2333.0447 | 449.521 | 590.44 | 3628.0467
2027-05-01 | 115.276 | 139.765 | 2333.0447 | 449.521 | 590.44 | 3628.0467
2027-06-01 | 115.276 | 139.765 | 2333.0447 | 449.521 | 590.44 | 3628.0467
2027-07-01 | 115.276 | 139.765 | 2333.0447 | 449.521 | 590.44 | 3628.0467
2027-08-01 | 115.276 | 139.765 | 2333.0447 | 449.521 | 590.44 | 3628.0467
2027-09-01 | 115.276 | 139.765 | 2333.0447 | 449.521 | 590.44 | 3628.0467
2027-10-01 | 115.276 | 139.765 | 2333.0447 | 449.521 | 590.44 | 3628.0467
2027-11-01 | 115.276 | 139.765 | 2333.0447 | 449.521 | 590.44 | 3628.0467
2027-12-01 | 115.276 | 139.765 | 2333.0447 | 449.521 | 590.44 | 3628.0467
2028-01-01 | 115.276 | 139.765 | 2333.0447 | 449.521 | 590.44 | 3628.0467
2028-02-01 | 115.276 | 139.765 | 2333.0447 | 449.521 | 590.44 | 3628.0467
2028-03-01 | 115.276 | 139.765 | 2333.0447 | 449.521 | 590.44 | 3628.0467
Back to main menu

## Table 2.1
Back to main menu
Table 2.1: Existing Grid-Connected Resource Capacity
Fuel Type | Total Installed Capacity (MW) | Forecast Capability at 2027 Summer Peak [Firm] (MW) | Forecast Capability at 2027 Summer Peak [Planned] (MW) | Number of Stations | Change in Number of Stations | Change in Installed Capacity (MW)
Nuclear | 12196.2 | 7514 | 7514 | 4 | 0 | 0
Hydroelectric | 8864.3044 | 4995.8621 | 4995.8621 | 76 | 0 | 0
Gas/Oil | 10993.79 | 10030.58 | 10081.13 | 30 | 0 | -106.5
Wind | 4942.811 | 751.7428 | 751.7428 | 42 | 0 | 0
Biofuel | 286.8 | 250 | 250 | 4 | 0 | 0
Solar | 478.04 | 94.6283 | 94.6283 | 10 | 0 | 0
Storage | 1219.847 | 809.375 | 837.375 | 13 | 3 | 56.3
Demand Measures | - | 2411.9961 | 2411.9961 | - | - | -
Firm Imports (+) / Exports (-) (MW) | - | 600 | 600 | - | - | -
Total | 38981.7924 | 27458.1843 | 27536.7343 | 179 | 3 | -50.2
Back to main menu

## Table 2.2
Back to main menu
Table 2.2: Committed Generation and Electricity Storage Resources Status over the 18-month Reliability Outlook Period
|  |  | Estimated |  | Capacity Considered
Project Name | Zone | Fuel Type | Effective Date | Project Status | Firm (MW) | Planned (MW)
E-LT1 Projects (Within next 18MN) | Various | Various | 2026-Q3 to 2027-Q2 | Under Development | 40 | 196
LT1 Projects (Within next 18MN) | Various | Various | 2026-Q2 to 2026-Q3 | Commercial Operation | 22 | 22
Pickering B | Toronto | Nuclear | 2026-Q4 | Facility OOS | -2064 | -2064
Total |  |  |  |  | -2002 | -1846
Back to main menu

## Table 2.3
Back to main menu
Table 2.3: Monthly Historical Hydroelectric Median Values for Expected Weather Conditions
Month | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Historical Hydroelectric Median Contribution (MW) | 6050.6093 | 5971.1694 | 5770.3863 | 5852.8357 | 5923.069 | 5627.4545 | 5524.8502 | 5215.6997 | 4966.5184 | 5306.8601 | 5581.4618 | 6050.0874
Historical Hydroelectric Median Contribution without Planned Outages (MW) | 6596.6933 | 6539.4715 | 6341.7407 | 6370.8662 | 6398.8543 | 6196.0154 | 6091.866 | 5882.3025 | 5896.4712 | 6156.349 | 6377.987 | 6574.8872
Back to main menu

## Table 2.4
Back to main menu
Table 2.4: Monthly Wind Capacity Contribution Values
Month | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Wind Capacity Contribution (% of Installed Capacity) | 39.82% | 39.82% | 40.77% | 28.93% | 21.65% | 15.21% | 15.21% | 15.21% | 14.96% | 30.7% | 42.12% | 39.82%
Back to main menu

## Table 2.5
Back to main menu
Table 2.5: Monthly Solar Capacity Contribution Values
Month | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Solar Capacity Contribution (% of Installed Capacity) | 0% | 0% | 0.1654% | 2.048% | 5.581% | 19.8% | 19.8% | 19.8% | 7.768% | 0% | 0% | 0%
Back to main menu

## Table 2.6
Back to main menu
Table 2.6: Monthly Off-Peak Wind Capacity Contribution Values
Month | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Off-Peak WCC (% of Installed Capacity) | 39.82% | 39.82% | 40.77% | 28.93% | 21.65% | 15.21% | 15.21% | 15.21% | 14.96% | 30.7% | 42.12% | 39.82%
Back to main menu

## Table 2.7
Back to main menu
Table 2.7: Summary of Available Resources under Expected Weather
| Description [Normal] | Winter Peak 2027 |  | Summer Peak 2027 |  | Winter Peak 2028
# |  | Firm Scenario | Planned Scenario | Firm Scenario | Planned Scenario | Firm Scenario | Planned Scenario
1 | Installed Resources (MW) | 38987.29 | 39133.29 | 38987.29 | 39133.29 | 38987.29 | 39143.27
2 | Total Reductions in Resources (MW) | 12879 | 12937 | 14541 | 14609 | 11609 | 11669
3 | Demand Measures (MW) | 715.7142 | 715.7142 | 2411.9961 | 2411.9961 | 1222.2 | 1222.2
4 | Firm Imports (+) / Exports (-) (MW) | 0 | 0 | 600 | 600 | -600 | -600
5 | Available Resources (MW) | 26824.0043 | 26912.0043 | 27458.2861 | 27536.2861 | 28000.49 | 28096.47
6 | Bottling | 136.2357 | 136.2357 | 0 | 0 | 399.2573 | 399.2573
7 | Available Resources without Bottling (MW) | 26960.2399 | 27048.2399 | 27458.2861 | 27536.2861 | 28399.7473 | 28495.7273
Back to main menu

## Table 3.1
Back to main menu
Table 3.1 Firm: Summary of Zonal Energy for Firm Scenario, Expected Weather
| 18-Month Energy Demand |  | 18-Month Energy Production |  | Net Inter-Zonal Energy Transfer | Zonal Energy Demand on Peak Day of 18-Month Period | Available Energy on Peak Day of 18 Month Period
| TWh | Average MW | TWh | Average MW | TWh | GWh | GWh
Ontario | 226 | 17183 | 228.2 | 17348 | 2.2 | 495.9 | 17.9
Bruce | 1.2 | 89 | 64.9 | 4934 | 63.7 | 1.8 | 0.1
East | 14.1 | 1073 | 23.3 | 1770 | 9.2 | 29.8 | 1.2
Essa | 16.5 | 1252 | 4.6 | 353 | -11.9 | 36.2 | 0.2
Niagara | 8.1 | 613 | 21.8 | 1660 | 13.7 | 17.5 | 1.8
Northeast | 17.4 | 1323 | 16.6 | 1266 | -0.8 | 28 | 0.8
Northwest | 5.9 | 451 | 7 | 532 | 1.1 | 9.8 | 0.3
Ottawa | 13.9 | 1054 | 1 | 80 | -12.9 | 30.7 | 0.8
Southwest | 45.2 | 3437 | 12.9 | 981 | -32.3 | 100.2 | 6.5
Toronto | 76.9 | 5848 | 39.7 | 3019 | -37.2 | 183.5 | 5.2
West | 26.9 | 2043 | 36.2 | 2755 | 9.3 | 58.4 | 0.9
Back to main menu

## Table 3.2
Back to main menu
Table 3.2 Planned: Summary of Zonal Energy for Planned Scenario, Expected Weather
| 18-Month Energy Demand |  | 18-Month Energy Production |  | Net Inter-Zonal Energy Transfer | Zonal Energy Demand on Peak Day of 18-Month Period | Available Energy on Peak Day of 18 Month Period
| TWh | Average MW | TWh | Average MW | TWh | GWh | GWh
Ontario | 228.1 | 17346 | 230.3 | 17511 | 2.2 | 500.4 | 547.6
Bruce | 1.2 | 89 | 64.9 | 4935 | 63.7 | 1.8 | 119.9
East | 14.1 | 1074 | 23.7 | 1800 | 9.6 | 29.8 | 101.1
Essa | 16.5 | 1253 | 4.8 | 363 | -11.7 | 36.2 | 19.2
Niagara | 8.1 | 613 | 21.9 | 1664 | 13.8 | 17.5 | 48.8
Northeast | 17.4 | 1323 | 16.7 | 1267 | -0.7 | 28 | 34.8
Northwest | 5.9 | 451 | 7 | 533 | 1.1 | 9.8 | 19.7
Ottawa | 13.9 | 1054 | 1.1 | 80 | -12.8 | 30.7 | 3.1
Southwest | 46.9 | 3568 | 13.1 | 994 | -33.8 | 103.6 | 25
Toronto | 76.9 | 5848 | 40.1 | 3046 | -36.8 | 183.6 | 95.9
West | 27.3 | 2075 | 37.2 | 2831 | 9.9 | 59.4 | 80
Back to main menu

## Table 3.3
Back to main menu
Table 3.3 Firm: Ontario Energy Production by Fuel Type for the Firm Scenario, Expected Weather
Fuel Type (Grid Connected) | 2026 | 2027 | 2028 | Total
Nuclear | 15798.2 | 58449.92 | 16927.05 | 91175.17
Hydro | 9074.11 | 37141.35 | 9621.41 | 55836.87
Gas & Oil | 7392.58 | 39036.57 | 11500.4 | 57929.55
Wind | 4047.29 | 12982.3 | 4010.17 | 21039.76
Bio Fuel | 88.54 | 384.91 | 96.73 | 570.18
Storage | 64.94 | 429.65 | 79.67 | 574.26
Other | 109.39 | 784.92 | 154.83 | 1049.14
Total | 36575.05 | 149209.62 | 42390.26 | 228174.93
Back to main menu

## Table 3.4
Back to main menu
Table 3.4 Planned: Ontario Energy Production by Fuel Type for the Planned Scenario, Expected Weather
Fuel Type (Grid Connected) | 2026 | 2027 | 2028 | Total
Nuclear | 15798.2 | 58449.98 | 16927.28 | 91175.46
Hydro | 9074.11 | 37145.05 | 9621.41 | 55840.57
Gas & Oil | 7449.15 | 40369.25 | 12149.72 | 59968.12
Wind | 4048.34 | 13009.33 | 4010.53 | 21068.2
Bio Fuel | 88.59 | 387.57 | 97.9 | 574.06
Storage | 66.42 | 478.78 | 89.94 | 635.14
Other | 109.42 | 791.91 | 154.8 | 1056.13
Total | 36634.23 | 150631.87 | 43051.58 | 230317.68
Back to main menu

## Table 3.5
Back to main menu
Table 3.5: Assessment of Resource Adequacy: Expected Weather, Firm Scenario
Week | Ontario | Total Installed | Total Reductions | Demand | Firm Imports (+) | Total Available | Required | Available | Available | Required | Required | Reserve Above
Ending | Demand | Capacity | in Resources | Measures | Exports (-) | Resources | Resources | Reserve | Reserve | Reserve | Reserve | Requirement
Day | MW | MW | MW | MW | MW | MW | MW | % | MW | % | MW | MW
2026-10-04 | 18417 | 38987.29 | 16657 | 1127.2138 | 896.1 | 23453.6038 | 23359 | 27.35 | 5037 | 26.83 | 4942 | 95
2026-10-11 | 17890 | 38987.29 | 16844 | 850.4636 | 596.1 | 22989.8536 | 22078 | 28.51 | 5100 | 23.41 | 4188 | 912
2026-10-18 | 17889 | 38987.29 | 16865 | 850.4636 | 596.1 | 22968.8536 | 21473 | 28.4 | 5080 | 20.03 | 3584 | 1496
2026-10-25 | 18166 | 38987.29 | 15799 | 850.4636 | 596.1 | 24034.8536 | 21994 | 32.31 | 5869 | 21.07 | 3828 | 2041
2026-11-01 | 18441 | 38987.29 | 16586 | 850.4636 | 596.1 | 23247.8536 | 22289 | 26.07 | 4807 | 20.87 | 3848 | 959
2026-11-08 | 18993 | 38987.29 | 15175 | 828.4437 | 0 | 24640.7337 | 23191 | 29.74 | 5648 | 22.1 | 4198 | 1450
2026-11-15 | 19490 | 38987.29 | 15464 | 828.4437 | 0 | 24351.7337 | 23796 | 24.95 | 4862 | 22.09 | 4306 | 556
2026-11-22 | 20074 | 38987.29 | 15025 | 828.4437 | 0 | 24790.7337 | 24116 | 23.5 | 4717 | 20.14 | 4042 | 675
2026-11-29 | 20588 | 38987.29 | 14779 | 828.4437 | 0 | 25036.7337 | 24620 | 21.61 | 4449 | 19.58 | 4032 | 417
2026-12-06 | 20952 | 38987.29 | 14490 | 828.4437 | 0 | 25325.7337 | 24755 | 20.88 | 4374 | 18.15 | 3803 | 571
2026-12-13 | 21278 | 38987.29 | 13546 | 828.4437 | 0 | 26269.7337 | 25365 | 23.46 | 4992 | 19.21 | 4087 | 905
2026-12-20 | 21481 | 38987.29 | 12920 | 828.4437 | 0 | 26895.7337 | 25699 | 25.21 | 5415 | 19.64 | 4218 | 1197
2026-12-27 | 20908 | 38987.29 | 12895 | 828.4437 | 0 | 26920.7337 | 25392 | 28.76 | 6013 | 21.45 | 4484 | 1529
2027-01-03 | 21056 | 38987.29 | 12166 | 828.4437 | 0 | 27649.7337 | 25861 | 31.32 | 6594 | 22.82 | 4805 | 1789
2027-01-10 | 21954 | 38987.29 | 12879 | 715.7142 | 0 | 26824.0043 | 26574 | 22.18 | 4870 | 21.04 | 4620 | 250
2027-01-17 | 21833 | 38987.29 | 13803 | 737.9142 | 0 | 25922.2043 | 26208 | 18.73 | 4089 | 20.04 | 4375 | -286
2027-01-24 | 21910 | 38987.29 | 13864 | 715.7142 | 0 | 25839.0043 | 26339 | 17.93 | 3929 | 20.21 | 4429 | -500
2027-01-31 | 21886 | 38987.29 | 13907 | 715.7142 | 0 | 25796.0043 | 26162 | 17.87 | 3910 | 19.54 | 4276 | -366
2027-02-07 | 21388 | 38987.29 | 14498 | 828.4437 | 0 | 25317.7337 | 25659 | 18.37 | 3930 | 19.97 | 4271 | -341
2027-02-14 | 21384 | 38987.29 | 14527 | 828.4437 | 0 | 25288.7337 | 25544 | 18.26 | 3905 | 19.45 | 4160 | -255
2027-02-21 | 21100 | 38987.29 | 14367 | 828.4437 | 0 | 25448.7337 | 25451 | 20.61 | 4349 | 20.62 | 4351 | -2
2027-02-28 | 20950 | 38987.29 | 14385 | 828.4437 | 0 | 25430.7337 | 25158 | 21.39 | 4481 | 20.09 | 4208 | 273
2027-03-07 | 20430 | 38987.29 | 14277 | 828.4437 | 0 | 25538.7337 | 24560 | 25.01 | 5109 | 20.22 | 4130 | 979
2027-03-14 | 19986 | 38987.29 | 14357 | 828.4437 | 0 | 25458.7337 | 24116 | 27.38 | 5473 | 20.66 | 4130 | 1343
2027-03-21 | 19556 | 38987.29 | 13910 | 828.4437 | 0 | 25905.7337 | 23686 | 32.47 | 6350 | 21.12 | 4130 | 2220
2027-03-28 | 19050 | 38987.29 | 14034 | 828.4437 | 0 | 25781.7337 | 23170 | 35.34 | 6732 | 21.63 | 4120 | 2612
2027-04-04 | 18696 | 38987.29 | 16409 | 828.4437 | 0 | 23406.7337 | 22104 | 25.2 | 4711 | 18.23 | 3408 | 1303
2027-04-11 | 18241 | 38987.29 | 16430 | 828.4437 | 0 | 23385.7337 | 21874 | 28.21 | 5145 | 19.92 | 3633 | 1512
2027-04-18 | 17922 | 38987.29 | 19608 | 828.4437 | 0 | 20207.7337 | 21243 | 12.76 | 2286 | 18.53 | 3321 | -1035
2027-04-25 | 17664 | 38987.29 | 19749 | 828.4437 | 0 | 20066.7337 | 21072 | 13.6 | 2403 | 19.29 | 3408 | -1005
2027-05-02 | 17482 | 38987.29 | 18319 | 828.4437 | 0 | 21496.7337 | 21037 | 22.97 | 4015 | 20.34 | 3555 | 460
2027-05-09 | 17402 | 38987.29 | 18588 | 1934.9294 | 600 | 22334.2194 | 20948 | 28.34 | 4932 | 20.38 | 3546 | 1386
2027-05-16 | 17475 | 38987.29 | 18615 | 1934.9294 | 600 | 22307.2194 | 21663 | 27.65 | 4832 | 23.97 | 4188 | 644
2027-05-23 | 17903 | 38987.29 | 17830 | 1934.9294 | 600 | 23092.2194 | 23273 | 28.98 | 5189 | 29.99 | 5370 | -181
2027-05-30 | 18201 | 38987.29 | 17336 | 1934.9294 | 600 | 23586.2194 | 25194 | 29.59 | 5385 | 38.42 | 6993 | -1608
2027-06-06 | 19047 | 38987.29 | 13894 | 2361.9961 | 600 | 27455.2861 | 26001 | 44.14 | 8408 | 36.51 | 6954 | 1454
2027-06-13 | 19547 | 38987.29 | 14151 | 2361.9961 | 600 | 27198.2861 | 26226 | 39.14 | 7651 | 34.17 | 6679 | 972
2027-06-20 | 20602 | 38987.29 | 13982 | 2361.9961 | 600 | 27367.2861 | 27047 | 32.84 | 6765 | 31.28 | 6445 | 320
2027-06-27 | 21480 | 38987.29 | 13944 | 2361.9961 | 600 | 27405.2861 | 26850 | 27.58 | 5925 | 25 | 5370 | 555
2027-07-04 | 21481 | 38987.29 | 14103 | 2361.9961 | 600 | 27246.2861 | 26949 | 26.84 | 5765 | 25.46 | 5468 | 297
2027-07-11 | 22244 | 38987.29 | 14439 | 2361.9961 | 600 | 26910.2861 | 27751 | 20.98 | 4666 | 24.76 | 5507 | -841
2027-07-18 | 22447 | 38987.29 | 14289 | 2361.9961 | 600 | 27060.2861 | 28033 | 20.55 | 4613 | 24.89 | 5586 | -973
2027-07-25 | 22455 | 38987.29 | 14541 | 2411.9961 | 600 | 26858.2861 | 27806 | 19.61 | 4403 | 23.83 | 5351 | -948
2027-08-01 | 22397 | 38987.29 | 14354 | 2411.9961 | 600 | 27045.2861 | 28022 | 20.75 | 4648 | 25.11 | 5625 | -977
2027-08-08 | 21844 | 38987.29 | 14720 | 2411.9961 | 600 | 26679.2861 | 27488 | 22.13 | 4835 | 25.84 | 5644 | -809
2027-08-15 | 21807 | 38987.29 | 15087 | 2411.9961 | 600 | 26312.2861 | 26827 | 20.66 | 4505 | 23.02 | 5020 | -515
2027-08-22 | 21612 | 38987.29 | 15126 | 2361.9961 | 600 | 26223.2861 | 26212 | 21.34 | 4611 | 21.28 | 4600 | 11
2027-08-29 | 21644 | 38987.29 | 15209 | 2361.9961 | 600 | 26140.2861 | 25960 | 20.77 | 4496 | 19.94 | 4316 | 180
2027-09-05 | 21298 | 38987.29 | 14916 | 2361.9961 | 600 | 26433.2861 | 26610 | 24.11 | 5135 | 24.94 | 5312 | -177
2027-09-12 | 20202 | 38987.29 | 15090 | 2411.9961 | 600 | 26309.2861 | 26394 | 30.23 | 6107 | 30.65 | 6192 | -85
2027-09-19 | 19727 | 38987.29 | 15108 | 2361.9961 | 600 | 26241.2861 | 25509 | 33.02 | 6514 | 29.31 | 5782 | 732
2027-09-26 | 19251 | 38987.29 | 16304 | 2361.9961 | 600 | 25045.2861 | 25053 | 30.1 | 5794 | 30.14 | 5802 | -8
2027-10-03 | 18975 | 38987.29 | 17364 | 2361.9961 | 600 | 23985.2861 | 24053 | 26.4 | 5010 | 26.76 | 5078 | -68
2027-10-10 | 18408 | 38987.29 | 17418 | 1934.9294 | 600 | 23504.2194 | 22606 | 27.68 | 5096 | 22.81 | 4198 | 898
2027-10-17 | 18548 | 38987.29 | 16908 | 1934.9294 | 600 | 24014.2194 | 21898 | 29.47 | 5466 | 18.06 | 3350 | 2116
2027-10-24 | 18642 | 38987.29 | 17587 | 1934.9294 | 600 | 23335.2194 | 21826 | 25.17 | 4693 | 17.08 | 3184 | 1509
2027-10-31 | 18917 | 38987.29 | 16410 | 1934.9294 | 600 | 24512.2194 | 21993 | 29.58 | 5595 | 16.26 | 3076 | 2519
2027-11-07 | 19471 | 38987.29 | 14580 | 1334.9294 | -600 | 25142.2194 | 23513 | 29.13 | 5671 | 20.76 | 4042 | 1629
2027-11-14 | 19918 | 38987.29 | 15636 | 1334.9294 | -600 | 24086.2194 | 23785 | 20.93 | 4168 | 19.41 | 3867 | 301
2027-11-21 | 20507 | 38987.29 | 13971 | 1334.9294 | -600 | 25751.2194 | 24647 | 25.57 | 5244 | 20.19 | 4140 | 1104
2027-11-28 | 21068 | 38987.29 | 13656 | 1334.9294 | -600 | 26066.2194 | 25276 | 23.72 | 4998 | 19.97 | 4208 | 790
2027-12-05 | 21396 | 38987.29 | 13324 | 1334.9294 | -600 | 26398.2194 | 25219 | 23.38 | 5002 | 17.87 | 3823 | 1179
2027-12-12 | 21764 | 38987.29 | 12864 | 1334.9294 | -600 | 26858.2194 | 25709 | 23.41 | 5094 | 18.13 | 3945 | 1149
2027-12-19 | 21987 | 38987.29 | 12724 | 1334.9294 | -600 | 26998.2194 | 26079 | 22.79 | 5011 | 18.61 | 4092 | 919
2027-12-26 | 22019 | 38987.29 | 12450 | 1334.9294 | -600 | 27272.2194 | 26394 | 23.86 | 5253 | 19.87 | 4375 | 878
2028-01-02 | 21771 | 38987.29 | 12549 | 1334.9294 | -600 | 27173.2194 | 26376 | 24.81 | 5402 | 21.15 | 4605 | 797
2028-01-09 | 22430 | 38987.29 | 12067 | 1334.9294 | -600 | 27655.2194 | 27006 | 23.29 | 5225 | 20.4 | 4576 | 649
2028-01-16 | 22841 | 38987.29 | 12264 | 1222.2 | -600 | 27345.49 | 27177 | 19.72 | 4504 | 18.98 | 4336 | 168
2028-01-23 | 22911 | 38987.29 | 11680 | 1222.2 | -600 | 27929.49 | 27399 | 21.9 | 5018 | 19.59 | 4488 | 530
2028-01-30 | 22916 | 38987.29 | 11609 | 1222.2 | -600 | 28000.49 | 27458 | 22.19 | 5084 | 19.82 | 4542 | 542
2028-02-06 | 22604 | 38987.29 | 12757 | 1334.9294 | -600 | 26965.2194 | 26905 | 19.29 | 4361 | 19.03 | 4301 | 60
2028-02-13 | 22256 | 38987.29 | 12762 | 1334.9294 | -600 | 26960.2194 | 26508 | 21.14 | 4704 | 19.1 | 4252 | 452
2028-02-20 | 22313 | 38987.29 | 12692 | 1244.4 | -600 | 26939.69 | 26561 | 20.74 | 4627 | 19.04 | 4248 | 379
2028-02-27 | 21733 | 38987.29 | 12529 | 1244.4 | -600 | 27102.69 | 26127 | 24.71 | 5370 | 20.22 | 4394 | 976
2028-03-05 | 21551 | 38987.29 | 13117 | 1334.9294 | -600 | 26605.2194 | 25696 | 23.45 | 5054 | 19.23 | 4145 | 909
2028-03-12 | 20986 | 38987.29 | 13336 | 1334.9294 | -600 | 26386.2194 | 25058 | 25.73 | 5400 | 19.4 | 4072 | 1328
2028-03-19 | 20557 | 38987.29 | 13462 | 1334.9294 | -600 | 26260.2194 | 24697 | 27.74 | 5703 | 20.14 | 4140 | 1563
2028-03-26 | 20011 | 38987.29 | 13596 | 1334.9294 | -600 | 26126.2194 | 24131 | 30.56 | 6115 | 20.59 | 4120 | 1995
2028-04-02 | 19616 | 38987.29 | 13129 | 1334.9294 | -600 | 26593.2194 | 23283 | 35.57 | 6977 | 18.69 | 3667 | 3310
Note: The reader should be aware that security and adequacy assessments are published on the IESO web site on a daily basis that progressively supersedes information presented
in this report.
Back to main menu

## Table 3.6
Back to main menu
Table 3.6: Assessment of Resource Adequacy: Expected Weather, Planned Scenario
Week | Ontario | Total Installed | Total Reductions | Demand | Firm Imports (+) | Total Available | Required | Available | Available | Required | Required | Reserve Above
Ending | Demand | Capacity | in Resources | Measures | Exports (-) | Resources | Resources | Reserve | Reserve | Reserve | Reserve | Requirement
Day | MW | MW | MW | MW | MW | MW | MW | % | MW | % | MW | MW
2026-10-04 | 18480 | 39027.29 | 16695 | 1127.2138 | 896.1 | 23455.6038 | 23422 | 26.93 | 4976 | 26.74 | 4942 | 34
2026-10-11 | 17971 | 39027.29 | 16805 | 850.4636 | 596.1 | 23068.8536 | 22169 | 28.37 | 5098 | 23.36 | 4198 | 900
2026-10-18 | 17975 | 39133.29 | 16932 | 850.4636 | 596.1 | 23047.8536 | 21559 | 28.22 | 5073 | 19.94 | 3584 | 1489
2026-10-25 | 18236 | 39133.29 | 15866 | 850.4636 | 596.1 | 24113.8536 | 22064 | 32.23 | 5878 | 20.99 | 3828 | 2050
2026-11-01 | 18523 | 39133.29 | 16662 | 850.4636 | 596.1 | 23317.8536 | 22376 | 25.89 | 4795 | 20.8 | 3853 | 942
2026-11-08 | 19107 | 39133.29 | 15234 | 828.4437 | 0 | 24727.7337 | 23310 | 29.42 | 5621 | 22 | 4203 | 1418
2026-11-15 | 19619 | 39133.29 | 15523 | 828.4437 | 0 | 24438.7337 | 23930 | 24.57 | 4820 | 21.97 | 4311 | 509
2026-11-22 | 20184 | 39133.29 | 15084 | 828.4437 | 0 | 24877.7337 | 24226 | 23.26 | 4694 | 20.03 | 4042 | 652
2026-11-29 | 20699 | 39133.29 | 14838 | 828.4437 | 0 | 25123.7337 | 24731 | 21.38 | 4425 | 19.48 | 4032 | 393
2026-12-06 | 21103 | 39133.29 | 14549 | 828.4437 | 0 | 25412.7337 | 24911 | 20.42 | 4310 | 18.04 | 3808 | 502
2026-12-13 | 21422 | 39133.29 | 13605 | 828.4437 | 0 | 26356.7337 | 25514 | 23.04 | 4935 | 19.1 | 4092 | 843
2026-12-20 | 21635 | 39133.29 | 12979 | 828.4437 | 0 | 26982.7337 | 25853 | 24.72 | 5348 | 19.5 | 4218 | 1130
2026-12-27 | 21040 | 39133.29 | 12954 | 828.4437 | 0 | 27007.7337 | 25533 | 28.37 | 5968 | 21.35 | 4493 | 1475
2027-01-03 | 21097 | 39133.29 | 12225 | 828.4437 | 0 | 27736.7337 | 25911 | 31.47 | 6640 | 22.82 | 4814 | 1826
2027-01-10 | 22128 | 39133.29 | 12937 | 715.7142 | 0 | 26912.0043 | 26753 | 21.62 | 4784 | 20.9 | 4625 | 159
2027-01-17 | 22015 | 39133.29 | 13860 | 737.9142 | 0 | 26011.2043 | 26390 | 18.15 | 3996 | 19.87 | 4375 | -379
2027-01-24 | 22080 | 39133.29 | 13921 | 715.7142 | 0 | 25928.0043 | 26514 | 17.43 | 3848 | 20.08 | 4434 | -586
2027-01-31 | 22066 | 39133.29 | 13964 | 715.7142 | 0 | 25885.0043 | 26342 | 17.31 | 3819 | 19.38 | 4276 | -457
2027-02-07 | 21554 | 39133.29 | 14555 | 828.4437 | 0 | 25406.7337 | 25830 | 17.88 | 3853 | 19.84 | 4276 | -423
2027-02-14 | 21554 | 39133.29 | 14584 | 828.4437 | 0 | 25377.7337 | 25719 | 17.74 | 3824 | 19.32 | 4165 | -341
2027-02-21 | 21266 | 39133.29 | 14424 | 828.4437 | 0 | 25537.7337 | 25622 | 20.09 | 4272 | 20.48 | 4356 | -84
2027-02-28 | 21115 | 39133.29 | 14442 | 828.4437 | 0 | 25519.7337 | 25323 | 20.86 | 4405 | 19.93 | 4208 | 197
2027-03-07 | 20572 | 39133.29 | 14334 | 828.4437 | 0 | 25627.7337 | 24707 | 24.58 | 5056 | 20.1 | 4135 | 921
2027-03-14 | 20134 | 39133.29 | 14414 | 828.4437 | 0 | 25547.7337 | 24269 | 26.89 | 5414 | 20.54 | 4135 | 1279
2027-03-21 | 19616 | 39133.29 | 13967 | 828.4437 | 0 | 25994.7337 | 23746 | 32.52 | 6379 | 21.05 | 4130 | 2249
2027-03-28 | 19190 | 39133.29 | 14091 | 828.4437 | 0 | 25870.7337 | 23315 | 34.82 | 6681 | 21.5 | 4125 | 2556
2027-04-04 | 18756 | 39133.29 | 16466 | 828.4437 | 0 | 23495.7337 | 22164 | 25.27 | 4740 | 18.17 | 3408 | 1332
2027-04-11 | 18407 | 39133.29 | 16487 | 828.4437 | 0 | 23474.7337 | 22049 | 27.53 | 5068 | 19.79 | 3642 | 1426
2027-04-18 | 18075 | 39133.29 | 19665 | 828.4437 | 0 | 20296.7337 | 21405 | 12.29 | 2222 | 18.42 | 3330 | -1108
2027-04-25 | 17821 | 39133.29 | 19806 | 828.4437 | 0 | 20155.7337 | 21229 | 13.1 | 2335 | 19.12 | 3408 | -1073
2027-05-02 | 17636 | 39133.29 | 18369 | 828.4437 | 0 | 21592.7337 | 21191 | 22.44 | 3957 | 20.16 | 3555 | 402
2027-05-09 | 17576 | 39133.29 | 18656 | 1934.9294 | 600 | 22412.2194 | 21122 | 27.51 | 4836 | 20.18 | 3546 | 1290
2027-05-16 | 17663 | 39133.29 | 18682 | 1934.9294 | 600 | 22386.2194 | 21861 | 26.74 | 4723 | 23.77 | 4198 | 525
2027-05-23 | 18088 | 39133.29 | 17897 | 1934.9294 | 600 | 23171.2194 | 23439 | 28.1 | 5083 | 29.58 | 5351 | -268
2027-05-30 | 18394 | 39133.29 | 17404 | 1934.9294 | 600 | 23664.2194 | 25387 | 28.65 | 5270 | 38.02 | 6993 | -1723
2027-06-06 | 19254 | 39133.29 | 13961 | 2361.9961 | 600 | 27534.2861 | 26208 | 43 | 8280 | 36.12 | 6954 | 1326
2027-06-13 | 19751 | 39133.29 | 14219 | 2361.9961 | 600 | 27276.2861 | 26430 | 38.1 | 7525 | 33.82 | 6679 | 846
2027-06-20 | 20796 | 39133.29 | 14049 | 2361.9961 | 600 | 27446.2861 | 27241 | 31.98 | 6650 | 30.99 | 6445 | 205
2027-06-27 | 21671 | 39133.29 | 14012 | 2361.9961 | 600 | 27483.2861 | 27041 | 26.82 | 5812 | 24.78 | 5370 | 442
2027-07-04 | 21710 | 39133.29 | 14170 | 2361.9961 | 600 | 27325.2861 | 27168 | 25.86 | 5615 | 25.14 | 5458 | 157
2027-07-11 | 22501 | 39133.29 | 14507 | 2361.9961 | 600 | 26988.2861 | 28008 | 19.94 | 4487 | 24.47 | 5507 | -1020
2027-07-18 | 22709 | 39133.29 | 14357 | 2361.9961 | 600 | 27138.2861 | 28295 | 19.5 | 4429 | 24.6 | 5586 | -1157
2027-07-25 | 22718 | 39133.29 | 14609 | 2411.9961 | 600 | 26936.2861 | 28069 | 18.57 | 4218 | 23.55 | 5351 | -1133
2027-08-01 | 22571 | 39133.29 | 14421 | 2411.9961 | 600 | 27124.2861 | 28196 | 20.17 | 4553 | 24.92 | 5625 | -1072
2027-08-08 | 22138 | 39133.29 | 14787 | 2411.9961 | 600 | 26758.2861 | 27782 | 20.87 | 4620 | 25.49 | 5644 | -1024
2027-08-15 | 22100 | 39133.29 | 15155 | 2411.9961 | 600 | 26390.2861 | 27130 | 19.41 | 4290 | 22.76 | 5030 | -740
2027-08-22 | 21895 | 39133.29 | 15194 | 2361.9961 | 600 | 26301.2861 | 26505 | 20.12 | 4406 | 21.06 | 4610 | -204
2027-08-29 | 21918 | 39133.29 | 15276 | 2361.9961 | 600 | 26219.2861 | 26234 | 19.62 | 4301 | 19.69 | 4316 | -15
2027-09-05 | 21614 | 39133.29 | 14977 | 2361.9961 | 600 | 26518.2861 | 26926 | 22.69 | 4904 | 24.58 | 5312 | -408
2027-09-12 | 20521 | 39133.29 | 15150 | 2411.9961 | 600 | 26395.2861 | 26713 | 28.62 | 5874 | 30.17 | 6192 | -318
2027-09-19 | 20055 | 39143.27 | 15178 | 2361.9961 | 600 | 26327.2661 | 25857 | 31.27 | 6272 | 28.93 | 5802 | 470
2027-09-26 | 19582 | 39143.27 | 16375 | 2361.9961 | 600 | 25130.2661 | 25384 | 28.33 | 5548 | 29.63 | 5802 | -254
2027-10-03 | 19281 | 39143.27 | 17434 | 2361.9961 | 600 | 24071.2661 | 24359 | 24.84 | 4790 | 26.34 | 5078 | -288
2027-10-10 | 18746 | 39143.27 | 17488 | 1934.9294 | 600 | 23590.1994 | 22944 | 25.84 | 4844 | 22.39 | 4198 | 646
2027-10-17 | 18790 | 39143.27 | 16978 | 1934.9294 | 600 | 24100.1994 | 22150 | 28.26 | 5310 | 17.88 | 3360 | 1950
2027-10-24 | 18969 | 39143.27 | 17657 | 1934.9294 | 600 | 23421.1994 | 22153 | 23.47 | 4452 | 16.79 | 3184 | 1268
2027-10-31 | 19251 | 39143.27 | 16480 | 1934.9294 | 600 | 24598.1994 | 22327 | 27.78 | 5347 | 15.98 | 3076 | 2271
2027-11-07 | 19837 | 39143.27 | 14644 | 1334.9294 | -600 | 25234.1994 | 23884 | 27.21 | 5397 | 20.4 | 4047 | 1350
2027-11-14 | 20294 | 39143.27 | 15700 | 1334.9294 | -600 | 24178.1994 | 24166 | 19.14 | 3884 | 19.08 | 3872 | 12
2027-11-21 | 20871 | 39143.27 | 14035 | 1334.9294 | -600 | 25843.1994 | 25016 | 23.82 | 4972 | 19.86 | 4145 | 827
2027-11-28 | 21419 | 39143.27 | 13720 | 1334.9294 | -600 | 26158.1994 | 25632 | 22.13 | 4739 | 19.67 | 4213 | 526
2027-12-05 | 21792 | 39143.27 | 13388 | 1334.9294 | -600 | 26490.1994 | 25620 | 21.56 | 4698 | 17.57 | 3828 | 870
2027-12-12 | 22162 | 39143.27 | 12928 | 1334.9294 | -600 | 26950.1994 | 26112 | 21.6 | 4788 | 17.82 | 3950 | 838
2027-12-19 | 22396 | 39143.27 | 12788 | 1334.9294 | -600 | 27090.1994 | 26488 | 20.96 | 4694 | 18.27 | 4092 | 602
2027-12-26 | 22417 | 39143.27 | 12514 | 1334.9294 | -600 | 27364.1994 | 26801 | 22.07 | 4947 | 19.56 | 4384 | 563
2028-01-02 | 22194 | 39143.27 | 12613 | 1334.9294 | -600 | 27265.1994 | 26804 | 22.85 | 5071 | 20.77 | 4610 | 461
2028-01-09 | 22866 | 39143.27 | 12127 | 1334.9294 | -600 | 27751.1994 | 27446 | 21.36 | 4885 | 20.03 | 4580 | 305
2028-01-16 | 23300 | 39143.27 | 12324 | 1222.2 | -600 | 27441.47 | 27636 | 17.77 | 4141 | 18.61 | 4336 | -195
2028-01-23 | 23349 | 39143.27 | 11740 | 1222.2 | -600 | 28025.47 | 27842 | 20.03 | 4676 | 19.24 | 4493 | 183
2028-01-30 | 23358 | 39143.27 | 11669 | 1222.2 | -600 | 28096.47 | 27905 | 20.28 | 4738 | 19.47 | 4547 | 191
2028-02-06 | 23042 | 39143.27 | 12817 | 1334.9294 | -600 | 27061.1994 | 27348 | 17.44 | 4019 | 18.69 | 4306 | -287
2028-02-13 | 22685 | 39143.27 | 12822 | 1334.9294 | -600 | 27056.1994 | 26942 | 19.27 | 4371 | 18.77 | 4257 | 114
2028-02-20 | 22610 | 39143.27 | 12752 | 1244.4 | -600 | 27035.67 | 26862 | 19.58 | 4426 | 18.81 | 4252 | 174
2028-02-27 | 22152 | 39143.27 | 12589 | 1244.4 | -600 | 27198.67 | 26546 | 22.78 | 5047 | 19.84 | 4394 | 653
2028-03-05 | 21977 | 39143.27 | 13177 | 1334.9294 | -600 | 26701.1994 | 26127 | 21.5 | 4724 | 18.88 | 4150 | 574
2028-03-12 | 21398 | 39143.27 | 13396 | 1334.9294 | -600 | 26482.1994 | 25470 | 23.76 | 5084 | 19.03 | 4072 | 1012
2028-03-19 | 20854 | 39143.27 | 13522 | 1334.9294 | -600 | 26356.1994 | 24999 | 26.38 | 5502 | 19.88 | 4145 | 1357
2028-03-26 | 20419 | 39143.27 | 13657 | 1334.9294 | -600 | 26221.1994 | 24544 | 28.41 | 5802 | 20.2 | 4125 | 1677
2028-04-02 | 20032 | 39143.27 | 13189 | 1334.9294 | -600 | 26689.1994 | 23704 | 33.23 | 6657 | 18.33 | 3672 | 2985
Note: The reader should be aware that security and adequacy assessments are published on the IESO web site on a daily basis that progressively supersedes
information presented in this report.
Back to main menu

## Table 3.7
Back to main menu
Table 3.7: Zonal Bottled Generation: Expected Weather, Both Scenarios
Week | Firm Scenario | Firm Scenario | Firm Scenario | Planned Scenario | Planned Scenario | Planned Scenario
Ending | Bruce & West | Northeast | Northwest | Bruce & West | Northeast | Northwest
Day | MW | MW | MW | MW | MW | MW
2026-10-04 | 135.2953 | 0 | 0 | 135.2953 | 0 | 0
2026-10-11 | 0 | 0 | 0 | 0 | 0 | 0
2026-10-18 | 742.6082 | 0 | 0 | 742.6082 | 0 | 0
2026-10-25 | 0 | 0 | 0 | 0 | 0 | 0
2026-11-01 | 0 | 0 | 0 | 0 | 0 | 0
2026-11-08 | 0 | 0 | 0 | 0 | 0 | 0
2026-11-15 | 0 | 0 | 0 | 0 | 0 | 0
2026-11-22 | 521.284 | 0 | 0 | 521.284 | 0 | 0
2026-11-29 | 440.6249 | 0 | 0 | 440.6249 | 0 | 0
2026-12-06 | 401.3628 | 0 | 0 | 401.3628 | 0 | 0
2026-12-13 | 0 | 0 | 0 | 0 | 0 | 0
2026-12-20 | 256.3936 | 0 | 0 | 256.3936 | 0 | 0
2026-12-27 | 482.9173 | 0 | 0 | 482.9173 | 0 | 0
2027-01-03 | 727.1187 | 0 | 0 | 727.1187 | 0 | 0
2027-01-10 | 136.2357 | 0 | 0 | 136.2357 | 0 | 0
2027-01-17 | 0.94872 | 0 | 0 | 0.94872 | 0 | 0
2027-01-24 | 69.0787 | 0 | 0 | 69.0787 | 0 | 0
2027-01-31 | 8.3245 | 0 | 0 | 8.3245 | 0 | 0
2027-02-07 | 432.5985 | 0 | 0 | 432.5985 | 0 | 0
2027-02-14 | 507.12 | 0 | 0 | 507.12 | 0 | 0
2027-02-21 | 497.1123 | 0 | 0 | 497.1123 | 0 | 0
2027-02-28 | 479.1103 | 0 | 0 | 479.1103 | 0 | 0
2027-03-07 | 558.7075 | 0 | 0 | 558.7075 | 0 | 0
2027-03-14 | 649.495 | 0 | 0 | 649.495 | 0 | 0
2027-03-21 | 1017.1057 | 0 | 0 | 1017.1057 | 0 | 0
2027-03-28 | 1237.7807 | 0 | 0 | 1237.7807 | 0 | 0
2027-04-04 | 297.4086 | 0 | 0 | 297.4086 | 0 | 0
2027-04-11 | 341.957 | 0 | 0 | 341.957 | 0 | 0
2027-04-18 | 901.2725 | 0 | 0 | 901.2725 | 0 | 0
2027-04-25 | 1208.0348 | 0 | 0 | 1208.0348 | 0 | 0
2027-05-02 | 1958.502 | 0 | 0 | 1958.502 | 0 | 0
2027-05-09 | 1507.1174 | 0 | 0 | 1507.1174 | 0 | 0
2027-05-16 | 1830.5224 | 0 | 0 | 1830.5224 | 0 | 0
2027-05-23 | 1278.4448 | 0 | 0 | 1278.4448 | 0 | 0
2027-05-30 | 1533.6428 | 0 | 0 | 1533.6428 | 0 | 0
2027-06-06 | 0 | 0 | 0 | 0 | 0 | 0
2027-06-13 | 0 | 0 | 0 | 0 | 0 | 0
2027-06-20 | 0 | 0 | 0 | 0 | 0 | 0
2027-06-27 | 0 | 0 | 0 | 0 | 0 | 0
2027-07-04 | 0 | 0 | 0 | 0 | 0 | 0
2027-07-11 | 0 | 0 | 0 | 0 | 0 | 0
2027-07-18 | 0 | 0 | 0 | 0 | 0 | 0
2027-07-25 | 0 | 0 | 0 | 0 | 0 | 0
2027-08-01 | 0 | 0 | 0 | 0 | 0 | 0
2027-08-08 | 0 | 0 | 0 | 0 | 0 | 0
2027-08-15 | 0 | 0 | 0 | 0 | 0 | 0
2027-08-22 | 0 | 0 | 0 | 0 | 0 | 0
2027-08-29 | 0 | 0 | 0 | 0 | 0 | 0
2027-09-05 | 0 | 0 | 0 | 0 | 0 | 0
2027-09-12 | 0 | 0 | 0 | 0 | 0 | 0
2027-09-19 | 0 | 0 | 0 | 0 | 0 | 0
2027-09-26 | 0 | 0 | 0 | 0 | 0 | 0
2027-10-03 | 0 | 0 | 0 | 0 | 0 | 0
2027-10-10 | 0 | 0 | 0 | 0 | 0 | 0
2027-10-17 | 0 | 0 | 0 | 0 | 0 | 0
2027-10-24 | 0 | 0 | 0 | 0 | 0 | 0
2027-10-31 | 0 | 0 | 0 | 0 | 0 | 0
2027-11-07 | 34.5621 | 0 | 0 | 34.5621 | 0 | 0
2027-11-14 | 530.6171 | 0 | 0 | 530.6171 | 0 | 0
2027-11-21 | 336.4296 | 0 | 0 | 336.4296 | 0 | 0
2027-11-28 | 192.2117 | 0 | 0 | 192.2117 | 0 | 0
2027-12-05 | 150.4319 | 0 | 0 | 150.4319 | 0 | 0
2027-12-12 | 0 | 0 | 0 | 0 | 0 | 0
2027-12-19 | 0 | 0 | 0 | 0 | 0 | 0
2027-12-26 | 4.4262 | 0 | 0 | 4.4262 | 0 | 0
2028-01-02 | 160.1103 | 0 | 0 | 160.1103 | 0 | 0
2028-01-09 | 479.845 | 0 | 0 | 479.845 | 0 | 0
2028-01-16 | 408.4988 | 0 | 0 | 408.4988 | 0 | 0
2028-01-23 | 362.5371 | 0 | 0 | 362.5371 | 0 | 0
2028-01-30 | 399.2573 | 0 | 0 | 399.2573 | 0 | 0
2028-02-06 | 792.4805 | 0 | 0 | 792.4805 | 0 | 0
2028-02-13 | 643.7385 | 0 | 0 | 643.7385 | 0 | 0
2028-02-20 | 784.2273 | 0 | 0 | 784.2273 | 0 | 0
2028-02-27 | 750.4379 | 0 | 0 | 750.4379 | 0 | 0
2028-03-05 | 245.8071 | 0 | 0 | 245.8071 | 0 | 0
2028-03-12 | 354.1091 | 0 | 0 | 354.1091 | 0 | 0
2028-03-19 | 542.8389 | 0 | 0 | 542.8389 | 0 | 0
2028-03-26 | 747.7785 | 0 | 0 | 747.7785 | 0 | 0
2028-04-02 | 297.7962 | 0 | 0 | 297.7962 | 0 | 0
Back to main menu

## Table 3.8
Back to main menu
Table 3.8: Energy Production Capability Forecast
Month | Firm Scenario Forecast Energy Production Capability (GWh) | Planned Scenario Forecast Energy Production Capability (GWh)
2026-10-01 | 15721.135 | 15726.095
2026-11-01 | 15510.06 | 15519.645
2026-12-01 | 17011.355 | 17016.315
2027-01-01 | 16304.875 | 16309.835
2027-02-01 | 14650.16 | 14668.995
2027-03-01 | 16465.545 | 16470.505
2027-04-01 | 14141.69 | 14151.275
2027-05-01 | 15662.145 | 15667.105
2027-06-01 | 16686.01 | 16695.595
2027-07-01 | 16614.485 | 16619.445
2027-08-01 | 16440.675 | 16445.635
2027-09-01 | 15633.71 | 15644.5325
2027-10-01 | 15269.805 | 15276.0025
2027-11-01 | 15930.19 | 15941.0125
2027-12-01 | 16926.595 | 16932.7925
2028-01-01 | 18022.975 | 18029.1725
2028-02-01 | 16662.23 | 16682.3025
2028-03-01 | 17162.865 | 17169.0625
Back to main menu

## Table 3.9
Back to main menu
Table 3.9: Reductions by Fuel Type: Expected Weather, Firm Scenario
Week | Ontario | Total Internal | Total Reductions | Nuclear | Biomass, Oil & Gas | Hydro, Wind, Solar & Storage | Total Bottled
Ending | Demand | Resources | in Resources | Reductions | Reductions | Capacity Unavailable | Generation
Day | MW | MW | MW | MW | MW | MW | MW
2026-10-04 | 18417 | 38987.29 | 16657 | 5624.2 | 2548.85 | 8349.1094 | 135.2953
2026-10-11 | 17890 | 38987.29 | 16844 | 4747.2 | 3831.74 | 8265.1094 | 0
2026-10-18 | 17889 | 38987.29 | 16865 | 4747.2 | 2702.64 | 8672.9618 | 742.6082
2026-10-25 | 18166 | 38987.29 | 15799 | 4747.2 | 2866.75 | 8185.3873 | 0
2026-11-01 | 18441 | 38987.29 | 16586 | 4747.2 | 3590.18 | 8249.4841 | 0
2026-11-08 | 18993 | 38987.29 | 15175 | 5556.2 | 2294.65 | 7325.0587 | 0
2026-11-15 | 19490 | 38987.29 | 15464 | 5556.2 | 2541.86 | 7366.337 | 0
2026-11-22 | 20074 | 38987.29 | 15025 | 4739.2 | 2102.3 | 7662.6253 | 521.284
2026-11-29 | 20588 | 38987.29 | 14779 | 4739.2 | 2032.92 | 7567.0729 | 440.6249
2026-12-06 | 20952 | 38987.29 | 14490 | 4731.2 | 1952.96 | 7404.5752 | 401.3628
2026-12-13 | 21278 | 38987.29 | 13546 | 5550.2 | 783.34 | 7213.3661 | 0
2026-12-20 | 21481 | 38987.29 | 12920 | 4731.2 | 783.34 | 7149.4788 | 256.3936
2026-12-27 | 20908 | 38987.29 | 12895 | 4731.2 | 783.34 | 6898.334 | 482.9173
2027-01-03 | 21056 | 38987.29 | 12166 | 3853.2 | 783.34 | 6802.5303 | 727.1187
2027-01-10 | 21954 | 38987.29 | 12879 | 4671.2 | 1249.58 | 6822.8906 | 136.2357
2027-01-17 | 21833 | 38987.29 | 13803 | 5489.2 | 1249.58 | 7064.0249 | 0.94872
2027-01-24 | 21910 | 38987.29 | 13864 | 5489.2 | 1249.58 | 7056.4682 | 69.0787
2027-01-31 | 21886 | 38987.29 | 13907 | 5489.2 | 1249.58 | 7159.9029 | 8.3245
2027-02-07 | 21388 | 38987.29 | 14498 | 5466.2 | 1447.16 | 7152.4519 | 432.5985
2027-02-14 | 21384 | 38987.29 | 14527 | 5466.2 | 1267.16 | 7287.0793 | 507.12
2027-02-21 | 21100 | 38987.29 | 14367 | 5466.2 | 1310.92 | 7093.6219 | 497.1123
2027-02-28 | 20950 | 38987.29 | 14385 | 5466.2 | 1267.16 | 7172.9754 | 479.1103
2027-03-07 | 20430 | 38987.29 | 14277 | 5461.2 | 826.82 | 7430.7294 | 558.7075
2027-03-14 | 19986 | 38987.29 | 14357 | 5461.2 | 826.82 | 7419.7133 | 649.495
2027-03-21 | 19556 | 38987.29 | 13910 | 4628.2 | 826.82 | 7438.3889 | 1017.1057
2027-03-28 | 19050 | 38987.29 | 14034 | 4628.2 | 826.82 | 7341.308 | 1237.7807
2027-04-04 | 18696 | 38987.29 | 16409 | 4628.2 | 3534.71 | 7949.0057 | 297.4086
2027-04-11 | 18241 | 38987.29 | 16430 | 4609.2 | 3795.29 | 7683.5985 | 341.957
2027-04-18 | 17922 | 38987.29 | 19608 | 7243.2 | 3543.27 | 7920.3229 | 901.2725
2027-04-25 | 17664 | 38987.29 | 19749 | 7243.2 | 3543.27 | 7755.3558 | 1208.0348
2027-05-02 | 17482 | 38987.29 | 18319 | 7243.2 | 1605.32 | 7512.8801 | 1958.502
2027-05-09 | 17402 | 38987.29 | 18588 | 7242.2 | 1819.26 | 8020.2057 | 1507.1174
2027-05-16 | 17475 | 38987.29 | 18615 | 7242.2 | 1742.52 | 7799.93 | 1830.5224
2027-05-23 | 17903 | 38987.29 | 17830 | 7242.2 | 1395.67 | 7913.8483 | 1278.4448
2027-05-30 | 18201 | 38987.29 | 17336 | 7242.2 | 688.48 | 7872.6672 | 1533.6428
2027-06-06 | 19047 | 38987.29 | 13894 | 4608.2 | 688.48 | 8597.4584 | 0
2027-06-13 | 19547 | 38987.29 | 14151 | 4613.2 | 883.01 | 8655.4811 | 0
2027-06-20 | 20602 | 38987.29 | 13982 | 4613.2 | 883.01 | 8486.1839 | 0
2027-06-27 | 21480 | 38987.29 | 13944 | 4613.2 | 883.01 | 8448.5975 | 0
2027-07-04 | 21481 | 38987.29 | 14103 | 4613.2 | 883.01 | 8607.1714 | 0
2027-07-11 | 22244 | 38987.29 | 14439 | 4682.2 | 1000.01 | 8757.4214 | 0
2027-07-18 | 22447 | 38987.29 | 14289 | 4682.2 | 1000.01 | 8607.7462 | 0
2027-07-25 | 22455 | 38987.29 | 14541 | 4682.2 | 1000.01 | 8859.3842 | 0
2027-08-01 | 22397 | 38987.29 | 14354 | 4682.2 | 1000.01 | 8672.2639 | 0
2027-08-08 | 21844 | 38987.29 | 14720 | 4709.2 | 945.88 | 9065.3601 | 0
2027-08-15 | 21807 | 38987.29 | 15087 | 4709.2 | 945.88 | 9432.4871 | 0
2027-08-22 | 21612 | 38987.29 | 15126 | 4709.2 | 945.88 | 9471.5485 | 0
2027-08-29 | 21644 | 38987.29 | 15209 | 4709.2 | 945.88 | 9554.178 | 0
2027-09-05 | 21298 | 38987.29 | 14916 | 4683.2 | 791.78 | 9441.9235 | 0
2027-09-12 | 20202 | 38987.29 | 15090 | 4683.2 | 971.78 | 9435.3206 | 0
2027-09-19 | 19727 | 38987.29 | 15108 | 4683.2 | 971.78 | 9453.5497 | 0
2027-09-26 | 19251 | 38987.29 | 16304 | 5498.2 | 1496.78 | 9309.9761 | 0
2027-10-03 | 18975 | 38987.29 | 17364 | 5498.2 | 2410.94 | 9454.9038 | 0
2027-10-10 | 18408 | 38987.29 | 17418 | 5488.2 | 3574.21 | 8356.0143 | 0
2027-10-17 | 18548 | 38987.29 | 16908 | 5488.2 | 2880.35 | 8539.626 | 0
2027-10-24 | 18642 | 38987.29 | 17587 | 5488.2 | 3439.67 | 8659.2631 | 0
2027-10-31 | 18917 | 38987.29 | 16410 | 5488.2 | 2500.03 | 8421.8349 | 0
2027-11-07 | 19471 | 38987.29 | 14580 | 5478.2 | 1608.08 | 7459.8465 | 34.5621
2027-11-14 | 19918 | 38987.29 | 15636 | 4655.2 | 2731.15 | 7719.6203 | 530.6171
2027-11-21 | 20507 | 38987.29 | 13971 | 4655.2 | 1337.89 | 7642.2588 | 336.4296
2027-11-28 | 21068 | 38987.29 | 13656 | 4655.2 | 1337.89 | 7471.2715 | 192.2117
2027-12-05 | 21396 | 38987.29 | 13324 | 4655.2 | 1063.08 | 7455.5893 | 150.4319
2027-12-12 | 21764 | 38987.29 | 12864 | 4647.2 | 831.02 | 7386.4883 | 0
2027-12-19 | 21987 | 38987.29 | 12724 | 4647.2 | 787.54 | 7290.2317 | 0
2027-12-26 | 22019 | 38987.29 | 12450 | 4647.2 | 787.54 | 7011.6071 | 4.4262
2028-01-02 | 21771 | 38987.29 | 12549 | 4647.2 | 787.54 | 6954.8526 | 160.1103
2028-01-09 | 22430 | 38987.29 | 12067 | 3858.2 | 728.78 | 7000.984 | 479.845
2028-01-16 | 22841 | 38987.29 | 12264 | 3858.2 | 728.78 | 7268.8046 | 408.4988
2028-01-23 | 22911 | 38987.29 | 11680 | 3858.2 | 203.78 | 7255.6345 | 362.5371
2028-01-30 | 22916 | 38987.29 | 11609 | 3858.2 | 203.78 | 7148.5562 | 399.2573
2028-02-06 | 22604 | 38987.29 | 12757 | 3858.2 | 728.78 | 7378.249 | 792.4805
2028-02-13 | 22256 | 38987.29 | 12762 | 3858.2 | 926.36 | 7333.8674 | 643.7385
2028-02-20 | 22313 | 38987.29 | 12692 | 3858.2 | 746.36 | 7303.5561 | 784.2273
2028-02-27 | 21733 | 38987.29 | 12529 | 3858.2 | 746.36 | 7174.1609 | 750.4379
2028-03-05 | 21551 | 38987.29 | 13117 | 4680.2 | 746.36 | 7445.1341 | 245.8071
2028-03-12 | 20986 | 38987.29 | 13336 | 4660.2 | 831.02 | 7490.7307 | 354.1091
2028-03-19 | 20557 | 38987.29 | 13462 | 4660.2 | 831.02 | 7428.6618 | 542.8389
2028-03-26 | 20011 | 38987.29 | 13596 | 4660.2 | 831.02 | 7357.9791 | 747.7785
2028-04-02 | 19616 | 38987.29 | 13129 | 4660.2 | 831.02 | 7340.5237 | 297.7962
Back to main menu

## Table 3.10
Back to main menu
Table 3.10: Reductions by Fuel Type: Expected Weather, Planned Scenario
Week | Ontario | Total Internal | Total Reductions | Nuclear | Biomass, Oil & Gas | Hydro, Wind, Solar & Storage | Total Bottled
Ending | Demand | Resources | in Resources | Reductions | Reductions | Capacity Unavailable | Generation
Day | MW | MW | MW | MW | MW | MW | MW
2026-10-04 | 18480 | 39027.29 | 16695 | 5624.2 | 2575.25 | 8361.1094 | 135.2953
2026-10-11 | 17971 | 39027.29 | 16805 | 4747.2 | 3781.19 | 8277.1094 | 0
2026-10-18 | 17975 | 39133.29 | 16932 | 4747.2 | 2758.09 | 8684.9618 | 742.6082
2026-10-25 | 18236 | 39133.29 | 15866 | 4747.2 | 2922.2 | 8197.3873 | 0
2026-11-01 | 18523 | 39133.29 | 16662 | 4747.2 | 3645.63 | 8269.4841 | 0
2026-11-08 | 19107 | 39133.29 | 15234 | 5556.2 | 2333.55 | 7345.0587 | 0
2026-11-15 | 19619 | 39133.29 | 15523 | 5556.2 | 2580.76 | 7386.337 | 0
2026-11-22 | 20184 | 39133.29 | 15084 | 4739.2 | 2141.2 | 7682.6253 | 521.284
2026-11-29 | 20699 | 39133.29 | 14838 | 4739.2 | 2071.82 | 7587.0729 | 440.6249
2026-12-06 | 21103 | 39133.29 | 14549 | 4731.2 | 1991.86 | 7424.5752 | 401.3628
2026-12-13 | 21422 | 39133.29 | 13605 | 5550.2 | 822.24 | 7233.3661 | 0
2026-12-20 | 21635 | 39133.29 | 12979 | 4731.2 | 822.24 | 7169.4788 | 256.3936
2026-12-27 | 21040 | 39133.29 | 12954 | 4731.2 | 822.24 | 6918.334 | 482.9173
2027-01-03 | 21097 | 39133.29 | 12225 | 3853.2 | 822.24 | 6822.5303 | 727.1187
2027-01-10 | 22128 | 39133.29 | 12937 | 4671.2 | 1286.68 | 6842.8906 | 136.2357
2027-01-17 | 22015 | 39133.29 | 13860 | 5489.2 | 1286.68 | 7084.0249 | 0.94872
2027-01-24 | 22080 | 39133.29 | 13921 | 5489.2 | 1286.68 | 7076.4682 | 69.0787
2027-01-31 | 22066 | 39133.29 | 13964 | 5489.2 | 1286.68 | 7179.9029 | 8.3245
2027-02-07 | 21554 | 39133.29 | 14555 | 5466.2 | 1484.26 | 7172.4519 | 432.5985
2027-02-14 | 21554 | 39133.29 | 14584 | 5466.2 | 1304.26 | 7307.0793 | 507.12
2027-02-21 | 21266 | 39133.29 | 14424 | 5466.2 | 1348.02 | 7113.6219 | 497.1123
2027-02-28 | 21115 | 39133.29 | 14442 | 5466.2 | 1304.26 | 7192.9754 | 479.1103
2027-03-07 | 20572 | 39133.29 | 14334 | 5461.2 | 863.92 | 7450.7294 | 558.7075
2027-03-14 | 20134 | 39133.29 | 14414 | 5461.2 | 863.92 | 7439.7133 | 649.495
2027-03-21 | 19616 | 39133.29 | 13967 | 4628.2 | 863.92 | 7458.3889 | 1017.1057
2027-03-28 | 19190 | 39133.29 | 14091 | 4628.2 | 863.92 | 7361.308 | 1237.7807
2027-04-04 | 18756 | 39133.29 | 16466 | 4628.2 | 3571.81 | 7969.0057 | 297.4086
2027-04-11 | 18407 | 39133.29 | 16487 | 4609.2 | 3832.39 | 7703.5985 | 341.957
2027-04-18 | 18075 | 39133.29 | 19665 | 7243.2 | 3580.37 | 7940.3229 | 901.2725
2027-04-25 | 17821 | 39133.29 | 19806 | 7243.2 | 3580.37 | 7775.3558 | 1208.0348
2027-05-02 | 17636 | 39133.29 | 18369 | 7243.2 | 1642.42 | 7524.8801 | 1958.502
2027-05-09 | 17576 | 39133.29 | 18656 | 7242.2 | 1874.71 | 8032.2057 | 1507.1174
2027-05-16 | 17663 | 39133.29 | 18682 | 7242.2 | 1797.97 | 7811.93 | 1830.5224
2027-05-23 | 18088 | 39133.29 | 17897 | 7242.2 | 1451.12 | 7925.8483 | 1278.4448
2027-05-30 | 18394 | 39133.29 | 17404 | 7242.2 | 743.93 | 7884.6672 | 1533.6428
2027-06-06 | 19254 | 39133.29 | 13961 | 4608.2 | 743.93 | 8609.4584 | 0
2027-06-13 | 19751 | 39133.29 | 14219 | 4613.2 | 938.46 | 8667.4811 | 0
2027-06-20 | 20796 | 39133.29 | 14049 | 4613.2 | 938.46 | 8498.1839 | 0
2027-06-27 | 21671 | 39133.29 | 14012 | 4613.2 | 938.46 | 8460.5975 | 0
2027-07-04 | 21710 | 39133.29 | 14170 | 4613.2 | 938.46 | 8619.1714 | 0
2027-07-11 | 22501 | 39133.29 | 14507 | 4682.2 | 1055.46 | 8769.4214 | 0
2027-07-18 | 22709 | 39133.29 | 14357 | 4682.2 | 1055.46 | 8619.7462 | 0
2027-07-25 | 22718 | 39133.29 | 14609 | 4682.2 | 1055.46 | 8871.3842 | 0
2027-08-01 | 22571 | 39133.29 | 14421 | 4682.2 | 1055.46 | 8684.2639 | 0
2027-08-08 | 22138 | 39133.29 | 14787 | 4709.2 | 1001.33 | 9077.3601 | 0
2027-08-15 | 22100 | 39133.29 | 15155 | 4709.2 | 1001.33 | 9444.4871 | 0
2027-08-22 | 21895 | 39133.29 | 15194 | 4709.2 | 1001.33 | 9483.5485 | 0
2027-08-29 | 21918 | 39133.29 | 15276 | 4709.2 | 1001.33 | 9566.178 | 0
2027-09-05 | 21614 | 39133.29 | 14977 | 4683.2 | 847.23 | 9446.9375 | 0
2027-09-12 | 20521 | 39133.29 | 15150 | 4683.2 | 1027.23 | 9440.3346 | 0
2027-09-19 | 20055 | 39143.27 | 15178 | 4683.2 | 1027.23 | 9468.5437 | 0
2027-09-26 | 19582 | 39143.27 | 16375 | 5498.2 | 1552.23 | 9324.9701 | 0
2027-10-03 | 19281 | 39143.27 | 17434 | 5498.2 | 2466.39 | 9469.8978 | 0
2027-10-10 | 18746 | 39143.27 | 17488 | 5488.2 | 3629.66 | 8371.0083 | 0
2027-10-17 | 18790 | 39143.27 | 16978 | 5488.2 | 2935.8 | 8554.62 | 0
2027-10-24 | 18969 | 39143.27 | 17657 | 5488.2 | 3495.12 | 8674.2571 | 0
2027-10-31 | 19251 | 39143.27 | 16480 | 5488.2 | 2555.48 | 8436.8289 | 0
2027-11-07 | 19837 | 39143.27 | 14644 | 5478.2 | 1646.98 | 7484.8365 | 34.5621
2027-11-14 | 20294 | 39143.27 | 15700 | 4655.2 | 2770.05 | 7744.6103 | 530.6171
2027-11-21 | 20871 | 39143.27 | 14035 | 4655.2 | 1376.79 | 7667.2488 | 336.4296
2027-11-28 | 21419 | 39143.27 | 13720 | 4655.2 | 1376.79 | 7496.2615 | 192.2117
2027-12-05 | 21792 | 39143.27 | 13388 | 4655.2 | 1101.98 | 7480.5793 | 150.4319
2027-12-12 | 22162 | 39143.27 | 12928 | 4647.2 | 869.92 | 7411.4783 | 0
2027-12-19 | 22396 | 39143.27 | 12788 | 4647.2 | 826.44 | 7315.2217 | 0
2027-12-26 | 22417 | 39143.27 | 12514 | 4647.2 | 826.44 | 7036.5971 | 4.4262
2028-01-02 | 22194 | 39143.27 | 12613 | 4647.2 | 826.44 | 6979.8426 | 160.1103
2028-01-09 | 22866 | 39143.27 | 12127 | 3858.2 | 763.88 | 7025.974 | 479.845
2028-01-16 | 23300 | 39143.27 | 12324 | 3858.2 | 763.88 | 7293.7946 | 408.4988
2028-01-23 | 23349 | 39143.27 | 11740 | 3858.2 | 238.88 | 7280.6245 | 362.5371
2028-01-30 | 23358 | 39143.27 | 11669 | 3858.2 | 238.88 | 7173.5462 | 399.2573
2028-02-06 | 23042 | 39143.27 | 12817 | 3858.2 | 763.88 | 7403.239 | 792.4805
2028-02-13 | 22685 | 39143.27 | 12822 | 3858.2 | 961.46 | 7358.8574 | 643.7385
2028-02-20 | 22610 | 39143.27 | 12752 | 3858.2 | 781.46 | 7328.5461 | 784.2273
2028-02-27 | 22152 | 39143.27 | 12589 | 3858.2 | 781.46 | 7199.1509 | 750.4379
2028-03-05 | 21977 | 39143.27 | 13177 | 4680.2 | 781.46 | 7470.1241 | 245.8071
2028-03-12 | 21398 | 39143.27 | 13396 | 4660.2 | 866.12 | 7515.7207 | 354.1091
2028-03-19 | 20854 | 39143.27 | 13522 | 4660.2 | 866.12 | 7453.6518 | 542.8389
2028-03-26 | 20419 | 39143.27 | 13657 | 4660.2 | 866.12 | 7382.9691 | 747.7785
2028-04-02 | 20032 | 39143.27 | 13189 | 4660.2 | 866.12 | 7365.5137 | 297.7962
Back to main menu

## Table 3.11
Back to main menu
Table 3.11: Firm Scenario - Expected Weather: Ontario Monthly Energy Production by Fuel Type
Month | Year | Nuclear (GWh) | Hydro (GWh) | Gas & Oil (GWh) | Wind (GWh) | Biofuel (GWh) | Storage (GWh) | Other (GWh) | Total (GWh)
Oct | 2026 | 5383.75 | 2793.64 | 1820.08 | 1264.71 | 19.31 | 18.77 | 51.33 | 11351.59
Nov | 2026 | 5037.9 | 3037 | 2446.04 | 1354.21 | 19.67 | 23.66 | 36.49 | 11954.97
Dec | 2026 | 5376.55 | 3243.47 | 3126.46 | 1428.37 | 49.56 | 22.51 | 21.57 | 13268.49
Jan | 2027 | 4756.96 | 3298.65 | 4202.74 | 1479.76 | 39.17 | 50.96 | 30.96 | 13859.2
Feb | 2027 | 4314.43 | 3078.7 | 3539.22 | 1235.09 | 32.15 | 40.23 | 49.07 | 12288.89
Mar | 2027 | 5094.25 | 3242.92 | 2907.2 | 1235.8 | 31.87 | 24.54 | 73.02 | 12609.6
Apr | 2027 | 4106.37 | 3178 | 2533.98 | 1211.93 | 34.92 | 21.03 | 78.11 | 11164.34
May | 2027 | 3917.51 | 3516.31 | 2647.59 | 945.18 | 31.67 | 17.48 | 90.32 | 11166.06
Jun | 2027 | 5313.93 | 3259.04 | 2396.9 | 723.78 | 30.74 | 19.12 | 86.59 | 11830.1
Jul | 2027 | 5386.64 | 3061.53 | 3775.65 | 602.56 | 31.69 | 50.89 | 94.88 | 13003.84
Aug | 2027 | 5386.21 | 2801 | 3949.7 | 633.07 | 32.28 | 55.73 | 92.23 | 12950.22
Sep | 2027 | 4976.19 | 2631.59 | 3078.31 | 826.75 | 25.89 | 39.74 | 76.2 | 11654.67
Oct | 2027 | 4843.36 | 2793.64 | 2675.89 | 1297.39 | 19.53 | 33.59 | 52.26 | 11715.66
Nov | 2027 | 5225.88 | 3036.5 | 3098.35 | 1360.98 | 22.5 | 35.46 | 37.13 | 12816.8
Dec | 2027 | 5128.19 | 3243.47 | 4231.04 | 1430.01 | 52.5 | 40.88 | 24.15 | 14150.24
Jan | 2028 | 5865.67 | 3298.68 | 4208.73 | 1480.04 | 35.13 | 34.27 | 31.15 | 14953.67
Feb | 2028 | 5520.21 | 3078.73 | 3733.65 | 1279 | 30.25 | 23.86 | 50.56 | 13716.26
Mar | 2028 | 5541.17 | 3244 | 3558.02 | 1251.13 | 31.35 | 21.54 | 73.12 | 13720.33
Back to main menu

## Table 3.12
Back to main menu
Table 3.12: Planned Scenario - Expected Weather: Ontario Monthly Energy Production by Fuel Type
Month | Year | Nuclear (GWh) | Hydro (GWh) | Gas & Oil (GWh) | Wind (GWh) | Biofuel (GWh) | Storage (GWh) | Other (GWh) | Total (GWh)
2026-10-01 | 2026 | 5383.75 | 2793.64 | 1819.86 | 1264.95 | 19.31 | 18.9 | 51.35 | 11351.76
2026-11-01 | 2026 | 5037.9 | 3037 | 2471.59 | 1354.89 | 19.67 | 24.43 | 36.5 | 11981.98
2026-12-01 | 2026 | 5376.55 | 3243.47 | 3157.7 | 1428.5 | 49.61 | 23.09 | 21.57 | 13300.49
2027-01-01 | 2027 | 4756.96 | 3298.65 | 4233.48 | 1479.83 | 39.49 | 52.84 | 30.95 | 13892.2
2027-02-01 | 2027 | 4314.43 | 3078.7 | 3576.14 | 1235.08 | 32.38 | 41.68 | 49.13 | 12327.54
2027-03-01 | 2027 | 5094.25 | 3242.81 | 2951.66 | 1236.66 | 31.89 | 25.47 | 73.07 | 12655.81
2027-04-01 | 2027 | 4106.37 | 3178 | 2575.32 | 1223.56 | 34.95 | 22.89 | 77.68 | 11218.77
2027-05-01 | 2027 | 3917.56 | 3516.31 | 2711.52 | 954.01 | 31.67 | 19.13 | 91.01 | 11241.21
2027-06-01 | 2027 | 5313.94 | 3259.23 | 2471.97 | 726.11 | 30.74 | 20.63 | 86.74 | 11909.36
Jul | 2027 | 5386.64 | 3061.53 | 3907.81 | 603.1 | 31.74 | 56.01 | 96.03 | 13142.86
Aug | 2027 | 5386.21 | 2801 | 4098.13 | 633.33 | 32.3 | 61.73 | 93.57 | 13106.27
Sep | 2027 | 4976.19 | 2635.1 | 3240.26 | 827.38 | 25.97 | 45.65 | 77.92 | 11828.47
Oct | 2027 | 4843.36 | 2793.64 | 2857.03 | 1298.66 | 19.52 | 39.61 | 52.28 | 11904.1
Nov | 2027 | 5225.88 | 3036.61 | 3297.55 | 1361.53 | 22.57 | 44.8 | 37.74 | 13026.68
Dec | 2027 | 5128.19 | 3243.47 | 4448.38 | 1430.08 | 54.35 | 48.34 | 25.79 | 14378.6
Jan | 2028 | 5865.67 | 3298.68 | 4429.7 | 1480.15 | 35.82 | 39.81 | 31.56 | 15181.39
Feb | 2028 | 5520.21 | 3078.73 | 3941.05 | 1279.1 | 30.77 | 27.57 | 50.08 | 13927.51
Mar | 2028 | 5541.4 | 3244 | 3778.97 | 1251.28 | 31.31 | 22.56 | 73.16 | 13942.68
Back to main menu

## Figure 3.1
Back to main menu
Figure 3.1: Reserve above Requirement
Back to main menu

## Table 4.1
Back to main menu
Table 4.1: Transmission Projects
Zone | ID | Transmitter | Description | Proposed I/S Date
Bruce | N/A | Hydro-One | Tara Battery Storage 230kV LT1 Connection | 2027 Q2
Bruce | 2021-698 | Hydro-One | Bruce A Transformer Station 500 kV Switchyard Rep | 2027 Q4
East | N/A | Hydro-One | Lennox TS - Replace 500kV Breaker KL526 | 2027 Q1
East | 2023-758 | Hydro-One | Belleville TS: Build 75/125 MVA, 230/44 kV DESN | 2026 Q4
East | N/A | Hydro-One | Picton TS - T1/T2 Transformer Replacement | 2026 Q4
East | 2024-800 | Hydro-One | Connect Skyview BESS | 2026 Q4
East | 2024-774 | Hydro-One | Connect Napanee Generating Station Expansion | 2027 Q3
East | N/A | Hydro-One | Gardiner TS: T1/T2 PCT Component Replacement | 2027 Q3
East | N/A | Hydro-One | Kingston area: Build new DESN | 2027 Q4
East | 2026-EX1314 | Hydro-One | D6, Des Joachims TS X Petawawa DS, Tx Line Refur | 2027 Q4
East | 2026-896 | Hydro-One | Bowmanville 500kV Breaker Protection Replacement | 2027 Q4
Essa | 2022-EX1208 | Hydro-One | Essa TS -T3 and Component Replacement | 2026 Q4
Essa | N/A | Hydro-One | Orillia TS: T2 Transformer Replacement | 2026 Q4
Essa | 2026-868 | Hydro-One | Connect New Chalk River CTS | 2027 Q4
Niagara | 2016-EX862 | Hydro-One | Beck 1 SS 115kV ABCB Replacement | 2026 Q3
Niagara | N/A | Hydro-One | Temporary A6C 115kV Line Tap | 2026 Q4
Niagara | N/A | Hydro-One | Q28A (Beck2 X Abitibi Jct): 230kV Line Section Upr | 2026 Q4
Niagara | 2024-791 | Hydro-One | Spring Creek MTS Tap | 2027 Q3
Northeast | 2020-EX1114 | Hydro-One | Kirkland Lake TS: Component Replacement | 2027 Q3
Northeast | 2020-676 | Hydro-One | Wikwemikong Pellet Plant Connection | 2026 Q4
Northeast | 2023-749 | Hydro-One | HOSSM Hollingsworth Circuit - Connection of Hollin | 2026 Q4
Northeast | 2020-EX1106 | Hydro-One | Porcupine TS: Component Replacement | 2026 Q3
Northeast | 2022-EX1196 | Hydro-One | Elliot Lake TS: Component Replacement | 2026 Q4
Northeast | N/A | Hydro-One | A4H/A5H, Tunis JCT-Fournier JCT, Tx Line Refurb. | 2027 Q1
Northeast | 2023-EX1230 | Hydro-One | HOSSM Thirdline T2 Replacement | 2026 Q4
Northeast | 2023-EX1230 | Hydro-One | HOSSM Third Line TS PUC 230kV Connections | 2027 Q2
Northeast | 2025-860 | Hydro-One | Porcupine TS: SVC Refurbishment | 2027 Q4
Northeast | 2024-EX1287 | Hydro-One | Porcupine TS: T7 and T8 Tertiary Reactors Installa | 2027 Q4
Northeast | N/A | Hydro-One | K1/K2, Krklnd Lk- A. Barrick, Tx Line Refurb (Cu) | 2027 Q4
Northwest | 2021-EX1156 | Hydro-One | Rabbit Lake SS: Component Replacement | 2027 Q4
Northwest | 2020-691 | Hydro-One | Mackenzie TS: 230kV Brownfield Refurb | 2026 Q4
Northwest | N/A | Hydro-One | 115kV E2R GBR CTS Connection | 2027 Q1
Northwest | N/A | Hydro-One | Ear Falls TS, EOL T5, Asset Replacement Project | 2027 Q4
Northwest | 2022-732 | Hydro-One | Waasigan Transmission Line - Development | 2027 Q4
Northwest | 2022-732 | Hydro-One | Waasigan Transmission Line Project - Station Work | 2027 Q4
Ottawa | 2024-EX1280 | Hydro-One | Russell TS - T1/T2 & Comp Replacement | 2027 Q2
Ottawa | N/A | Hydro-One | South East Ottawa Build New 230kV line Tap | 2026 Q3
Ottawa | N/A | Hydro-One | Lisgar TS: T1 and Component Replacement | 2026 Q4
Ottawa | N/A | Hydro-One | Longueuil TS: T3/T4 Replacement | 2026 Q4
Ottawa | 2024-822 | Hydro-One | Connect Fitzroy BESS | 2027 Q2
Ottawa | 2024-793 | Hydro-One | Connect Trailroad BESS | 2027 Q2
Ottawa | 2023-EX1243 | Hydro-One | Merivale TS Add 230/115kV Autotransformers | 2026 Q4
Southwest | N/A | Hydro-One | Tx Line Refurb. B7/B8 ¦Burlington TS-Bronte TS | 2026 Q2
Southwest | N/A | Hydro-One | B5/6C, BurlingtonTS X WestoverCTS, Tx Line Refurb. | 2026 Q3
Southwest | 2020-EX1142 | Hydro-One | Seaforth TS: T1, T2, T5, T6, PCT & Component Repl. | 2027 Q3
Southwest | 2024-776 | Hydro-One | Elora BESS LP1 Connection | 2026 Q3
Southwest | 2022-EX1217 | Hydro-One | Nanticoke TS; ABCB Project | 2027 Q1
Southwest | 2024-EX1285 | Hydro-One | M31W: Reinforce Buchanan x St Thomas Line Tap Poin | 2027 Q1
Southwest | N/A | Hydro-One | Preston TS: T3, T4 & Component Replacement | 2027 Q2
Southwest | 2024-780 | Hydro-One | Oxford Battery Energy Storage Project | 2026 Q4
Southwest | 2024-818 | Hydro-One | Palermo TS: T3, T4 Replacement & Station Expansion | 2027 Q2
Toronto | 2016-EX869 | Hydro-One | Main TS: T3, T4 & Component Replacement | 2026 Q4
Toronto | 2019-EX1083 | Hydro-One | Strachan TS: T14 & Component Replacement | 2027 Q2
Toronto | 2018-637 | Hydro-One | Richview Manby Transmission Reinforcement - Line | 2027 Q4
Toronto | 2019-EX1041 | Hydro-One | Bridgman TS: T11,T12,T13,T14 & Component Replacem | 2026 Q3
Toronto | N/A | Hydro-One | Clarington TS: Install Surge Capacitors | 2026 Q3
Toronto | 2019-EX1034 | Hydro-One | Claireville TS: Component Replacements | 2026 Q4
Toronto | 2020-EX1104 | Hydro-One | HV UG Cable - Replace C5E/C7E | 2026 Q4
Toronto | N/A | Hydro-One | Scarboro TS: T23 & Component Replacements | 2026 Q4
Toronto | N/A | Hydro-One | Malvern T3 EOL Replacement | 2027 Q1
Toronto | 2022-738 | Hydro-One | Connect Darlington SMR GS | 2027 Q1
Toronto | N/A | Hydro-One | Charles TS: T3, T4 & Component Replacements | 2027 Q4
Toronto | 2024-EX1275 | Hydro-One | Claireville TS: T13 & Component Replacements | 2027 Q4
Toronto | N/A | Hydro-One | Holt Switching Station SMR Connection | 2027 Q4
Toronto | 2022-735 | Hydro-One | Vaughan MTS6 –Provide 230 kV Connection to new TS | 2027 Q4
West | 2022-718 | Hydro-One | Connect East Windsor (Expansion) L.P. ELT1 | 2026 Q3
West | 2023-766 | Hydro-One | Centennial TS: Project Connect PowerCo | 2027 Q3
West | 2021-EX1166 | Hydro-One | Lauzon TS: T6, T5 & Component Replacement | 2026 Q4
West | N/A | Hydro-One | St. Andrews TS: T3, T4 & Switchyard Refurbishment | 2026 Q4
West | N/A | Hydro-One | St Clair Transmission Line: Stations Work | 2027 Q4
Back to main menu
Back to main menu

## Table 4.2
Back to main menu
Table 4.2: Interface Limits with All Elements in Service
Interface | Limit (MW) | Notes
BLIP | 3000
NBLIP | 1800
QFW | 2000 | ****
FABCW | 7500 | *
FETT | 5000 / 3500 | **
CLAN | 2000
FIO | 2900
SLW | 1350
FN | 1500 | ***
FS | 1750
P502X South | 1000
EWTE | 500
EWTW | 500
(*) FABCW limit varies according to BLIP flow.
For each recognized contingency, separate voltage and stability limit ranges are defined.
Published limit range based on the most restrictive contigency under optimal
Bruce System Conditions in SCO-South Tab1.
(**) FETT is a fixed boundary condition limit. FETT interface changes from 5000 MW to 3500 MW only during the Darlington VBO.
(***) FN is a fixed boundary condition limit.
(****) With Q26M and Q35M being 3-ended circuits (connected to Middleport TS), the
QFW limit is improved to the boundary limit of 2000 MW.
Back to main menu

## Table 4.3
Back to main menu
Table 4.3: Interconnection Flow Limits
Interconnection | Limit - Flows Out of Ontario (MW) |  | Limit - Flows Into Ontario (MW)
Manitoba – Summer* | 246 | 255 | 260 | (3,6)325
Manitoba – Winter* | 300 | (3) | 300 | (3,6)
Minnesota | 150 |  | 100 | (3)
Quebec North (Northeast) – Summer* | 105 |  | 65
D4Z | 0 | (5) | 65
H4Z | 105 | (5) | 0
Quebec North (Northeast)– Winter* | 105 |  | 85
D4Z | 0 |  | 85
H4Z | 105 |  | 0
Quebec South (Ottawa) – Summer* | 1570 |  | 1865
X2Y | 0 |  | 65
Q4C | 120 |  | not of concern
P33C | 0 | 60 | 300
D5A | 200 |  | 250
H9A | 0 |  | 0
HVDC | 1250 |  | 1250
Quebec South (Ottawa) – Winter* | 1590 |  | 1865
X2Y | 0 |  | 65
Q4C | 140 |  | not of concern
P33C | 0 |  | 300
D5A | 200 |  | 250
H9A | 0 |  | 0
HVDC | 1250 |  | 1250
Quebec South (East) – Summer* | 470 |  | 400
B31L + B5D | 470 |  | 400
Quebec South (East) – Winter* | 470 |  | 400
B31L + B5D | 470 |  | 400
New York St. Lawrence – Summer* | 300 |  | 300
New York St. Lawrence – Winter* | 300 |  | 300
New York Niagara – Summer* | 1500 | (1) | 1200 | (1,7)
Emergency Transfer Limit - Summer* | 2160 | (1) | 1860 | (1,7)
New York Niagara – Winter* | 1800 | (1) | 1600 | (1,7)
Emergency Transfer Limit - Winter* | 2200 | (1) | 2200 | (1,7)
Michigan – Summer* | 1650 | (2,3) | 1550 | (2,3)
Emergency Transfer Limit - Summer* | N/A | (2,3) | N/A | (2,3)
Michigan – Winter* | 1650 | (2,3) | 1700 | (2,3)
Emergency Transfer Limit - Winter* | N/A | (2,3) | N/A | (2,3)
* Summer Limits apply from May 1 to October 31. Winter Limits apply from November 1 to April 30.
(1) Flow limits depend on generation dispatch outside Ontario.
(2) Normal limits are based on LT ratings and phase shifters bypassed and Emergency limits are based on
ST ratings and phase shifters regulating. Flow limits vary depending on the generation dispatch
within Ontario.
(3) For real time operation of the interconnection, limits are based on ambient conditions.
(5) Limit based on 0 to 4 km/h wind speed and 30˚C ambient temperature.
(6) Flows into Ontario include flows on circuit SK1.
(7) Flow limits into Ontario are shown without considering QFW transmission constraints within Ontario.
Back to main menu

## Table 4.4
Back to main menu
Table 4.4: Bruce Zone Transmission Outages
Planned Start | Planned End | Duration (Days) | Station | Equipment Name | Outage ID | Max Recall | Major Transmission Interface Impacted | Reduction in Limit
2027-02-28 10:00 | 2027-03-11 18:00 | 11 | BRUCE A TS | K1K2, K1L24, K1_BUS, K1L22 | 1-00309650 Rev. #3 | Non-recallable | No Impact | #N/A
2027-06-20 10:00 | 2027-06-25 18:00 | 5 | BRUCE A TS | K1K2, K1L24, K1_BUS, K1L22 | 1-00312390 Rev. #3 | Non-recallable | No Impact | #N/A
2026-08-30 08:00 | 2026-09-10 16:00 | 11 | WILLOW CREEK JCT, MILTON SS, BRUCE B SS, BRUCE JCT | B501M.BBXBJ, B501M.BJXWJ, B501M.WJXMI, HL501, L501L570, 40-B501M, 29-B501M | 1-00295573 Rev. #26 | 4 Hour(s) | FABCW NBLIP BLIP | 1750 300 300
2026-08-30 08:00 | 2026-09-11 16:00 | 12 | WILLOW CREEK JCT, MILTON SS, BRUCE B SS, BRUCE JCT | B501M.BBXBJ, B501M.BJXWJ, B501M.WJXMI, 40-B501M, 29-B501M | 1-00293593 Rev. #19 | 4 Hour(s) | FABCW NBLIP BLIP | 1750 300 300
2026-08-30 08:00 | 2026-09-10 16:00 | 11 | WILLOW CREEK JCT, MILTON SS, BRUCE B SS, BRUCE JCT | B501M.BBXBJ, B501M.BJXWJ, B501M.WJXMI, HL501, L501L570, 40-B501M, 29-B501M | 1-00295573 Rev. #26 | 4 Hour(s) | FABCW NBLIP BLIP | 1750 300 300
2026-08-30 08:00 | 2026-09-11 16:00 | 12 | WILLOW CREEK JCT, MILTON SS, BRUCE B SS, BRUCE JCT | B501M.BBXBJ, B501M.BJXWJ, B501M.WJXMI, 40-B501M, 29-B501M | 1-00293593 Rev. #19 | 4 Hour(s) | FABCW NBLIP BLIP | 1750 300 300
2026-01-27 09:00 | 2026-11-23 07:00 | 300 | BRUCE A TS | T27-WT27 | 1-00301875 Rev. #8 | Non-recallable | FABCW NBLIP BLIP | 150 0 0
2026-07-19 12:15 | 2026-10-02 13:00 | 75 | BRUCE B SS | P-P5 | 1-00295508 Rev. #22 | Non-recallable | No Impact | #N/A
2026-10-18 07:00 | 2026-11-04 18:00 | 17 | BRUCE A TS | HT1_BUS, HT1L22, HT1L20 | 1-00295500 Rev. #16 | Non-recallable | No Impact | #N/A
2026-11-01 08:00 | 2026-12-04 16:00 | 33 | BRUCE A TS | HT1_BUS, HT1L22, HT1L20 | 1-00321675 Rev. #2 | Non-recallable | No Impact | #N/A
2027-02-23 07:00 | 2027-03-04 18:00 | 9 | BRUCE B SS | P-P5 | 1-00308922 Rev. #3 | 6 Hour(s) | No Impact | #N/A
2027-03-29 08:00 | 2027-04-26 16:00 | 28 | BRUCE B SS | P-P5 | 1-00315502 Rev. #4 | Non-recallable | No Impact | #N/A
2027-05-03 08:00 | 2027-08-13 16:00 | 102 | BRUCE B SS | J-J6 | 1-00315541 Rev. #2 | Non-recallable | No Impact | #N/A
2027-09-20 07:00 | 2027-09-30 19:00 | 11 | BRUCE B SS | P-P7 | 1-00252425 Rev. #3 | 6 Hour(s) | No Impact | #N/A
Back to main menu

## Table 4.5
Back to main menu
Table 4.5: East Zone Transmission Outages
Planned Start | Planned End | Duration (Days) | Station | Equipment Name | Outage ID | Max Recall | Major Transmission Interface Impacted | Reduction in Limit (MW)
2026-09-28 08:00 | 2026-10-09 16:00 | 11 | ST. LAWRENCE TS, MASSENA JCT | L33P.ROXLA, 49-L33P, PSR33-L33 | 1-00275118 Rev. #11 | 4 Hour(s) | No Impact | #N/A
2026-10-29 08:00 | 2026-11-13 16:00 | 15 | ST. LAWRENCE TS, MASSENA JCT | L34P.ROXLA, 49-L34P | 1-00275119 Rev. #10 | 4 Hour(s) | No Impact | #N/A
2027-12-06 03:30 | 2027-12-17 16:00 | 12 | HAWTHORNE TS, MASSON GS, IPB MASSON JCT, ST. ISIDORE TS, ORLEANS JCT 2, ORLEANS TS, CUMBERLAND JCT, LONGUEUIL JCT, LONGUEUIL TS | D5A.CUXGA, D5A.CUXIS, D5A.CUXO2, D5A.HAXO2, D5A.IPXMA, D5A.LOXIS, D5A.LOXLO, D5A.O2XOR, A1A2, HT5L5, KL5, 325T2-D5A, 48-D5A, 62D5A-26, T3-D5A, T1-A1, 62D5A-625 | 1-00296584 Rev. #4 | 6 Hour(s) | D5A | 250
2026-03-31 08:00 | 2026-10-29 16:00 | 212 | BOWMANVILLE SS | H3E, H3L521, H3_BUS | 1-00285558 Rev. #18 | 8 Hour(s) | No Impact | #N/A
2026-10-19 08:00 | 2026-10-30 16:00 | 11 | BOWMANVILLE SS | H3E, H3L521, H3_BUS | 1-00309159 Rev. #19 | 4 Hour(s) | No Impact | #N/A
2026-10-22 08:00 | 2026-10-29 16:00 | 7 | BOWMANVILLE SS | H3E, H3L521, H3_BUS | 1-00292311 Rev. #9 | 4 Hour(s) | No Impact | #N/A
2027-01-07 08:00 | 2027-10-26 16:00 | 292 | BOWMANVILLE SS | H2A, H2L520, H2_BUS | 1-00314776 Rev. #3 | 24 Hour(s) | No Impact | #N/A
2027-05-30 07:00 | 2027-07-09 09:00 | 40 | LENNOX TS, BOWMANVILLE SS | X520B.BOXLE, H2L520, KL520, L20L42, X3L520 | 1-00276876 Rev. #12 | 8 Hour(s) | No Impact | #N/A
2027-07-11 07:00 | 2027-07-30 08:01 | 19 | LENNOX TS, BOWMANVILLE SS | X521B.BOXLE, H3L521, L21L41, PL521, X4L521 | 1-00311127 Rev. #1 | 8 Hour(s) | No Impact | #N/A
2026-11-16 06:30 | 2026-11-27 16:30 | 11 | CHATS FALLS TS, SOUTH MARCH TS | C3S.CFXSO, 2-C3S, A9-C3S | 1-00321633 Rev. #1 | 4 Hour(s) | FIO BEAU P33C | 500 0 150
2026-11-16 06:30 | 2026-11-27 16:30 | 11 | CHATS FALLS TS, SOUTH MARCH TS | C3S.CFXSO, DL3, HL3, 2-C3S, A9-C3S | 1-00299036 Rev. #6 | 8 Hour(s) | FIO BEAU P33C | 500 0 150
2026-11-16 06:30 | 2026-11-27 16:30 | 11 | CHATS FALLS TS, SOUTH MARCH TS | C3S.CFXSO, 2-C3S, A9-C3S | 1-00299033 Rev. #6 | 4 Hour(s) | FIO BEAU P33C | 500 0 150
2026-11-16 06:30 | 2026-11-27 16:30 | 11 | CHATS FALLS TS, SOUTH MARCH TS | C3S.CFXSO, A1A2, 2-C3S, A9-C3S, A2_BUS, T2-A | 1-00196163 Rev. #53 | 6 Hour(s) | FIO BEAU P33C | 500 0 150
2026-09-14 06:30 | 2026-09-29 16:00 | 15 | DOBBIN TS | DL3, DL4, KL4, 20-P4S, D_BUS, T5-D | 1-00290612 Rev. #18 | 8 Hour(s) | No Impact | #N/A
2026-09-30 06:30 | 2026-10-14 16:00 | 14 | DOBBIN TS, DALE JCT, DOBBIN JCT | P4S.DOXDA, DL4, KL3, KL4, 20-P4S, 65P4S-52, K_BUS, T1-K, T2-K, P4S-2001 | 1-00290615 Rev. #13 | 8 Hour(s) | No Impact | #N/A
2026-10-18 06:30 | 2026-11-02 16:00 | 15 | DOBBIN TS | DL3, DL4, KL3, 20-P3S, D_BUS, P3-P, T5-D | 1-00290621 Rev. #20 | 8 Hour(s) | No Impact | #N/A
2026-10-18 08:00 | 2026-11-02 16:00 | 15 | DOBBIN TS | DL3, KL3, 20-P3S, P3-P | 1-00321253 Rev. #1 | 1 Hour(s) | No Impact | #N/A
2026-11-28 08:00 | 2026-12-23 16:00 | 25 | NORTHBROOKE DS, LODGEROOM DS | B1S.LOXNO, 74B1S-12, Q38B1S-14 | 1-00297913 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2027-05-24 04:30 | 2027-06-06 09:30 | 13 | DOBBIN TS | HL27 | 1-00319284 Rev. #1 | 24 Hour(s) | No Impact | #N/A
2027-06-12 06:30 | 2028-04-30 13:00 | 323 | DOBBIN TS | T5, T5-D, T5-H | 1-00319297 Rev. #1 | 250 Day(s) | No Impact | #N/A
2026-09-14 06:30 | 2026-09-25 16:00 | 11 | MERIVALE TS, TERRY FOX JCT | 319E34M-6, 6-E34M | 1-00295134 Rev. #4 | 6 Hour(s) | No Impact | #N/A
2026-10-13 08:00 | 2026-11-04 16:00 | 22 | CLARINGTON TS, HAVELOCK TS, MARINE JCT, OTONABEE TS, SEATON JCT, WILSON JCT | 128T1-T31H, K2L28, L23L28, L23L31, P2L31, 296-T28C, 296-T31H, L28_BUS, L31_BUS, T31H.HAXMJ, T31H.MJXCL, T31H.MJXOT, 57-T31H, 72T23C-BO1, 527T28C-MSO2, L23_BUS | 1-00295709 Rev. #9 | 12 Hour(s) | No Impact | #N/A
2026-11-16 06:30 | 2026-11-27 16:30 | 11 | CHATS FALLS TS, SOUTH MARCH TS | C3S.CFXSO, 2-C3S, A9-C3S | 1-00321633 Rev. #1 | 4 Hour(s) | FIO BEAU P33C | 500 0 150
2026-11-16 06:30 | 2026-11-27 16:30 | 11 | CHATS FALLS TS, SOUTH MARCH TS | C3S.CFXSO, DL3, HL3, 2-C3S, A9-C3S | 1-00299036 Rev. #6 | 8 Hour(s) | FIO BEAU P33C | 500 0 150
2026-11-16 06:30 | 2026-11-27 16:30 | 11 | CHATS FALLS TS, SOUTH MARCH TS | C3S.CFXSO, 2-C3S, A9-C3S | 1-00299033 Rev. #6 | 4 Hour(s) | FIO BEAU P33C | 500 0 150
2026-11-16 06:30 | 2026-11-27 16:30 | 11 | CHATS FALLS TS, SOUTH MARCH TS | C3S.CFXSO, A1A2, 2-C3S, A9-C3S, A2_BUS, T2-A | 1-00196163 Rev. #53 | 6 Hour(s) | FIO BEAU P33C | 500 0 150
2027-12-06 03:30 | 2027-12-17 16:00 | 12 | HAWTHORNE TS, MASSON GS, IPB MASSON JCT, ST. ISIDORE TS, ORLEANS JCT 2, ORLEANS TS, CUMBERLAND JCT, LONGUEUIL JCT, LONGUEUIL TS | D5A.CUXGA, D5A.CUXIS, D5A.CUXO2, D5A.HAXO2, D5A.IPXMA, D5A.LOXIS, D5A.LOXLO, D5A.O2XOR, A1A2, HT5L5, KL5, 325T2-D5A, 48-D5A, 62D5A-26, T3-D5A, T1-A1, 62D5A-625 | 1-00296584 Rev. #4 | 6 Hour(s) | D5A | 250
2026-09-01 08:00 | 2026-12-13 23:00 | 104 | HINCHINBROOKE SS, CATARAQUI TS, LENNOX TS, LAFARGE JCT, GARDINER TS, GARDINER STR 44 JCT, WESTBROOK JCT, NPIF KINGSTON JCT | X2H.DEXWE, X2H.HIXCA, X2H.LAXDE, X2H.LAXLE, X2H.WEXGA, 10-X2H, 12-X2H, 1A-X2H, 1T3-X2H, H1T2-X2H | 1-00292309 Rev. #7 | 4 Hour(s) | No Impact | #N/A
2027-04-04 07:00 | 2027-05-07 17:00 | 33 | CROSBY TS, ST. LAWRENCE TS, HINCHINBROOKE SS, SMITHS FALLS TS, CROSBY JCT, EASTON YULE JCT | L21H.CRXCR, L21H.CRXEA, L21H.CRXHI, L21H.EAXLA, L21H.EAXSM, 10-L21H, 23T1-L21H, 49-L21H, T3-L21H, T4-L21H | 1-00319244 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2027-12-06 03:30 | 2027-12-17 16:00 | 12 | HAWTHORNE TS, MASSON GS, IPB MASSON JCT, ST. ISIDORE TS, ORLEANS JCT 2, ORLEANS TS, CUMBERLAND JCT, LONGUEUIL JCT, LONGUEUIL TS | D5A.CUXGA, D5A.CUXIS, D5A.CUXO2, D5A.HAXO2, D5A.IPXMA, D5A.LOXIS, D5A.LOXLO, D5A.O2XOR, A1A2, HT5L5, KL5, 325T2-D5A, 48-D5A, 62D5A-26, T3-D5A, T1-A1, 62D5A-625 | 1-00296584 Rev. #4 | 6 Hour(s) | D5A | 250
2026-11-28 08:00 | 2026-12-23 16:00 | 25 | NORTHBROOKE DS, LODGEROOM DS | B1S.LOXNO, 74B1S-12, Q38B1S-14 | 1-00297913 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2026-09-28 08:00 | 2026-10-09 16:00 | 11 | ST. LAWRENCE TS, MASSENA JCT | L33P.ROXLA, 49-L33P, PSR33-L33 | 1-00275118 Rev. #11 | 4 Hour(s) | No Impact | #N/A
2026-10-29 08:00 | 2026-11-13 16:00 | 15 | ST. LAWRENCE TS, MASSENA JCT | L34P.ROXLA, 49-L34P | 1-00275119 Rev. #10 | 4 Hour(s) | No Impact | #N/A
2025-11-25 08:00 | 2031-12-31 16:00 | 2227 | ST. LAWRENCE TS | 49-L5C | 1-00301379 Rev. #2 | 2 Hour(s) | No Impact | #N/A
2026-03-17 15:30 | 2026-11-11 16:00 | 239 | PICTON TS | OLDT1, OLD28T1-X21 | 1-00304973 Rev. #23 | Immediate | No Impact | #N/A
2026-05-08 08:00 | 2026-10-16 08:00 | 161 | PIPERVILLE JCT | 644L24A-48, 644L24A-MSO6, 644L24A-MSO7 | 1-00313515 Rev. #10 | Non-recallable | FIO BEAU P33C | 0 0 0
2026-05-08 16:00 | 2026-10-16 08:00 | 161 | PIPERVILLE JCT | 644L24A-MSO3 | 1-00314063 Rev. #6 | 2 Hour(s) | FIO BEAU P33C | 0 0 0
2026-06-08 09:30 | 2026-09-02 16:00 | 86 | DOBBIN TS | T2-K, T7-K | 1-00307293 Rev. #10 | 135 Min(s) | No Impact | #N/A
2026-09-04 08:00 | 2027-02-23 17:00 | 172 | LENNOX TS | KL526 | 1-00317843 Rev. #1 | Non-recallable | No Impact | #N/A
2026-09-04 08:00 | 2027-03-23 17:00 | 200 | LENNOX TS | KL526 | 1-00285554 Rev. #12 | Non-recallable | No Impact | #N/A
2026-09-04 23:00 | 2026-09-18 20:00 | 14 | BOWMANVILLE SS | EL527, EL542, H1E, H3E, E1_BUS, E2_BUS, E1-E2 | 1-00317863 Rev. #8 | 15 Min(s) | No Impact | #N/A
2026-09-08 08:00 | 2026-09-14 16:00 | 6 | BOWMANVILLE SS | EL527, EL542, H1E, H3E, E1_BUS, E2_BUS, E1-E2 | 1-00295505 Rev. #8 | 4 Hour(s) | No Impact | #N/A
2026-09-18 20:00 | 2026-10-02 16:00 | 14 | BOWMANVILLE SS | EL542, H1E, E1_BUS, E1-E2 | 1-00317341 Rev. #9 | 15 Min(s) | No Impact | #N/A
2026-09-28 06:00 | 2026-10-15 16:00 | 17 | LENNOX TS, BOWMANVILLE SS | X520B.BOXLE, 12-X520B, R56-X520B | 1-00316087 Rev. #4 | 4 Hour(s) | No Impact | #N/A
2026-09-28 08:00 | 2026-10-09 16:00 | 11 | MARINE JCT, OTONABEE TS, CHATS FALLS TS, CLARINGTON TS | 128T2-T22C, 296-T22C, T22C.CHXMJ, T22C.MJXCL, T22C.MJXOT, 2-T22C | 1-00320737 Rev. #2 | 4 Hour(s) | FIO BEAU P33C | 0 0 100
2026-09-29 05:30 | 2026-11-11 11:30 | 43 | LENNOX TS, GRETNA JCT, NAPANEE TS, PICTON TS | X22.GRXLE, X22.GRXNA, X22.GRXPI, 12-X22, T2-X22 | 1-00292505 Rev. #8 | 6 Hour(s) | No Impact | #N/A
2026-09-30 08:00 | 2026-11-30 16:00 | 61 | DOBBIN TS | T2-K, T7-K | 1-00290614 Rev. #5 | 4 Hour(s) | No Impact | #N/A
2026-10-13 08:00 | 2026-11-11 09:30 | 29 | LENNOX TS | PX3, X3L520, X3_BUS | 1-00320747 Rev. #5 | 6 Hour(s) | No Impact | #N/A
2026-10-18 06:00 | 2026-10-23 16:00 | 5 | ST. LAWRENCE TS, R. H. SAUNDERS GS | S30L.SAXLA, 49-S30L, S30L-D | 1-00298374 Rev. #7 | 4 Hour(s) | No Impact | #N/A
2026-11-12 08:00 | 2026-12-03 16:00 | 21 | LENNOX TS | KX4, X4L521, X4_BUS | 1-00320864 Rev. #1 | 6 Hour(s) | No Impact | #N/A
2026-11-27 16:00 | 2026-12-04 16:00 | 7 | BOWMANVILLE SS | EL527, EL542, H1E, H3E, E1_BUS, E2_BUS, E1-E2 | 1-00317343 Rev. #7 | 15 Min(s) | No Impact | #N/A
2026-12-07 08:00 | 2027-03-19 16:00 | 102 | BOWMANVILLE SS | L27L43 | 1-00319087 Rev. #2 | 28 Day(s) | No Impact | #N/A
2026-12-10 08:00 | 2026-12-18 17:31 | 8 | LENNOX TS, GRETNA JCT, NAPANEE TS, PICTON TS | X22.GRXLE, X22.GRXNA, X22.GRXPI, 12-X22, T2-X22 | 1-00297891 Rev. #4 | 4 Hour(s) | No Impact | #N/A
2027-02-27 08:00 | 2027-06-06 16:00 | 99 | DOBBIN TS | T2, T2-A, T2-K | 1-00318909 Rev. #1 | 80 Day(s) | No Impact | #N/A
2027-09-13 08:00 | 2027-09-18 16:00 | 5 | BOWMANVILLE SS | AL526, AL541, H2A, H4A, A1_BUS, A2_BUS, A1-A2 | 1-00319730 Rev. #2 | 4 Hour(s) | No Impact | #N/A
2026-09-28 08:00 | 2026-10-09 16:00 | 11 | ST. LAWRENCE TS, MASSENA JCT | L33P.ROXLA, 49-L33P, PSR33-L33 | 1-00275118 Rev. #11 | 4 Hour(s) | No Impact | #N/A
2026-10-29 08:00 | 2026-11-13 16:00 | 15 | ST. LAWRENCE TS, MASSENA JCT | L34P.ROXLA, 49-L34P | 1-00275119 Rev. #10 | 4 Hour(s) | No Impact | #N/A
2027-12-06 03:30 | 2027-12-17 16:00 | 11 | HAWTHORNE TS, MASSON GS, IPB MASSON JCT, ST. ISIDORE TS, ORLEANS JCT 2, ORLEANS TS, CUMBERLAND JCT, LONGUEUIL JCT, LONGUEUIL TS | D5A.CUXGA, D5A.CUXIS, D5A.CUXO2, D5A.HAXO2, D5A.IPXMA, D5A.LOXIS, D5A.LOXLO, D5A.O2XOR, A1A2, HT5L5, KL5, 325T2-D5A, 48-D5A, 62D5A-26, T3-D5A, T1-A1, 62D5A-625 | 1-00296584 Rev. #4 | 6 Hour(s) | D5A | 250
2027-06-22 07:00 | 2027-06-29 17:00 | 7 | CHERRYWOOD TS, BOWMANVILLE SS | B542C.CHXBO, EL542, L20L42, 81-B542C, R56-B542C | 1-00319585 Rev. #1 | 4 Hour(s) | No Impact | #N/A
Back to main menu

## Table 4.6
Back to main menu
Table 4.6: Essa Zone Transmission Outages
Planned Start | Planned End | Duration (Days) | Station | Equipment Name | Outage ID | Max Recall | Major Transmission Interface Impacted | Reduction in Limit (MW)
2026-09-12 08:00 | 2026-10-08 16:01 | 26 | WOODBRIDGE JCT, CLAIREVILLE TS, VAUGHAN 4 JCT, VAUGHAN MTS #4, HOLLAND TS, HOLLAND JCT | 51-H82V, 153-H82V, H82V.WJXCL, H82V.4JXV4, H82V.4JXWJ, H82V.HJX4J, H82V.HOXHJ | 1-00296672 Rev. #9 | 4 Hour(s) | No Impact | #N/A
2026-09-12 08:00 | 2026-10-08 16:01 | 26 | WOODBRIDGE JCT, CLAIREVILLE TS, VAUGHAN 4 JCT, VAUGHAN MTS #4, HOLLAND TS, HOLLAND JCT | 51-H82V, 153-H82V, H82V.WJXCL, H82V.4JXV4, H82V.4JXWJ, H82V.HJX4J, H82V.HOXHJ | 1-00296672 Rev. #9 | 4 Hour(s) | No Impact | #N/A
2026-11-15 08:00 | 2026-12-11 16:00 | 26 | BEAVER JCT, BROWN HILL TS, BEAVERTON JCT, LINDSAY TS, MINDEN TS, BEAVERTON TS | M81B.BEXBE, M81B.BEXBV, M81B.BSXBE, M81B.BVXLI, M81B.BVXMI, L81L89, 4T1-M81B, 87-M81B, T4-M81B | 1-00320592 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2026-11-15 08:00 | 2026-12-11 16:00 | 26 | BEAVER JCT, BROWN HILL TS, BEAVERTON JCT, LINDSAY TS, MINDEN TS, BEAVERTON TS | M81B.BEXBE, M81B.BEXBV, M81B.BSXBE, M81B.BVXLI, M81B.BVXMI, L81L89, 4T1-M81B, 87-M81B, T4-M81B | 1-00320592 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2026-10-02 06:15 | 2026-10-09 14:00 | 7 | ORILLIA TS, MUSKOKA TS, BRACEBRIDGE JCT, ESSA TS, MIDHURST TS, COOPERS FALLS JCT, MINDEN TS | M7E.BRXMU, M7E.COXBR, M7E.COXMI, M7E.MIXES, M7E.MIXOR, M7E.ORXCO, 18-M7E, 87-M7E, T1-M7E, T2-M7E, T4-M7E | 1-00300271 Rev. #4 | 4 Hour(s) | No Impact | #N/A
2026-08-31 07:00 | 2026-09-11 16:00 | 11 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, 18-E510V, 51-E510V | 1-00308103 Rev. #15 | 4 Hour(s) | FS FN P502X CLAN | -100 0 -100 700
2026-09-12 08:00 | 2026-09-25 16:00 | 13 | ESSA TS, EVERETT JCT, ORANGEVILLE TS, EVERETT TS, ALLISTON TS, ALLISTON JCT | E8V.ALXAL, E8V.ALXES, E8V.ALXEV, E8V.EVXOR, HL8, TL7L8, 138E8V-MSO, 138T2-E8V, 18-E8V, 1807E8V-BO, 22-E8V, T2-E8V, 9T3-E8V | 1-00315398 Rev. #1 | 8 Hour(s) | No Impact | #N/A
2026-10-29 06:15 | 2026-11-06 07:15 | 8 | ESSA TS, CLAIREVILLE TS, MIDDLEPORT TS | E510V.CLXES, V586M.MDXCL, AL510, L552L586, PL586, W3L510, 18-E510V, 25-V586M, 51-E510V, 51-V586M | 1-00313522 Rev. #5 | 48 Hour(s) | FS FN P502X CLAN | -100 0 -100 700
2026-11-16 07:00 | 2026-12-04 16:00 | 18 | STAYNER TS, MEAFORD TS | S2S.MEXST, 234-S2S, A2-ST | 1-00321548 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2027-02-19 08:00 | 2027-02-26 16:00 | 7 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, 18-E510V, 51-E510V | 1-00308208 Rev. #2 | 8 Hour(s) | FS FN P502X CLAN | -100 0 -100 700
2026-11-15 08:00 | 2026-12-11 16:00 | 26 | BEAVER JCT, BROWN HILL TS, BEAVERTON JCT, LINDSAY TS, MINDEN TS, BEAVERTON TS | M81B.BEXBE, M81B.BEXBV, M81B.BSXBE, M81B.BVXLI, M81B.BVXMI, L81L89, 4T1-M81B, 87-M81B, T4-M81B | 1-00320592 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2026-08-31 07:00 | 2026-09-11 16:00 | 11 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, 18-E510V, 51-E510V | 1-00308103 Rev. #15 | 4 Hour(s) | FS FN P502X CLAN | -100 0 -100 700
2026-10-29 06:15 | 2026-11-06 07:15 | 8 | ESSA TS, CLAIREVILLE TS, MIDDLEPORT TS | E510V.CLXES, V586M.MDXCL, AL510, L552L586, PL586, W3L510, 18-E510V, 25-V586M, 51-E510V, 51-V586M | 1-00313522 Rev. #5 | 48 Hour(s) | FS FN P502X CLAN | -100 0 -100 700
2027-02-19 08:00 | 2027-02-26 16:00 | 7 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, 18-E510V, 51-E510V | 1-00308208 Rev. #2 | 8 Hour(s) | FS FN P502X CLAN | -100 0 -100 700
2026-08-31 07:00 | 2026-09-11 16:00 | 11 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, 18-E510V, 51-E510V | 1-00308103 Rev. #15 | 4 Hour(s) | FS FN P502X CLAN | -100 0 -100 700
2026-10-29 06:15 | 2026-11-06 07:15 | 8 | ESSA TS, CLAIREVILLE TS, MIDDLEPORT TS | E510V.CLXES, V586M.MDXCL, AL510, L552L586, PL586, W3L510, 18-E510V, 25-V586M, 51-E510V, 51-V586M | 1-00313522 Rev. #5 | 48 Hour(s) | FS FN P502X CLAN | -100 0 -100 700
2027-02-19 08:00 | 2027-02-26 16:00 | 7 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, 18-E510V, 51-E510V | 1-00308208 Rev. #2 | 8 Hour(s) | FS FN P502X CLAN | -100 0 -100 700
2027-11-01 12:00 | 2027-11-19 09:30 | 18 | DES JOACHIMS TS, OTTO HOLDEN TS | D5H.DEXHO, AL5, L1L5, L5L24 | 1-00300283 Rev. #1 | 8 Hour(s) | FS FN P502X CLAN | 25 0 25 0
2026-08-31 07:00 | 2026-09-11 16:00 | 11 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, 18-E510V, 51-E510V | 1-00308103 Rev. #15 | 4 Hour(s) | FS FN P502X CLAN | -100 0 -100 700
2026-10-29 06:15 | 2026-11-06 07:15 | 8 | ESSA TS, CLAIREVILLE TS, MIDDLEPORT TS | E510V.CLXES, V586M.MDXCL, AL510, L552L586, PL586, W3L510, 18-E510V, 25-V586M, 51-E510V, 51-V586M | 1-00313522 Rev. #5 | 48 Hour(s) | FS FN P502X CLAN | -100 0 -100 700
2027-02-19 08:00 | 2027-02-26 16:00 | 7 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, 18-E510V, 51-E510V | 1-00308208 Rev. #2 | 8 Hour(s) | FS FN P502X CLAN | -100 0 -100 700
2027-11-01 12:00 | 2027-11-19 09:30 | 18 | DES JOACHIMS TS, OTTO HOLDEN TS | D5H.DEXHO, AL5, L1L5, L5L24 | 1-00300283 Rev. #1 | 8 Hour(s) | FS FN P502X CLAN | 25 0 25 0
2027-11-01 12:00 | 2027-11-19 09:30 | 18 | DES JOACHIMS TS, OTTO HOLDEN TS | D5H.DEXHO, AL5, L1L5, L5L24 | 1-00300283 Rev. #1 | 8 Hour(s) | FS FN P502X CLAN | 25 0 25 0
2026-08-03 06:15 | 2026-10-01 16:00 | 59 | OTTER CREEK JCT, DES JOACHIMS TS, MINDEN TS | D4M.OTXDE, D4M.OTXMI, 5-D4M, 87-D4M, B9D4M-B8 | 1-00295116 Rev. #16 | 4 Hour(s) | No Impact | #N/A
2026-10-03 04:30 | 2027-10-02 04:00 | 364 | OTTER CREEK JCT | B9D2M-B8, B9D4M-B8 | 1-00319617 Rev. #2 | 2 Hour(s) | No Impact | #N/A
2026-10-13 06:15 | 2026-11-06 16:00 | 24 | DES JOACHIMS TS, MINDEN TS | D1M.MIXDE, 5-D1M, 87-D1M | 1-00295094 Rev. #8 | 4 Hour(s) | No Impact | #N/A
2026-11-09 06:15 | 2026-11-27 16:00 | 18 | OTTER CREEK JCT, DES JOACHIMS TS, MINDEN TS | D2M.OTXDE, D2M.OTXMI, 5-D2M, 87-D2M, B9D2M-B8, B9D4M-B8 | 1-00299045 Rev. #4 | 4 Hour(s) | No Impact | #N/A
2026-11-30 07:15 | 2026-12-15 16:00 | 15 | DES JOACHIMS TS, MINDEN TS | D3M.MIXDE, 5-D3M, 87-D3M | 1-00295024 Rev. #6 | 4 Hour(s) | No Impact | #N/A
Back to main menu

## Table 4.7
Back to main menu
Table 4.7: Niagara Zone Transmission Outages
Planned Start | Planned End | Duration (Days) | Station | Equipment Name | Outage ID | Max Recall | Major Transmission Interface Impacted | Reduction in Limit (MW)
2026-09-15 08:00 | 2026-11-17 16:00 | 63 | BECK 2 TS, NY NIAGARA 345 KV | PA27.NIXBE, 28R27-PA27, R27-S | 1-00308330 Rev. #11 | Non-recallable | No Impact | #N/A
2026-10-15 06:15 | 2026-10-23 16:00 | 8 | BURLINGTON TS, BURLINGTON DESN TS, BURLINGTON JCT, BECK 2 TS, NIAGARA WEST JCT, MIDDLEPORT TS, NEALE JCT, CARLUKE JCT | Q25BM.BEXNI, Q25BM.BUXBD, Q25BM.BUXBU, Q25BM.MIXCA, Q25BM.NEXBU, 25-Q25BM, 28-Q25BM, 39-Q25BM, T15-Q25BM | 1-00313527 Rev. #4 | 4 Hour(s) | No Impact | #N/A
2026-09-15 08:00 | 2026-11-17 16:00 | 63 | BECK 2 TS, NY NIAGARA 345 KV | PA27.NIXBE, 28R27-PA27, R27-S | 1-00308330 Rev. #11 | Non-recallable | No Impact | #N/A
2026-10-15 06:15 | 2026-10-23 16:00 | 8 | BURLINGTON TS, BURLINGTON DESN TS, BURLINGTON JCT, BECK 2 TS, NIAGARA WEST JCT, MIDDLEPORT TS, NEALE JCT, CARLUKE JCT | Q25BM.BEXNI, Q25BM.BUXBD, Q25BM.BUXBU, Q25BM.MIXCA, Q25BM.NEXBU, 25-Q25BM, 28-Q25BM, 39-Q25BM, T15-Q25BM | 1-00313527 Rev. #4 | 4 Hour(s) | No Impact | #N/A
2026-09-15 08:00 | 2026-11-17 16:00 | 63 | BECK 2 TS, NY NIAGARA 345 KV | PA27.NIXBE, 28R27-PA27, R27-S | 1-00308330 Rev. #11 | Non-recallable | No Impact | #N/A
2026-11-01 07:00 | 2026-11-13 16:00 | 12 | BECK 2 TS | K2L76 | 1-00315352 Rev. #13 | 3 Day(s) | No Impact | #N/A
2027-05-30 06:00 | 2027-06-04 15:00 | 5 | BECK 2 TS | TL26L27, 28-Q26M, TL26_BUS, K1TL26 | 1-00259298 Rev. #51 | 6 Hour(s) | No Impact | #N/A
2026-01-23 08:00 | 2026-09-03 17:00 | 223 | BECK 1 SS | 6E-7, E3_BUS, E4_BUS, E5_BUS, E6_BUS, E7_BUS, E5-E15, E6-E16, E8-E18, E9-E19, E8_BUS, E5-E6, E4-E5, E3-E4, E8-E9, AQ11S-A11, E9_BUS, A1-A11, E7-E8, A11_BUSNORTH, A11_BUSSOUTH, E3-E13, E4-E14 | 1-00305350 Rev. #29 | Non-recallable | No Impact | #N/A
2026-05-28 12:27 | 2026-12-31 16:00 | 217 | ALLANBURG TS | A8-D2 | 1-00315931 Rev. #1 | Non-recallable | No Impact | #N/A
2026-08-24 06:00 | 2026-09-04 15:00 | 11 | BECK 2 TS | K1K2 | 1-00259341 Rev. #18 | 3 Day(s) | No Impact | #N/A
2026-09-03 16:30 | 2026-09-25 08:00 | 22 | BECK 1 SS | E8-E9, AQ11S-A11, A1-A11, A11_BUSSOUTH | 1-00285434 Rev. #11 | 4 Hour(s) | No Impact | #N/A
2026-09-13 06:00 | 2026-09-25 15:00 | 12 | BECK 2 TS | D1D2 | 1-00259300 Rev. #15 | 3 Day(s) | No Impact | #N/A
2026-09-16 04:00 | 2026-11-06 19:00 | 52 | NY NIAGARA 230 KV | 2102, 2002, 2202, 2322, 2302 | 1-00286541 Rev. #3 | Non-recallable | No Impact | #N/A
2026-10-01 08:15 | 2026-10-30 16:00 | 29 | ALLANBURG TS, ALLANBURG WEST JCT, MIDDLEPORT TS, ABITIBI CONSOLIDATED NAN91 JCT, BECK 2 TS | Q26M.MIXAW, Q28A.ALXAB, 25-Q26M, 28-Q28A, 45-Q28A, 64Q26M-25, Q26M-Q10P, Q28A-Q10P | 1-00289214 Rev. #8 | 60 Hour(s) | No Impact | #N/A
2026-10-02 15:00 | 2026-10-18 05:30 | 16 | BECK 2 TS | K2L29, K2-BO4, K1K2 | 1-00268449 Rev. #6 | Non-recallable | No Impact | #N/A
2026-10-19 06:00 | 2026-10-30 16:00 | 11 | BECK 2 TS | K1L25 | 1-00259343 Rev. #9 | 3 Day(s) | No Impact | #N/A
2026-11-15 06:30 | 2026-11-27 16:00 | 12 | BECK 2 TS | D1L27 | 1-00259303 Rev. #10 | 3 Day(s) | No Impact | #N/A
2027-03-07 06:00 | 2027-03-25 16:00 | 18 | BECK 1 SS | AQ11S-A11, A1-A11, A11_BUSNORTH, A11_BUSSOUTH | 1-00285435 Rev. #27 | 2 Day(s) | No Impact | #N/A
Back to main menu

## Table 4.8
Back to main menu
Table 4.8: Northeast Zone Transmission Outages
Planned Start | Planned End | Duration (Days) | Station | Equipment Name | Outage ID | Max Recall | Major Transmission Interface Impacted | Reduction in Limit (MW)
2026-10-13 07:00 | 2026-11-06 16:00 | 24 | HUNTA SS | L2L9 | 1-00287779 Rev. #6 | 8 Hour(s) | No Impact | #N/A
2026-11-23 08:00 | 2026-12-06 16:00 | 13 | HUNTA SS, WARKUS JCT | H7T.HUXWA, L3L7, L4L7, 50-H7T, 62H7T-50, L7_BUS, H7T-62 | 1-00321842 Rev. #1 | 6 Hour(s) | No Impact | #N/A
2026-08-04 08:00 | 2026-09-01 16:00 | 28 | LOWER NOTCH JCT, DYMOND TS | T1-L71, T2-L71, W71D-32, W71D.LOXDY | 1-00313264 Rev. #51 | 5 Hour(s) | No Impact | #N/A
2026-10-18 08:00 | 2026-11-08 07:00 | 21 | RAMORE TS | 120A9K-16 | 1-00302108 Rev. #4 | 2 Hour(s) | No Impact | #N/A
2026-10-19 06:00 | 2026-11-08 07:00 | 20 | KIRKLAND LAKE TS | D4D9, D8D9, SC11D9, SC11SC, 16-A9K, D9_BUS, SC11, SC11D9-D9 | 1-00299098 Rev. #6 | 6 Hour(s) | No Impact | #N/A
2026-11-16 08:00 | 2026-12-03 16:00 | 17 | KIRKLAND LAKE TS, DYMOND TS, DANE JCT, GULL LAKE SOUTH JCT, NINE MILE JCT, NORTHLAND KIRKLAND LAKE CGS | D3K.DAXGU, D3K.DYXNI, D3K.GUXKI, D3K.GUXNP, D3K.NIXDA, 16-D3K, 32-D3K, 59D3K-16, 59D3K-68, 68D3K-32, 68D3K-16 | 1-00299028 Rev. #4 | 5 Hour(s) | No Impact | #N/A
2026-09-01 07:00 | 2026-09-22 16:30 | 21 | BURLINGTON TS, PALERMO TS, GLENORCHY JCT | 39-T37B, 7402T37B-MSO, T4-T37B | 1-00296683 Rev. #11 | 12 Hour(s) | No Impact | #N/A
2026-09-23 07:00 | 2026-10-20 16:00 | 27 | PALERMO TS, TRAFALGAR TS, BURLINGTON TS, PALERMO TXB JCT, GLENORCHY JCT, LANTZ JCT, GLENORCHY MTS1 | T36B.GJXGL, T36B.GJXLA, T36B.PAXBU, T36B.PAXTR, T36B.PJXGJ, 31-T36B, 31SC21L-T36B, 39-T36B, T3-T36B | 1-00310816 Rev. #4 | 8 Hour(s) | No Impact | #N/A
2026-10-21 07:00 | 2026-11-20 10:00 | 30 | TRAFALGAR TS, PALERMO TS, BURLINGTON TS, GLENORCHY JCT, PALERMO TXB JCT, LANTZ JCT, GLENORCHY MTS1 | T37B.GJXGL, T37B.GJXLA, T37B.PAXBU, T37B.PAXTR, T37B.PJXGJ, 31-T37B, 31SC21L-T37B, 39-T37B, T4-T37B | 1-00309267 Rev. #7 | 12 Hour(s) | No Impact | #N/A
2027-11-01 12:00 | 2027-11-19 09:30 | 18 | DES JOACHIMS TS, OTTO HOLDEN TS | D5H.DEXHO, AL5, L1L5, L5L24 | 1-00300283 Rev. #1 | 8 Hour(s) | FS FN P502X CLAN | 25 0 25 0
2027-08-09 08:00 | 2027-10-01 16:00 | 53 | HANMER TS | W6L502 | 1-00319861 Rev. #1 | 35 Day(s) | FS FN P502X CLAN | 70 0 110 0
2027-11-01 12:00 | 2027-11-19 09:30 | 18 | DES JOACHIMS TS, OTTO HOLDEN TS | D5H.DEXHO, AL5, L1L5, L5L24 | 1-00300283 Rev. #1 | 8 Hour(s) | FS FN P502X CLAN | 25 0 25 0
2026-11-08 09:00 | 2026-11-24 17:00 | 16 | HANMER TS, MARTINDALE TS, HANMER PARALLEL B JCT, MARTINDALE PARALLEL B JCT | X25S.MAXHA, 33-X25S, 9-X25S, X29S.HAXHB, X29S.HBXMB, X29S.MBXMA | 1-00299046 Rev. #4 | 5 Hour(s) | No Impact | #N/A
2026-09-02 08:00 | 2026-10-03 16:00 | 31 | OTTO HOLDEN TS, WIDDIFIELD TS | H24S.WIXHO, 6-H24S, H24S-6 | 1-00294340 Rev. #14 | 5 Hour(s) | No Impact | #N/A
2026-10-06 08:00 | 2026-10-29 16:00 | 23 | CRYSTAL FALLS TS, MARTINDALE TS, PEDLEY JCT, WIDDIFIELD TS | H23S.PEXCR, H23S.PEXMA, H23S.PEXWI, 7T5-H23S, 9-H23S, H23S-9 | 1-00299061 Rev. #5 | 5 Hour(s) | No Impact | #N/A
2026-10-18 08:00 | 2026-11-08 07:00 | 21 | RAMORE TS | 120A9K-16 | 1-00302108 Rev. #4 | 2 Hour(s) | No Impact | #N/A
2026-10-19 06:00 | 2026-11-08 07:00 | 20 | KIRKLAND LAKE TS | D4D9, D8D9, SC11D9, SC11SC, 16-A9K, D9_BUS, SC11, SC11D9-D9 | 1-00299098 Rev. #6 | 6 Hour(s) | No Impact | #N/A
2026-11-16 08:00 | 2026-12-03 16:00 | 17 | KIRKLAND LAKE TS, DYMOND TS, DANE JCT, GULL LAKE SOUTH JCT, NINE MILE JCT, NORTHLAND KIRKLAND LAKE CGS | D3K.DAXGU, D3K.DYXNI, D3K.GUXKI, D3K.GUXNP, D3K.NIXDA, 16-D3K, 32-D3K, 59D3K-16, 59D3K-68, 68D3K-32, 68D3K-16 | 1-00299028 Rev. #4 | 5 Hour(s) | No Impact | #N/A
2027-11-01 12:00 | 2027-11-19 09:30 | 18 | DES JOACHIMS TS, OTTO HOLDEN TS | D5H.DEXHO, AL5, L1L5, L5L24 | 1-00300283 Rev. #1 | 8 Hour(s) | FS FN P502X CLAN | 25 0 25 0
2026-08-04 08:00 | 2026-09-01 16:00 | 28 | LOWER NOTCH JCT, DYMOND TS | T1-L71, T2-L71, W71D-32, W71D.LOXDY | 1-00313264 Rev. #51 | 5 Hour(s) | No Impact | #N/A
2026-09-23 06:00 | 2026-09-29 17:00 | 6 | PINARD TS, PORCUPINE TS | D501P.POXPI, 30-D501P, T1-D501P, T2-D501P | 1-00320668 Rev. #1 | 3 Hour(s) | No Impact | #N/A
2026-09-23 06:00 | 2026-09-29 17:00 | 6 | PINARD TS, PORCUPINE TS | D501P.POXPI, 30-D501P, T1-D501P, T2-D501P | 1-00294189 Rev. #9 | 4 Hour(s) | No Impact | #N/A
2026-09-23 07:00 | 2026-09-29 16:00 | 6 | PINARD TS, PORCUPINE TS | D501P.POXPI, KL21, KL22, 30-D501P, 31T1-K, 31T2-K, K_BUS, T1-D501P, T2-D501P | 1-00313210 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2026-09-23 07:00 | 2026-09-29 16:00 | 6 | PORCUPINE TS, PINARD TS | D501P.POXPI, H1L501, H2L501, 30-D501P, T1-D501P, T2-D501P | 1-00313113 Rev. #1 | 5 Hour(s) | No Impact | #N/A
2026-10-05 16:00 | 2026-11-09 07:00 | 35 | PINARD TS | L20L21, PL20, 31-L20D | 1-00304043 Rev. #4 | 6 Hour(s) | No Impact | #N/A
2026-10-05 16:00 | 2026-11-09 07:00 | 35 | PINARD TS | 31-L20D | 1-00302163 Rev. #6 | 5 Hour(s) | No Impact | #N/A
2026-10-13 07:00 | 2026-11-06 16:00 | 24 | HUNTA SS | L2L9 | 1-00287779 Rev. #6 | 8 Hour(s) | No Impact | #N/A
2026-10-18 08:00 | 2026-11-08 07:00 | 21 | RAMORE TS | 120A9K-16 | 1-00302108 Rev. #4 | 2 Hour(s) | No Impact | #N/A
2026-10-19 06:00 | 2026-11-08 07:00 | 20 | KIRKLAND LAKE TS | D4D9, D8D9, SC11D9, SC11SC, 16-A9K, D9_BUS, SC11, SC11D9-D9 | 1-00299098 Rev. #6 | 6 Hour(s) | No Impact | #N/A
2026-11-16 08:00 | 2026-12-03 16:00 | 17 | KIRKLAND LAKE TS, DYMOND TS, DANE JCT, GULL LAKE SOUTH JCT, NINE MILE JCT, NORTHLAND KIRKLAND LAKE CGS | D3K.DAXGU, D3K.DYXNI, D3K.GUXKI, D3K.GUXNP, D3K.NIXDA, 16-D3K, 32-D3K, 59D3K-16, 59D3K-68, 68D3K-32, 68D3K-16 | 1-00299028 Rev. #4 | 5 Hour(s) | No Impact | #N/A
2026-11-23 08:00 | 2026-12-06 16:00 | 13 | HUNTA SS, WARKUS JCT | H7T.HUXWA, L3L7, L4L7, 50-H7T, 62H7T-50, L7_BUS, H7T-62 | 1-00321842 Rev. #1 | 6 Hour(s) | No Impact | #N/A
2026-08-04 08:00 | 2026-09-01 16:00 | 28 | LOWER NOTCH JCT, DYMOND TS | T1-L71, T2-L71, W71D-32, W71D.LOXDY | 1-00313264 Rev. #51 | 5 Hour(s) | No Impact | #N/A
2026-08-04 08:00 | 2026-09-01 16:00 | 28 | LOWER NOTCH JCT, DYMOND TS | T1-L71, T2-L71, W71D-32, W71D.LOXDY | 1-00313264 Rev. #51 | 5 Hour(s) | No Impact | #N/A
2026-08-23 08:00 | 2026-09-24 16:00 | 32 | AUBREY FALLS JCT, WAWA TS, MISSISSAGI TS | P25W.AUXMI, P25W.AUXWA, 14-P25W, 34-P25W | 1-00294347 Rev. #11 | 5 Hour(s) | EWTE EWTW | 280 200
2026-10-25 08:00 | 2026-11-19 16:00 | 25 | AUBREY FALLS JCT, WAWA TS, MISSISSAGI TS | P26W.AUXMI, P26W.AUXWA, 34-P26W, 14-P26W | 1-00302105 Rev. #4 | 5 Hour(s) | EWTE EWTW | 280 200
2026-12-06 08:00 | 2026-12-17 16:00 | 11 | MISSISSAGI TS, ALGOMA TS | A23P.MIXAL, 26-A23P, 34-A23P | 1-00298969 Rev. #4 | 5 Hour(s) | EWTE EWTW | 175 150
2024-06-20 18:00 | 2027-12-31 16:00 | 1289 | PATRICK ST TS | 1900-07-23 | 1-00257104 Rev. #19 | Non-recallable | No Impact | #N/A
2026-03-05 08:47 | 2026-12-31 16:00 | 301 | CLERGUE TS | 1900-06-17 | 1-00309843 Rev. #7 | Non-recallable | No Impact | #N/A
2026-03-12 16:30 | 2026-09-30 16:00 | 202 | BFN JCT | 653W4H-9989 | 1-00309134 Rev. #11 | Non-recallable | No Impact | #N/A
2026-04-27 07:00 | 2027-12-16 16:00 | 598 | PORCUPINE TS | T1-D1, SVC1 | 1-00312403 Rev. #6 | Non-recallable | No Impact | #N/A
2026-06-01 17:45 | 2026-09-21 08:00 | 112 | PORCUPINE TS | T8, T8-HT8, 30T8-H2, TEMPH2-BO1 | 1-00305822 Rev. #33 | 46 Day(s) | No Impact | #N/A
2026-06-01 19:20 | 2026-09-22 16:00 | 113 | PORCUPINE TS | H2L501 | 1-00316167 Rev. #5 | Non-recallable | No Impact | #N/A
2026-06-05 16:00 | 2026-12-31 16:00 | 209 | ANTOINE TS | 583L5A-MSO | 1-00316544 Rev. #7 | Non-recallable | No Impact | #N/A
2026-06-09 16:00 | 2026-09-01 08:00 | 84 | THIRD LINE TS | T3-WT3, T3 | 1-00315159 Rev. #11 | Non-recallable | No Impact | #N/A
2026-06-10 17:00 | 2026-12-31 16:00 | 204 | ANTOINE TS | 583A4Z-MSO | 1-00316545 Rev. #8 | Non-recallable | No Impact | #N/A
2026-08-31 06:00 | 2026-09-20 18:00 | 21 | HOGG GS, GARTSHORE TS | HOGG1.1, 1404 | 1-00321741 Rev. #2 | Non-recallable | No Impact | #N/A
2026-09-03 16:00 | 2026-09-09 08:00 | 6 | THIRD LINE TS | T3-WT3, T3 | 1-00320657 Rev. #1 | Non-recallable | No Impact | #N/A
2026-09-11 16:00 | 2026-10-13 12:00 | 32 | THIRD LINE TS | T3-WT3, T3 | 1-00320659 Rev. #1 | Non-recallable | No Impact | #N/A
2026-09-13 12:00 | 2026-09-25 09:00 | 12 | THIRD LINE TS | 408, DL21, DL22, AL25, DL26, L25L26, 1709-G25, 1709-G26 | 1-00291016 Rev. #10 | 8 Hour(s) | No Impact | #N/A
2026-09-28 07:00 | 2026-10-08 09:00 | 10 | THIRD LINE TS | K24G-BO, AWT3, AL25, DL26, L25L26, 1709-G25, 1709-G26, AWT1, AWT2, 1709-K24G | 1-00292533 Rev. #11 | 8 Hour(s) | EWTE EWTW | 175 150
2026-10-29 08:00 | 2026-11-13 16:00 | 15 | MARTINDALE TS | AL6 | 1-00299156 Rev. #5 | 6 Hour(s) | No Impact | #N/A
2026-11-16 12:00 | 2026-11-27 08:00 | 11 | THIRD LINE TS | 412, 415, 1657, 549, T2, T2H_BUS | 1-00289949 Rev. #8 | 6 Hour(s) | No Impact | #N/A
2026-11-24 08:00 | 2026-12-03 16:00 | 9 | MISSISSAGI TS, P21G POLE 6 JCT, THIRD LINE TS | P21G.MIXP8, 34-P21G, P21G.P8XTH, 1709-K24G | 1-00320475 Rev. #1 | 5 Hour(s) | EWTE EWTW | 175 150
2026-12-07 08:00 | 2026-12-17 16:00 | 10 | MATTAWA JCT, NORTH BAY TS | 15L5A-A3, 583L5A-387 | 1-00298970 Rev. #3 | 5 Hour(s) | No Impact | #N/A
2027-10-12 11:00 | 2027-10-20 16:00 | 8 | ANJIGAMI TS, WAWA TS, DA WATSON TS | GL1.ANXWA, HIGHFAL2.AJXDA, 1335, 844, DL1, 14-GL1, DL1_BUS, 1306, HIGHFAL2.AGXAJ, HIGHFAL2.AJXWA | 1-00298960 Rev. #5 | 8 Hour(s) | No Impact | #N/A
2026-12-06 08:00 | 2026-12-17 16:00 | 11 | MISSISSAGI TS, ALGOMA TS | A23P.MIXAL, 26-A23P, 34-A23P | 1-00298969 Rev. #4 | 5 Hour(s) | EWTE EWTW | 175 150
Back to main menu

## Table 4.9
Back to main menu
Table 4.9: Northwest Zone Transmission Outages
Planned Start | Planned End | Duration (Days) | Station | Equipment Name | Outage ID | Max Recall | Major Transmission Interface Impacted | Reduction in Limit (MW)
2026-09-14 07:00 | 2026-10-15 07:00 | 31 | MOOSE LAKE TS | T2B, T3B, TL2, TL6, AT-MSO, ATPT-AT, T2, T3, TSS2, T2-AT, T3-AT | 1-00295125 Rev. #12 | 8 Hour(s) | No Impact | #N/A
2026-10-09 06:00 | 2026-10-18 19:00 | 10 | TCPL VERMILLION BAY JCT, KENORA TS | K23D.KEXVE, 34-K23D, 3411-34 | 1-00320435 Rev. #1 | 5 Hour(s) | EWTE EWTW | 175 125
2026-09-18 08:00 | 2026-10-20 16:00 | 32 | MARGACH DS, RABBIT LAKE SS | 15-K6F, 24T2-L, K6FT1-T2 | 1-00304036 Rev. #6 | 5 Hour(s) | EWTE EWTW | 175 125
2027-03-15 08:00 | 2027-04-22 16:00 | 38 | RABBIT LAKE SS | L2L4 | 1-00298951 Rev. #6 | 8 Hour(s) | No Impact | #N/A
2024-05-14 13:00 | 2026-12-31 16:00 | 961 | KENORA TS, WHITESHELL TS | K21W.WHXKE, 34-K21W | 1-00254393 Rev. #22 | 6 Hour(s) | EWTE EWTW | 25 25
2024-05-14 15:54 | 2026-12-31 23:59 | 961 | WHITESHELL TS | R4, R70, PS7 | 1-00254335 Rev. #14 | Non-recallable | No Impact | #N/A
2025-11-18 08:00 | 2026-12-31 16:00 | 408 | KENORA TS, WHITESHELL TS | K21W.WHXKE, 34-K21W | 1-00299527 Rev. #10 | 2 Hour(s) | EWTE EWTW | 25 25
2026-08-21 08:00 | 2026-09-03 16:00 | 13 | MARATHON DS, MARATHON TS, TERRACE BAY SS, PIC JCT, MARATHON DS JCT | T1M.PIXMA, T1M.PIXMD, 77T1M, 15-T1M, 2735T1-L | 1-00294349 Rev. #12 | 8 Hour(s) | EWTE EWTW | 175 125
2026-08-21 08:00 | 2026-09-03 16:00 | 13 | MARATHON DS, MARATHON TS, TERRACE BAY SS, PIC JCT, MARATHON DS JCT | T1M.PIXMA, T1M.PIXMD, 77T1M, 15-T1M, 2735T1-L | 1-00300375 Rev. #9 | 5 Hour(s) | EWTE EWTW | 175 125
2026-09-18 08:00 | 2026-10-20 16:00 | 32 | MARGACH DS, RABBIT LAKE SS | 15-K6F, 24T2-L, K6FT1-T2 | 1-00304036 Rev. #6 | 5 Hour(s) | EWTE EWTW | 175 125
2026-10-06 07:00 | 2026-10-21 17:00 | 15 | MACKENZIE TS | PL30 | 1-00288960 Rev. #12 | 5 Day(s) | No Impact | #N/A
2026-10-06 08:00 | 2026-10-29 16:00 | 23 | LAKEHEAD TS, BIRCH TS, PINE PORTAGE SS | R2LB.BIXLA, R2LB.LAXPI, 12-R2LB, 17-R2LB, 26-R2LB | 1-00295286 Rev. #4 | 5 Hour(s) | No Impact | #N/A
2026-10-09 06:00 | 2026-10-18 19:00 | 10 | TCPL VERMILLION BAY JCT, KENORA TS | K23D.KEXVE, 34-K23D, 3411-34 | 1-00320435 Rev. #1 | 5 Hour(s) | EWTE EWTW | 175 125
2026-10-22 08:00 | 2026-11-06 16:00 | 15 | MACKENZIE TS, MOOSE LAKE TS | A3M.MAXMO, 20-A3M, 3-A3M | 1-00287613 Rev. #4 | 5 Hour(s) | EWTE EWTW | 175 125
2026-10-23 08:00 | 2026-11-22 16:00 | 30 | KENORA TS, WHITESHELL TS | K22W.WHXKE, 34-K22W | 1-00320445 Rev. #1 | 25 Day(s) | EWTE EWTW | 25 25
2026-10-26 07:00 | 2026-11-09 16:00 | 14 | MACKENZIE TS | HL93 | 1-00288959 Rev. #13 | 7 Day(s) | EWTE EWTW | 175 125
2026-11-04 07:00 | 2026-11-18 16:00 | 14 | MOOSE LAKE TS | L1L3, L3L6, 3-A3M | 1-00299139 Rev. #7 | 4 Hour(s) | EWTE EWTW | 175 125
2026-11-22 08:00 | 2026-12-06 16:00 | 14 | ALEXANDER SS, MINNOVA JCT | 4-A5A, A5A-5 | 1-00299012 Rev. #5 | 6 Hour(s) | EWTE EWTW | 175 125
2026-11-23 08:00 | 2026-12-01 16:00 | 8 | LAKEHEAD TS, RESERVE JCT, ALEXANDER SS | A7L.M1XAS, A7L.M1XLA, 12-A7L, 4-A7L, 57M1-J7 | 1-00320474 Rev. #1 | 16 Hour(s) | No Impact | #N/A
2026-11-23 08:00 | 2026-12-05 16:00 | 12 | FORT FRANCES TS, MACKENZIE TS | F25A.FOXMK, 20-F25A, 22-F25A | 1-00287614 Rev. #4 | 2 Day(s) | EWTE EWTW | 175 125
2026-12-02 08:00 | 2026-12-10 16:00 | 8 | LAKEHEAD TS, BIRCH TS, PINE PORTAGE SS | R1LB.BIXLA, R1LB.LAXPI, 12-R1LB, 17-R1LB, 26-R1LB | 1-00320483 Rev. #1 | 16 Hour(s) | No Impact | #N/A
2027-11-02 08:00 | 2027-12-14 16:00 | 42 | LAKEHEAD TS, MACKENZIE TS | A22L.MKXLA, L22L93, L22L23, PL22, L22_BUS | 1-00299000 Rev. #5 | 8 Hour(s) | EWTE EWTW | 230 150
2019-05-29 08:00 | 2026-12-31 16:00 | 2773 | FORT FRANCES TS | SC1.2, SC1, SC1.2-1 | 1-00117652 Rev. #14 | Non-recallable | No Impact | #N/A
2025-06-26 09:50 | 2026-09-23 16:00 | 454 | BIRCH TS | SC11R11, SC11SC, SC11, L15-R11 | 1-00288214 Rev. #10 | Non-recallable | No Impact | #N/A
2026-07-27 07:00 | 2026-09-15 17:00 | 50 | RABBIT LAKE SS | HL7 | 1-00295115 Rev. #28 | 30 Day(s) | No Impact | #N/A
2026-08-20 17:00 | 2026-09-08 17:00 | 19 | MACKENZIE TS | HL21 | 1-00288970 Rev. #7 | 5 Day(s) | No Impact | #N/A
2026-08-25 08:00 | 2026-09-26 16:00 | 32 | BIRCH TS, PORT ARTHUR TS 1 | P7B.BIXPO, 2P7B, 17-P7B | 1-00295071 Rev. #9 | 4 Hour(s) | No Impact | #N/A
2026-08-31 09:00 | 2026-09-11 09:00 | 11 | PINE PORTAGE SS | AT2L9, AT2_BUS, AT2L1 | 1-00321782 Rev. #2 | 4 Hour(s) | No Impact | #N/A
2026-09-21 11:30 | 2026-10-01 12:00 | 10 | ALEXANDER JCT | 4C2A-BO | 1-00318844 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2026-10-04 08:00 | 2026-10-09 16:00 | 5 | EAR FALLS TS, MANITOU FALLS GS | M3E.EAXMA, 1-M3E | 1-00320427 Rev. #1 | 8 Hour(s) | No Impact | #N/A
2026-10-09 08:00 | 2026-10-22 16:00 | 13 | DRYDEN TS | HL23, PL2, PL3, T22R22, 25-D5D, P_BUS, T22, TSS22, R22, T22-H, T22-P, T22-T22R22, TSS22-T | 1-00299072 Rev. #4 | 4 Hour(s) | No Impact | #N/A
2026-10-29 08:00 | 2026-12-03 16:00 | 35 | RABBIT LAKE SS | L2L7 | 1-00298950 Rev. #7 | 8 Hour(s) | No Impact | #N/A
2026-11-05 07:00 | 2026-11-15 16:00 | 10 | LAKEHEAD TS, MARATHON TS | PL37, W1L37, 12-M37L, L37_BUS, 15-M37L | 1-00288977 Rev. #16 | 8 Hour(s) | EWTE EWTW | 175 125
2026-11-05 16:00 | 2026-11-15 06:01 | 10 | LAKEHEAD TS | PL37, 12-M37L, L37_BUS, W1L37 | 1-00321369 Rev. #1 | 12 Hour(s) | EWTE EWTW | 175 125
2026-11-16 08:00 | 2026-11-22 16:00 | 6 | SAPAWE JCT, KASHABOWIE JCT | FR67-3, SPWE-17 | 1-00299031 Rev. #4 | 8 Hour(s) | No Impact | #N/A
2027-06-23 07:00 | 2027-09-04 17:00 | 73 | MARATHON TS | KL1 | 1-00297200 Rev. #4 | Non-recallable | No Impact | #N/A
Back to main menu

## Table 4.10
Back to main menu
Table 4.10: Ottawa Zone Transmission Outages
Planned Start | Planned End | Duration (Days) | Station | Equipment Name | Outage ID | Max Recall | Major Transmission Interface Impacted | Reduction in Limit (MW)
2026-09-17 08:00 | 2026-09-23 16:00 | 6 | HAWTHORNE TS | HT5L31 | 1-00297864 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2026-11-30 08:00 | 2026-12-11 16:00 | 11 | HAWTHORNE TS | HT5L5, KL5 | 1-00297876 Rev. #6 | 4 Hour(s) | No Impact | #N/A
2027-12-06 03:30 | 2027-12-17 16:00 | 12 | HAWTHORNE TS, MASSON GS, IPB MASSON JCT, ST. ISIDORE TS, ORLEANS JCT 2, ORLEANS TS, CUMBERLAND JCT, LONGUEUIL JCT, LONGUEUIL TS | D5A.CUXGA, D5A.CUXIS, D5A.CUXO2, D5A.HAXO2, D5A.IPXMA, D5A.LOXIS, D5A.LOXLO, D5A.O2XOR, A1A2, HT5L5, KL5, 325T2-D5A, 48-D5A, 62D5A-26, T3-D5A, T1-A1, 62D5A-625 | 1-00296584 Rev. #4 | 6 Hour(s) | FIO BEAU P33C | 250 690 0
2026-11-16 06:30 | 2026-11-27 16:30 | 11 | CHATS FALLS TS, SOUTH MARCH TS | C3S.CFXSO, 2-C3S, A9-C3S | 1-00321633 Rev. #1 | 4 Hour(s) | FIO BEAU P33C | 500 0 150
2026-11-16 06:30 | 2026-11-27 16:30 | 11 | CHATS FALLS TS, SOUTH MARCH TS | C3S.CFXSO, DL3, HL3, 2-C3S, A9-C3S | 1-00299036 Rev. #6 | 8 Hour(s) | FIO BEAU P33C | 500 0 150
2026-11-16 06:30 | 2026-11-27 16:30 | 11 | CHATS FALLS TS, SOUTH MARCH TS | C3S.CFXSO, 2-C3S, A9-C3S | 1-00299033 Rev. #6 | 4 Hour(s) | FIO BEAU P33C | 500 0 150
2026-11-16 06:30 | 2026-11-27 16:30 | 11 | CHATS FALLS TS, SOUTH MARCH TS | C3S.CFXSO, A1A2, 2-C3S, A9-C3S, A2_BUS, T2-A | 1-00196163 Rev. #53 | 6 Hour(s) | FIO BEAU P33C | 500 0 150
2026-05-19 06:52 | 2026-09-17 16:00 | 121 | HAWTHORNE TS | T2, R2-T2, T2-HT2, T2-LT2 | 1-00315158 Rev. #7 | Non-recallable | FIO BEAU P33C | 150 0 0
2026-09-14 06:30 | 2026-09-25 16:00 | 11 | MERIVALE TS, TERRY FOX JCT | 319E34M-6, 6-E34M | 1-00295134 Rev. #4 | 6 Hour(s) | No Impact | #N/A
2026-09-27 14:30 | 2026-10-16 14:30 | 19 | ALBION TS, ALBION JCT, MERIVALE TS, ELLWOOD MTS JCT, HAWTHORNE TS | M30A.AJXEJ, M30A.ALXME, M30A.EJXHA, L30L34, PL30, 48-M30A, 6-M30A, 84T2-M30A | 1-00290050 Rev. #3 | 6 Hour(s) | FIO BEAU P33C | 0 0 0
2026-09-27 14:30 | 2026-10-16 15:30 | 19 | ALBION TS, ALBION JCT, MERIVALE TS, ELLWOOD MTS JCT, HAWTHORNE TS | M30A.AJXEJ, M30A.ALXME, M30A.EJXHA, 48-M30A, 6-M30A, 84T2-M30A | 1-00313177 Rev. #1 | 4 Hour(s) | FIO BEAU P33C | 0 0 0
2026-10-18 14:30 | 2026-11-06 14:30 | 19 | MERIVALE TS, ALBION JCT, ELLWOOD MTS JCT, HAWTHORNE TS, ALBION TS | M31A.AJXEJ, M31A.ALXME, M31A.EJXHA, L31L32, OLDPL31, 48-M31A, 6-M31A, 84T1-M31A, L31WT24, PL31, B6-M31A | 1-00320732 Rev. #4 | 6 Hour(s) | FIO BEAU P33C | 0 0 0
2026-10-18 14:30 | 2026-11-06 15:30 | 19 | MERIVALE TS, ALBION JCT, ELLWOOD MTS JCT, HAWTHORNE TS, ALBION TS | M31A.AJXEJ, M31A.ALXME, M31A.EJXHA, 48-M31A, 6-M31A, 84T1-M31A | 1-00320731 Rev. #1 | 4 Hour(s) | FIO BEAU P33C | 0 0 0
2026-11-16 06:30 | 2026-11-27 16:30 | 11 | CHATS FALLS TS, SOUTH MARCH TS | C3S.CFXSO, 2-C3S, A9-C3S | 1-00321633 Rev. #1 | 4 Hour(s) | FIO BEAU P33C | 500 0 150
2026-11-16 06:30 | 2026-11-27 16:30 | 11 | CHATS FALLS TS, SOUTH MARCH TS | C3S.CFXSO, DL3, HL3, 2-C3S, A9-C3S | 1-00299036 Rev. #6 | 8 Hour(s) | FIO BEAU P33C | 500 0 150
2026-11-16 06:30 | 2026-11-27 16:30 | 11 | CHATS FALLS TS, SOUTH MARCH TS | C3S.CFXSO, 2-C3S, A9-C3S | 1-00299033 Rev. #6 | 4 Hour(s) | FIO BEAU P33C | 500 0 150
2026-11-16 06:30 | 2026-11-27 16:30 | 11 | CHATS FALLS TS, SOUTH MARCH TS | C3S.CFXSO, A1A2, 2-C3S, A9-C3S, A2_BUS, T2-A | 1-00196163 Rev. #53 | 6 Hour(s) | FIO BEAU P33C | 500 0 150
2027-12-06 03:30 | 2027-12-17 16:00 | 12 | HAWTHORNE TS, MASSON GS, IPB MASSON JCT, ST. ISIDORE TS, ORLEANS JCT 2, ORLEANS TS, CUMBERLAND JCT, LONGUEUIL JCT, LONGUEUIL TS | D5A.CUXGA, D5A.CUXIS, D5A.CUXO2, D5A.HAXO2, D5A.IPXMA, D5A.LOXIS, D5A.LOXLO, D5A.O2XOR, A1A2, HT5L5, KL5, 325T2-D5A, 48-D5A, 62D5A-26, T3-D5A, T1-A1, 62D5A-625 | 1-00296584 Rev. #4 | 6 Hour(s) | FIO BEAU P33C | 250 690 0
2026-11-30 08:00 | 2026-12-11 16:00 | 11 | HAWTHORNE TS | HT5L5, KL5 | 1-00297876 Rev. #6 | 4 Hour(s) | No Impact | #N/A
2027-12-06 03:30 | 2027-12-17 16:00 | 12 | HAWTHORNE TS, MASSON GS, IPB MASSON JCT, ST. ISIDORE TS, ORLEANS JCT 2, ORLEANS TS, CUMBERLAND JCT, LONGUEUIL JCT, LONGUEUIL TS | D5A.CUXGA, D5A.CUXIS, D5A.CUXO2, D5A.HAXO2, D5A.IPXMA, D5A.LOXIS, D5A.LOXLO, D5A.O2XOR, A1A2, HT5L5, KL5, 325T2-D5A, 48-D5A, 62D5A-26, T3-D5A, T1-A1, 62D5A-625 | 1-00296584 Rev. #4 | 6 Hour(s) | FIO BEAU P33C | 250 690 0
2025-11-27 08:00 | 2026-10-14 08:00 | 321 | RUSSELL TS | 36T2-A5RK, A5RK-TEMPNEWT2 | 1-00296803 Rev. #11 | Immediate | No Impact | #N/A
2025-11-27 08:00 | 2027-04-04 07:00 | 493 | RUSSELL TS | 36T1-A6R, A6R-TEMPNEWT1 | 1-00296798 Rev. #9 | Immediate | No Impact | #N/A
2026-06-26 04:00 | 2026-09-30 23:59 | 97 | MERIVALE TS | T23-HT23, T24-HT24, T24, T23, T23-WT23, B6-E34M, B6-M30A, B6-M31A, B6-M32S, T24-WT24, WT21-WT21 | 1-00317920 Rev. #10 | Immediate | FIO BEAU P33C | 0 0 0
2026-09-08 06:00 | 2026-09-17 09:30 | 9 | MERIVALE TS | T23-HT23, T24-HT24, SS24-T24R, T24, T23, SS23-T23R | 1-00313126 Rev. #4 | Non-recallable | No Impact | #N/A
2026-09-09 08:00 | 2026-09-15 16:00 | 6 | HAWTHORNE TS | KL41 | 1-00297862 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2026-09-22 16:30 | 2026-12-01 09:30 | 70 | MERIVALE TS | T23-WT23 | 1-00313130 Rev. #2 | Non-recallable | No Impact | #N/A
2026-09-24 08:00 | 2026-09-30 16:00 | 6 | HAWTHORNE TS | LT1L41 | 1-00297867 Rev. #3 | 4 Hour(s) | FIO BEAU P33C | 0 0 0
2026-09-25 16:30 | 2026-12-01 07:30 | 67 | MERIVALE TS | T24-WT24 | 1-00318101 Rev. #1 | Non-recallable | No Impact | #N/A
2026-09-26 12:00 | 2026-10-10 08:00 | 14 | CUMBERLAND JCT | 625D5A-BO | 1-00308402 Rev. #3 | 8 Hour(s) | FIO BEAU P33C | 0 0 0
2026-10-08 08:00 | 2026-10-15 16:00 | 7 | HAWTHORNE TS | DLT1 | 1-00297871 Rev. #5 | 4 Hour(s) | FIO BEAU P33C | 0 0 0
2026-10-16 15:30 | 2026-12-01 07:30 | 46 | MERIVALE TS | B6-M30A | 1-00321617 Rev. #1 | Non-recallable | No Impact | #N/A
2026-10-25 08:00 | 2026-11-06 16:00 | 12 | HAWTHORNE TS, KING EDWARD TS, OVERBROOK TS, CYRVILLE JCT, BLACKBURN JCT, MOULTON JCT | A4K.BLXCY, A4K.HAXBL, A4K.KIXOV, 48-A4K, 63-A4K, 8A4K-48, A4K-63, A4K-48 | 1-00302104 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2026-11-06 15:30 | 2026-12-01 07:30 | 25 | MERIVALE TS | B6-M31A | 1-00321629 Rev. #1 | Non-recallable | No Impact | #N/A
2026-12-01 07:30 | 2027-04-26 14:00 | 146 | MERIVALE TS | T22-LT22 | 1-00321649 Rev. #1 | 2 Hour(s) | No Impact | #N/A
2027-05-31 07:00 | 2027-06-07 17:00 | 7 | HAWTHORNE TS | KL42 | 1-00298961 Rev. #2 | 4 Hour(s) | No Impact | #N/A
2027-06-19 16:00 | 2027-09-20 07:00 | 93 | HAWTHORNE TS | KL42 | 1-00298958 Rev. #2 | Non-recallable | No Impact | #N/A
2026-09-17 08:00 | 2026-09-23 16:00 | 6 | HAWTHORNE TS | HT5L31 | 1-00297864 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2026-11-30 08:00 | 2026-12-11 16:00 | 11 | HAWTHORNE TS | HT5L5, KL5 | 1-00297876 Rev. #6 | 4 Hour(s) | No Impact | #N/A
2027-12-06 03:30 | 2027-12-17 16:00 | 12 | HAWTHORNE TS, MASSON GS, IPB MASSON JCT, ST. ISIDORE TS, ORLEANS JCT 2, ORLEANS TS, CUMBERLAND JCT, LONGUEUIL JCT, LONGUEUIL TS | D5A.CUXGA, D5A.CUXIS, D5A.CUXO2, D5A.HAXO2, D5A.IPXMA, D5A.LOXIS, D5A.LOXLO, D5A.O2XOR, A1A2, HT5L5, KL5, 325T2-D5A, 48-D5A, 62D5A-26, T3-D5A, T1-A1, 62D5A-625 | 1-00296584 Rev. #4 | 6 Hour(s) | FIO BEAU P33C | 250 690 0
Back to main menu

## Table 4.11
Back to main menu
Table 4.11: Southwest Zone Transmission Outages
Planned Start | Planned End | Duration (Days) | Station | Equipment Name | Outage ID | Max Recall | Major Transmission Interface Impacted | Reduction in Limit (MW)
2026-05-04 07:00 | 2026-10-15 16:30 | 164 | MIDDLEPORT TS | T3, T3-L580, T3-HT3 | 1-00313634 Rev. #24 | Non-recallable | No Impact | #N/A
2026-07-29 06:15 | 2026-09-04 14:00 | 37 | BURLINGTON TS, HORNING TS, HORNING JCT, MIDDLEPORT TS | M28B.HOXBU, M28B.HOXHO, M28B.HOXMI, 25-M28B, 39-M28B, 4T3-M28B | 1-00296669 Rev. #34 | 6 Hour(s) | No Impact | #N/A
2026-09-08 06:15 | 2026-09-18 16:00 | 10 | GALT NORTH JCT, DETWEILER TS | 26-M21D, 399M21D-48 | 1-00295590 Rev. #14 | 8 Hour(s) | FABCW NBLIP BLIP | 100 0 0
2026-09-12 08:00 | 2026-09-25 16:00 | 13 | ESSA TS, EVERETT JCT, ORANGEVILLE TS, EVERETT TS, ALLISTON TS, ALLISTON JCT | E8V.ALXAL, E8V.ALXES, E8V.ALXEV, E8V.EVXOR, HL8, TL7L8, 138E8V-MSO, 138T2-E8V, 18-E8V, 1807E8V-BO, 22-E8V, T2-E8V, 9T3-E8V | 1-00315398 Rev. #1 | 8 Hour(s) | FABCW NBLIP BLIP | 100 0 0
2026-09-13 06:00 | 2026-10-16 16:00 | 33 | NANTICOKE TS, LONGWOOD TS | N582L.LOXNA, AWT13, DL582, HT8L582, L582WT13, 59-N582L, HT13_BUS, HT8_BUS, T13-WT13, W52-N582L | 1-00293595 Rev. #12 | 16 Hour(s) | FABCW NBLIP BLIP | 1100 300 800
2026-09-13 08:00 | 2026-09-18 16:00 | 5 | LONGWOOD TS, NANTICOKE TS | N582L.LOXNA, HL582, KL582, 59-N582L, W52-N582L | 1-00295560 Rev. #18 | 4 Hour(s) | FABCW NBLIP BLIP | 1100 300 800
2026-09-14 06:15 | 2026-10-02 17:00 | 18 | MEAFORD TS, OWEN SOUND TS | S2S.MEXOW, A1-OS, C2-S2S | 1-00312938 Rev. #6 | 4 Hour(s) | No Impact | #N/A
2026-09-20 06:15 | 2026-10-02 16:00 | 12 | DETWEILER TS, GALT JCT | 26-M20D, M20D-TEMP1 | 1-00295586 Rev. #14 | 12 Hour(s) | FABCW NBLIP BLIP | 100 0 0
2026-09-20 15:15 | 2027-03-05 08:30 | 166 | BUCHANAN TS, SALFORD JCT | 19-M31W, M31W-TEMP1 | 1-00297259 Rev. #18 | 90 Day(s) | No Impact | #N/A
2026-09-28 06:15 | 2026-10-05 16:00 | 7 | SCHEIFELE JCT, GUELPH NORTH JCT, WATERLOO NORTH 3 JCT, WATERLOO MTS 3, DETWEILER TS | D6V.DEXWA, D6V.SCXGU, D6V.WAXSC, D6V.WAXWA, 26-D6V, 2613D6V-2602 | 1-00320692 Rev. #1 | 4 Hour(s) | FABCW NBLIP BLIP | 100 0 0
2026-10-06 06:15 | 2026-10-29 16:00 | 23 | CAMPBELL TS, SPEED RIVER JCT, CEDAR TS, WATERLOO NORTH 3 JCT, SCHEIFELE JCT, WATERLOO MTS 3, GUELPH NORTH JCT, DETWEILER TS | D7V.CAXCJ, D7V.DEXWA, D7V.GUXCA, D7V.WAXSC, D7V.WAXWA, 26-D7V, 2613D7V-2608, 5T4-D7V, T2-D7V, T4-D7V | 1-00295584 Rev. #8 | 4 Hour(s) | FABCW NBLIP BLIP | 100 0 0
2026-10-15 06:15 | 2026-10-23 16:00 | 8 | BURLINGTON TS, BURLINGTON DESN TS, BURLINGTON JCT, BECK 2 TS, NIAGARA WEST JCT, MIDDLEPORT TS, NEALE JCT, CARLUKE JCT | Q25BM.BEXNI, Q25BM.BUXBD, Q25BM.BUXBU, Q25BM.MIXCA, Q25BM.NEXBU, 25-Q25BM, 28-Q25BM, 39-Q25BM, T15-Q25BM | 1-00313527 Rev. #4 | 4 Hour(s) | No Impact | #N/A
2026-10-19 06:15 | 2026-10-29 06:15 | 10 | MIDDLEPORT TS, CLAIREVILLE TS | V586M.MDXCL, L552L586, PL586, 25-V586M, 51-V586M | 1-00313524 Rev. #5 | 48 Hour(s) | FABCW NBLIP BLIP | 300 0 0
2026-10-19 07:30 | 2026-12-11 16:00 | 53 | MIDDLEPORT TS, CLAIREVILLE TS | V586M.MDXCL, L80L86, 25-V586M, 51-V586M | 1-00288368 Rev. #6 | Non-recallable | FABCW NBLIP BLIP | 300 0 0
2026-10-29 06:15 | 2026-11-06 07:15 | 8 | ESSA TS, CLAIREVILLE TS, MIDDLEPORT TS | E510V.CLXES, V586M.MDXCL, AL510, L552L586, PL586, W3L510, 18-E510V, 25-V586M, 51-E510V, 51-V586M | 1-00313522 Rev. #5 | 48 Hour(s) | FABCW NBLIP BLIP | 300 0 0
2026-11-01 08:00 | 2027-03-19 16:00 | 138 | CLAIREVILLE TS, MIDDLEPORT TS | V586M.MDXCL, AL510, W3L510, 25-V586M, 51-E510V, 51-V586M | 1-00311616 Rev. #4 | Non-recallable | FABCW NBLIP BLIP | 300 0 0
2026-11-03 07:15 | 2026-11-13 17:00 | 10 | BURLINGTON TS, HORNING JCT, MIDDLEPORT TS, HORNING TS | M27B.HOXBU, M27B.HOXHO, M27B.HOXMI, 25-M27B, 39-M27B, 4T4-M27B | 1-00316981 Rev. #2 | 6 Hour(s) | No Impact | #N/A
2026-11-09 06:15 | 2026-12-04 16:00 | 25 | SCHEIFELE JCT, GUELPH NORTH JCT, WATERLOO NORTH 3 JCT, WATERLOO MTS 3, DETWEILER TS | D6V.DEXWA, D6V.SCXGU, D6V.WAXSC, D6V.WAXWA, 26-D6V, 2613D6V-2602 | 1-00295582 Rev. #8 | 4 Hour(s) | FABCW NBLIP BLIP | 100 0 0
2026-11-16 07:00 | 2026-12-04 16:00 | 18 | STAYNER TS, MEAFORD TS | S2S.MEXST, 234-S2S, A2-ST | 1-00321548 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2026-11-16 07:15 | 2026-12-03 17:00 | 17 | BURLINGTON TS, HORNING TS, HORNING JCT, MIDDLEPORT TS | M28B.HOXBU, M28B.HOXHO, M28B.HOXMI, 25-M28B, 39-M28B, 4T3-M28B | 1-00318440 Rev. #1 | 6 Hour(s) | No Impact | #N/A
2027-02-07 08:00 | 2027-03-25 16:00 | 46 | NANTICOKE TS, LONGWOOD TS | N582L.LOXNA, AWT13, DL582, HT8L582, L582WT13, 59-N582L, HT13_BUS, T13-WT13, W52-N582L | 1-00308115 Rev. #5 | Non-recallable | FABCW NBLIP BLIP | 1100 300 800
2026-07-29 06:15 | 2026-09-04 14:00 | 37 | BURLINGTON TS, HORNING TS, HORNING JCT, MIDDLEPORT TS | M28B.HOXBU, M28B.HOXHO, M28B.HOXMI, 25-M28B, 39-M28B, 4T3-M28B | 1-00296669 Rev. #34 | 6 Hour(s) | No Impact | #N/A
2026-10-15 06:15 | 2026-10-23 16:00 | 8 | BURLINGTON TS, BURLINGTON DESN TS, BURLINGTON JCT, BECK 2 TS, NIAGARA WEST JCT, MIDDLEPORT TS, NEALE JCT, CARLUKE JCT | Q25BM.BEXNI, Q25BM.BUXBD, Q25BM.BUXBU, Q25BM.MIXCA, Q25BM.NEXBU, 25-Q25BM, 28-Q25BM, 39-Q25BM, T15-Q25BM | 1-00313527 Rev. #4 | 4 Hour(s) | No Impact | #N/A
2026-11-03 07:15 | 2026-11-13 17:00 | 10 | BURLINGTON TS, HORNING JCT, MIDDLEPORT TS, HORNING TS | M27B.HOXBU, M27B.HOXHO, M27B.HOXMI, 25-M27B, 39-M27B, 4T4-M27B | 1-00316981 Rev. #2 | 6 Hour(s) | No Impact | #N/A
2026-11-16 07:15 | 2026-12-03 17:00 | 17 | BURLINGTON TS, HORNING TS, HORNING JCT, MIDDLEPORT TS | M28B.HOXBU, M28B.HOXHO, M28B.HOXMI, 25-M28B, 39-M28B, 4T3-M28B | 1-00318440 Rev. #1 | 6 Hour(s) | No Impact | #N/A
2026-09-20 15:15 | 2027-03-05 08:30 | 166 | BUCHANAN TS, SALFORD JCT | 19-M31W, M31W-TEMP1 | 1-00297259 Rev. #18 | 90 Day(s) | No Impact | #N/A
2026-09-01 07:00 | 2026-09-22 16:30 | 21 | BURLINGTON TS, PALERMO TS, GLENORCHY JCT | 39-T37B, 7402T37B-MSO, T4-T37B | 1-00296683 Rev. #11 | 12 Hour(s) | No Impact | #N/A
2026-09-13 06:00 | 2026-10-16 16:00 | 33 | NANTICOKE TS, LONGWOOD TS | N582L.LOXNA, AWT13, DL582, HT8L582, L582WT13, 59-N582L, HT13_BUS, HT8_BUS, T13-WT13, W52-N582L | 1-00293595 Rev. #12 | 16 Hour(s) | FABCW NBLIP BLIP | 1100 300 800
2026-09-13 08:00 | 2026-09-18 16:00 | 5 | LONGWOOD TS, NANTICOKE TS | N582L.LOXNA, HL582, KL582, 59-N582L, W52-N582L | 1-00295560 Rev. #18 | 4 Hour(s) | FABCW NBLIP BLIP | 1100 300 800
2026-09-23 07:00 | 2026-10-20 16:00 | 27 | PALERMO TS, TRAFALGAR TS, BURLINGTON TS, PALERMO TXB JCT, GLENORCHY JCT, LANTZ JCT, GLENORCHY MTS1 | T36B.GJXGL, T36B.GJXLA, T36B.PAXBU, T36B.PAXTR, T36B.PJXGJ, 31-T36B, 31SC21L-T36B, 39-T36B, T3-T36B | 1-00310816 Rev. #4 | 8 Hour(s)
2026-10-19 06:15 | 2026-10-29 06:15 | 10 | MIDDLEPORT TS, CLAIREVILLE TS | V586M.MDXCL, L552L586, PL586, 25-V586M, 51-V586M | 1-00313524 Rev. #5 | 48 Hour(s) | FABCW NBLIP BLIP | 300 0 0
2026-10-19 07:30 | 2026-12-11 16:00 | 53 | MIDDLEPORT TS, CLAIREVILLE TS | V586M.MDXCL, L80L86, 25-V586M, 51-V586M | 1-00288368 Rev. #6 | Non-recallable | FABCW NBLIP BLIP | 300 0 0
2026-10-21 07:00 | 2026-11-20 10:00 | 30 | TRAFALGAR TS, PALERMO TS, BURLINGTON TS, GLENORCHY JCT, PALERMO TXB JCT, LANTZ JCT, GLENORCHY MTS1 | T37B.GJXGL, T37B.GJXLA, T37B.PAXBU, T37B.PAXTR, T37B.PJXGJ, 31-T37B, 31SC21L-T37B, 39-T37B, T4-T37B | 1-00309267 Rev. #7 | 12 Hour(s) | No Impact | #N/A
2026-10-29 06:15 | 2026-11-06 07:15 | 8 | ESSA TS, CLAIREVILLE TS, MIDDLEPORT TS | E510V.CLXES, V586M.MDXCL, AL510, L552L586, PL586, W3L510, 18-E510V, 25-V586M, 51-E510V, 51-V586M | 1-00313522 Rev. #5 | 48 Hour(s) | FABCW NBLIP BLIP | 300 0 0
2026-11-01 08:00 | 2027-03-19 16:00 | 138 | CLAIREVILLE TS, MIDDLEPORT TS | V586M.MDXCL, AL510, W3L510, 25-V586M, 51-E510V, 51-V586M | 1-00311616 Rev. #4 | Non-recallable | FABCW NBLIP BLIP | 300 0 0
2027-02-07 08:00 | 2027-03-25 16:00 | 46 | NANTICOKE TS, LONGWOOD TS | N582L.LOXNA, AWT13, DL582, HT8L582, L582WT13, 59-N582L, HT13_BUS, T13-WT13, W52-N582L | 1-00308115 Rev. #5 | Non-recallable | FABCW NBLIP BLIP | 1100 300 800
2026-10-29 06:15 | 2026-11-06 07:15 | 8 | ESSA TS, CLAIREVILLE TS, MIDDLEPORT TS | E510V.CLXES, V586M.MDXCL, AL510, L552L586, PL586, W3L510, 18-E510V, 25-V586M, 51-E510V, 51-V586M | 1-00313522 Rev. #5 | 48 Hour(s) | FABCW NBLIP BLIP | 300 0 0
2026-11-01 08:00 | 2027-03-19 16:00 | 138 | CLAIREVILLE TS, MIDDLEPORT TS | V586M.MDXCL, AL510, W3L510, 25-V586M, 51-E510V, 51-V586M | 1-00311616 Rev. #4 | Non-recallable | FABCW NBLIP BLIP | 300 0 0
2026-10-29 06:15 | 2026-11-06 07:15 | 8 | ESSA TS, CLAIREVILLE TS, MIDDLEPORT TS | E510V.CLXES, V586M.MDXCL, AL510, L552L586, PL586, W3L510, 18-E510V, 25-V586M, 51-E510V, 51-V586M | 1-00313522 Rev. #5 | 48 Hour(s) | FABCW NBLIP BLIP | 300 0 0
2026-11-01 08:00 | 2027-03-19 16:00 | 138 | CLAIREVILLE TS, MIDDLEPORT TS | V586M.MDXCL, AL510, W3L510, 25-V586M, 51-E510V, 51-V586M | 1-00311616 Rev. #4 | Non-recallable | FABCW NBLIP BLIP | 300 0 0
2026-10-22 07:00 | 2026-10-30 16:00 | 8 | NANTICOKE TS | SC22K1, SC22SC, SC22 | 1-00298903 Rev. #4 | 6 Hour(s) | No Impact | #N/A
2024-08-22 14:20 | 2026-12-31 16:00 | 861 | NANTICOKE TS | SVC1 | 1-00263077 Rev. #9 | Non-recallable | No Impact | #N/A
2024-10-27 08:00 | 2026-12-31 16:00 | 795 | NANTICOKE TS | T13, SVC1, T13-WT13 | 1-00269611 Rev. #7 | Non-recallable | No Impact | #N/A
2026-03-05 15:55 | 2026-08-31 16:00 | 179 | DOFASCO BAYFRONT CTS | A2H2 | 1-00309856 Rev. #5 | Non-recallable | No Impact | #N/A
2026-06-15 08:00 | 2026-12-25 16:00 | 193 | MIDDLEPORT TS | SS3, SS3-K | 1-00308162 Rev. #13 | 4 Hour(s) | No Impact | #N/A
2026-08-25 16:00 | 2026-09-17 06:00 | 23 | OWEN SOUND TS | L1L2, L1BUS-TEMP, L2BUS-TEMP | 1-00321671 Rev. #2 | 10 Day(s) | No Impact | #N/A
2026-08-31 08:00 | 2026-09-11 16:00 | 11 | DETWEILER TS | T1, T1-HT1, SVC1 | 1-00295860 Rev. #28 | 6 Hour(s) | No Impact | #N/A
2026-09-13 08:00 | 2026-10-16 16:00 | 33 | NANTICOKE TS | HT8L582 | 1-00309262 Rev. #4 | 4 Hour(s) | No Impact | #N/A
2026-09-22 08:00 | 2026-09-30 16:00 | 8 | BURLINGTON TS | L23L37 | 1-00298863 Rev. #4 | 6 Hour(s) | No Impact | #N/A
2026-09-26 16:00 | 2026-10-29 08:30 | 33 | OXFORD JCT | 639K7-MSO | 1-00321319 Rev. #1 | Non-recallable | No Impact | #N/A
2026-09-29 17:00 | 2026-11-09 06:00 | 41 | PRESTON TS | 21-F11C | 1-00313968 Rev. #3 | 10 Day(s) | No Impact | #N/A
2026-10-01 08:15 | 2026-10-30 16:00 | 29 | ALLANBURG TS, ALLANBURG WEST JCT, MIDDLEPORT TS, ABITIBI CONSOLIDATED NAN91 JCT, BECK 2 TS | Q26M.MIXAW, Q28A.ALXAB, 25-Q26M, 28-Q28A, 45-Q28A, 64Q26M-25, Q26M-Q10P, Q28A-Q10P | 1-00289214 Rev. #8 | 60 Hour(s) | No Impact | #N/A
2026-10-05 06:15 | 2026-10-30 17:00 | 25 | BRANT TS, POWERLINE JCT, BURLINGTON TS, DUNDAS 2 JCT, DUNDAS 2 TS, HORNING MOUNTAIN JCT, ALFORD JCT, NEWTON TS | 117T5-B12BL, 12-B12BL, 26-B12BL, 26-B13BL, 39-B12BL, B12BL.BRXPO, B12BL.DUXDU, B12BL.HOXAL, B12BL.HOXDU, B12BL.ALXBR, B12BL.BUXDU, B12BL.NEXHO | 1-00296675 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2026-10-08 07:15 | 2026-10-14 16:00 | 6 | SUMMERHAVEN SS, MIDDLEPORT TS, CALEDONIA JCT, CALEDONIA TS | S39M.CAXCA, S39M.CAXMI, S39M.SUXCA, 25-S39M, 262-S39M, N27T1-S39M | 1-00296671 Rev. #7 | 4 Hour(s) | No Impact | #N/A
2026-10-16 16:00 | 2027-02-22 08:00 | 129 | NANTICOKE TS | AWT13, HT8L582, L582WT13, HT13_BUS, HT8_BUS, T13-WT13 | 1-00298901 Rev. #5 | Non-recallable | No Impact | #N/A
2026-11-02 06:15 | 2026-11-27 17:00 | 25 | DUNDAS JCT, MCMASTER JCT, BURLINGTON TS, GLANFORD JCT, HORNING MOUNTAIN JCT, MOHAWK TS, NEWTON TS, DUNDAS TS | B3.DUXBU, B3.GLXHO, B3.HOXNE, B3.MCXDU, B3.MOXGL, 26B3-39, 26B4-39, 39-B3, 76B3-1, T2, T2-B3, 20T2-B3, B3.MCXHO | 1-00298907 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2026-11-02 08:00 | 2026-11-13 16:00 | 11 | SEAFORTH TS | T11B, T11-TL7, T11 | 1-00321218 Rev. #1 | 6 Hour(s) | No Impact | #N/A
2026-11-16 07:15 | 2026-12-03 16:00 | 17 | BURLINGTON TS, GAGE TS, GAGE JCT, BIRMINGHAM TS | B10.BIXGA, B10.BUXGA, B10.GAXGA, B11.BIXGA, B11.BUXGA, B11.GAXGA, 24-B11, 24-K2G, 24-B10, 24-K1G, 39-B11, 39-B10, 50-B11, 50-B10 | 1-00298916 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2027-01-11 07:15 | 2027-03-12 16:00 | 60 | BRONTE TS, BURLINGTON TS, PALERMO JCT | B8.BRXBR, B8.BRXBU, 39-B8, T2-B8, T2-B7, T4, 13T4-B8 | 1-00298822 Rev. #10 | 6 Hour(s) | No Impact | #N/A
2026-09-15 07:30 | 2026-09-21 16:30 | 6 | SEAFORTH TS, SEAFORTH LSO JCT, ST. MARYS TS | BY, DL6, DTL18, DTL7, KTL7, 61-L7S, D_BUS, L7S-M18, T1-TL7, T6-D | 1-00296312 Rev. #5 | 12 Hour(s) | No Impact | #N/A
2026-09-22 07:30 | 2026-09-29 07:30 | 7 | SEAFORTH TS, SEAFORTH LSO JCT, ST. MARYS TS | BY, DTL7, KL6, KTL18, KTL7, 61-L7S, K_BUS, L7S-M18, T1-TL7, T5-K, DBUS-TEMP2 | 1-00296313 Rev. #5 | 6 Hour(s) | No Impact | #N/A
2026-09-29 07:30 | 2026-10-13 07:30 | 14 | SEAFORTH TS, ST. MARYS TS | BY, DL6, DTL18, DTL7, D_BUS, T6-D | 1-00296314 Rev. #9 | 4 Hour(s) | No Impact | #N/A
2026-10-13 07:30 | 2026-10-26 07:30 | 13 | SEAFORTH TS, ST. MARYS TS | BY, DL6, DTL18, DTL7, KTL7, 61-L7S, D_BUS, T6-D, T11-TL7 | 1-00321127 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2026-10-22 07:00 | 2026-11-13 16:00 | 22 | BEACH TS | H3H5, H3L9, H4H8, H5H7, H6H7, H8L9, 17-HL3, H7_BUS, H8_BUS, T7-H7, T8-H8, H3_BUS | 1-00313526 Rev. #2 | 0 Hour(s) | No Impact | #N/A
2026-10-29 07:30 | 2026-11-12 16:30 | 14 | SEAFORTH TS, SEAFORTH LSO JCT | DTL7, KTL7, 61-L7S, L7S-M18, T11-TL7 | 1-00296315 Rev. #6 | 4 Hour(s) | No Impact | #N/A
Back to main menu

## Table 4.12
Back to main menu
Table 4.12: Toronto Zone Transmission Outages
Planned Start | Planned End | Duration (Days) | Station | Equipment Name | Outage ID | Max Recall | Major Transmission Interface Impacted | Reduction in Limit (MW)
2026-08-21 07:00 | 2026-08-31 16:00 | 10 | GERRARD JCT, HEARN SS, DON FLEET JCT, LEASIDE TS, CECIL TS, BLOOR STREET JCT | H6LC.BLXLE, H6LC.CEXGE, H6LC.DOXHE, H6LC.GEXBL, H6LC.GEXDO, H1L6, L5L6, L6L13, PL6, 22-H6LC-L6-G, 34-H6LC, 49-H6LC, 80H6LC-34, 80H6LC-22, 80H6LC-49 | 1-00266296 Rev. #28 | 24 Hour(s) | No Impact | #N/A
2026-09-12 08:00 | 2026-10-08 16:01 | 26 | WOODBRIDGE JCT, CLAIREVILLE TS, VAUGHAN 4 JCT, VAUGHAN MTS #4, HOLLAND TS, HOLLAND JCT | 51-H82V, 153-H82V, H82V.WJXCL, H82V.4JXV4, H82V.4JXWJ, H82V.HJX4J, H82V.HOXHJ | 1-00296672 Rev. #9 | 4 Hour(s) | No Impact | #N/A
2026-11-15 08:00 | 2026-11-21 16:00 | 6 | LEASIDE TS, BALFOUR JCT, BRIDGMAN JCT, WILTSHIRE TS, BAYVIEW JCT, BIRCH JCT, BRIDGMAN TS | L13W.BAXLE, L13W.BRXBA, L14W.BAXBI, L14W.BAXLE, L14W.BRXBI, H2L18W, H2L13W, H2L14W, JL14, L14L15, 31-L15, 31-L13W, 321L18W-34, 321L14W-34, 34-L13W, 34-L14W, 34-L18W, L13W-34 | 1-00315199 Rev. #7 | 4 Hour(s) | No Impact | #N/A
2026-11-22 08:00 | 2026-11-27 16:00 | 5 | HEARN SS, DON FLEET JCT, ESPLANADE TS | H1L10, L10L12, 22-H10DE, 36H10DE-22, H10DE.HEXDO | 1-00315368 Rev. #6 | 6 Hour(s) | No Impact | #N/A
2027-05-12 06:00 | 2027-05-19 16:30 | 7 | CHERRYWOOD TS, CLARINGTON TS, DUFFIN JCT | 81-T28C, K2L28, L23L28, 296-T28C, T28C.CLXDJ | 1-00297185 Rev. #4 | 4 Hour(s) | No Impact | #N/A
2026-09-12 08:00 | 2026-10-08 16:01 | 26 | WOODBRIDGE JCT, CLAIREVILLE TS, VAUGHAN 4 JCT, VAUGHAN MTS #4, HOLLAND TS, HOLLAND JCT | 51-H82V, 153-H82V, H82V.WJXCL, H82V.4JXV4, H82V.4JXWJ, H82V.HJX4J, H82V.HOXHJ | 1-00296672 Rev. #9 | 4 Hour(s) | No Impact | #N/A
2027-03-28 08:00 | 2027-04-23 16:00 | 26 | WOODBRIDGE JCT, VAUGHAN 3 JCT, WOODBRIDGE TS, KLEINBURG TS, CLAIREVILLE TS | V44.CLXWJ, V44.KLXV3, V44.V3XWJ, V44.WJXWO, 45T1-V44, 51-V44, D6T5-V44 | 1-00308228 Rev. #2 | 8 Hour(s) | No Impact | #N/A
2026-08-30 08:00 | 2026-09-10 16:00 | 11 | WILLOW CREEK JCT, MILTON SS, BRUCE B SS, BRUCE JCT | B501M.BBXBJ, B501M.BJXWJ, B501M.WJXMI, HL501, L501L570, 40-B501M, 29-B501M | 1-00295573 Rev. #26 | 4 Hour(s) | FABCW | 1750
2026-08-30 08:00 | 2026-09-11 16:00 | 12 | WILLOW CREEK JCT, MILTON SS, BRUCE B SS, BRUCE JCT | B501M.BBXBJ, B501M.BJXWJ, B501M.WJXMI, 40-B501M, 29-B501M | 1-00293593 Rev. #19 | 4 Hour(s) | FABCW | 1750
2026-08-31 07:00 | 2026-09-11 16:00 | 11 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, 18-E510V, 51-E510V | 1-00308103 Rev. #15 | 4 Hour(s) | No Impact | #N/A
2026-10-04 07:00 | 2026-10-17 16:00 | 13 | CLAIREVILLE TS | HT16L75, HT16L72, HT16_BUS, T16, T16-W4, T16-HT16 | 1-00295577 Rev. #8 | 4 Hour(s) | FABCW | 250
2026-10-19 06:15 | 2026-10-29 06:15 | 10 | MIDDLEPORT TS, CLAIREVILLE TS | V586M.MDXCL, L552L586, PL586, 25-V586M, 51-V586M | 1-00313524 Rev. #5 | 48 Hour(s) | FABCW | 300
2026-10-19 07:30 | 2026-12-11 16:00 | 53 | MIDDLEPORT TS, CLAIREVILLE TS | V586M.MDXCL, L80L86, 25-V586M, 51-V586M | 1-00288368 Rev. #6 | Non-recallable | FABCW | 300
2026-10-26 08:00 | 2026-11-20 16:00 | 25 | CLAIREVILLE TS, RICHVIEW JCT, RICHVIEW DESN TS, RICHVIEW TS, WESTMORE JCT, REXDALE TS | V74R.RIXRD, V74R.RIXRI, V74R.RIXWE, V74R.WEXCL, V74R.WEXRE, H2L74, HT13L74, 51-V74R, 88-V74R, T1-V74R, T5-V74R, 51V74R-BO | 1-00308160 Rev. #5 | 36 Hour(s) | No Impact | #N/A
2026-10-29 06:15 | 2026-11-06 07:15 | 8 | ESSA TS, CLAIREVILLE TS, MIDDLEPORT TS | E510V.CLXES, V586M.MDXCL, AL510, L552L586, PL586, W3L510, 18-E510V, 25-V586M, 51-E510V, 51-V586M | 1-00313522 Rev. #5 | 48 Hour(s) | FABCW | 300
2026-11-01 08:00 | 2027-03-19 16:00 | 138 | CLAIREVILLE TS, MIDDLEPORT TS | V586M.MDXCL, AL510, W3L510, 25-V586M, 51-E510V, 51-V586M | 1-00311616 Rev. #4 | Non-recallable | FABCW | 300
2027-02-19 08:00 | 2027-02-26 16:00 | 7 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, 18-E510V, 51-E510V | 1-00308208 Rev. #2 | 8 Hour(s) | No Impact | #N/A
2026-09-24 07:00 | 2026-10-02 16:00 | 8 | CLAIREVILLE TS, RICHVIEW TS | V73R.CLXRI, H1L73, HT15L73, 51-V73R, 88-V73R | 1-00296670 Rev. #9 | 4 Hour(s) | No Impact | #N/A
2026-10-26 08:00 | 2026-11-20 16:00 | 25 | CLAIREVILLE TS, RICHVIEW JCT, RICHVIEW DESN TS, RICHVIEW TS, WESTMORE JCT, REXDALE TS | V74R.RIXRD, V74R.RIXRI, V74R.RIXWE, V74R.WEXCL, V74R.WEXRE, H2L74, HT13L74, 51-V74R, 88-V74R, T1-V74R, T5-V74R, 51V74R-BO | 1-00308160 Rev. #5 | 36 Hour(s) | No Impact | #N/A
2026-08-30 08:00 | 2026-09-10 16:00 | 11 | WILLOW CREEK JCT, MILTON SS, BRUCE B SS, BRUCE JCT | B501M.BBXBJ, B501M.BJXWJ, B501M.WJXMI, HL501, L501L570, 40-B501M, 29-B501M | 1-00295573 Rev. #26 | 4 Hour(s) | FABCW | 1750
2026-08-30 08:00 | 2026-09-11 16:00 | 12 | WILLOW CREEK JCT, MILTON SS, BRUCE B SS, BRUCE JCT | B501M.BBXBJ, B501M.BJXWJ, B501M.WJXMI, 40-B501M, 29-B501M | 1-00293593 Rev. #19 | 4 Hour(s) | FABCW | 1750
2026-08-31 07:00 | 2026-09-11 16:00 | 11 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, 18-E510V, 51-E510V | 1-00308103 Rev. #15 | 4 Hour(s) | No Impact | #N/A
2026-09-01 07:00 | 2026-09-22 16:30 | 21 | BURLINGTON TS, PALERMO TS, GLENORCHY JCT | 39-T37B, 7402T37B-MSO, T4-T37B | 1-00296683 Rev. #11 | 12 Hour(s) | No Impact | #N/A
2026-09-23 07:00 | 2026-10-20 16:00 | 27 | PALERMO TS, TRAFALGAR TS, BURLINGTON TS, PALERMO TXB JCT, GLENORCHY JCT, LANTZ JCT, GLENORCHY MTS1 | T36B.GJXGL, T36B.GJXLA, T36B.PAXBU, T36B.PAXTR, T36B.PJXGJ, 31-T36B, 31SC21L-T36B, 39-T36B, T3-T36B | 1-00310816 Rev. #4 | 8 Hour(s) | No Impact | #N/A
2026-09-24 07:00 | 2026-10-02 16:00 | 8 | CLAIREVILLE TS, RICHVIEW TS | V73R.CLXRI, H1L73, HT15L73, 51-V73R, 88-V73R | 1-00296670 Rev. #9 | 4 Hour(s) | No Impact | #N/A
2026-10-04 07:00 | 2026-10-17 16:00 | 13 | CLAIREVILLE TS | HT16L75, HT16L72, HT16_BUS, T16, T16-W4, T16-HT16 | 1-00295577 Rev. #8 | 4 Hour(s) | FABCW | 250
2026-10-19 06:15 | 2026-10-29 06:15 | 10 | MIDDLEPORT TS, CLAIREVILLE TS | V586M.MDXCL, L552L586, PL586, 25-V586M, 51-V586M | 1-00313524 Rev. #5 | 48 Hour(s) | FABCW | 300
2026-10-19 07:30 | 2026-12-11 16:00 | 53 | MIDDLEPORT TS, CLAIREVILLE TS | V586M.MDXCL, L80L86, 25-V586M, 51-V586M | 1-00288368 Rev. #6 | Non-recallable | FABCW | 300
2026-10-21 07:00 | 2026-11-20 10:00 | 30 | TRAFALGAR TS, PALERMO TS, BURLINGTON TS, GLENORCHY JCT, PALERMO TXB JCT, LANTZ JCT, GLENORCHY MTS1 | T37B.GJXGL, T37B.GJXLA, T37B.PAXBU, T37B.PAXTR, T37B.PJXGJ, 31-T37B, 31SC21L-T37B, 39-T37B, T4-T37B | 1-00309267 Rev. #7 | 12 Hour(s) | No Impact | #N/A
2026-10-26 07:00 | 2026-11-20 16:00 | 25 | CLAIREVILLE TS, RICHVIEW TS | V77R.CLXCL, L41L77, L71L77, 51-V77R, 88-V77R | 1-00296680 Rev. #4 | 4 Hour(s) | No Impact | #N/A
2026-10-29 06:15 | 2026-11-06 07:15 | 8 | ESSA TS, CLAIREVILLE TS, MIDDLEPORT TS | E510V.CLXES, V586M.MDXCL, AL510, L552L586, PL586, W3L510, 18-E510V, 25-V586M, 51-E510V, 51-V586M | 1-00313522 Rev. #5 | 48 Hour(s) | FABCW | 300
2026-11-01 08:00 | 2027-03-19 16:00 | 138 | CLAIREVILLE TS, MIDDLEPORT TS | V586M.MDXCL, AL510, W3L510, 25-V586M, 51-E510V, 51-V586M | 1-00311616 Rev. #4 | Non-recallable | FABCW | 300
2026-11-04 08:00 | 2026-11-10 16:00 | 6 | RICHVIEW TS, CLAIREVILLE TS | V77R.CLXCL, A1L77, L21L77, 51-V77R, 88-V77R | 1-00295786 Rev. #4 | 4 Hour(s) | No Impact | #N/A
2027-02-19 08:00 | 2027-02-26 16:00 | 7 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, 18-E510V, 51-E510V | 1-00308208 Rev. #2 | 8 Hour(s) | No Impact | #N/A
2026-10-13 08:00 | 2026-11-04 16:00 | 22 | CLARINGTON TS, HAVELOCK TS, MARINE JCT, OTONABEE TS, SEATON JCT, WILSON JCT | 128T1-T31H, K2L28, L23L28, L23L31, P2L31, 296-T28C, 296-T31H, L28_BUS, L31_BUS, T31H.HAXMJ, T31H.MJXCL, T31H.MJXOT, 57-T31H, 72T23C-BO1, 527T28C-MSO2, L23_BUS | 1-00295709 Rev. #9 | 12 Hour(s) | No Impact | #N/A
2027-05-12 06:00 | 2027-05-19 16:30 | 7 | CHERRYWOOD TS, CLARINGTON TS, DUFFIN JCT | 81-T28C, K2L28, L23L28, 296-T28C, T28C.CLXDJ | 1-00297185 Rev. #4 | 4 Hour(s) | No Impact | #N/A
2026-08-31 07:00 | 2026-09-11 16:00 | 11 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, 18-E510V, 51-E510V | 1-00308103 Rev. #15 | 4 Hour(s) | No Impact | #N/A
2026-10-29 06:15 | 2026-11-06 07:15 | 8 | ESSA TS, CLAIREVILLE TS, MIDDLEPORT TS | E510V.CLXES, V586M.MDXCL, AL510, L552L586, PL586, W3L510, 18-E510V, 25-V586M, 51-E510V, 51-V586M | 1-00313522 Rev. #5 | 48 Hour(s) | FABCW | 300
2026-11-01 08:00 | 2027-03-19 16:00 | 138 | CLAIREVILLE TS, MIDDLEPORT TS | V586M.MDXCL, AL510, W3L510, 25-V586M, 51-E510V, 51-V586M | 1-00311616 Rev. #4 | Non-recallable | FABCW | 300
2027-02-19 08:00 | 2027-02-26 16:00 | 7 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, 18-E510V, 51-E510V | 1-00308208 Rev. #2 | 8 Hour(s) | No Impact | #N/A
2026-08-31 07:00 | 2026-09-11 16:00 | 11 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, 18-E510V, 51-E510V | 1-00308103 Rev. #15 | 4 Hour(s) | No Impact | #N/A
2026-10-29 06:15 | 2026-11-06 07:15 | 8 | ESSA TS, CLAIREVILLE TS, MIDDLEPORT TS | E510V.CLXES, V586M.MDXCL, AL510, L552L586, PL586, W3L510, 18-E510V, 25-V586M, 51-E510V, 51-V586M | 1-00313522 Rev. #5 | 48 Hour(s) | FABCW | 300
2026-11-01 08:00 | 2027-03-19 16:00 | 138 | CLAIREVILLE TS, MIDDLEPORT TS | V586M.MDXCL, AL510, W3L510, 25-V586M, 51-E510V, 51-V586M | 1-00311616 Rev. #4 | Non-recallable | FABCW | 300
2027-02-19 08:00 | 2027-02-26 16:00 | 7 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, 18-E510V, 51-E510V | 1-00308208 Rev. #2 | 8 Hour(s) | No Impact | #N/A
2022-06-22 16:50 | 2026-09-01 16:00 | 1532 | CLARINGTON TS | K1K2, P1P2 | 1-00202079 Rev. #20 | Non-recallable | No Impact | #N/A
2025-12-06 08:52 | 2026-08-31 16:00 | 268 | CLARINGTON TS | HT3L32 | 1-00302902 Rev. #11 | Non-recallable | No Impact | #N/A
2026-07-23 17:00 | 2026-08-31 17:01 | 39 | OSHAWA GM TS | H2-H3 | 1-00320213 Rev. #2 | 1 Day(s) | No Impact | #N/A
2026-08-09 06:00 | 2026-09-06 16:00 | 28 | WILTSHIRE TS, RUNNYMEDE TS, MANBY EAST TS | K11W.MAXRU, K11W.RUXWI, H2K11W, H2K12W, H1H2, H2H3, H2L18W, H2L13W, H2L14W, 38-K11W, H2_BUS, T1J, 11T1-K11W, T1, T6Z, 11T6-K11W, T6 | 1-00308747 Rev. #31 | 6 Hour(s) | No Impact | #N/A
2026-08-09 17:00 | 2026-12-05 18:00 | 118 | CHARLES TS | H2-T4, H2BUS-TEMP | 1-00313374 Rev. #7 | Non-recallable | No Impact | #N/A
2026-08-25 06:00 | 2026-09-08 16:00 | 14 | ESPLANADE TS, JOHN TS | H2JK.JOXES, H2JK-36, T11-K, 36H2JK-22, 36H2JK-37 | 1-00315706 Rev. #7 | 4 Hour(s) | No Impact | #N/A
2026-09-10 06:00 | 2026-09-25 12:00 | 15 | CECIL TS, TERAULEY TS, ESPLANADE TS | C5E.CEXTE, L7L9, 1C5E-49, 1C5E-36, 1C7E-36, 36-C5E, 36-C7E, 49-C5E, T3-D3, T4-D4 | 1-00315906 Rev. #5 | 6 Hour(s) | No Impact | #N/A
2026-09-13 08:00 | 2026-09-25 16:00 | 12 | CLAIREVILLE TS | D1L552, DL511, DL560, DL551, DL570, D1_BUS, D2_BUS, D1-D2 | 1-00298848 Rev. #7 | 4 Hour(s) | No Impact | #N/A
2026-09-13 08:00 | 2026-10-02 08:00 | 19 | CLAIREVILLE TS | D1L552, DL511, DL560, DL551, DL570, D1_BUS, D2_BUS, D1-D2 | 1-00238542 Rev. #21 | 1 Day(s) | No Impact | #N/A
2026-09-14 08:00 | 2026-09-22 16:00 | 8 | HEARN SS | SC11H1, SC11SC, SS1, SC11, SC11CA-SS1 | 1-00314058 Rev. #3 | 6 Hour(s) | No Impact | #N/A
2026-09-15 07:00 | 2026-09-22 16:00 | 7 | LEASIDE TS | T17, T17-K, T17-L17 | 1-00295733 Rev. #4 | 6 Hour(s) | No Impact | #N/A
2026-09-21 07:00 | 2026-09-26 16:00 | 5 | LEASIDE TS | Q2A2, T21Q1, T21, T21-HL16, T21Y1 | 1-00305846 Rev. #25 | 4 Hour(s) | No Impact | #N/A
2026-09-22 08:00 | 2026-10-09 20:00 | 18 | GLENGROVE TS, DUPLEX TS | D6Y.DUXGL, T1A3, T1A4, P3_BUS, D6Y-K, D6Y-44, D6Y-P, T1, T2, P1-P3, P2-P3, UFLS1, T1-P, T2-P | 1-00296240 Rev. #23 | 9 Hour(s) | No Impact | #N/A
2026-09-28 07:00 | 2026-10-03 16:00 | 5 | LEASIDE TS | T20A1, SS1, T20, T20-HL3, T20Z | 1-00305848 Rev. #45 | 4 Hour(s) | No Impact | #N/A
2026-09-28 08:00 | 2026-10-09 16:00 | 11 | MARINE JCT, OTONABEE TS, CHATS FALLS TS, CLARINGTON TS | 128T2-T22C, 296-T22C, T22C.CHXMJ, T22C.MJXCL, T22C.MJXOT, 2-T22C | 1-00320737 Rev. #2 | 4 Hour(s) | No Impact | #N/A
2026-10-05 07:00 | 2026-10-10 16:00 | 5 | LEASIDE TS | Q2A2, T19A2, T19, T19-HL2, T19B1 | 1-00305847 Rev. #41 | 4 Hour(s) | No Impact | #N/A
2026-10-05 08:00 | 2026-10-16 16:00 | 11 | APPLEWOOD JCT, COOKSVILLE TS, MANBY WEST TS, MANBY EAST TS | K23C.APXCO, K23C.APXMA, 38-K23C, 46-K23C | 1-00314227 Rev. #5 | 4 Hour(s) | No Impact | #N/A
2026-10-09 08:00 | 2026-10-23 16:00 | 14 | PARKWAY TS, CHERRYWOOD TS | 52-C36P, 81-C36P | 1-00292312 Rev. #6 | 12 Hour(s) | No Impact | #N/A
2026-10-13 07:00 | 2026-10-27 16:00 | 14 | RUNNYMEDE TS, WILTSHIRE TS, MANBY EAST TS | K12W.RUXMA, K12W.RUXWI, H2K11W, H2K12W, H1H2, H2H3, H2L18W, H2L13W, H2L14W, 38-K12W, H2_BUS, T2Q, 11T2-K12W, T2, T5E, 11T5-K12W, T5 | 1-00308748 Rev. #9 | 6 Hour(s) | No Impact | #N/A
2026-10-19 08:00 | 2026-10-30 16:00 | 11 | RICHVIEW TS | H1H2, H2L20, H2L18, H2L22, H2L72, H2L76, 88-R13K, H2_BUS, SC21H-H2, T7-H2 | 1-00295740 Rev. #4 | 4 Hour(s) | No Impact | #N/A
2026-11-01 08:00 | 2026-12-11 16:00 | 40 | BATHURST JCT, FAIRCHILD TS, BATHURST TS, RICHVIEW TS, CHERRYWOOD TS | C18R.BAXBA, C18R.BAXFA, C18R.BAXRI, C18R.FAXCH, 81-C18R, 88-C18R, T1-C18R, T2-C18R, T3-C18R, T4-C18R | 1-00295785 Rev. #8 | 12 Hour(s) | No Impact | #N/A
2026-11-03 08:00 | 2026-11-12 16:00 | 9 | CHERRYWOOD TS | K1K2, KL18, K1L2, KL35, KL8, K1_BUS, SS1 | 1-00296246 Rev. #4 | 4 Hour(s) | No Impact | #N/A
2026-11-06 17:00 | 2027-04-08 18:00 | 153 | STRACHAN TS | T14, T14A11, T14A12, T14A15, T14A16, T14-TEMP1, T14-TEMP2 | 1-00314530 Rev. #6 | Non-recallable | No Impact | #N/A
2026-11-16 07:30 | 2026-11-30 16:00 | 14 | MANBY WEST TS | T2, T2-H1, T2-K3 | 1-00295971 Rev. #10 | 4 Hour(s) | No Impact | #N/A
2026-12-04 07:00 | 2026-12-11 16:00 | 7 | LEASIDE TS, SCARBORO TS, BERMONDSEY TS, SCARBORO JCT, CHERRYWOOD TS, WARDEN TS | C14L.BEXLE, C14L.BEXSC, C14L.SCXCH, C14L.SCXSC, C14L.SCXWA, D14L3, D14L1, HL14HL16, 34-C14L, 81-C14L, D14_BUS, T14, T14-CA, T14-HL14, T2-C14L, T21-C14L, T3-C14L, T4-C14L, SS14-X, T14R-SS14 | 1-00316991 Rev. #6 | 6 Hour(s) | No Impact | #N/A
2027-01-11 07:15 | 2027-03-12 16:00 | 60 | BRONTE TS, BURLINGTON TS, PALERMO JCT | B8.BRXBR, B8.BRXBU, 39-B8, T2-B8, T2-B7, T4, 13T4-B8 | 1-00298822 Rev. #10 | 6 Hour(s) | No Impact | #N/A
2027-01-11 08:00 | 2027-01-29 16:00 | 18 | CHERRYWOOD TS | KL15, L15L31, 81-C15L | 1-00318764 Rev. #3 | 24 Hour(s) | No Impact | #N/A
2027-01-24 08:00 | 2027-02-18 16:00 | 25 | PARKWAY TS, CHERRYWOOD TS | 52-C35P, 81-C35P | 1-00318866 Rev. #1 | 12 Hour(s) | No Impact | #N/A
2027-02-21 07:00 | 2027-03-05 16:00 | 12 | CHERRYWOOD TS, MALVERN TS, AGINCOURT TS, FINCH TS, AGINCOURT JCT, FINCH JCT, RICHVIEW TS | C4R.AGXAG, C4R.AGXMA, C4R.FIXAG, C4R.FIXFI, C4R.FIXRI, C4R.MAXCH, 63T5-C4R, 81-C4R, 88-C4R, T3-C4R, T4-C4R | 1-00292284 Rev. #13 | 4 Hour(s) | No Impact | #N/A
2027-03-08 07:00 | 2027-03-26 16:00 | 18 | RICHVIEW TS, MALVERN TS, CHERRYWOOD TS, LESLIE TS, AGINCOURT JCT | C5R.AGXMA, C5R.LEXAG, C5R.LEXRI, C5R.MAXCH, 81-C5R, 88-C5R, T2-C5R, T3-C5R, T4-C5R | 1-00292209 Rev. #15 | 4 Hour(s) | No Impact | #N/A
2027-03-08 08:00 | 2027-03-19 16:00 | 11 | PICKERING B SS, CHERRYWOOD TS | P30C.CHXPI, L30Z, T6L30, 30-P30C, 81-P30C | 1-00319028 Rev. #1 | 16 Hour(s) | No Impact | #N/A
2027-03-08 08:00 | 2027-03-19 16:00 | 11 | PICKERING B SS, CHERRYWOOD TS | P31C.CHXPI, L31N, T8L31, 30-P31C, 81-P31C | 1-00318959 Rev. #1 | 16 Hour(s) | No Impact | #N/A
2027-03-14 08:00 | 2027-03-28 08:00 | 14 | GOREWAY PH JCT, GOREWAY TS, CLAIREVILLE TS, GOREWAY JCT, WOODBRIDGE JCT, KLEINBURG TS, VAUGHAN 3 JCT, WOODBRIDGE TS | V43.CLXGJ, V43.CLXWJ, V43.GJXGO, V43.GOXGO, V43.KLXV3, V43.V3XWJ, V43.WJXWO, 136T2-V43, 136T4-V43, 136T6-V43, 45T2-V43, 51-V43, D6T3-V43 | 1-00308101 Rev. #2 | 8 Hour(s) | No Impact | #N/A
2027-03-22 08:00 | 2027-04-02 16:00 | 11 | CHERRYWOOD TS, PICKERING B SS | P32C.CHXPI, L32P, T7L32, 30-P32C, 81-P32C | 1-00319103 Rev. #2 | 16 Hour(s) | No Impact | #N/A
2027-03-29 07:00 | 2027-04-09 16:00 | 11 | CHERRYWOOD TS, MALVERN TS, AGINCOURT TS, FINCH TS, AGINCOURT JCT, FINCH JCT, RICHVIEW TS | C4R.AGXAG, C4R.AGXMA, C4R.FIXAG, C4R.FIXFI, C4R.FIXRI, C4R.MAXCH, 63T5-C4R, 81-C4R, 88-C4R, T3-C4R, T4-C4R | 1-00292210 Rev. #18 | 4 Hour(s) | No Impact | #N/A
2027-08-23 08:00 | 2027-09-10 16:00 | 18 | MANBY EAST TS | DL11, L11L12, 38-K11W | 1-00319620 Rev. #2 | Non-recallable | No Impact | #N/A
2027-10-16 06:30 | 2028-05-01 11:30 | 198 | CLARINGTON TS | SC21K1-K1, SC21 | 1-00294515 Rev. #5 | 200 Day(s) | No Impact | #N/A
2027-06-22 07:00 | 2027-06-29 17:00 | 7 | CHERRYWOOD TS, BOWMANVILLE SS | B542C.CHXBO, EL542, L20L42, 81-B542C, R56-B542C | 1-00319585 Rev. #1 | 4 Hour(s) | No Impact | #N/A
Back to main menu

## Table 4.13
Back to main menu
Table 4.13: West Zone Transmission Outages
Planned Start | Planned End | Duration (Days) | Station | Equipment Name | Outage ID | Max Recall | Major Transmission Interface Impacted | Reduction in Limit (MW)
2027-03-02 06:45 | 2027-03-09 16:00 | 7 | KEITH TS | AL20, AL5, T11, T23, T11-A, T23-A, AL25 | 1-00310054 Rev. #2 | 6 Hour(s) | No Impact | #N/A
2026-09-06 08:45 | 2026-09-25 15:00 | 19 | CHATHAM SS | DL28, DL31, DL44, D_BUS, SC22D-D, SC23D-D, DL42, DL64, KL43, KL65, DL88, K1-TEMP1, K2-TEMP1 | 1-00285801 Rev. #18 | 6 Hour(s) | No Impact | #N/A
2026-11-29 09:00 | 2026-12-18 09:30 | 19 | CHATHAM SS | DL28, DL31, DL44, D_BUS, SC22D-D, SC23D-D, DL42, DL64, DL88 | 1-00295731 Rev. #4 | 6 Hour(s) | No Impact | #N/A
2026-09-13 06:00 | 2026-10-16 16:00 | 33 | NANTICOKE TS, LONGWOOD TS | N582L.LOXNA, AWT13, DL582, HT8L582, L582WT13, 59-N582L, HT13_BUS, HT8_BUS, T13-WT13, W52-N582L | 1-00293595 Rev. #12 | 16 Hour(s) | No Impact | #N/A
2026-09-13 08:00 | 2026-09-18 16:00 | 5 | LONGWOOD TS, NANTICOKE TS | N582L.LOXNA, HL582, KL582, 59-N582L, W52-N582L | 1-00295560 Rev. #18 | 4 Hour(s) | No Impact | #N/A
2026-09-20 15:15 | 2027-03-05 08:30 | 166 | BUCHANAN TS, SALFORD JCT | 19-M31W, M31W-TEMP1 | 1-00297259 Rev. #18 | 90 Day(s) | No Impact | #N/A
2027-02-07 08:00 | 2027-03-25 16:00 | 46 | NANTICOKE TS, LONGWOOD TS | N582L.LOXNA, AWT13, DL582, HT8L582, L582WT13, 59-N582L, HT13_BUS, T13-WT13, W52-N582L | 1-00308115 Rev. #5 | Non-recallable | No Impact | #N/A
2026-09-20 15:15 | 2027-03-05 08:30 | 166 | BUCHANAN TS, SALFORD JCT | 19-M31W, M31W-TEMP1 | 1-00297259 Rev. #18 | 90 Day(s) | No Impact | #N/A
2026-09-13 06:00 | 2026-10-16 16:00 | 33 | NANTICOKE TS, LONGWOOD TS | N582L.LOXNA, AWT13, DL582, HT8L582, L582WT13, 59-N582L, HT13_BUS, HT8_BUS, T13-WT13, W52-N582L | 1-00293595 Rev. #12 | 16 Hour(s) | No Impact | #N/A
2026-09-13 08:00 | 2026-09-18 16:00 | 5 | LONGWOOD TS, NANTICOKE TS | N582L.LOXNA, HL582, KL582, 59-N582L, W52-N582L | 1-00295560 Rev. #18 | 4 Hour(s) | No Impact | #N/A
2027-02-07 08:00 | 2027-03-25 16:00 | 46 | NANTICOKE TS, LONGWOOD TS | N582L.LOXNA, AWT13, DL582, HT8L582, L582WT13, 59-N582L, HT13_BUS, T13-WT13, W52-N582L | 1-00308115 Rev. #5 | Non-recallable | No Impact | #N/A
2027-03-02 06:45 | 2027-03-09 16:00 | 7 | KEITH TS | AL20, AL5, T11, T23, T11-A, T23-A, AL25 | 1-00310054 Rev. #2 | 6 Hour(s) | No Impact | #N/A
2025-09-29 12:00 | 2026-12-31 16:00 | 458 | LAKESHORE TS | 530-H76 | 1-00295205 Rev. #20 | 4 Hour(s) | No Impact | #N/A
2025-12-04 07:00 | 2026-08-31 17:30 | 270 | KENT TS, WALLACEBURG TS, BORALEX TILBURY JCT | N5K.KEXWA, L2L5, 5-N5K, 647K2Z-54 | 1-00266753 Rev. #35 | Non-recallable | No Impact | #N/A
2025-12-18 17:30 | 2026-12-31 17:30 | 378 | SCOTT TS, KIMBALL JCT, WALLACEBURG TS | N5K.KIXSC, N5K.WAXKI, 1N5K-A1, 40-N5K | 1-00267335 Rev. #27 | Non-recallable | No Impact | #N/A
2026-05-15 11:30 | 2026-12-31 08:00 | 230 | ST. ANDREWS TS | TMP1 | 1-00314809 Rev. #8 | Non-recallable | No Impact | #N/A
2026-06-18 15:00 | 2026-12-31 23:59 | 196 | ST. ANDREWS TS | TMP2 | 1-00317299 Rev. #8 | Non-recallable | No Impact | #N/A
2026-07-01 08:00 | 2026-10-01 08:00 | 92 | TILBURY JCT, BELLE RIVER JCT | 53K6Z-K2Z, 2316K2Z-53 | 1-00314272 Rev. #9 | 6 Hour(s) | No Impact | #N/A
2026-08-16 08:00 | 2026-09-05 15:45 | 20 | CHATHAM SS | KL29, KL47, SC21K, K_BUS, SC21, SC21K-K, SS1-K, KL43, KL65, KL87, KL88 | 1-00295732 Rev. #44 | 6 Hour(s) | No Impact | #N/A
2026-09-14 08:00 | 2026-10-02 16:00 | 18 | LANXESS INC JCT | 103N7S-TEMP1 | 1-00291878 Rev. #10 | Non-recallable | No Impact | #N/A
2026-09-28 07:00 | 2026-10-13 07:00 | 15 | WINDSOR LAUZON TS | T12Y, T12Z, T12 | 1-00313932 Rev. #3 | 24 Hour(s) | No Impact | #N/A
2026-10-03 16:00 | 2026-10-09 14:00 | 6 | KEITH TS, BRIGHTON BEACH CGS | J1B.KEXBR, 23-J1B | 1-00321365 Rev. #1 | Non-recallable | No Impact | #N/A
2026-10-27 16:00 | 2026-12-04 08:00 | 38 | BUCHANAN TS | L2K, K1BUS-TEMP1, L2BUS-TEMP1 | 1-00313986 Rev. #2 | Non-recallable | No Impact | #N/A
2026-11-01 08:00 | 2026-11-06 16:00 | 5 | CLARKE TS, TALBOT TS, BUCHANAN TS, OXFORD STREET JCT | W36.OXXBU, W36.OXXCL, W36.OXXTA, 19-W36, 26-W36, T3-W36 | 1-00295612 Rev. #4 | 4 Hour(s) | No Impact | #N/A
2026-11-01 08:45 | 2026-11-20 09:30 | 19 | CHATHAM SS, LAKESHORE TS | KL29, KL47, SC21K, K_BUS, SC21, SC21K-K, SS1-K, 530-C88H, KL43, KL65, C88H.CHXLA, DL88, KL87, KL88, 86-C88H | 1-00295669 Rev. #6 | 6 Hour(s) | No Impact | #N/A
2026-11-15 08:00 | 2026-11-20 16:00 | 5 | ESSEX TS, CHRYSLER WINDSOR ASS. PLANT CTS | E8F.ESXCH, 15-E8F | 1-00295751 Rev. #4 | 4 Hour(s) | No Impact | #N/A
2026-11-20 09:00 | 2026-11-29 09:00 | 9 | CHATHAM SS | K2L34 | 1-00321554 Rev. #1 | Non-recallable | No Impact | #N/A
2026-11-22 08:00 | 2026-11-27 16:00 | 5 | ESSEX TS, CHRYSLER WINDSOR ASS. PLANT CTS | E9F.ESXCH, 15-E9F | 1-00295752 Rev. #4 | 4 Hour(s) | No Impact | #N/A
2027-09-08 08:00 | 2027-09-13 16:00 | 5 | SCOTT TS, LANXESS INC JCT, SARNIA SCOTT JCT | N7S.SAXBA, N7S.SAXSC, 40-N7S | 1-00318106 Rev. #1 | Non-recallable | No Impact | #N/A
2027-09-15 08:00 | 2027-09-22 16:00 | 7 | SCOTT TS, LANXESS INC JCT, SARNIA SCOTT JCT | N6S.SAXBA, N6S.SAXSC, 40-N6S | 1-00318105 Rev. #1 | Non-recallable | No Impact | #N/A
2026-09-17 07:00 | 2026-10-08 17:00 | 21 | WINDSOR LAUZON TS | A_BUS, T1-A, T5-A, T8-A, 56-H54Z | 1-00293516 Rev. #19 | 6 Hour(s) | No Impact | #N/A
2026-09-20 08:00 | 2026-10-02 16:00 | 12 | WINDSOR LAUZON TS | SS1, T1, T1-A, T1-P | 1-00300160 Rev. #6 | 6 Hour(s) | No Impact | #N/A
2026-10-25 12:30 | 2026-11-13 16:00 | 19 | ESSEX TS, CRAWFORD JCT | 15-J3E, 2329J3E-TEMP1 | 1-00321525 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2026-10-25 12:30 | 2026-12-18 12:30 | 54 | ESSEX TS, CRAWFORD JCT | L3L4, L3L9, 15-J3E, L3_BUS, 2329J3E-TEMP1, L9BUS-TEMP1 | 1-00306028 Rev. #9 | 10 Hour(s) | No Impact | #N/A
2027-03-02 06:45 | 2027-03-09 16:00 | 7 | KEITH TS | AL20, AL5, T11, T23, T11-A, T23-A, AL25 | 1-00310054 Rev. #2 | 6 Hour(s) | No Impact | #N/A
Back to main menu

## Table 4.14
Back to main menu
Table 4.14: External Interties Transmission Outages
Planned Start | Planned End | Duration (Days) | Station | Equipment Name | Outage ID | Max Recall | Major Transmission Interface Impacted | Reduction in Limit (MW)
2026-09-28 08:00 | 2026-10-09 16:00 | 11 | ST. LAWRENCE TS, MASSENA JCT | L33P.ROXLA, 49-L33P, PSR33-L33 | 1-00275118 Rev. #11 | 4 Hour(s) | No Impact | #N/A
2026-09-15 08:00 | 2026-11-17 16:00 | 63 | BECK 2 TS, NY NIAGARA 345 KV | PA27.NIXBE, 28R27-PA27, R27-S | 1-00308330 Rev. #11 | Non-recallable | No Impact | #N/A
2024-05-14 13:00 | 2026-12-31 16:00 | 961 | KENORA TS, WHITESHELL TS | K21W.WHXKE, 34-K21W | 1-00254393 Rev. #22 | 6 Hour(s) | EWTE EWTW | 25 25
2027-12-06 03:30 | 2027-12-17 16:00 | 12 | HAWTHORNE TS, MASSON GS, IPB MASSON JCT, ST. ISIDORE TS, ORLEANS JCT 2, ORLEANS TS, CUMBERLAND JCT, LONGUEUIL JCT, LONGUEUIL TS | D5A.CUXGA, D5A.CUXIS, D5A.CUXO2, D5A.HAXO2, D5A.IPXMA, D5A.LOXIS, D5A.LOXLO, D5A.O2XOR, A1A2, HT5L5, KL5, 325T2-D5A, 48-D5A, 62D5A-26, T3-D5A, T1-A1, 62D5A-625 | 1-00296584 Rev. #4 | 6 Hour(s) | FIO BEAU P33C | 250 690 0
2025-11-18 08:00 | 2026-12-31 16:00 | 408 | KENORA TS, WHITESHELL TS | K21W.WHXKE, 34-K21W | 1-00299527 Rev. #10 | 2 Hour(s) | EWTE EWTW | 25 25
2026-10-23 08:00 | 2026-11-22 16:00 | 30 | KENORA TS, WHITESHELL TS | K22W.WHXKE, 34-K22W | 1-00320445 Rev. #1 | 25 Day(s) | EWTE EWTW | 25 25
Back to main menu