## Menu
Reliability Outlook
2026-06-18
2026 Q2 Outlook
From July 2026 – December 2027
1.0 Demand Forecast: First 18 Months
Table 1.1 Firm: Historical and Forecast Energy Summary
Table 1.1 Planned: Historical and Forecast Energy Summary
Table 1.1.1 Firm: Monthly Peak and Energy Demand
Table 1.1.1 Planned: Monthly Peak and Energy Demand | NOTE(S):
Table 1.1.2 Firm: Weekly Coincident Peak Demand by Zone
Table 1.1.2 Planned: Weekly Coincident Peak Demand by Zone | 1. Demand Forecast, Supply Forecast, and Transmission Outlook Considerations
Table 1.1.3 Firm: Weekly Energy Demand by Zone | The demand models use actual demand, weather, and economic data through the end of March 2026. The latest business intelligence regarding large step loads was incorporated in mid‑May. Actual weather and demand data for April and May 2026, which were observed after demand modeling, are also included in the tables for informational purposes.
Table 1.1.3 Planned: Weekly Energy Demand by Zone
Table 1.2 Firm: Forecasted Seasonal Peaks
Table 1.2 Planned: Forecasted Seasonal Peaks | b) This Reliability Outlook includes planned generator outages over the 18‑month period, submitted by market participants to the IESO’s outage management system by late May 2026.
Table 1.3: Large Step Load Impacts, Firm and Planned Demand
Table 1.4 Firm: Weekly Energy and Peak Demand Forecast | c) This Reliability Outlook includes planned transmission outages that were submitted to the IESO’s outage management system by May 2026.
Table 1.4 Planned: Weekly Energy and Peak Demand Forecast
Table 1.4.1: Weekly Weather and Demand History
Table 1.4.2: Monthly Weather and Demand History | 2. Additional Table
Table 1.4.3: Monthly Consumption by Market Participant Type | A new table has been introduced for Q2 2026 titled “Reductions by Fuel Type: Expected Weather, Planned Scenario.” This table complements the existing Firm Scenario table. This table is now labeled Table 3.10. As a result, the tables previously numbered 3.10 and 3.11 in the prior quarter have been renumbered to 3.11 and 3.12, respectively.
Table 1.4.4: Economic Assumptions
Table 1.4.5: Estimate of Contracted Embedded Generation Capacity (MW)
2.0 Resource Supply Forecast: First 18 Months | 3. New Figure
Table 2.1: Existing Grid-Connected Resource Capacity | A new figure has been introduced for Q2 2026 titled "Figure 3.1: Reserve Above Requirement". This figure illustrates the Reserve Above Requirement over 18-months and is obtained by subtracting the Required Resources (equal to the peak demand plus Required Reserve) from the Available Resources.
Table 2.2: Committed Generation and Electricity Storage Resources Status over the 18-month Reliability Outlook Period
Table 2.3: Monthly Historical Hydroelectric Median Values for Expected Weather Conditions
Table 2.4: Monthly Wind Capacity Contribution Values
Table 2.5: Monthly Solar Capacity Contribution Values | 4. Table 4.2 - FETT Interface
Table 2.6: Monthly Off-Peak Wind Capacity Contribution Values | The FETT interface base limit has been updated for the period of the Darlington VBO.
Table 2.7: Summary of Available Resources under Expected Weather
3.0 Resource Adequacy Assessment: First 18 Months
Table 3.1 Firm: Summary of Zonal Energy for Firm Scenario, Expected Weather
Table 3.2 Planned: Summary of Zonal Energy for Planned Scenario, Expected Weather
Table 3.3 Firm: Ontario Energy Production by Fuel Type for the Firm Scenario, Expected Weather
Table 3.4 Planned: Ontario Energy Production by Fuel Type for the Planned Scenario, Expected Weather
Table 3.5: Assessment of Resource Adequacy: Expected Weather, Firm Scenario
Table 3.6: Assessment of Resource Adequacy: Expected Weather, Planned Scenario
Table 3.7: Zonal Bottled Generation: Expected Weather, Both Scenarios
Table 3.8: Energy Production Capability Forecast
Table 3.9: Reductions by Fuel Type: Expected Weather, Firm Scenario
Table 3.10: Reductions by Fuel Type: Expected Weather, Planned Scenario
Table 3.11: Firm Scenario - Expected Weather: Ontario Monthly Energy Production by Fuel Type
Table 3.12: Planned Scenario - Expected Weather: Ontario Monthly Energy Production by Fuel Type
Figure 3.1: Reserve Above Requirement
4.0 Transmission
Table 4.1: Transmission Projects
Table 4.2: Interface Limits with All Elements in Service
Table 4.3: Interconnection Flow Limits
Table 4.4: Bruce Zone Transmission Outages
Table 4.5: East Zone Transmission Outages
Table 4.6: Essa Zone Transmission Outages
Table 4.7: Niagara Zone Transmission Outages
Table 4.8: Northeast Zone Transmission Outages
Table 4.9: Northwest Zone Transmission Outages
Table 4.10: Ottawa Zone Transmission Outages
Table 4.11: Southwest Zone Transmission Outages
Table 4.12: Toronto Zone Transmission Outages
Table 4.13: West Zone Transmission Outages
Table 4.14: External Interties Transmission Outages

## Table 1.1 Firm
Back to main menu
Table 1.1 Firm: Historical and Forecast Energy Summary
Year | Normal Weather Energy (TWh) | % Growth in Energy
2006 | 152.349 | -1.858%
2007 | 151.6029 | -0.4897%
2008 | 148.9203 | -1.769%
2009 | 140.59 | -5.594%
2010 | 141.7415 | 0.819%
2011 | 141.0103 | -0.5158%
2012 | 140.7232 | -0.2036%
2013 | 140.4483 | -0.1954%
2014 | 139.4864 | -0.6848%
2015 | 136.3504 | -2.248%
2016 | 135.9259 | -0.3113%
2017 | 132.1965 | -2.744%
2018 | 135.5109 | 2.507%
2019 | 134.6666 | -0.6231%
2020 | 131.9143 | -2.044%
2021 | 133.7042 | 1.357%
2022 | 136.6504 | 2.204%
2023 | 138.0378 | 1.015%
2024 | 141.0947 | 2.215%
2025 | 145.3951 | 3.048%
2026 (Forecast) | 146.1887 | 0.5458%
2027 (Forecast) | 148.2404 | 1.403%
Back to main menu

## Table 1.1 Planned
Back to main menu
Table 1.1 Planned: Historical and Forecast Energy Summary
Year | Normal Weather Energy (TWh) | % Growth in Energy
2006 | 152.349 | -1.858%
2007 | 151.6029 | -0.4897%
2008 | 148.9203 | -1.769%
2009 | 140.59 | -5.594%
2010 | 141.7415 | 0.819%
2011 | 141.0103 | -0.5158%
2012 | 140.7232 | -0.2036%
2013 | 140.4483 | -0.1954%
2014 | 139.4864 | -0.6848%
2015 | 136.3504 | -2.248%
2016 | 135.9259 | -0.3113%
2017 | 132.1965 | -2.744%
2018 | 135.5109 | 2.507%
2019 | 134.6666 | -0.6231%
2020 | 131.9143 | -2.044%
2021 | 133.7042 | 1.357%
2022 | 136.6504 | 2.204%
2023 | 138.0378 | 1.015%
2024 | 141.0947 | 2.215%
2025 | 145.3951 | 3.048%
2026 (Forecast) | 146.2462 | 0.5854%
2027 (Forecast) | 149.6059 | 2.297%
Back to main menu

## Table 1.1.1 Firm
Back to main menu
Table 1.1.1 Firm: Monthly Peak and Energy Demand
Forecasted Peak and Energy Demand
| Peak Demand (MW) |  |  | Energy Demand (GWh)
Month | Current Forecast | Previous Forecast | Weather Corrected Actual | Current Forecast | Previous Forecast | Weather Corrected Actual
2012-01-01 | 22160.0997 | 22160.0997 | 22084.7322 | 13280.0235 | 13280.0235 | 12932.2873
2012-02-01 | 21813.8691 | 21813.8691 | 20756.8677 | 12202.5791 | 12202.5791 | 11380.2015
2012-03-01 | 20708.9072 | 20708.9072 | 20595.0545 | 12264.8125 | 12264.8125 | 11726.1779
2012-04-01 | 18745.092 | 18745.092 | 19830.1533 | 10866.5786 | 10866.5786 | 10883.4994
2012-05-01 | 19038.2309 | 19038.2309 | 19736.9901 | 10943.6824 | 10943.6824 | 10838.5019
2012-06-01 | 22569.1521 | 22569.1521 | 22832.4909 | 11398.2442 | 11398.2442 | 11511.081
2012-07-01 | 23298.1422 | 23298.1422 | 23630.2664 | 12319.3311 | 12319.3311 | 13057.6199
2012-08-01 | 22956.5741 | 22956.5741 | 22726.501 | 12419.0386 | 12419.0386 | 12373.2613
2012-09-01 | 20506.0631 | 20506.0631 | 20370.1157 | 10811.3017 | 10811.3017 | 10900.4102
2012-10-01 | 18345.9037 | 18345.9037 | 18684.153 | 11199.8353 | 11199.8353 | 11149.8822
2012-11-01 | 20571.5606 | 20571.5606 | 20258.2258 | 11629.6439 | 11629.6439 | 11663.449
2012-12-01 | 21693.287 | 21693.287 | 20910.8981 | 12612.0073 | 12612.0073 | 12306.8289
2012 | 23298.1422 | 23298.1422 | 23630.2664 | 141947.0782 | 141947.0782 | 140723.2004
2013-01-31 | 22013.997 | 22013.997 | 22610 | 13314.3055 | 13314.3055 | 13061.0693
2013-02-28 | 21773.6201 | 21773.6201 | 21333.0082 | 11819.7381 | 11819.7381 | 11668.8474
2013-03-31 | 20634.9497 | 20634.9497 | 20784.4526 | 12283.0437 | 12283.0437 | 11869.9986
2013-04-30 | 18492.3312 | 18492.3312 | 19284.8182 | 11018.1303 | 11018.1303 | 11090.2932
2013-05-31 | 19100.9692 | 19100.9692 | 18341.9804 | 10932.3105 | 10932.3105 | 10533.5712
2013-06-30 | 22499.2459 | 22499.2459 | 22719.4401 | 11406.4319 | 11406.4319 | 11283.4325
2013-07-31 | 23212.9348 | 23212.9348 | 24352.1456 | 12479.5529 | 12479.5529 | 12736.3503
2013-08-31 | 22359.7987 | 22359.7987 | 23255.371 | 12227.7513 | 12227.7513 | 12084.9413
2013-09-30 | 20513.3592 | 20513.3592 | 20422.3176 | 11015.3041 | 11015.3041 | 10767.0057
2013-10-31 | 18388.3002 | 18388.3002 | 18981.007 | 11279.1846 | 11279.1846 | 11114.0467
2013-11-30 | 20326.4941 | 20326.4941 | 20034.8189 | 11686.9287 | 11686.9287 | 11709.7788
2013-12-31 | 21395.0558 | 21395.0558 | 21184.5386 | 12699.9803 | 12699.9803 | 12528.9266
2013 | 23212.9348 | 23212.9348 | 24352.1456 | 142162.6617 | 142162.6617 | 140448.2614
2014-01-31 | 22319.8106 | 22319.8106 | 22043.8439 | 13356.427 | 13356.427 | 13409.7767
2014-02-28 | 20964.0592 | 20964.0592 | 21218.2216 | 11748.3799 | 11748.3799 | 11812.9441
2014-03-31 | 19906 | 19906 | 20728.4579 | 12054.5719 | 12054.5719 | 12242.1563
2014-04-30 | 17649 | 17649 | 19249.9632 | 10731.1367 | 10731.1367 | 11038.5265
2014-05-31 | 18964 | 18964 | 18750.4605 | 10790.2174 | 10790.2174 | 10546.4252
2014-06-30 | 22469.55 | 22469.55 | 20705.1957 | 11346.2756 | 11346.2756 | 11140.5499
2014-07-31 | 22948.69 | 22948.69 | 22294.8035 | 12360.0815 | 12360.0815 | 12324.9268
2014-08-31 | 21403.44 | 21403.44 | 21644.3547 | 11992.5131 | 11992.5131 | 11819.2371
2014-09-30 | 19023.2704 | 19023.2704 | 19449.0766 | 10579.5258 | 10579.5258 | 10671.4853
2014-10-31 | 18638.7361 | 18638.7361 | 18447.2196 | 11126.7565 | 11126.7565 | 10814.1957
2014-11-30 | 20302.34 | 20302.34 | 19923.2587 | 11497.4835 | 11497.4835 | 11410.1121
2014-12-31 | 21237.74 | 21237.74 | 21582.6701 | 12769.4956 | 12769.4956 | 12256.0958
2014 | 22948.69 | 22948.69 | 22294.8035 | 140352.8643 | 140352.8643 | 139486.4317
2015-01-31 | 22293.59 | 22293.59 | 21503.4489 | 13068.9431 | 13068.9431 | 12937.1182
2015-02-28 | 21016.81 | 21016.81 | 19709.6284 | 11528.5197 | 11528.5197 | 11740.7311
2015-03-31 | 19840.93 | 19840.93 | 20109.8817 | 11856.8161 | 11856.8161 | 11748.227
2015-04-30 | 18121.2 | 18121.2 | 19362.8308 | 10542.0267 | 10542.0267 | 10624.618
2015-05-31 | 19370.33 | 19370.33 | 17881.7583 | 10635.9243 | 10635.9243 | 10231.5964
2015-06-30 | 22276.64 | 22276.64 | 20554.6293 | 11410.2692 | 11410.2692 | 10908.724
2015-07-31 | 22888.49 | 22888.49 | 22638.5319 | 12174.2184 | 12174.2184 | 12273.6405
2015-08-31 | 21463.69 | 21463.69 | 22383 | 11821.2763 | 11821.2763 | 11782.7212
2015-09-30 | 18485 | 18485 | 19299.6325 | 10512.648 | 10512.648 | 10718.9879
2015-10-31 | 18339 | 18339 | 18444.3181 | 11150.1256 | 11150.1256 | 10731.7474
2015-11-30 | 20306 | 20306 | 19631.9089 | 11595.0899 | 11595.0899 | 10867.5486
2015-12-31 | 21160.04 | 21160.04 | 20418.0801 | 12611.2501 | 12611.2501 | 11784.7123
2015 | 22888.49 | 22888.49 | 22638.5319 | 138907.1073 | 138907.1073 | 136350.3725
2016-01-31 | 22360.24 | 22360.24 | 21249.7402 | 12982.1466 | 12982.1466 | 12523.599
2016-02-28 | 20985.25 | 20985.25 | 20194.6163 | 11806.8997 | 11806.8997 | 11502.97
2016-03-31 | 20075.21 | 20075.21 | 20324.618 | 11758.7447 | 11758.7447 | 11445.7227
2016-04-30 | 17405.08 | 17405.08 | 18912.1728 | 10309.6515 | 10309.6515 | 10578.9099
2016-05-31 | 19235.65 | 19235.65 | 19707.6447 | 10530.0143 | 10530.0143 | 10115.8584
2016-06-30 | 22315.7305 | 22315.7305 | 21568.912 | 11378.6081 | 11378.6081 | 11141.3797
2016-07-31 | 22599.9414 | 22599.9414 | 22288.7672 | 11896.1402 | 11896.1402 | 12345.0421
2016-08-31 | 21440.3166 | 21440.3166 | 22375.997 | 11771.834 | 11771.834 | 12295.9028
2016-09-30 | 18289 | 18289 | 19712.7154 | 10401.8861 | 10401.8861 | 10659.2295
2016-10-31 | 18079 | 18079 | 18394.9922 | 10947.5325 | 10947.5325 | 10453.1463
2016-11-30 | 20296 | 20296 | 19544.7667 | 11524.026 | 11524.026 | 10913.6011
2016-12-31 | 20888 | 20888 | 20286.7849 | 12430.7427 | 12430.7427 | 11950.5536
2016 | 22599.9414 | 22599.9414 | 22375.997 | 137738.2263 | 137738.2263 | 135925.9151
2017-01-31 | 21913.73 | 21913.73 | 20965.9674 | 12818.8508 | 12818.8508 | 12369.7298
2017-02-28 | 20966.2287 | 20966.2287 | 20379.4501 | 11294.713 | 11294.713 | 10787.4931
2017-03-31 | 20137.3 | 20137.3 | 18692.3503 | 11824.0632 | 11824.0632 | 11413.3465
2017-04-30 | 17969.79 | 17969.79 | 18482.7844 | 10366.7129 | 10366.7129 | 10105.7565
2017-05-31 | 19193.19 | 19193.19 | 18260.3078 | 10576.9018 | 10576.9018 | 10012.8427
2017-06-30 | 22454.87 | 22454.87 | 21144.8187 | 11159.3312 | 11159.3312 | 10682.999
2017-07-31 | 22492.73 | 22492.73 | 22152.8524 | 11984.7355 | 11984.7355 | 11851.6211
2017-08-31 | 22376.43 | 22376.43 | 21323.3584 | 12105.5471 | 12105.5471 | 11513.597
2017-09-30 | 19490.21 | 19490.21 | 17821.4732 | 10494.2948 | 10494.2948 | 10155.927
2017-10-31 | 18030.62 | 18030.62 | 17407.7858 | 10942.7953 | 10942.7953 | 10260.3837
2017-11-30 | 20230.97 | 20230.97 | 19195.4397 | 11371.7451 | 11371.7451 | 10946.7668
2017-12-31 | 20901.44 | 20901.44 | 21439.6493 | 12303.6865 | 12303.6865 | 12096.0133
2017 | 22492.73 | 22492.73 | 22152.8524 | 137243.3774 | 137243.3774 | 132196.4765
2018-01-31 | 21618.93 | 21618.93 | 20177.5339 | 12685.9178 | 12685.9178 | 12679.8037
2018-02-28 | 20242.21 | 20242.21 | 20042.2165 | 11074.1738 | 11074.1738 | 11081.1365
2018-03-31 | 19551.97 | 19551.97 | 19330.8728 | 11423.555 | 11423.555 | 11267.3415
2018-04-30 | 17669.81 | 17669.81 | 18107.9593 | 10157.8502 | 10157.8502 | 10586.2978
2018-05-31 | 18817.47 | 18817.47 | 19262.1307 | 10289.6502 | 10289.6502 | 10081.137
2018-06-30 | 21890.0001 | 21890.0001 | 20626.9619 | 10863.4062 | 10863.4062 | 10980.4534
2018-07-31 | 22076.0001 | 22076.0001 | 22409.0792 | 11652.7714 | 11652.7714 | 12483.776
2018-08-31 | 21946.0001 | 21946.0001 | 21385.6483 | 11685.5744 | 11685.5744 | 12040.5393
2018-09-30 | 19019 | 19019 | 19505.5646 | 10189.9802 | 10189.9802 | 10579.1906
2018-10-31 | 17788 | 17788 | 17751.4152 | 10750.0648 | 10750.0648 | 10526.7735
2018-11-30 | 19828 | 19828 | 19266.3918 | 11170.7506 | 11170.7506 | 11184.9393
2018-12-31 | 20503 | 20503 | 20375.1864 | 12007.3958 | 12007.3958 | 12019.553
2018 | 22076.0001 | 22076.0001 | 22409.0792 | 133951.0905 | 133951.0905 | 135510.9416
2019-01-31 | 21506 | 21506 | 21058.2817 | 12973.2132 | 12973.2132 | 12688.8389
2019-02-28 | 20008 | 20008 | 20420.3692 | 11162.2057 | 11162.2057 | 11212.4836
2019-03-31 | 19457 | 19457 | 19573.6921 | 11522.1982 | 11522.1982 | 11458.0531
2019-04-30 | 17548 | 17548 | 18796.3299 | 10252.9314 | 10252.9314 | 10432.2785
2019-05-31 | 18663 | 18663 | 17977.0308 | 10412.0446 | 10412.0446 | 10218.7126
2019-06-30 | 21623 | 21623 | 21239.1838 | 10939.3571 | 10939.3571 | 10608.5215
2019-07-31 | 22061 | 22061 | 21120.5208 | 11763.9974 | 11763.9974 | 12446.1887
2019-08-31 | 21200 | 21200 | 22490.4547 | 11598.2109 | 11598.2109 | 11798.5843
2019-09-30 | 19469.84 | 19469.84 | 18958.9757 | 10564.4926 | 10564.4926 | 10167.6302
2019-10-31 | 17559 | 17559 | 18814.592 | 10788.0047 | 10788.0047 | 10446.8836
2019-11-30 | 19597 | 19597 | 19001.8635 | 11194.6524 | 11194.6524 | 11094.2081
2019-12-31 | 20307 | 20307 | 20974 | 12086.6766 | 12086.6766 | 12094.1802
2019 | 22061 | 22061 | 22490.4547 | 135257.9849 | 135257.9849 | 134666.5633
2020-01-31 | 21185.0004 | 21185.0004 | 21137.8728 | 12859.4588 | 12859.4588 | 12460.9405
2020-02-28 | 19917.0004 | 19917.0004 | 19776.0281 | 11586.6754 | 11586.6754 | 11253.1814
2020-03-31 | 19377.0004 | 19377.0004 | 19680.948 | 11522.322 | 11522.322 | 11058.3098
2020-04-30 | 17302.0004 | 17302.0004 | 16515.7848 | 10229.1483 | 10229.1483 | 9383.3554
2020-05-31 | 17426 | 17426 | 18761.2836 | 9434.378 | 9434.378 | 9306.4436
2020-06-30 | 20034 | 20034 | 20741.8718 | 10274.389 | 10274.389 | 10596.6512
2020-07-31 | 22364.4404 | 22364.4404 | 24057.7367 | 11731.6936 | 11731.6936 | 12529.7172
2020-08-31 | 21631.4406 | 21631.4406 | 25317.7535 | 11441.5908 | 11441.5908 | 12338.1938
2020-09-30 | 20312.4408 | 20312.4408 | 19254.2062 | 10356.1124 | 10356.1124 | 10011.2355
2020-10-31 | 17039.9727 | 17039.9727 | 17587.3164 | 10040.7873 | 10040.7873 | 10349.5982
2020-11-30 | 18891.9134 | 18891.9134 | 19416.1975 | 10531.6058 | 10531.6058 | 10693.8532
2020-12-31 | 19805.1651 | 19805.1651 | 20975.3455 | 11815.0887 | 11815.0887 | 11932.8039
2020 | 22364.4404 | 22364.4404 | 25317.7535 | 131823.25 | 131823.25 | 131914.2838
2021-01-31 | 21176.0005 | 21176.0005 | 20951.6431 | 12539.1611 | 12539.1611 | 12307.6071
2021-02-28 | 20760.0005 | 20760.0005 | 20175.4672 | 11073.4765 | 11073.4765 | 11144.3783
2021-03-31 | 19384.0005 | 19384.0005 | 19868.2566 | 11497.7125 | 11497.7125 | 11249.5616
2021-04-30 | 17070.0009 | 17070.0009 | 17618.7846 | 10244.8035 | 10244.8035 | 10097.7166
2021-05-31 | 18055.3342 | 18055.3342 | 18021.5172 | 10152.0681 | 10152.0681 | 9986.9371
2021-06-30 | 22162.0009 | 22162.0009 | 21528.4908 | 10747.5852 | 10747.5852 | 10840.8856
2021-07-31 | 22413.0005 | 22413.0005 | 22251.4821 | 11806.5074 | 11806.5074 | 11970.9832
2021-08-31 | 22235.0005 | 22235.0005 | 21854.4728 | 11706.2663 | 11706.2663 | 12072.0791
2021-09-30 | 21212.0005 | 21212.0005 | 18979.8917 | 10472.6839 | 10472.6839 | 10401.3058
2021-10-31 | 17270.7147 | 17270.7147 | 17606.8602 | 10365.0376 | 10365.0376 | 10429.4829
2021-11-30 | 19227.38 | 19227.38 | 19684.7166 | 10886.7659 | 10886.7659 | 11017.3258
2021-12-31 | 20088.8968 | 20088.8968 | 21331.5579 | 11984.4925 | 11984.4925 | 12185.9418
2021 | 22413.0005 | 22413.0005 | 22251.4821 | 133476.5604 | 133476.5604 | 133704.2048
2022-01-31 | 20983.6671 | 20983.6671 | 21334.1018 | 12536.9576 | 12536.9576 | 12928.5532
2022-02-28 | 20446.0004 | 20446.0004 | 20782.3287 | 11208.712 | 11208.712 | 11400.5165
2022-03-31 | 19401.3338 | 19401.3338 | 19941.2707 | 11617.5125 | 11617.5125 | 11793.6956
2022-04-30 | 17251.0005 | 17251.0005 | 17752.3935 | 10239.112 | 10239.112 | 10311.1592
2022-05-31 | 18269.0005 | 18269.0005 | 20136.0014 | 10372.2878 | 10372.2878 | 10137.6947
2022-06-30 | 22161.0005 | 22161.0005 | 22101.7092 | 10967.9836 | 10967.9836 | 11002.2267
2022-07-31 | 22542.0005 | 22542.0005 | 22484.9516 | 11893.9057 | 11893.9057 | 12411.016
2022-08-31 | 22430.0005 | 22430.0005 | 23477.9346 | 12028.3221 | 12028.3221 | 11998.9314
2022-09-30 | 21489.0005 | 21489.0005 | 20446.2276 | 10551.0851 | 10551.0851 | 10678.4907
2022-10-31 | 17559.0005 | 17559.0005 | 17724.6236 | 10603.0084 | 10603.0084 | 10447.0825
2022-11-30 | 19812.0005 | 19812.0005 | 19389.6575 | 11151.0711 | 11151.0711 | 11128.3255
2022-12-31 | 20241.0005 | 20241.0005 | 20584.5241 | 12191.9609 | 12191.9609 | 12412.7534
2022 | 22542.0005 | 22542.0005 | 23477.9346 | 135361.9188 | 135361.9188 | 136650.4453
2023-01-31 | 21170.3338 | 21170.3338 | 21435.1399 | 12663.6554 | 12663.6554 | 13052.768
2023-02-28 | 20892.3338 | 20892.3338 | 20433.0112 | 11375.0622 | 11375.0622 | 11325.8235
2023-03-31 | 19701.0485 | 19701.0485 | 19000.8853 | 11846.6528 | 11846.6528 | 11814.7494
2023-04-30 | 17785.9996 | 17785.9996 | 19103.3719 | 10349.2653 | 10349.2653 | 10374.8437
2023-05-31 | 18869.9996 | 18869.9996 | 18001.5877 | 10418.8057 | 10418.8057 | 10473.6584
2023-06-30 | 21884.9996 | 21884.9996 | 22417.4764 | 10652.496 | 10652.496 | 11230.6805
2023-07-31 | 22445.9996 | 22445.9996 | 23368.3724 | 11858.9002 | 11858.9002 | 12455.0186
2023-08-31 | 22396.9996 | 22396.9996 | 21865.1956 | 12249.9171 | 12249.9171 | 12005.3253
2023-09-30 | 21479.9996 | 21479.9996 | 21317.3942 | 10718.9739 | 10718.9739 | 10685.1004
2023-10-31 | 17668.0452 | 17668.0452 | 19208.5675 | 10593.967 | 10593.967 | 10757.1302
2023-11-30 | 19742.0453 | 19742.0453 | 20453.2108 | 11007.299 | 11007.299 | 11478.5016
2023-12-31 | 20346.0453 | 20346.0453 | 21211.1571 | 12018.94 | 12018.94 | 12384.2261
2023 | 22445.9996 | 22445.9996 | 23368.3724 | 135753.9345 | 135753.9345 | 138037.826
2024-01-31 | 21418.2553 | 21418.2553 | 21405.4347 | 12929.406 | 12929.406 | 13208.8176
2024-02-28 | 20987.7553 | 20987.7553 | 20022.691 | 11956.6273 | 11956.6273 | 11729.9509
2024-03-31 | 19645.2454 | 19645.2454 | 18939.8337 | 11836.2413 | 11836.2413 | 11632.2959
2024-04-30 | 17839.6154 | 17839.6154 | 18586.0743 | 10616.6408 | 10616.6408 | 10650.6806
2024-05-31 | 19148.7554 | 19148.7554 | 19498.7984 | 10660.6544 | 10660.6544 | 10640.585
2024-06-30 | 22502.1655 | 22502.1655 | 22585.2284 | 10892.6773 | 10892.6773 | 11334.1111
2024-07-31 | 22729.3704 | 22729.3704 | 23182.1746 | 12334.9116 | 12334.9116 | 12956.8035
2024-08-31 | 22592.9271 | 22592.9271 | 22518.533 | 12432.5962 | 12432.5962 | 12419.372
2024-09-30 | 21998.022 | 21998.022 | 21462.7165 | 11042.347 | 11042.347 | 10932.1478
2024-10-31 | 17976.8176 | 17976.8176 | 18603.2901 | 11073.6096 | 11073.6096 | 11048.6213
2024-11-30 | 20217.9361 | 20217.9361 | 19942.2233 | 11500.099 | 11500.099 | 11494.5336
2024-12-31 | 21036.6297 | 21036.6297 | 21342.8087 | 12626.6472 | 12626.6472 | 13046.7703
2024 | 22729.3704 | 22729.3704 | 23182.1746 | 139902.4576 | 139902.4576 | 141094.6899
2025-01-31 | 21835.8361 | 21835.8361 | 22379.5336 | 13253.9945 | 13253.9945 | 13661.657
2025-02-28 | 21259.4124 | 21259.4124 | 21116.0479 | 11671.9004 | 11671.9004 | 12130.7045
2025-03-31 | 20000.0174 | 20000.0174 | 19614.4739 | 12058.4394 | 12058.4394 | 12091.2745
2025-04-30 | 18154.8411 | 18154.8411 | 19246.3001 | 10619.601 | 10619.601 | 10891.1786
2025-05-31 | 19064.5516 | 19064.5516 | 18891.1849 | 10649.1943 | 10649.1943 | 10886.6628
2025-06-30 | 22279.0506 | 22279.0506 | 22678.4237 | 11223.7937 | 11223.7937 | 11544.6629
2025-07-31 | 23249.8525 | 23168.1551 | 23249.8525 | 13471.3387 | 12424.9641 | 13471.3387
2025-08-31 | 23530.1953 | 22782.3554 | 23530.1953 | 12734.6294 | 12363.8608 | 12734.6294
2025-09-30 | 21192.8937 | 21288.0486 | 21192.8937 | 11125.7506 | 11069.0052 | 11125.7506
2025-10-31 | 18572.3296 | 18320.7967 | 18572.3296 | 11323.7934 | 11076.979 | 11323.7934
2025-11-30 | 19963.3073 | 20153.1936 | 19963.3073 | 12004.1764 | 11562.3458 | 12004.1764
2025-12-31 | 21487.8851 | 21447.1157 | 21487.8851 | 13529.2595 | 12900.8568 | 13529.2595
2025 | 23530.1953 | 23168.1551 | 23530.1953 | 143665.8713 | 140874.935 | 145395.0883
2026-01-31 | 22160.5721 | 22550.57 | 22160.5721 | 13936.0406 | 13826.1993 | 13936.0406
2026-02-28 | 21428.1773 | 21686.2 | 21428.1773 | 12322.8713 | 12168.7162 | 12322.8713
2026-03-31 | 19889.5794 | 20412.11 | 19889.5794 | 12592.448 | 12554.0826 | 12592.448
2026-04-30 | 19288.6539 | 18337.2522 | 19288.6539 | 11162.0081 | 10995.8665 | 11162.0081
2026-05-31 | 19510.8225 | 19510.8225 | 19345.3919 | 11100.8529 | 11100.8529 | 11107.4819
2026-06-30 | 23026.9762 | 23042.9438 |  | 11828.0828 | 11828.0828
2026-07-31 | 23592.6172 | 23973.6189 |  | 12841.511 | 13121.8125
2026-08-31 | 22878.6943 | 23293.3615 |  | 12548.2185 | 12783.8086
2026-09-30 | 21567.0555 | 21815.8926 |  | 11316.3439 | 11458.4665
2026-10-31 | 18776.2167 | 18879.1352 |  | 11361.2904 | 11459.1403
2026-11-30 | 20782.6292 | 20971.9767 |  | 11941.9091 | 11992.6391
2026-12-31 | 21776.078 | 21888.7283 |  | 13237.142 | 13255.3489
2026 | 23592.6172 | 23973.6189 | 22160.5721 | 146188.7185 | 146545.0162 | 61120.8499
2027-01-31 | 22691.8172 | 22630.4034 |  | 13819.6005 | 13840.577
2027-02-28 | 21828.0782 | 21777.8129 |  | 12216.558 | 12202.647
2027-03-31 | 20549.573 | 20561.0762 |  | 12602.6329 | 12592.3294
2027-04-30 | 18549.026 | 18611.4466 |  | 11156.5115 | 11183.6297
2027-05-31 | 19799.6603 | 19989.4873 |  | 11191.4602 | 11204.398
2027-06-30 | 22933.15 | 23256.858 |  | 11863.8487 | 11967.6244
2027-07-31 | 23950.1198 | 24070.4954 |  | 13113.7809 | 13244.5826
2027-08-31 | 23398.2764 | 23573.6086 |  | 12909.1628 | 12981.5398
2027-09-30 | 21969.6568 | 22039.8582 |  | 11649.7134 | 11629.9325
2027-10-31 | 19242.8644 |  |  | 11695.8399
2027-11-30 | 21389.042 |  |  | 12357.4073
2027-12-31 | 22399.3819 |  |  | 13663.8436
Back to main menu

## Table 1.1.1 Planned
Back to main menu
Table 1.1.1 Planned: Monthly Peak and Energy Demand
Forecasted Peak and Energy Demand
| Peak Demand (MW) |  |  | Energy Demand (GWh)
Month | Current Forecast | Previous Forecast | Weather Corrected Actual | Current Forecast | Previous Forecast | Weather Corrected Actual
2012-01-01 | 22160.0997 | 22160.0997 | 22084.7322 | 13280.0235 | 13280.0235 | 12932.2873
2012-02-01 | 21813.8691 | 21813.8691 | 20756.8677 | 12202.5791 | 12202.5791 | 11380.2015
2012-03-01 | 20708.9072 | 20708.9072 | 20595.0545 | 12264.8125 | 12264.8125 | 11726.1779
2012-04-01 | 18745.092 | 18745.092 | 19830.1533 | 10866.5786 | 10866.5786 | 10883.4994
2012-05-01 | 19038.2309 | 19038.2309 | 19736.9901 | 10943.6824 | 10943.6824 | 10838.5019
2012-06-01 | 22569.1521 | 22569.1521 | 22832.4909 | 11398.2442 | 11398.2442 | 11511.081
2012-07-01 | 23298.1422 | 23298.1422 | 23630.2664 | 12319.3311 | 12319.3311 | 13057.6199
2012-08-01 | 22956.5741 | 22956.5741 | 22726.501 | 12419.0386 | 12419.0386 | 12373.2613
2012-09-01 | 20506.0631 | 20506.0631 | 20370.1157 | 10811.3017 | 10811.3017 | 10900.4102
2012-10-01 | 18345.9037 | 18345.9037 | 18684.153 | 11199.8353 | 11199.8353 | 11149.8822
2012-11-01 | 20571.5606 | 20571.5606 | 20258.2258 | 11629.6439 | 11629.6439 | 11663.449
2012-12-01 | 21693.287 | 21693.287 | 20910.8981 | 12612.0073 | 12612.0073 | 12306.8289
2012 | 23298.1422 | 23298.1422 | 23630.2664 | 141947.0782 | 141947.0782 | 140723.2004
2013-01-31 | 22013.997 | 22013.997 | 22610 | 13314.3055 | 13314.3055 | 13061.0693
2013-02-28 | 21773.6201 | 21773.6201 | 21333.0082 | 11819.7381 | 11819.7381 | 11668.8474
2013-03-31 | 20634.9497 | 20634.9497 | 20784.4526 | 12283.0437 | 12283.0437 | 11869.9986
2013-04-30 | 18492.3312 | 18492.3312 | 19284.8182 | 11018.1303 | 11018.1303 | 11090.2932
2013-05-31 | 19100.9692 | 19100.9692 | 18341.9804 | 10932.3105 | 10932.3105 | 10533.5712
2013-06-30 | 22499.2459 | 22499.2459 | 22719.4401 | 11406.4319 | 11406.4319 | 11283.4325
2013-07-31 | 23212.9348 | 23212.9348 | 24352.1456 | 12479.5529 | 12479.5529 | 12736.3503
2013-08-31 | 22359.7987 | 22359.7987 | 23255.371 | 12227.7513 | 12227.7513 | 12084.9413
2013-09-30 | 20513.3592 | 20513.3592 | 20422.3176 | 11015.3041 | 11015.3041 | 10767.0057
2013-10-31 | 18388.3002 | 18388.3002 | 18981.007 | 11279.1846 | 11279.1846 | 11114.0467
2013-11-30 | 20326.4941 | 20326.4941 | 20034.8189 | 11686.9287 | 11686.9287 | 11709.7788
2013-12-31 | 21395.0558 | 21395.0558 | 21184.5386 | 12699.9803 | 12699.9803 | 12528.9266
2013 | 23212.9348 | 23212.9348 | 24352.1456 | 142162.6617 | 142162.6617 | 140448.2614
2014-01-31 | 22319.8106 | 22319.8106 | 22043.8439 | 13356.427 | 13356.427 | 13409.7767
2014-02-28 | 20964.0592 | 20964.0592 | 21218.2216 | 11748.3799 | 11748.3799 | 11812.9441
2014-03-31 | 19906 | 19906 | 20728.4579 | 12054.5719 | 12054.5719 | 12242.1563
2014-04-30 | 17649 | 17649 | 19249.9632 | 10731.1367 | 10731.1367 | 11038.5265
2014-05-31 | 18964 | 18964 | 18750.4605 | 10790.2174 | 10790.2174 | 10546.4252
2014-06-30 | 22469.55 | 22469.55 | 20705.1957 | 11346.2756 | 11346.2756 | 11140.5499
2014-07-31 | 22948.69 | 22948.69 | 22294.8035 | 12360.0815 | 12360.0815 | 12324.9268
2014-08-31 | 21403.44 | 21403.44 | 21644.3547 | 11992.5131 | 11992.5131 | 11819.2371
2014-09-30 | 19023.2704 | 19023.2704 | 19449.0766 | 10579.5258 | 10579.5258 | 10671.4853
2014-10-31 | 18638.7361 | 18638.7361 | 18447.2196 | 11126.7565 | 11126.7565 | 10814.1957
2014-11-30 | 20302.34 | 20302.34 | 19923.2587 | 11497.4835 | 11497.4835 | 11410.1121
2014-12-31 | 21237.74 | 21237.74 | 21582.6701 | 12769.4956 | 12769.4956 | 12256.0958
2014 | 22948.69 | 22948.69 | 22294.8035 | 140352.8643 | 140352.8643 | 139486.4317
2015-01-31 | 22293.59 | 22293.59 | 21503.4489 | 13068.9431 | 13068.9431 | 12937.1182
2015-02-28 | 21016.81 | 21016.81 | 19709.6284 | 11528.5197 | 11528.5197 | 11740.7311
2015-03-31 | 19840.93 | 19840.93 | 20109.8817 | 11856.8161 | 11856.8161 | 11748.227
2015-04-30 | 18121.2 | 18121.2 | 19362.8308 | 10542.0267 | 10542.0267 | 10624.618
2015-05-31 | 19370.33 | 19370.33 | 17881.7583 | 10635.9243 | 10635.9243 | 10231.5964
2015-06-30 | 22276.64 | 22276.64 | 20554.6293 | 11410.2692 | 11410.2692 | 10908.724
2015-07-31 | 22888.49 | 22888.49 | 22638.5319 | 12174.2184 | 12174.2184 | 12273.6405
2015-08-31 | 21463.69 | 21463.69 | 22383 | 11821.2763 | 11821.2763 | 11782.7212
2015-09-30 | 18485 | 18485 | 19299.6325 | 10512.648 | 10512.648 | 10718.9879
2015-10-31 | 18339 | 18339 | 18444.3181 | 11150.1256 | 11150.1256 | 10731.7474
2015-11-30 | 20306 | 20306 | 19631.9089 | 11595.0899 | 11595.0899 | 10867.5486
2015-12-31 | 21160.04 | 21160.04 | 20418.0801 | 12611.2501 | 12611.2501 | 11784.7123
2015 | 22888.49 | 22888.49 | 22638.5319 | 138907.1073 | 138907.1073 | 136350.3725
2016-01-31 | 22360.24 | 22360.24 | 21249.7402 | 12982.1466 | 12982.1466 | 12523.599
2016-02-28 | 20985.25 | 20985.25 | 20194.6163 | 11806.8997 | 11806.8997 | 11502.97
2016-03-31 | 20075.21 | 20075.21 | 20324.618 | 11758.7447 | 11758.7447 | 11445.7227
2016-04-30 | 17405.08 | 17405.08 | 18912.1728 | 10309.6515 | 10309.6515 | 10578.9099
2016-05-31 | 19235.65 | 19235.65 | 19707.6447 | 10530.0143 | 10530.0143 | 10115.8584
2016-06-30 | 22315.7305 | 22315.7305 | 21568.912 | 11378.6081 | 11378.6081 | 11141.3797
2016-07-31 | 22599.9414 | 22599.9414 | 22288.7672 | 11896.1402 | 11896.1402 | 12345.0421
2016-08-31 | 21440.3166 | 21440.3166 | 22375.997 | 11771.834 | 11771.834 | 12295.9028
2016-09-30 | 18289 | 18289 | 19712.7154 | 10401.8861 | 10401.8861 | 10659.2295
2016-10-31 | 18079 | 18079 | 18394.9922 | 10947.5325 | 10947.5325 | 10453.1463
2016-11-30 | 20296 | 20296 | 19544.7667 | 11524.026 | 11524.026 | 10913.6011
2016-12-31 | 20888 | 20888 | 20286.7849 | 12430.7427 | 12430.7427 | 11950.5536
2016 | 22599.9414 | 22599.9414 | 22375.997 | 137738.2263 | 137738.2263 | 135925.9151
2017-01-31 | 21913.73 | 21913.73 | 20965.9674 | 12818.8508 | 12818.8508 | 12369.7298
2017-02-28 | 20966.2287 | 20966.2287 | 20379.4501 | 11294.713 | 11294.713 | 10787.4931
2017-03-31 | 20137.3 | 20137.3 | 18692.3503 | 11824.0632 | 11824.0632 | 11413.3465
2017-04-30 | 17969.79 | 17969.79 | 18482.7844 | 10366.7129 | 10366.7129 | 10105.7565
2017-05-31 | 19193.19 | 19193.19 | 18260.3078 | 10576.9018 | 10576.9018 | 10012.8427
2017-06-30 | 22454.87 | 22454.87 | 21144.8187 | 11159.3312 | 11159.3312 | 10682.999
2017-07-31 | 22492.73 | 22492.73 | 22152.8524 | 11984.7355 | 11984.7355 | 11851.6211
2017-08-31 | 22376.43 | 22376.43 | 21323.3584 | 12105.5471 | 12105.5471 | 11513.597
2017-09-30 | 19490.21 | 19490.21 | 17821.4732 | 10494.2948 | 10494.2948 | 10155.927
2017-10-31 | 18030.62 | 18030.62 | 17407.7858 | 10942.7953 | 10942.7953 | 10260.3837
2017-11-30 | 20230.97 | 20230.97 | 19195.4397 | 11371.7451 | 11371.7451 | 10946.7668
2017-12-31 | 20901.44 | 20901.44 | 21439.6493 | 12303.6865 | 12303.6865 | 12096.0133
2017 | 22492.73 | 22492.73 | 22152.8524 | 137243.3774 | 137243.3774 | 132196.4765
2018-01-31 | 21618.93 | 21618.93 | 20177.5339 | 12685.9178 | 12685.9178 | 12679.8037
2018-02-28 | 20242.21 | 20242.21 | 20042.2165 | 11074.1738 | 11074.1738 | 11081.1365
2018-03-31 | 19551.97 | 19551.97 | 19330.8728 | 11423.555 | 11423.555 | 11267.3415
2018-04-30 | 17669.81 | 17669.81 | 18107.9593 | 10157.8502 | 10157.8502 | 10586.2978
2018-05-31 | 18817.47 | 18817.47 | 19262.1307 | 10289.6502 | 10289.6502 | 10081.137
2018-06-30 | 21890.0001 | 21890.0001 | 20626.9619 | 10863.4062 | 10863.4062 | 10980.4534
2018-07-31 | 22076.0001 | 22076.0001 | 22409.0792 | 11652.7714 | 11652.7714 | 12483.776
2018-08-31 | 21946.0001 | 21946.0001 | 21385.6483 | 11685.5744 | 11685.5744 | 12040.5393
2018-09-30 | 19019 | 19019 | 19505.5646 | 10189.9802 | 10189.9802 | 10579.1906
2018-10-31 | 17788 | 17788 | 17751.4152 | 10750.0648 | 10750.0648 | 10526.7735
2018-11-30 | 19828 | 19828 | 19266.3918 | 11170.7506 | 11170.7506 | 11184.9393
2018-12-31 | 20503 | 20503 | 20375.1864 | 12007.3958 | 12007.3958 | 12019.553
2018 | 22076.0001 | 22076.0001 | 22409.0792 | 133951.0905 | 133951.0905 | 135510.9416
2019-01-31 | 21506 | 21506 | 21058.2817 | 12973.2132 | 12973.2132 | 12688.8389
2019-02-28 | 20008 | 20008 | 20420.3692 | 11162.2057 | 11162.2057 | 11212.4836
2019-03-31 | 19457 | 19457 | 19573.6921 | 11522.1982 | 11522.1982 | 11458.0531
2019-04-30 | 17548 | 17548 | 18796.3299 | 10252.9314 | 10252.9314 | 10432.2785
2019-05-31 | 18663 | 18663 | 17977.0308 | 10412.0446 | 10412.0446 | 10218.7126
2019-06-30 | 21623 | 21623 | 21239.1838 | 10939.3571 | 10939.3571 | 10608.5215
2019-07-31 | 22061 | 22061 | 21120.5208 | 11763.9974 | 11763.9974 | 12446.1887
2019-08-31 | 21200 | 21200 | 22490.4547 | 11598.2109 | 11598.2109 | 11798.5843
2019-09-30 | 19469.84 | 19469.84 | 18958.9757 | 10564.4926 | 10564.4926 | 10167.6302
2019-10-31 | 17559 | 17559 | 18814.592 | 10788.0047 | 10788.0047 | 10446.8836
2019-11-30 | 19597 | 19597 | 19001.8635 | 11194.6524 | 11194.6524 | 11094.2081
2019-12-31 | 20307 | 20307 | 20974 | 12086.6766 | 12086.6766 | 12094.1802
2019 | 22061 | 22061 | 22490.4547 | 135257.9849 | 135257.9849 | 134666.5633
2020-01-31 | 21185.0004 | 21185.0004 | 21137.8728 | 12859.4588 | 12859.4588 | 12460.9405
2020-02-28 | 19917.0004 | 19917.0004 | 19776.0281 | 11586.6754 | 11586.6754 | 11253.1814
2020-03-31 | 19377.0004 | 19377.0004 | 19680.948 | 11522.322 | 11522.322 | 11058.3098
2020-04-30 | 17302.0004 | 17302.0004 | 16515.7848 | 10229.1483 | 10229.1483 | 9383.3554
2020-05-31 | 17426 | 17426 | 18761.2836 | 9434.378 | 9434.378 | 9306.4436
2020-06-30 | 20034 | 20034 | 20741.8718 | 10274.389 | 10274.389 | 10596.6512
2020-07-31 | 22364.4404 | 22364.4404 | 24057.7367 | 11731.6936 | 11731.6936 | 12529.7172
2020-08-31 | 21631.4406 | 21631.4406 | 25317.7535 | 11441.5908 | 11441.5908 | 12338.1938
2020-09-30 | 20312.4408 | 20312.4408 | 19254.2062 | 10356.1124 | 10356.1124 | 10011.2355
2020-10-31 | 17039.9727 | 17039.9727 | 17587.3164 | 10040.7873 | 10040.7873 | 10349.5982
2020-11-30 | 18891.9134 | 18891.9134 | 19416.1975 | 10531.6058 | 10531.6058 | 10693.8532
2020-12-31 | 19805.1651 | 19805.1651 | 20975.3455 | 11815.0887 | 11815.0887 | 11932.8039
2020 | 22364.4404 | 22364.4404 | 25317.7535 | 131823.25 | 131823.25 | 131914.2838
2021-01-31 | 21176.0005 | 21176.0005 | 20951.6431 | 12539.1611 | 12539.1611 | 12307.6071
2021-02-28 | 20760.0005 | 20760.0005 | 20175.4672 | 11073.4765 | 11073.4765 | 11144.3783
2021-03-31 | 19384.0005 | 19384.0005 | 19868.2566 | 11497.7125 | 11497.7125 | 11249.5616
2021-04-30 | 17070.0009 | 17070.0009 | 17618.7846 | 10244.8035 | 10244.8035 | 10097.7166
2021-05-31 | 18055.3342 | 18055.3342 | 18021.5172 | 10152.0681 | 10152.0681 | 9986.9371
2021-06-30 | 22162.0009 | 22162.0009 | 21528.4908 | 10747.5852 | 10747.5852 | 10840.8856
2021-07-31 | 22413.0005 | 22413.0005 | 22251.4821 | 11806.5074 | 11806.5074 | 11970.9832
2021-08-31 | 22235.0005 | 22235.0005 | 21854.4728 | 11706.2663 | 11706.2663 | 12072.0791
2021-09-30 | 21212.0005 | 21212.0005 | 18979.8917 | 10472.6839 | 10472.6839 | 10401.3058
2021-10-31 | 17270.7147 | 17270.7147 | 17606.8602 | 10365.0376 | 10365.0376 | 10429.4829
2021-11-30 | 19227.38 | 19227.38 | 19684.7166 | 10886.7659 | 10886.7659 | 11017.3258
2021-12-31 | 20088.8968 | 20088.8968 | 21331.5579 | 11984.4925 | 11984.4925 | 12185.9418
2021 | 22413.0005 | 22413.0005 | 22251.4821 | 133476.5604 | 133476.5604 | 133704.2048
2022-01-31 | 20983.6671 | 20983.6671 | 21334.1018 | 12536.9576 | 12536.9576 | 12928.5532
2022-02-28 | 20446.0004 | 20446.0004 | 20782.3287 | 11208.712 | 11208.712 | 11400.5165
2022-03-31 | 19401.3338 | 19401.3338 | 19941.2707 | 11617.5125 | 11617.5125 | 11793.6956
2022-04-30 | 17251.0005 | 17251.0005 | 17752.3935 | 10239.112 | 10239.112 | 10311.1592
2022-05-31 | 18269.0005 | 18269.0005 | 20136.0014 | 10372.2878 | 10372.2878 | 10137.6947
2022-06-30 | 22161.0005 | 22161.0005 | 22101.7092 | 10967.9836 | 10967.9836 | 11002.2267
2022-07-31 | 22542.0005 | 22542.0005 | 22484.9516 | 11893.9057 | 11893.9057 | 12411.016
2022-08-31 | 22430.0005 | 22430.0005 | 23477.9346 | 12028.3221 | 12028.3221 | 11998.9314
2022-09-30 | 21489.0005 | 21489.0005 | 20446.2276 | 10551.0851 | 10551.0851 | 10678.4907
2022-10-31 | 17559.0005 | 17559.0005 | 17724.6236 | 10603.0084 | 10603.0084 | 10447.0825
2022-11-30 | 19812.0005 | 19812.0005 | 19389.6575 | 11151.0711 | 11151.0711 | 11128.3255
2022-12-31 | 20241.0005 | 20241.0005 | 20584.5241 | 12191.9609 | 12191.9609 | 12412.7534
2022 | 22542.0005 | 22542.0005 | 23477.9346 | 135361.9188 | 135361.9188 | 136650.4453
2023-01-31 | 21170.3338 | 21170.3338 | 21435.1399 | 12663.6554 | 12663.6554 | 13052.768
2023-02-28 | 20892.3338 | 20892.3338 | 20433.0112 | 11375.0622 | 11375.0622 | 11325.8235
2023-03-31 | 19701.0485 | 19701.0485 | 19000.8853 | 11846.6528 | 11846.6528 | 11814.7494
2023-04-30 | 17785.9996 | 17785.9996 | 19103.3719 | 10349.2653 | 10349.2653 | 10374.8437
2023-05-31 | 18869.9996 | 18869.9996 | 18001.5877 | 10418.8057 | 10418.8057 | 10473.6584
2023-06-30 | 21884.9996 | 21884.9996 | 22417.4764 | 10652.496 | 10652.496 | 11230.6805
2023-07-31 | 22445.9996 | 22445.9996 | 23368.3724 | 11858.9002 | 11858.9002 | 12455.0186
2023-08-31 | 22396.9996 | 22396.9996 | 21865.1956 | 12249.9171 | 12249.9171 | 12005.3253
2023-09-30 | 21479.9996 | 21479.9996 | 21317.3942 | 10718.9739 | 10718.9739 | 10685.1004
2023-10-31 | 17668.0452 | 17668.0452 | 19208.5675 | 10593.967 | 10593.967 | 10757.1302
2023-11-30 | 19742.0453 | 19742.0453 | 20453.2108 | 11007.299 | 11007.299 | 11478.5016
2023-12-31 | 20346.0453 | 20346.0453 | 21211.1571 | 12018.94 | 12018.94 | 12384.2261
2023 | 22445.9996 | 22445.9996 | 23368.3724 | 135753.9345 | 135753.9345 | 138037.826
2024-01-31 | 21418.2553 | 21418.2553 | 21405.4347 | 12929.406 | 12929.406 | 13208.8176
2024-02-28 | 20987.7553 | 20987.7553 | 20022.691 | 11956.6273 | 11956.6273 | 11729.9509
2024-03-31 | 19645.2454 | 19645.2454 | 18939.8337 | 11836.2413 | 11836.2413 | 11632.2959
2024-04-30 | 17839.6154 | 17839.6154 | 18586.0743 | 10616.6408 | 10616.6408 | 10650.6806
2024-05-31 | 19148.7554 | 19148.7554 | 19498.7984 | 10660.6544 | 10660.6544 | 10640.585
2024-06-30 | 22502.1655 | 22502.1655 | 22585.2284 | 10892.6773 | 10892.6773 | 11334.1111
2024-07-31 | 22729.3249 | 22729.3249 | 23182.1746 | 12334.9116 | 12334.9116 | 12956.8035
2024-08-31 | 22604.8475 | 22604.8475 | 22518.533 | 12446.9545 | 12446.9545 | 12419.372
2024-09-30 | 22015.6938 | 22015.6938 | 21462.7165 | 11057.7009 | 11057.7009 | 10932.1478
2024-10-31 | 17976.8176 | 17976.8176 | 18603.2901 | 11073.6096 | 11073.6096 | 11048.6213
2024-11-30 | 20217.9361 | 20217.9361 | 19942.2233 | 11500.099 | 11500.099 | 11494.5336
2024-12-31 | 21036.6297 | 21036.6297 | 21342.8087 | 12626.6472 | 12626.6472 | 13046.7703
2024 | 22729.3249 | 22729.3249 | 23182.1746 | 139932.1699 | 139932.1699 | 141094.6899
2025-01-31 | 21856.1165 | 21856.1165 | 22379.5336 | 13268.2621 | 13268.2621 | 13661.657
2025-02-28 | 21278.651 | 21278.651 | 21116.0479 | 11685.5171 | 11685.5171 | 12130.7045
2025-03-31 | 20023.5778 | 20023.5778 | 19614.4739 | 12075.4951 | 12075.4951 | 12091.2745
2025-04-30 | 18154.8411 | 18154.8411 | 19246.3001 | 10619.601 | 10619.601 | 10891.1786
2025-05-31 | 19064.5516 | 19064.5516 | 18891.1849 | 10649.1943 | 10649.1943 | 10886.6628
2025-06-30 | 22279.0506 | 22279.0506 | 22678.4237 | 11223.7937 | 11223.7937 | 11544.6629
2025-07-31 | 23249.8525 | 23171.0268 | 23249.8525 | 13471.3387 | 12427.0436 | 13471.3387
2025-08-31 | 23530.1953 | 22852.8201 | 23530.1953 | 12734.6294 | 12416.3112 | 12734.6294
2025-09-30 | 21192.8937 | 21301.525 | 21192.8937 | 11125.7506 | 11078.9473 | 11125.7506
2025-10-31 | 18572.3296 | 18359.0116 | 18572.3296 | 11323.7934 | 11105.4864 | 11323.7934
2025-11-30 | 19963.3073 | 20191.9546 | 19963.3073 | 12004.1764 | 11589.9091 | 12004.1764
2025-12-31 | 21487.8851 | 21485.0415 | 21487.8851 | 13529.2595 | 12929.668 | 13529.2595
2025 | 23530.1953 | 23171.0268 | 23530.1953 | 143710.8115 | 141069.229 | 145395.0883
2026-01-31 | 22160.5721 | 22588.04 | 22160.5721 | 13936.0406 | 13853.6597 | 13936.0406
2026-02-28 | 21428.1773 | 21723.91 | 21428.1773 | 12322.8713 | 12193.5192 | 12322.8713
2026-03-31 | 19889.5794 | 20449.45 | 19889.5794 | 12592.448 | 12581.543 | 12592.448
2026-04-30 | 19288.6539 | 18337.2522 | 19288.6539 | 11162.0081 | 10995.8665 | 11162.0081
2026-05-31 | 19345.3919 | 19510.8225 | 19345.3919 | 11100.8529 | 11100.8529 | 11107.4819
2026-06-30 | 23042.9438 | 23042.9438 |  | 11828.0828 | 11828.0828
2026-07-31 | 23592.6172 | 23973.6189 |  | 12841.511 | 13121.8125
2026-08-31 | 22878.6943 | 23293.3615 |  | 12548.2185 | 12783.8086
2026-09-30 | 21567.0555 | 21815.8926 |  | 11316.3439 | 11458.4665
2026-10-31 | 18776.2167 | 18879.1352 |  | 11361.2904 | 11459.1403
2026-11-30 | 20818.305 | 20971.9767 |  | 11968.0337 | 11992.6391
2026-12-31 | 21816.9411 | 21888.7283 |  | 13268.4915 | 13255.3489
2026 | 23592.6172 | 23973.6189 | 22160.5721 | 146246.1928 | 146624.7401 | 61120.8499
2027-01-31 | 22731.4904 | 22657.0485 |  | 13850.95 | 13860.0144
2027-02-28 | 21882.7566 | 21813.2523 |  | 12254.1775 | 12225.9719
2027-03-31 | 20608.9854 | 20599.4645 |  | 12647.7763 | 12620.3194
2027-04-30 | 18621.6016 | 18659.1268 |  | 11208.7608 | 11217.2176
2027-05-31 | 19897.0195 | 20045.1252 |  | 11264.7095 | 11244.7035
2027-06-30 | 23036.5659 | 23324.881 |  | 11941.298 | 12015.991
2027-07-31 | 24123.2668 | 24148.4464 |  | 13246.6702 | 13302.6224
2027-08-31 | 23593.1747 | 23661.6362 |  | 13058.1801 | 13046.3313
2027-09-30 | 22196.6676 | 22143.7022 |  | 11816.5387 | 11703.1939
2027-10-31 | 19242.8644 |  |  | 11695.8399
2027-11-30 | 21389.042 |  |  | 12357.4073
2027-12-31 | 22399.3819 |  |  | 13663.8436
Back to main menu

## Table 1.1.2 Firm
Back to main menu
Table 1.1.2 Firm: Weekly Coincident Peak Demand by Zone
Week Ending | Firm Hourly Coincident Peak Demand (MW)
| Bruce | East | Essa | Niagara | NorthEast | NorthWest | Ottawa | SouthWest | Toronto | West | Ontario | Load Forecast Uncertainty
2026-07-05 23:00 | 67.6323 | 1198.6769 | 1507.4816 | 762.2221 | 1159.9496 | 385.5152 | 1448.2457 | 4353.8332 | 8166.1227 | 2347.1268 | 21396.806 | 1713.5289
2026-07-12 23:00 | 74.7105 | 1341.3582 | 1608.7771 | 792.6825 | 1178.7582 | 404.8117 | 1408.4878 | 4515.2213 | 8371.3977 | 2371.8858 | 22068.091 | 1804.8307
2026-07-19 23:00 | 96.0205 | 1361.3267 | 1702.2481 | 758.4709 | 1135.9472 | 412.1576 | 1484.918 | 4583.8063 | 8126.4641 | 2606.3816 | 22267.7409 | 1731.1839
2026-07-26 23:00 | 98.4229 | 1352.866 | 1692.5714 | 763.1765 | 1133.3096 | 413.1848 | 1482.0389 | 4596.4646 | 8097.7229 | 2617.6275 | 22247.3853 | 1785.9605
2026-08-02 23:00 | 93.395 | 1358.4805 | 1596.8912 | 761.7748 | 1164.8976 | 390.1204 | 1386.931 | 4522.7147 | 8265.8086 | 2508.4228 | 22049.4367 | 1743.6169
2026-08-09 23:00 | 89.3054 | 1242.4559 | 1545.9995 | 753.227 | 1165.6326 | 424.3764 | 1424.9591 | 4370.1314 | 8198.16 | 2359.9984 | 21574.2457 | 1795.4011
2026-08-16 23:00 | 89.539 | 1279.5659 | 1592.4928 | 758.0157 | 1203.5693 | 406.3308 | 1347.9157 | 4380.3178 | 8099.2296 | 2391.6165 | 21548.5929 | 1632.57
2026-08-23 23:00 | 92.8456 | 1269.1095 | 1536.9825 | 778.3211 | 1162.9272 | 407.7115 | 1224.872 | 4395.9667 | 8065.8783 | 2450.7744 | 21385.3888 | 1457.2797
2026-08-30 23:00 | 87.677 | 1255.3065 | 1459.7213 | 759.705 | 1262.0595 | 394.0239 | 1347.5084 | 4268.4825 | 8153.7866 | 2383.7188 | 21371.9894 | 1441.5837
2026-09-06 23:00 | 91.0931 | 1243.6821 | 1483.8245 | 751.3198 | 1208.0374 | 387.7199 | 1231.396 | 4270.4236 | 7804.2588 | 2508.6228 | 20980.3781 | 1788.9372
2026-09-13 23:00 | 109.3372 | 1229.5769 | 1485.8291 | 715.8173 | 1210.9787 | 397.7413 | 1279.464 | 3765.7057 | 7302.7143 | 2334.7404 | 19831.9049 | 2008.6081
2026-09-20 23:00 | 88.542 | 1174.5293 | 1310.6283 | 667.6962 | 1215.8401 | 391.8726 | 1276.6972 | 3905.0041 | 7147.3018 | 2211.4208 | 19389.5324 | 1730.6165
2026-09-27 23:00 | 99.3112 | 1213.5518 | 1372.4262 | 660.1754 | 1232.3074 | 402.4571 | 1093.1325 | 3816.4412 | 6742.2518 | 2317.0537 | 18949.1082 | 1605.8954
2026-10-04 23:00 | 79.4722 | 1181.9391 | 1299.0285 | 649.0819 | 1238.9419 | 368.0285 | 1056.9988 | 3836.5307 | 6681.3771 | 2207.71 | 18599.1085 | 1285.0451
2026-10-11 23:00 | 92.7885 | 1221.9788 | 1343.1462 | 629.7184 | 1316.9476 | 403.3765 | 1102.7206 | 3589.0028 | 6355.6719 | 2036.6881 | 18092.0394 | 880.7728
2026-10-18 23:00 | 89.8242 | 1220.4784 | 1331.0551 | 634.2438 | 1305.9719 | 409.8678 | 1098.3592 | 3595.5308 | 6370.7343 | 2037.6674 | 18093.733 | 619.7428
2026-10-25 23:00 | 91.8874 | 1266.1716 | 1359.3776 | 632.2783 | 1324.6223 | 451.9078 | 1112.7023 | 3640.7676 | 6412.653 | 2059.2063 | 18351.5744 | 473.36
2026-11-01 23:00 | 94.871 | 1332.3608 | 1419.1185 | 637.4203 | 1321.5614 | 419.7886 | 1208.801 | 3625.3044 | 6555.09 | 2026.71 | 18641.0261 | 475.763
2026-11-08 23:00 | 98.9832 | 1321.3567 | 1436.8322 | 664.5161 | 1337.8861 | 454.8337 | 1241.5015 | 3785.9088 | 6596.0574 | 2241.865 | 19179.7407 | 508.4769
2026-11-15 23:00 | 105.4768 | 1371.5408 | 1522.5477 | 671.0601 | 1399.1453 | 518.8227 | 1231.7173 | 3872.0035 | 6695.5328 | 2301.4653 | 19689.3124 | 673.689
2026-11-22 23:00 | 108.8936 | 1460.4553 | 1638.4512 | 686.8181 | 1429.6321 | 493.7102 | 1317.5117 | 3834.4659 | 6969.4178 | 2313.0445 | 20252.4004 | 655.3915
2026-11-29 23:00 | 111.9922 | 1452.1361 | 1605.5998 | 714.5527 | 1454.0984 | 518.1362 | 1278.2435 | 4093.5934 | 7097.4153 | 2438.2004 | 20763.968 | 560.7902
2026-12-06 23:00 | 119.1204 | 1466.6666 | 1755.1652 | 724.0236 | 1490.1572 | 545.0117 | 1388.6835 | 4144.2862 | 7199.8178 | 2321.0179 | 21153.9501 | 571.1375
2026-12-13 23:00 | 126.8215 | 1521.8958 | 1829.2484 | 716.766 | 1501.0586 | 585.4615 | 1375.5588 | 4206.194 | 7168.7644 | 2438.856 | 21470.6251 | 690.9023
2026-12-20 23:00 | 119.6158 | 1524.2532 | 1839.8014 | 737.1782 | 1535.2573 | 586.6696 | 1422.1299 | 4234.4632 | 7218.9698 | 2466.9005 | 21685.2389 | 716.129
2026-12-27 23:00 | 119.9979 | 1502.7237 | 1812.5241 | 702.8798 | 1539.74 | 598.5556 | 1390.4305 | 4130.5529 | 6973.2648 | 2322.4935 | 21093.1629 | 731.1707
2027-01-03 23:00 | 117.8546 | 1534.2001 | 1871.2542 | 688.3213 | 1562.4684 | 604.1327 | 1377.8422 | 4116.9879 | 6819.7253 | 2373.141 | 21065.9277 | 737.546
2027-01-10 23:00 | 128.5991 | 1619.6643 | 1861.7148 | 728.824 | 1591.1138 | 547.3974 | 1496.8302 | 4245.0095 | 7347.9336 | 2381.8242 | 21948.9109 | 836.9625
2027-01-17 23:00 | 133.7822 | 1635.1895 | 1860.9769 | 721.1095 | 1600.6155 | 565.9681 | 1504.6155 | 4240.7536 | 7227.8683 | 2348.4265 | 21839.3056 | 858.1992
2027-01-24 23:00 | 135.1316 | 1626.4165 | 1906.1781 | 731.5186 | 1594.614 | 610.4888 | 1427.2538 | 4290.6354 | 7264.6049 | 2316.7616 | 21903.6033 | 893.3354
2027-01-31 23:00 | 135.4723 | 1638.163 | 1871.7642 | 720.783 | 1615.0248 | 566.3916 | 1497.3369 | 4183.5829 | 7330.9764 | 2330.8043 | 21890.2994 | 851.2674
2027-02-07 23:00 | 121.0026 | 1540.864 | 1770.7856 | 733.5671 | 1591.8914 | 528.0132 | 1454.944 | 4163.3647 | 7147.1522 | 2320.2805 | 21371.8652 | 768.9404
2027-02-14 23:00 | 122.9035 | 1497.9687 | 1771.0543 | 748.0926 | 1563.5994 | 584.2494 | 1339.0736 | 4186.4733 | 7174.2602 | 2385.5083 | 21373.1834 | 766.6268
2027-02-21 23:00 | 120.8227 | 1497.2278 | 1729.699 | 739.5956 | 1535.5637 | 520.2546 | 1378.3147 | 4118.1299 | 7158.3787 | 2287.0132 | 21085 | 772.3928
2027-02-28 23:00 | 122.104 | 1483.5719 | 1722.6914 | 721.3111 | 1505.3069 | 521.1679 | 1389.7664 | 4048.4151 | 7173.4688 | 2243.3192 | 20931.1226 | 705.8723
2027-03-07 23:00 | 117.9198 | 1452.5708 | 1682.6918 | 668.1967 | 1590.6677 | 558.9381 | 1326.1526 | 3999.8692 | 6861.386 | 2140.3158 | 20398.7084 | 692.705
2027-03-14 23:00 | 113.5432 | 1365.9997 | 1548.6007 | 674.2428 | 1551.9175 | 545.8801 | 1289.2413 | 3930.9399 | 6814.9136 | 2127.0803 | 19962.359 | 689.5613
2027-03-21 23:00 | 115.289 | 1325.4635 | 1499.0318 | 657.9706 | 1441.9992 | 458.8691 | 1238.3768 | 3870.8165 | 6749.3296 | 2089.195 | 19446.3412 | 641.2432
2027-03-28 23:00 | 104.5499 | 1317.1865 | 1474.3305 | 658.9149 | 1526.4011 | 478.2714 | 1205.0056 | 3732.3434 | 6519.2485 | 2007.1916 | 19023.4433 | 553.4418
2027-04-04 23:00 | 106.1146 | 1224.1822 | 1385.7509 | 642.0611 | 1464.5873 | 472.5718 | 1158.0601 | 3693.6889 | 6392.2906 | 2050.0906 | 18589.3982 | 560.5975
2027-04-11 23:00 | 96.8311 | 1289.027 | 1359.7406 | 595.0793 | 1456.2641 | 465.5147 | 1126.7744 | 3495.858 | 6430.3889 | 1915.6969 | 18231.1751 | 569.2375
2027-04-18 23:00 | 96.4647 | 1140.1041 | 1217.1824 | 601.1733 | 1362.1534 | 428.5143 | 1059.2048 | 3667.2434 | 6347.6986 | 1977.5595 | 17897.2985 | 719.6402
2027-04-25 23:00 | 93.8019 | 1238.8435 | 1303.6994 | 587.0097 | 1416.3771 | 418.3231 | 1118.4446 | 3421.9996 | 6219.4673 | 1826.8851 | 17644.8513 | 643.7582
2027-05-02 23:00 | 99.7752 | 1175.0842 | 1234.7776 | 567.1654 | 1368.9023 | 424.4505 | 1085.858 | 3439.854 | 6109.7228 | 1954.4188 | 17460.0087 | 612.6004
2027-05-09 23:00 | 100.396 | 1190.3328 | 1320.4233 | 549.1581 | 1319.0724 | 407.1978 | 1094.9996 | 3386.5066 | 6109.277 | 1899.8786 | 17377.2422 | 746.1358
2027-05-16 23:00 | 86.7525 | 940.0471 | 1240.2159 | 587.0473 | 1147.7278 | 350.7653 | 1135.1809 | 3566.2218 | 6314.79 | 2095.5484 | 17464.2971 | 969.049
2027-05-23 23:00 | 82.8055 | 1065.8738 | 1290.0178 | 622.472 | 1180.1029 | 352.4732 | 1105.2467 | 3751.4468 | 6601.9921 | 2096.5157 | 18148.9467 | 1307.7464
2027-05-30 23:00 | 83.9428 | 1082.3641 | 1300.6793 | 693.124 | 1180.0567 | 353.4868 | 1082.4661 | 3736.8493 | 6481.6501 | 2214.1886 | 18208.8078 | 2034.8531
2027-06-06 23:00 | 91.9833 | 1108.8599 | 1285.5847 | 680.1722 | 1119.8703 | 365.5886 | 1137.4362 | 3747.9423 | 7280.0973 | 2242.9522 | 19060.487 | 2183.5316
2027-06-13 23:00 | 78.5794 | 1168.4435 | 1475.9569 | 721.6733 | 1186.6179 | 368.6208 | 1372.1478 | 3984.8517 | 6850.6651 | 2342.4737 | 19550.0301 | 2176.7571
2027-06-20 23:00 | 90.0828 | 1161.4533 | 1466.6092 | 702.9736 | 1132.2288 | 382.2793 | 1529.8309 | 3897.3894 | 7927.4465 | 2307.199 | 20597.4928 | 2123.8008
2027-06-27 23:00 | 77.12 | 1124.4993 | 1526.5709 | 764.027 | 1123.176 | 397.1702 | 1386.4111 | 4168.327 | 8303.7617 | 2602.4935 | 21473.5568 | 1748.9026
2027-07-04 23:00 | 89.0829 | 1232.4604 | 1604.5925 | 744.4867 | 1122.5639 | 406.3726 | 1642.6626 | 4174.0972 | 7961.8481 | 2512.81 | 21490.9768 | 1720.4203
2027-07-11 23:00 | 77.3895 | 1256.9709 | 1566.2061 | 792.9376 | 1196.2558 | 380.667 | 1490.0665 | 4439.4949 | 8363.7316 | 2673.058 | 22236.778 | 1805.392
2027-07-18 23:00 | 87.6395 | 1457.2275 | 1771.9755 | 821.5629 | 1220.4859 | 402.0722 | 1508.5603 | 4226.0888 | 8441.1712 | 2511.8789 | 22448.6626 | 1776.2444
2027-07-25 23:00 | 79.8699 | 1268.8713 | 1482.9091 | 803.1539 | 1143.4046 | 384.5388 | 1529.8288 | 4663.0931 | 8445.0197 | 2659.2931 | 22459.9822 | 1794.3197
2027-08-01 23:00 | 77.6878 | 1372.853 | 1607.6173 | 801.781 | 1147.6488 | 382.6859 | 1423.7917 | 4525.6648 | 8330.5346 | 2642.375 | 22312.64 | 1682.3722
2027-08-08 23:00 | 96.4196 | 1286.2915 | 1609.6636 | 754.8615 | 1211.8406 | 396.0995 | 1485.7204 | 4121.9282 | 8283.4858 | 2614.5581 | 21860.8689 | 1789.7942
2027-08-15 23:00 | 80.9536 | 1233.4164 | 1543.7956 | 774.632 | 1204.4969 | 411.2868 | 1305.4899 | 4417.2 | 8216.3458 | 2632.511 | 21820.128 | 1666.1063
2027-08-22 23:00 | 82.1102 | 1378.638 | 1586.1371 | 776.2869 | 1225.2814 | 392.1578 | 1272.3477 | 4191.0963 | 8250.9409 | 2459.2681 | 21614.2644 | 1493.868
2027-08-29 23:00 | 94.3657 | 1268.2721 | 1594.8994 | 743.2587 | 1246.4778 | 419.9437 | 1467.3779 | 4037.6193 | 8217.3431 | 2544.3744 | 21633.9319 | 1411.3369
2027-09-05 23:00 | 87.5264 | 1253.5762 | 1502.8404 | 781.8326 | 1178.8726 | 382.705 | 1097.6123 | 4538.4523 | 7711.3217 | 2776.4197 | 21311.1592 | 1751.8942
2027-09-12 23:00 | 92.1389 | 1161.8653 | 1367.2494 | 696.1897 | 1247.393 | 415.8814 | 1321.6921 | 3966.5252 | 7415.4423 | 2519.1254 | 20203.5027 | 1994.1296
2027-09-19 23:00 | 93.048 | 1169.6059 | 1396.7863 | 674.218 | 1208.5181 | 396.2446 | 1236.4128 | 3793.3205 | 7405.528 | 2357.6848 | 19731.367 | 1770.1976
2027-09-26 23:00 | 91.1517 | 1240.5177 | 1419.2738 | 719.629 | 1251.9338 | 395.1485 | 1170.541 | 3786.0578 | 6711.3805 | 2479.3165 | 19264.9503 | 1644.0278
2027-10-03 23:00 | 82.9799 | 1221.7393 | 1336.6383 | 646.7067 | 1317.5982 | 399.6486 | 1125.7534 | 3803.6808 | 6866.7244 | 2376.7222 | 19178.1919 | 1232.3517
2027-10-10 23:00 | 81.6137 | 1181.573 | 1281.5541 | 647.2776 | 1300.8433 | 415.8928 | 1094.1249 | 3575.1033 | 6533.1787 | 2297.1885 | 18408.35 | 927.3887
2027-10-17 23:00 | 91.6023 | 1273.3947 | 1359.7104 | 636.7474 | 1314.1369 | 446.9134 | 1139.1999 | 3578.7288 | 6351.9889 | 2205.9352 | 18398.3578 | 647.4782
2027-10-24 23:00 | 88.4559 | 1211.6704 | 1309.7793 | 672.4681 | 1290.4794 | 446.7646 | 1075.8317 | 3582.4628 | 6689.7279 | 2260.649 | 18628.2892 | 470.556
2027-10-31 23:00 | 99.7594 | 1310.045 | 1437.6587 | 637.2566 | 1305.5235 | 482.5432 | 1152.6697 | 3607.6371 | 6551.6493 | 2325.6438 | 18910.3862 | 484.7125
2027-11-07 23:00 | 99.6983 | 1290.0351 | 1452.8421 | 672.8212 | 1346.8958 | 466.2735 | 1193.2208 | 3745.7345 | 6721.3613 | 2472.1248 | 19461.0074 | 498.9884
2027-11-14 23:00 | 95.0848 | 1358.8836 | 1531.6225 | 685.7277 | 1344.2461 | 497.3293 | 1206.4515 | 3859.722 | 6812.9796 | 2525.5435 | 19917.5905 | 632.01
2027-11-21 23:00 | 101.5736 | 1396.7004 | 1572.0281 | 693.8544 | 1419.2148 | 528.1327 | 1243.5488 | 3976.7787 | 6975.3356 | 2583.1055 | 20490.2726 | 665.8711
2027-11-28 23:00 | 112.4314 | 1456.5868 | 1613.1379 | 708.4925 | 1446.4755 | 544.6526 | 1290.4468 | 4107.0638 | 7181.6733 | 2573.5896 | 21034.5501 | 574.9633
2027-12-05 23:00 | 119.07 | 1417.2406 | 1707.0302 | 730.1423 | 1428.8061 | 564.5901 | 1336.5495 | 4207.9584 | 7251.7365 | 2630.7734 | 21393.8971 | 564.9823
2027-12-12 23:00 | 126.5103 | 1520.5852 | 1815.6929 | 719.6323 | 1510.9915 | 588.3868 | 1424.0217 | 4149.2279 | 7284.729 | 2616.6805 | 21756.458 | 677.5458
2027-12-19 23:00 | 122.2052 | 1550.8975 | 1851.8464 | 726.8576 | 1573.6248 | 554.5427 | 1475.4446 | 4183.2964 | 7335.2509 | 2616.8642 | 21990.8301 | 712.2488
2027-12-26 23:00 | 122.3025 | 1558.2843 | 1880.563 | 721.4456 | 1550.1112 | 584.6502 | 1501.9921 | 4157.4523 | 7308.5133 | 2625.8618 | 22011.1762 | 722.5903
2028-01-02 23:00 | 120.8146 | 1524.5746 | 1867.6222 | 726.6962 | 1515.1801 | 592.5877 | 1404.2205 | 4186.4186 | 7161.2715 | 2660.2835 | 21759.6694 | 834.75
Back to main menu

## Table 1.1.2 Planned
Back to main menu
Table 1.1.2 Planned: Weekly Coincident Peak Demand by Zone
Week Ending | Planned Hourly Coincident Peak Demand (MW)
| Bruce | East | Essa | Niagara | NorthEast | NorthWest | Ottawa | SouthWest | Toronto | West | Ontario | Load Forecast Uncertainty
2026-07-05 23:00 | 67.6307 | 1198.6486 | 1507.4461 | 762.2041 | 1159.9223 | 385.5061 | 1448.2116 | 4353.7307 | 8165.9303 | 2347.0715 | 21396.3019 | 1712.9338
2026-07-12 23:00 | 74.7139 | 1341.419 | 1608.8501 | 792.7185 | 1178.8117 | 404.8301 | 1408.5516 | 4515.4261 | 8371.7773 | 2371.9934 | 22069.0917 | 1804.454
2026-07-19 23:00 | 96.0183 | 1361.2961 | 1702.2099 | 758.4539 | 1135.9217 | 412.1484 | 1484.8847 | 4583.7035 | 8126.2818 | 2606.3231 | 22267.2414 | 1732.3949
2026-07-26 23:00 | 98.4196 | 1352.8203 | 1692.5141 | 763.1507 | 1133.2713 | 413.1709 | 1481.9888 | 4596.3091 | 8097.449 | 2617.539 | 22246.6329 | 1786.0592
2026-08-02 23:00 | 93.3958 | 1358.4912 | 1596.9037 | 761.7807 | 1164.9067 | 390.1235 | 1386.9419 | 4522.7501 | 8265.8732 | 2508.4424 | 22049.609 | 1742.6001
2026-08-09 23:00 | 89.308 | 1242.4924 | 1546.0449 | 753.249 | 1165.6668 | 424.3889 | 1425.0009 | 4370.2595 | 8198.4005 | 2360.0676 | 21574.8785 | 1794.7044
2026-08-16 23:00 | 89.5368 | 1279.534 | 1592.4531 | 757.9968 | 1203.5393 | 406.3206 | 1347.8821 | 4380.2086 | 8099.0278 | 2391.5569 | 21548.056 | 1632.511
2026-08-23 23:00 | 92.8486 | 1269.1494 | 1537.0308 | 778.3455 | 1162.9638 | 407.7243 | 1224.9105 | 4396.1047 | 8066.1316 | 2450.8513 | 21386.0604 | 1456.3156
2026-08-30 23:00 | 87.6729 | 1255.2478 | 1459.653 | 759.6695 | 1262.0005 | 394.0054 | 1347.4454 | 4268.283 | 8153.4055 | 2383.6073 | 21370.9905 | 1442.617
2026-09-06 23:00 | 91.0931 | 1243.6828 | 1483.8254 | 751.3203 | 1208.0381 | 387.7201 | 1231.3967 | 4270.426 | 7804.2633 | 2508.6243 | 20980.3902 | 1788.81
2026-09-13 23:00 | 109.339 | 1229.5978 | 1485.8544 | 715.8295 | 1210.9993 | 397.7481 | 1279.4858 | 3765.7698 | 7302.8387 | 2334.7801 | 19832.2425 | 2009.2182
2026-09-20 23:00 | 88.5421 | 1174.5312 | 1310.6304 | 667.6972 | 1215.842 | 391.8732 | 1276.6992 | 3905.0103 | 7147.3132 | 2211.4243 | 19389.5633 | 1729.8153
2026-09-27 23:00 | 99.3152 | 1213.6012 | 1372.482 | 660.2022 | 1232.3575 | 402.4734 | 1093.1769 | 3816.5963 | 6742.5258 | 2317.1479 | 18949.8784 | 1605.0828
2026-10-04 23:00 | 79.4716 | 1181.9304 | 1299.0189 | 649.0771 | 1238.9328 | 368.0258 | 1056.9911 | 3836.5026 | 6681.3282 | 2207.6938 | 18598.9724 | 1285.2387
2026-10-11 23:00 | 92.7892 | 1221.9877 | 1343.156 | 629.7229 | 1316.9572 | 403.3794 | 1102.7286 | 3589.0289 | 6355.7182 | 2036.7029 | 18092.1711 | 881.1839
2026-10-18 23:00 | 89.8228 | 1220.4594 | 1331.0345 | 634.2339 | 1305.9516 | 409.8614 | 1098.3422 | 3595.475 | 6370.6353 | 2037.6358 | 18093.4519 | 619.7529
2026-10-25 23:00 | 91.8875 | 1266.1722 | 1359.3783 | 632.2787 | 1324.623 | 451.908 | 1112.7029 | 3640.7695 | 6412.6563 | 2059.2074 | 18351.5839 | 473.5571
2026-11-01 23:00 | 94.8676 | 1332.3137 | 1419.0683 | 637.3977 | 1321.5146 | 419.7738 | 1208.7582 | 3625.1761 | 6554.8579 | 2026.6382 | 18640.366 | 476.0595
2026-11-08 23:00 | 101.9123 | 1321.1941 | 1512.1741 | 686.0471 | 1330.1071 | 472.7622 | 1078.556 | 3847.7285 | 6590.985 | 2272.9647 | 19214.4312 | 508.6541
2026-11-15 23:00 | 105.4763 | 1371.535 | 1522.5412 | 671.0572 | 1399.1393 | 518.8205 | 1231.712 | 3906.2864 | 6695.5043 | 2301.4555 | 19723.528 | 673.665
2026-11-22 23:00 | 108.8903 | 1460.4113 | 1638.4018 | 686.7974 | 1429.589 | 493.6953 | 1317.472 | 3869.7974 | 6969.2078 | 2312.9748 | 20287.2371 | 655.5649
2026-11-29 23:00 | 111.987 | 1452.0683 | 1605.5249 | 714.5194 | 1454.0305 | 518.112 | 1278.1838 | 4129.3129 | 7097.0841 | 2438.0867 | 20798.9096 | 561.151
2026-12-06 23:00 | 119.1138 | 1466.5849 | 1755.0675 | 723.9833 | 1490.0742 | 544.9814 | 1388.6061 | 4185.7727 | 7199.4168 | 2320.8886 | 21194.4892 | 571.4712
2026-12-13 23:00 | 126.8213 | 1521.8937 | 1829.2459 | 716.7651 | 1501.0565 | 585.4607 | 1375.557 | 4246.8778 | 7168.7547 | 2438.8527 | 21511.2855 | 690.6589
2026-12-20 23:00 | 119.614 | 1524.2292 | 1839.7725 | 737.1666 | 1535.2331 | 586.6604 | 1422.1075 | 4275.6995 | 7218.8563 | 2466.8617 | 21726.2008 | 716.2678
2026-12-27 23:00 | 119.995 | 1502.6875 | 1812.4804 | 702.8629 | 1539.7029 | 598.5411 | 1390.397 | 4171.877 | 6973.0967 | 2322.4375 | 21134.078 | 731.1988
2027-01-03 23:00 | 117.8584 | 1534.2502 | 1871.3153 | 688.3438 | 1562.5194 | 604.1524 | 1377.8872 | 4157.8302 | 6819.9481 | 2373.2185 | 21107.3235 | 737.7394
2027-01-10 23:00 | 128.6049 | 1619.737 | 1861.7984 | 728.8567 | 1591.1853 | 547.422 | 1496.8974 | 4285.2523 | 7348.2637 | 2381.9312 | 21989.949 | 836.4791
2027-01-17 23:00 | 133.784 | 1635.2125 | 1861.0031 | 721.1196 | 1600.638 | 565.9761 | 1504.6367 | 4280.7196 | 7227.97 | 2348.4596 | 21879.5192 | 858.3034
2027-01-24 23:00 | 135.1284 | 1626.3784 | 1906.1335 | 731.5014 | 1594.5767 | 610.4745 | 1427.2204 | 4331.4277 | 7264.4348 | 2316.7074 | 21943.9833 | 893.6936
2027-01-31 23:00 | 135.4682 | 1638.113 | 1871.7072 | 720.7611 | 1614.9756 | 566.3743 | 1497.2912 | 4224.3064 | 7330.753 | 2330.7332 | 21930.4833 | 852.0167
2027-02-07 23:00 | 121.0033 | 1540.8733 | 1770.7962 | 733.5715 | 1591.9009 | 528.0163 | 1454.9527 | 4217.5187 | 7147.1949 | 2320.2943 | 21426.1221 | 768.92
2027-02-14 23:00 | 122.9058 | 1497.9968 | 1771.0876 | 748.1066 | 1563.6287 | 584.2604 | 1339.0987 | 4241.1806 | 7174.3949 | 2385.5531 | 21428.2132 | 766.9482
2027-02-21 23:00 | 120.821 | 1497.2062 | 1729.6741 | 739.585 | 1535.5415 | 520.2471 | 1378.2948 | 4173.0935 | 7158.2754 | 2286.9802 | 21139.7187 | 772.268
2027-02-28 23:00 | 122.0996 | 1483.5185 | 1722.6294 | 721.2852 | 1505.2527 | 521.1491 | 1389.7164 | 4103.9994 | 7173.2107 | 2243.2385 | 20986.0995 | 706.0873
2027-03-07 23:00 | 117.9103 | 1452.4547 | 1682.5573 | 668.1433 | 1590.5406 | 558.8935 | 1326.0466 | 4060.9776 | 6860.8376 | 2140.1447 | 20458.5063 | 692.8336
2027-03-14 23:00 | 113.5382 | 1365.9392 | 1548.5321 | 674.2129 | 1551.8487 | 545.8559 | 1289.1842 | 3991.157 | 6814.6118 | 2126.9861 | 20021.8661 | 689.605
2027-03-21 23:00 | 115.2913 | 1325.4895 | 1499.0611 | 657.9835 | 1442.0274 | 458.8781 | 1238.401 | 3929.7597 | 6749.4615 | 2089.2358 | 19505.5889 | 641.0788
2027-03-28 23:00 | 119.0803 | 1300.5493 | 1508.6413 | 648.5564 | 1502.2279 | 497.7664 | 1182.0013 | 3784.6611 | 6476.2911 | 2062.9248 | 19082.6999 | 553.6607
2027-04-04 23:00 | 106.1151 | 1224.1883 | 1385.7579 | 642.0643 | 1464.5947 | 472.5742 | 1158.0659 | 3753.9539 | 6392.3227 | 2050.1009 | 18649.738 | 559.7393
2027-04-11 23:00 | 96.8297 | 1289.0072 | 1359.7198 | 595.0702 | 1456.2418 | 465.5076 | 1126.7572 | 3568.4746 | 6430.2904 | 1915.6675 | 18303.5659 | 569.6436
2027-04-18 23:00 | 110.9226 | 1235.883 | 1356.8077 | 595.2415 | 1361.7116 | 418.3079 | 1065.6445 | 3605.2237 | 6273.6976 | 1946.5253 | 17969.9654 | 719.4186
2027-04-25 23:00 | 93.7975 | 1238.7846 | 1303.6374 | 586.9818 | 1416.3098 | 418.3033 | 1118.3914 | 3495.131 | 6219.1716 | 1826.7982 | 17717.3066 | 643.76
2027-05-02 23:00 | 99.7783 | 1175.1208 | 1234.8161 | 567.1831 | 1368.9451 | 424.4637 | 1085.8919 | 3512.0765 | 6109.9135 | 1954.4798 | 17532.6688 | 612.1177
2027-05-09 23:00 | 100.3766 | 1190.1027 | 1320.168 | 549.0519 | 1318.8174 | 407.1191 | 1094.7879 | 3457.4466 | 6108.0961 | 1928.3895 | 17474.3557 | 745.5743
2027-05-16 23:00 | 86.7458 | 939.9743 | 1240.1198 | 587.0019 | 1147.6388 | 350.7381 | 1135.0929 | 3634.2704 | 6314.3007 | 2124.2826 | 17560.1653 | 968.794
2027-05-23 23:00 | 90.5431 | 1162.7378 | 1330.6074 | 613.3497 | 1291.6901 | 425.3203 | 1150.6408 | 3649.4411 | 6529.3311 | 2002.6192 | 18246.2806 | 1306.4682
2027-05-30 23:00 | 83.9232 | 1082.1124 | 1300.3768 | 692.9628 | 1179.7823 | 353.4046 | 1082.2143 | 3807.4446 | 6480.1427 | 2242.8512 | 18305.215 | 2033.3509
2027-06-06 23:00 | 91.9803 | 1108.8226 | 1285.5415 | 680.1493 | 1119.8327 | 365.5763 | 1137.398 | 3817.0153 | 7279.8526 | 2278.5007 | 19164.6692 | 2183.6641
2027-06-13 23:00 | 78.5657 | 1168.2397 | 1475.6996 | 721.5475 | 1186.4111 | 368.5565 | 1371.9086 | 4056.3654 | 6849.4707 | 2377.8558 | 19654.6205 | 2178.7438
2027-06-20 23:00 | 90.0657 | 1161.2328 | 1466.3308 | 702.8401 | 1132.0139 | 382.2067 | 1529.5404 | 3967.8526 | 7925.9412 | 2343.4166 | 20701.4407 | 2124.0263
2027-06-27 23:00 | 77.1063 | 1124.3 | 1526.3004 | 763.8917 | 1122.977 | 397.0998 | 1386.1655 | 4240.0528 | 8302.2906 | 2637.5891 | 21577.7732 | 1748.7284
2027-07-04 23:00 | 82.1535 | 1441.9831 | 1742.1964 | 782.6021 | 1212.7612 | 379.7729 | 1441.0909 | 4216.3448 | 7846.6751 | 2477.8466 | 21623.4266 | 1714.4683
2027-07-11 23:00 | 77.3791 | 1256.8017 | 1565.9952 | 792.8309 | 1196.0948 | 380.6158 | 1489.866 | 4573.0369 | 8362.6059 | 2714.5133 | 22409.7396 | 1804.2303
2027-07-18 23:00 | 87.5915 | 1456.4287 | 1771.0042 | 821.1126 | 1219.8169 | 401.8518 | 1507.7334 | 4365.6324 | 8436.5444 | 2552.8376 | 22620.5534 | 1776.1171
2027-07-25 23:00 | 79.8568 | 1268.6641 | 1482.6669 | 803.0228 | 1143.2179 | 384.4761 | 1529.579 | 4796.491 | 8443.6406 | 2700.3936 | 22632.0086 | 1793.7347
2027-08-01 23:00 | 77.6817 | 1372.746 | 1607.492 | 801.7186 | 1147.5594 | 382.6561 | 1423.6807 | 4658.287 | 8329.8854 | 2683.9999 | 22485.7067 | 1681.8204
2027-08-08 23:00 | 97.9392 | 1383.1673 | 1700.5168 | 807.698 | 1237.9838 | 403.9257 | 1417.0763 | 4407.5939 | 7916.8362 | 2684.6414 | 22057.3785 | 1788.8375
2027-08-15 23:00 | 80.9441 | 1233.2727 | 1543.6157 | 774.5417 | 1204.3565 | 411.2389 | 1305.3378 | 4566.5574 | 8215.3884 | 2681.6542 | 22016.9074 | 1665.0329
2027-08-22 23:00 | 82.1096 | 1378.6283 | 1586.1259 | 776.2814 | 1225.2728 | 392.1551 | 1272.3387 | 4338.6286 | 8250.8828 | 2508.72 | 21811.1432 | 1494.1413
2027-08-29 23:00 | 94.34 | 1267.9264 | 1594.4647 | 743.0561 | 1246.1381 | 419.8292 | 1466.978 | 4189.3058 | 8215.1037 | 2594.0926 | 21831.2348 | 1410.1769
2027-09-05 23:00 | 95.6848 | 1211.3143 | 1474.4111 | 740.6654 | 1196.4392 | 418.0585 | 1293.2688 | 4353.584 | 8047.9859 | 2695.4996 | 21526.9118 | 1747.7641
2027-09-12 23:00 | 92.1096 | 1161.4962 | 1366.8151 | 695.9686 | 1246.9967 | 415.7493 | 1321.2723 | 4138.4356 | 7413.0867 | 2577.7298 | 20429.6599 | 1996.5405
2027-09-19 23:00 | 93.0381 | 1169.4823 | 1396.6386 | 674.1468 | 1208.3903 | 396.2027 | 1236.2821 | 3964.3868 | 7404.745 | 2416.7337 | 19960.0465 | 1769.4741
2027-09-26 23:00 | 91.1344 | 1240.2818 | 1419.0039 | 719.4922 | 1251.6957 | 395.0734 | 1170.3184 | 3958.8274 | 6710.1044 | 2538.1318 | 19494.0635 | 1645.1374
2027-10-03 23:00 | 83.8115 | 1190.3524 | 1423.6597 | 722.4991 | 1229.6402 | 427.9817 | 1138.2196 | 4010.43 | 6633.5443 | 2547.9047 | 19408.0433 | 1231.4519
2027-10-10 23:00 | 81.5945 | 1181.2948 | 1281.2523 | 647.1251 | 1300.537 | 415.7949 | 1093.8672 | 3762.0943 | 6531.6401 | 2354.2483 | 18649.4485 | 927.4101
2027-10-17 23:00 | 88.9515 | 1212.691 | 1318.2752 | 641.5119 | 1319.1726 | 457.521 | 1093.8003 | 3778.8769 | 6403.9951 | 2324.2476 | 18639.0431 | 647.3394
2027-10-24 23:00 | 88.4365 | 1211.4051 | 1309.4925 | 672.3208 | 1290.1968 | 446.6668 | 1075.5961 | 3769.1379 | 6688.263 | 2317.6403 | 18869.156 | 470.3916
2027-10-31 23:00 | 99.7435 | 1309.8361 | 1437.4295 | 637.155 | 1305.3153 | 482.4662 | 1152.486 | 3793.3498 | 6550.6049 | 2382.2025 | 19150.589 | 484.7625
2027-11-07 23:00 | 99.6837 | 1289.8458 | 1452.629 | 672.7225 | 1346.6982 | 466.2051 | 1193.0458 | 3961.676 | 6720.3752 | 2530.8585 | 19733.7398 | 498.8323
2027-11-14 23:00 | 104.6925 | 1338.0059 | 1523.5864 | 684.8943 | 1349.0932 | 489.769 | 1173.9436 | 4156.6738 | 6757.9993 | 2611.386 | 20190.0441 | 632.5584
2027-11-21 23:00 | 99.8857 | 1399.4966 | 1582.0904 | 690.0748 | 1422.0794 | 496.2563 | 1288.6715 | 4145.7165 | 7057.5255 | 2581.5735 | 20763.3701 | 666.1389
2027-11-28 23:00 | 109.4667 | 1458.1312 | 1612.1631 | 713.1821 | 1464.4714 | 533.7663 | 1329.4089 | 4234.763 | 7168.2605 | 2684.3039 | 21307.917 | 574.9958
2027-12-05 23:00 | 116.1441 | 1434.8626 | 1699.2835 | 732.4538 | 1448.1352 | 557.455 | 1429.1067 | 4367.2109 | 7234.6377 | 2662.1443 | 21681.4336 | 566.2123
2027-12-12 23:00 | 126.4914 | 1520.3585 | 1815.4222 | 719.525 | 1510.7662 | 588.299 | 1423.8094 | 4387.5773 | 7283.6428 | 2673.3972 | 22049.289 | 677.9277
2027-12-19 23:00 | 122.1781 | 1550.5527 | 1851.4347 | 726.696 | 1573.275 | 554.4195 | 1475.1166 | 4422.7708 | 7333.6204 | 2673.6129 | 22283.6768 | 712.9325
2027-12-26 23:00 | 122.2687 | 1557.853 | 1880.0426 | 721.2459 | 1549.6822 | 584.4884 | 1501.5765 | 4397.622 | 7306.4908 | 2682.8041 | 22304.0743 | 722.998
2028-01-02 23:00 | 120.7567 | 1523.8438 | 1866.7269 | 726.3478 | 1514.4538 | 592.3036 | 1403.5474 | 4431.9711 | 7157.8388 | 2718.1901 | 22055.9799 | 834.7544
Back to main menu

## Table 1.1.3 Firm
Back to main menu
Table 1.1.3 Firm: Weekly Energy Demand by Zone
Week Ending | Firm Weekly Normal Energy (GWh)
| Bruce | East | Essa | Niagara | NorthEast | NorthWest | Ottawa | SouthWest | Toronto | West | Ontario
2026-07-05 23:00 | 11.1656 | 165.3466 | 191.6136 | 97.9027 | 195.3538 | 61.3116 | 163.9037 | 569.5959 | 1007.9103 | 304.2006 | 2768.3044
2026-07-12 23:00 | 10.5877 | 170.0942 | 196.6121 | 99.3613 | 203.2361 | 64.3882 | 175.9348 | 588.227 | 1053.1545 | 312.5242 | 2874.12
2026-07-19 23:00 | 11.6963 | 173.3493 | 204.997 | 103.0812 | 190.788 | 62.2494 | 175.5039 | 594.6038 | 1076.2637 | 326.2992 | 2918.8318
2026-07-26 23:00 | 11.8565 | 172.6206 | 204.722 | 103.0507 | 190.4748 | 62.9872 | 174.8007 | 595.5453 | 1073.2063 | 328.1511 | 2917.4153
2026-08-02 23:00 | 11.8177 | 168.3392 | 198.4751 | 100.8629 | 202.4982 | 65.5454 | 177.7071 | 586.2399 | 1075.5029 | 315.5942 | 2902.5826
2026-08-09 23:00 | 12.7662 | 164.5594 | 195.3789 | 101.6732 | 198.5059 | 64.9214 | 169.9205 | 576.361 | 1042.1011 | 318.8958 | 2845.0833
2026-08-16 23:00 | 12.4527 | 160.9041 | 190.5193 | 103.5646 | 197.1021 | 61.8276 | 164.3612 | 586.5259 | 1038.2877 | 322.3625 | 2837.9077
2026-08-23 23:00 | 12.7331 | 166.6906 | 194.8859 | 101.8804 | 199.3761 | 63.0197 | 164.3706 | 570.6161 | 1025.7838 | 311.9938 | 2811.3501
2026-08-30 23:00 | 13.1138 | 162.8953 | 189.8655 | 100.9619 | 203.5607 | 63.7915 | 159.7392 | 561.6091 | 1032.5723 | 306.8194 | 2794.9288
2026-09-06 23:00 | 13.8733 | 164.5545 | 184.8006 | 96.0924 | 204.414 | 63.4228 | 160.0296 | 544.5138 | 982.5415 | 319.4641 | 2733.7066
2026-09-13 23:00 | 13.85 | 156.2008 | 175.4146 | 91.9031 | 193.3799 | 60.8007 | 150.9066 | 519.7212 | 923.3785 | 310.1413 | 2595.6966
2026-09-20 23:00 | 13.2203 | 158.1241 | 176.6119 | 90.9252 | 191.962 | 60.8147 | 155.8143 | 518.1852 | 926.3808 | 306.749 | 2598.7875
2026-09-27 23:00 | 13.6555 | 156.2868 | 178.7285 | 88.932 | 202.2009 | 65.9426 | 151.8006 | 512.752 | 909.8152 | 297.7926 | 2577.9067
2026-10-04 23:00 | 11.8063 | 152.9435 | 172.2421 | 90.4765 | 202.3282 | 61.2965 | 148.8634 | 506.6529 | 906.102 | 294.2713 | 2546.9827
2026-10-11 23:00 | 12.0438 | 159.253 | 175.4956 | 92.5735 | 200.5092 | 62.0315 | 148.233 | 494.6161 | 892.3794 | 299.0207 | 2536.1558
2026-10-18 23:00 | 11.7963 | 158.99 | 174.5279 | 92.3612 | 199.9017 | 62.3624 | 147.2648 | 490.8081 | 882.4851 | 298.3227 | 2518.8203
2026-10-25 23:00 | 13.149 | 167.6204 | 184.2494 | 92.8966 | 204.1879 | 67.4369 | 152.2742 | 512.8639 | 893.3781 | 302.369 | 2590.4255
2026-11-01 23:00 | 12.5087 | 170.4849 | 186.1987 | 95.2838 | 208.0737 | 67.8542 | 159.273 | 518.4757 | 910.2661 | 310.9429 | 2639.3616
2026-11-08 23:00 | 13.5008 | 169.8802 | 192.053 | 96.0835 | 212.1049 | 71.689 | 162.7227 | 529.2488 | 926.8463 | 320.5611 | 2694.6904
2026-11-15 23:00 | 14.4431 | 185.081 | 208.3619 | 97.2593 | 219.7968 | 78.7927 | 161.0195 | 533.2534 | 929.2424 | 325.5675 | 2752.8175
2026-11-22 23:00 | 14.8308 | 190.7396 | 215.142 | 100.392 | 226.3415 | 75.9985 | 173.1676 | 543.65 | 968.8352 | 330.1011 | 2839.1983
2026-11-29 23:00 | 15.7053 | 199.0467 | 221.3366 | 104.3562 | 224.6121 | 79.4464 | 174.6863 | 558.3376 | 984.4248 | 343.5506 | 2905.5026
2026-12-06 23:00 | 16.0399 | 197.1386 | 235.2266 | 106.6846 | 231.1435 | 85.2887 | 181.8962 | 578.6091 | 997.0883 | 347.1633 | 2976.2788
2026-12-13 23:00 | 17.4772 | 207.5287 | 248.9338 | 106.0417 | 235.0688 | 87.6518 | 186.2891 | 585.2046 | 1001.8247 | 348.0843 | 3024.1047
2026-12-20 23:00 | 16.9202 | 209.5723 | 250.633 | 106.746 | 239.3704 | 86.6721 | 196.4013 | 583.9036 | 1001.6026 | 352.3658 | 3044.1873
2026-12-27 23:00 | 16.1971 | 202.0743 | 242.0235 | 104.8039 | 236.9378 | 87.1955 | 188.2768 | 563.8249 | 962.3799 | 342.3182 | 2946.0318
2027-01-03 23:00 | 16.8279 | 208.0959 | 247.4314 | 103.4633 | 243.861 | 87.6189 | 188.4502 | 559.1373 | 951.5446 | 332.7352 | 2939.1656
2027-01-10 23:00 | 17.2873 | 217.7935 | 252.3324 | 109.1941 | 253.109 | 91.5684 | 198.0291 | 604.18 | 1023.1949 | 351.1255 | 3117.8143
2027-01-17 23:00 | 18.4718 | 223.9779 | 258.5208 | 109.6262 | 252.8941 | 88.4078 | 205.1483 | 605.3236 | 1026.2623 | 348.4075 | 3137.0404
2027-01-24 23:00 | 19.0456 | 225.6877 | 261.3287 | 110.9489 | 254.8758 | 91.5007 | 201.8553 | 615.652 | 1031.3797 | 350.8686 | 3163.1431
2027-01-31 23:00 | 19.7443 | 220.4962 | 257.7007 | 110.8243 | 255.9825 | 87.3041 | 204.7381 | 606.8762 | 1045.8274 | 351.2976 | 3160.7915
2027-02-07 23:00 | 17.3037 | 212.3788 | 247.6962 | 109.4656 | 253.1256 | 86.1849 | 203.1493 | 591.7034 | 1030.2621 | 342.9849 | 3094.2547
2027-02-14 23:00 | 17.8693 | 211.7967 | 246.9669 | 111.7717 | 248.9021 | 90.6383 | 194.7779 | 593.4029 | 1021.9318 | 350.5433 | 3088.6008
2027-02-21 23:00 | 17.2491 | 202.139 | 236.3906 | 108.1837 | 252.8398 | 83.684 | 196.5738 | 581.1765 | 1012.4044 | 336.3155 | 3026.9563
2027-02-28 23:00 | 16.8334 | 195.5371 | 227.2931 | 109.1871 | 239.2621 | 81.8673 | 193.4809 | 588.6811 | 1028.1987 | 345.6171 | 3025.9577
2027-03-07 23:00 | 16.9892 | 194.4065 | 227.6257 | 101.3201 | 245.7571 | 86.8828 | 183.0999 | 575.0673 | 990.0091 | 327.8028 | 2948.9606
2027-03-14 23:00 | 16.5178 | 186.03 | 217.0065 | 99.8656 | 238.8853 | 81.3014 | 185.8902 | 561.5097 | 982.4024 | 320.1471 | 2889.5561
2027-03-21 23:00 | 17.0524 | 183.3886 | 212.1225 | 97.7407 | 226.7341 | 74.8658 | 177.9697 | 554.6654 | 966.4388 | 312.0715 | 2823.0494
2027-03-28 23:00 | 16.2193 | 173.3608 | 201.9965 | 94.8358 | 227.4719 | 75.1627 | 171.5134 | 534.2112 | 928.5116 | 307.8817 | 2731.1649
2027-04-04 23:00 | 15.1863 | 172.892 | 194.3031 | 91.6472 | 225.2054 | 73.8065 | 167.0716 | 525.1442 | 919.8594 | 305.0676 | 2690.1834
2027-04-11 23:00 | 14.8728 | 174.192 | 191.5847 | 86.0783 | 225.9766 | 75.0468 | 162.2436 | 507.5606 | 913.4122 | 292.2871 | 2643.2547
2027-04-18 23:00 | 13.5185 | 156.7893 | 173.5648 | 85.8468 | 215.1712 | 69.525 | 152.6432 | 513.6975 | 906.4003 | 296.269 | 2583.4256
2027-04-25 23:00 | 14.8303 | 162.3441 | 180.3937 | 83.0663 | 214.5859 | 67.7813 | 155.1684 | 492.6583 | 900.1308 | 282.7164 | 2553.6755
2027-05-02 23:00 | 13.6189 | 154.6822 | 173.0581 | 83.6152 | 207.9735 | 65.9657 | 150.401 | 502.9377 | 887.0754 | 289.9555 | 2529.2832
2027-05-09 23:00 | 14.1237 | 153.3869 | 178.5574 | 84.3259 | 199.5603 | 62.7479 | 150.8317 | 495.6852 | 892.0185 | 280.5183 | 2511.7559
2027-05-16 23:00 | 12.8759 | 143.3559 | 172.2225 | 85.6445 | 195.6841 | 61.0716 | 149.9012 | 503.0427 | 893.7365 | 290.7355 | 2508.2706
2027-05-23 23:00 | 12.3103 | 145.318 | 171.0682 | 86.7491 | 194.1073 | 60.0281 | 154.5631 | 506.9717 | 906.0883 | 290.7376 | 2527.9417
2027-05-30 23:00 | 12.8389 | 145.202 | 173.393 | 86.5821 | 192.7024 | 59.8737 | 146.3201 | 499.7986 | 887.6276 | 293.3561 | 2497.6944
2027-06-06 23:00 | 11.8432 | 147.263 | 178.6875 | 93.9065 | 189.5195 | 59.2481 | 158.8668 | 526.8305 | 946.4948 | 308.5624 | 2621.2222
2027-06-13 23:00 | 11.4759 | 146.5039 | 180.7045 | 95.9649 | 188.232 | 59.6517 | 162.6061 | 546.2858 | 950.0439 | 324.4546 | 2665.9233
2027-06-20 23:00 | 11.9938 | 156.667 | 191.9288 | 99.0974 | 186.2276 | 58.1345 | 177.7183 | 553.4092 | 1000.9401 | 331.329 | 2767.4456
2027-06-27 23:00 | 11.0562 | 160.4813 | 197.1402 | 103.0612 | 181.7254 | 59.093 | 173.2624 | 562.6144 | 1048.6982 | 337.5123 | 2834.6447
2027-07-04 23:00 | 11.0405 | 171.819 | 207.9843 | 102.0867 | 188.9254 | 59.3932 | 185.1711 | 553.3726 | 1016.5634 | 338.0408 | 2834.3971
2027-07-11 23:00 | 10.6441 | 165.6654 | 195.7623 | 106.314 | 194.5617 | 61.8036 | 167.8411 | 610.1882 | 1051.138 | 366.1383 | 2930.0568
2027-07-18 23:00 | 11.2178 | 173.9056 | 205.6644 | 106.4081 | 199.8524 | 64.2481 | 181.5368 | 594.0628 | 1092.1423 | 359.5972 | 2988.6355
2027-07-25 23:00 | 11.8569 | 168.9694 | 199.4173 | 106.8146 | 206.0102 | 66.9658 | 176.1471 | 618.8341 | 1064.9705 | 370.6166 | 2990.6025
2027-08-01 23:00 | 11.8171 | 176.7869 | 207.2605 | 107.4413 | 192.6808 | 61.4883 | 181.6664 | 592.0145 | 1084.1357 | 361.1701 | 2976.4618
2027-08-08 23:00 | 13.1267 | 172.0542 | 203.1869 | 105.436 | 197.0889 | 61.3656 | 179.5369 | 568.1643 | 1067.0004 | 357.3527 | 2924.3126
2027-08-15 23:00 | 12.6979 | 167.0876 | 196.2612 | 106.5143 | 194.7431 | 62.9888 | 169.5451 | 591.796 | 1043.969 | 367.982 | 2913.585
2027-08-22 23:00 | 12.3982 | 171.3173 | 201.8094 | 103.6152 | 204.7555 | 65.156 | 170.1433 | 566.8133 | 1039.1919 | 346.6875 | 2881.8878
2027-08-29 23:00 | 12.7884 | 170.5622 | 204.7984 | 102.8512 | 196.2431 | 62.726 | 180.2977 | 549.9151 | 1044.669 | 346.75 | 2871.6012
2027-09-05 23:00 | 13.1045 | 161.7767 | 184.4257 | 101.3744 | 203.7474 | 64.8022 | 157.5477 | 579.7745 | 989.7185 | 365.333 | 2821.6047
2027-09-12 23:00 | 13.3815 | 157.5633 | 177.0099 | 93.8088 | 202.7067 | 62.3822 | 157.7267 | 527.6635 | 947.3114 | 342.2305 | 2681.7844
2027-09-19 23:00 | 12.3934 | 156.3611 | 177.6919 | 92.8274 | 200.4264 | 63.5078 | 155.4429 | 521.8046 | 962.036 | 336.5354 | 2679.0268
2027-09-26 23:00 | 12.5846 | 151.4796 | 173.2732 | 93.2846 | 200.1043 | 62.2202 | 152.1841 | 531.7431 | 937.4301 | 341.6178 | 2655.9217
2027-10-03 23:00 | 11.7908 | 153.8976 | 174.7852 | 93.7631 | 195.4967 | 60.9122 | 145.3958 | 527.6135 | 919.8983 | 349.1774 | 2632.7306
2027-10-10 23:00 | 12.1381 | 162.8965 | 179.5187 | 92.9094 | 206.8644 | 66.4038 | 150.1419 | 508.165 | 904.1641 | 334.5571 | 2617.7591
2027-10-17 23:00 | 13.216 | 167.9717 | 185.0808 | 91.9996 | 205.8102 | 69.5682 | 151.6519 | 498.1891 | 882.3278 | 332.6926 | 2598.5078
2027-10-24 23:00 | 12.57 | 168.1114 | 184.3655 | 95.3499 | 202.9488 | 71.7187 | 149.1634 | 518.9436 | 919.3538 | 346.731 | 2669.2561
2027-10-31 23:00 | 13.5262 | 174.6648 | 191.5522 | 95.4919 | 209.5316 | 75.523 | 154.0423 | 526.1564 | 925.6645 | 348.026 | 2714.1789
2027-11-07 23:00 | 13.4338 | 172.3065 | 192.5082 | 98.6533 | 213.4828 | 74.1904 | 162.5218 | 534.6771 | 949.1337 | 364.2302 | 2775.1376
2027-11-14 23:00 | 13.3716 | 176.8293 | 199.8677 | 100.6356 | 216.6037 | 78.7842 | 161.7099 | 549.2912 | 958.1809 | 372.9076 | 2828.1816
2027-11-21 23:00 | 15.0594 | 192.2113 | 215.5706 | 102.1951 | 224.5128 | 81.176 | 175.482 | 556.0862 | 982.4989 | 373.124 | 2917.9162
2027-11-28 23:00 | 16.0161 | 198.5814 | 221.2646 | 105.2141 | 226.8222 | 85.2375 | 175.0645 | 571.1195 | 1004.071 | 378.5166 | 2981.9074
2027-12-05 23:00 | 16.5515 | 199.9891 | 233.3746 | 107.8894 | 228.0026 | 85.5945 | 180.1451 | 585.4656 | 1021.3558 | 390.1146 | 3048.4828
2027-12-12 23:00 | 17.1538 | 207.5879 | 248.1098 | 107.4915 | 243.6944 | 94.4665 | 189.7113 | 587.4977 | 1023.429 | 385.4328 | 3104.5749
2027-12-19 23:00 | 16.9165 | 207.9043 | 247.7958 | 108.7664 | 238.3003 | 86.5235 | 199.0386 | 596.3036 | 1037.3668 | 388.9726 | 3127.8884
2027-12-26 23:00 | 17.0958 | 213.0234 | 255.0484 | 107.9606 | 245.6014 | 88.1768 | 203.1008 | 589.4916 | 1034.4154 | 384.8092 | 3138.7234
2028-01-02 23:00 | 16.4722 | 202.9202 | 249.6424 | 106.9111 | 234.1779 | 90.1791 | 185.1963 | 576.6164 | 985.783 | 387.0126 | 3034.9114
Back to main menu

## Table 1.1.3 Planned
Back to main menu
Table 1.1.3 Planned: Weekly Energy Demand by Zone
Week Ending | Planned Weekly Normal Energy (GWh)
| Bruce | East | Essa | Niagara | NorthEast | NorthWest | Ottawa | SouthWest | Toronto | West | Ontario
2026-07-05 23:00 | 11.1656 | 165.3466 | 191.6136 | 97.9027 | 195.3538 | 61.3116 | 163.9037 | 569.5959 | 1007.9103 | 304.2006 | 2768.3044
2026-07-12 23:00 | 10.5877 | 170.0942 | 196.6121 | 99.3613 | 203.2361 | 64.3882 | 175.9348 | 588.227 | 1053.1545 | 312.5242 | 2874.12
2026-07-19 23:00 | 11.6963 | 173.3493 | 204.997 | 103.0812 | 190.788 | 62.2494 | 175.5039 | 594.6038 | 1076.2637 | 326.2992 | 2918.8318
2026-07-26 23:00 | 11.8565 | 172.6206 | 204.722 | 103.0507 | 190.4748 | 62.9872 | 174.8007 | 595.5453 | 1073.2063 | 328.1511 | 2917.4153
2026-08-02 23:00 | 11.8177 | 168.3392 | 198.4751 | 100.8629 | 202.4982 | 65.5454 | 177.7071 | 586.2399 | 1075.5029 | 315.5942 | 2902.5826
2026-08-09 23:00 | 12.7662 | 164.5594 | 195.3789 | 101.6732 | 198.5059 | 64.9214 | 169.9205 | 576.361 | 1042.1011 | 318.8958 | 2845.0833
2026-08-16 23:00 | 12.4527 | 160.9041 | 190.5193 | 103.5646 | 197.1021 | 61.8276 | 164.3612 | 586.5259 | 1038.2877 | 322.3625 | 2837.9077
2026-08-23 23:00 | 12.7331 | 166.6906 | 194.8859 | 101.8804 | 199.3761 | 63.0197 | 164.3706 | 570.6161 | 1025.7838 | 311.9938 | 2811.3501
2026-08-30 23:00 | 13.1138 | 162.8953 | 189.8655 | 100.9619 | 203.5607 | 63.7915 | 159.7392 | 561.6091 | 1032.5723 | 306.8194 | 2794.9288
2026-09-06 23:00 | 13.8733 | 164.5545 | 184.8006 | 96.0924 | 204.414 | 63.4228 | 160.0296 | 544.5138 | 982.5415 | 319.4641 | 2733.7066
2026-09-13 23:00 | 13.85 | 156.2008 | 175.4146 | 91.9031 | 193.3799 | 60.8007 | 150.9066 | 519.7212 | 923.3785 | 310.1413 | 2595.6966
2026-09-20 23:00 | 13.2203 | 158.1241 | 176.6119 | 90.9252 | 191.962 | 60.8147 | 155.8143 | 518.1852 | 926.3808 | 306.749 | 2598.7875
2026-09-27 23:00 | 13.6555 | 156.2868 | 178.7285 | 88.932 | 202.2009 | 65.9426 | 151.8006 | 512.752 | 909.8152 | 297.7926 | 2577.9067
2026-10-04 23:00 | 11.8063 | 152.9435 | 172.2421 | 90.4765 | 202.3282 | 61.2965 | 148.8634 | 506.6529 | 906.102 | 294.2713 | 2546.9827
2026-10-11 23:00 | 12.0438 | 159.253 | 175.4956 | 92.5735 | 200.5092 | 62.0315 | 148.233 | 494.6161 | 892.3794 | 299.0207 | 2536.1558
2026-10-18 23:00 | 11.7963 | 158.99 | 174.5279 | 92.3612 | 199.9017 | 62.3624 | 147.2648 | 490.8081 | 882.4851 | 298.3227 | 2518.8203
2026-10-25 23:00 | 13.149 | 167.6204 | 184.2494 | 92.8966 | 204.1879 | 67.4369 | 152.2742 | 512.8639 | 893.3781 | 302.369 | 2590.4255
2026-11-01 23:00 | 12.5087 | 170.4847 | 186.1985 | 95.2837 | 208.0734 | 67.8541 | 159.2728 | 519.3681 | 910.2649 | 310.9425 | 2640.2512
2026-11-08 23:00 | 14.1713 | 178.7147 | 199.4618 | 97.3325 | 209.2261 | 73.3563 | 153.2662 | 536.0296 | 912.3981 | 326.8231 | 2700.7798
2026-11-15 23:00 | 14.4438 | 185.091 | 208.3732 | 97.2645 | 219.8087 | 78.7969 | 161.0282 | 539.223 | 929.2924 | 325.5851 | 2758.9069
2026-11-22 23:00 | 14.8308 | 190.7399 | 215.1422 | 100.3921 | 226.3417 | 75.9986 | 173.1678 | 549.7367 | 968.8363 | 330.1016 | 2845.2877
2026-11-29 23:00 | 15.7056 | 199.0501 | 221.3403 | 104.3579 | 224.6158 | 79.4478 | 174.6892 | 564.3879 | 984.4411 | 343.5564 | 2911.592
2026-12-06 23:00 | 16.0394 | 197.1315 | 235.218 | 106.6807 | 231.1352 | 85.2856 | 181.8896 | 585.654 | 997.0516 | 347.1509 | 2983.2363
2026-12-13 23:00 | 17.4781 | 207.5391 | 248.9463 | 106.047 | 235.0806 | 87.6562 | 186.2984 | 592.1659 | 1001.875 | 348.1019 | 3031.1886
2026-12-20 23:00 | 16.9201 | 209.5708 | 250.6313 | 106.7452 | 239.3686 | 86.6714 | 196.3999 | 591.0047 | 1001.5956 | 352.3634 | 3051.2712
2026-12-27 23:00 | 16.1963 | 202.0649 | 242.0123 | 104.7989 | 236.9267 | 87.1914 | 188.268 | 571.0199 | 962.3349 | 342.3022 | 2953.1156
2027-01-03 23:00 | 16.8279 | 208.0962 | 247.4317 | 103.4633 | 243.8612 | 87.619 | 188.4504 | 566.2354 | 951.5458 | 332.7358 | 2946.2668
2027-01-10 23:00 | 17.2861 | 217.7782 | 252.3146 | 109.1864 | 253.0913 | 91.562 | 198.0151 | 611.4237 | 1023.1225 | 351.1009 | 3124.8809
2027-01-17 23:00 | 18.4713 | 223.9719 | 258.5139 | 109.6233 | 252.8873 | 88.4055 | 205.1428 | 612.4578 | 1026.2349 | 348.3982 | 3144.107
2027-01-24 23:00 | 19.0456 | 225.6875 | 261.3284 | 110.9488 | 254.8755 | 91.5006 | 201.855 | 622.7219 | 1031.3782 | 350.8683 | 3170.2097
2027-01-31 23:00 | 19.7435 | 220.4872 | 257.6902 | 110.8198 | 255.9721 | 87.3005 | 204.7298 | 614.047 | 1045.7847 | 351.2834 | 3167.8581
2027-02-07 23:00 | 17.3027 | 212.3659 | 247.6812 | 109.459 | 253.1103 | 86.1797 | 203.137 | 601.2597 | 1030.1998 | 342.9643 | 3103.6596
2027-02-14 23:00 | 17.8698 | 211.8021 | 246.9731 | 111.7745 | 248.9086 | 90.6407 | 194.7828 | 602.7443 | 1021.9573 | 350.5525 | 3098.0057
2027-02-21 23:00 | 17.2473 | 202.1184 | 236.3664 | 108.1726 | 252.814 | 83.6754 | 196.5536 | 590.8319 | 1012.3003 | 336.2813 | 3036.3611
2027-02-28 23:00 | 16.8303 | 195.5013 | 227.2514 | 109.1671 | 239.2183 | 81.8523 | 193.4454 | 598.5326 | 1028.01 | 345.5539 | 3035.3626
2027-03-07 23:00 | 16.9896 | 194.4107 | 227.6305 | 101.3222 | 245.7624 | 86.8847 | 183.1037 | 585.2295 | 990.0295 | 327.8099 | 2959.1727
2027-03-14 23:00 | 16.5178 | 186.0298 | 217.0062 | 99.8654 | 238.8849 | 81.3013 | 185.89 | 571.7253 | 982.4007 | 320.1468 | 2899.7681
2027-03-21 23:00 | 17.0535 | 183.4001 | 212.1358 | 97.7468 | 226.7482 | 74.8705 | 177.9808 | 564.7364 | 966.4987 | 312.0908 | 2833.2614
2027-03-28 23:00 | 16.7076 | 173.0615 | 204.8916 | 94.8304 | 228.1519 | 76.8182 | 170.758 | 544.0374 | 927.4462 | 304.6742 | 2741.3769
2027-04-04 23:00 | 15.1865 | 172.8943 | 194.3055 | 91.6483 | 225.2084 | 73.8075 | 167.0735 | 536.417 | 919.8697 | 305.0711 | 2701.4818
2027-04-11 23:00 | 14.8731 | 174.1954 | 191.5885 | 86.08 | 225.9809 | 75.0483 | 162.2468 | 519.7133 | 913.4302 | 292.293 | 2655.4494
2027-04-18 23:00 | 14.3416 | 161.8295 | 179.1552 | 86.3712 | 214.8185 | 66.8162 | 151.3962 | 522.1242 | 902.4187 | 296.3488 | 2595.6203
2027-04-25 23:00 | 14.831 | 162.3515 | 180.4022 | 83.0701 | 214.5957 | 67.7844 | 155.1755 | 504.758 | 900.1722 | 282.7297 | 2565.8702
2027-05-02 23:00 | 13.6185 | 154.6785 | 173.0535 | 83.6131 | 207.9684 | 65.9644 | 150.3977 | 515.0441 | 887.0562 | 291.3324 | 2542.7268
2027-05-09 23:00 | 14.1216 | 153.3641 | 178.5313 | 84.3135 | 199.5305 | 62.7386 | 150.8098 | 507.6579 | 891.8882 | 285.3246 | 2528.28
2027-05-16 23:00 | 12.8737 | 143.3305 | 172.1921 | 85.6292 | 195.6493 | 61.0607 | 149.8743 | 515.0543 | 893.5762 | 295.5544 | 2524.7948
2027-05-23 23:00 | 13.3373 | 146.5322 | 176.0128 | 85.7731 | 199.3767 | 64.5558 | 151.3472 | 513.889 | 901.7766 | 291.865 | 2544.4658
2027-05-30 23:00 | 12.8379 | 145.1891 | 173.3782 | 86.5745 | 192.6853 | 59.8685 | 146.3076 | 511.6914 | 887.5516 | 298.1345 | 2514.2186
2027-06-06 23:00 | 11.8409 | 147.2346 | 178.6535 | 93.8882 | 189.4826 | 59.2365 | 158.8364 | 539.2524 | 946.3136 | 314.3816 | 2639.1202
2027-06-13 23:00 | 11.474 | 146.4806 | 180.6755 | 95.9496 | 188.2015 | 59.6419 | 162.5798 | 558.6894 | 949.8897 | 330.4228 | 2684.0048
2027-06-20 23:00 | 11.9942 | 156.6712 | 191.9339 | 99.1002 | 186.2325 | 58.1362 | 177.7225 | 565.5751 | 1000.9675 | 337.1938 | 2785.5271
2027-06-27 23:00 | 11.0572 | 160.4959 | 197.159 | 103.0708 | 181.7413 | 59.0983 | 173.2784 | 574.6894 | 1048.7982 | 343.3376 | 2852.7262
2027-07-04 23:00 | 10.9237 | 164.9305 | 200.8447 | 102.3458 | 185.9767 | 59.0125 | 183.139 | 579.4682 | 1030.6885 | 341.9513 | 2859.2809
2027-07-11 23:00 | 10.641 | 165.6161 | 195.7051 | 106.2829 | 194.5038 | 61.7854 | 167.7912 | 633.8524 | 1050.8296 | 373.0555 | 2960.063
2027-07-18 23:00 | 11.2142 | 173.8505 | 205.5994 | 106.3742 | 199.7881 | 64.2276 | 181.4788 | 617.7865 | 1091.7947 | 366.5276 | 3018.6418
2027-07-25 23:00 | 11.8469 | 168.8259 | 199.2488 | 106.7243 | 205.8355 | 66.9093 | 175.9985 | 643.4392 | 1064.0747 | 377.7057 | 3020.6087
2027-08-01 23:00 | 11.817 | 176.7846 | 207.2583 | 107.4399 | 192.6778 | 61.4874 | 181.6643 | 615.5288 | 1084.1227 | 368.1961 | 3006.977
2027-08-08 23:00 | 12.7022 | 167.0004 | 200.0321 | 107.0181 | 196.7303 | 63.9851 | 168.0101 | 620.3144 | 1044.1468 | 378.018 | 2957.9575
2027-08-15 23:00 | 12.6979 | 167.0882 | 196.2626 | 106.5147 | 194.7423 | 62.9888 | 169.546 | 617.2406 | 1043.9746 | 376.1743 | 2947.2299
2027-08-22 23:00 | 12.3934 | 171.2503 | 201.7312 | 103.5746 | 204.6746 | 65.1305 | 170.0772 | 592.8926 | 1038.7889 | 355.0193 | 2915.5327
2027-08-29 23:00 | 12.7928 | 170.6209 | 204.8689 | 102.8862 | 196.3102 | 62.7476 | 180.3595 | 574.8095 | 1045.0273 | 354.8231 | 2905.246
2027-09-05 23:00 | 13.3945 | 166.2869 | 192.8642 | 100.5614 | 194.5957 | 60.9768 | 164.3092 | 579.9129 | 1025.7386 | 360.3555 | 2858.9957
2027-09-12 23:00 | 13.3766 | 157.5056 | 176.9449 | 93.774 | 202.6315 | 62.359 | 157.6684 | 557.3469 | 946.9597 | 352.154 | 2720.7205
2027-09-19 23:00 | 12.3907 | 156.3265 | 177.6531 | 92.8066 | 200.381 | 63.4936 | 155.4071 | 551.2725 | 961.8187 | 346.4132 | 2717.9629
2027-09-26 23:00 | 12.5816 | 151.4426 | 173.232 | 93.2625 | 200.0559 | 62.2051 | 152.1465 | 561.2322 | 937.2001 | 351.4993 | 2694.8578
2027-10-03 23:00 | 12.3032 | 153.9957 | 175.5655 | 91.3896 | 198.44 | 66.2382 | 150.0265 | 560.013 | 907.3448 | 357.2661 | 2672.5826
2027-10-10 23:00 | 12.1362 | 162.8713 | 179.4906 | 92.8947 | 206.8325 | 66.3935 | 150.1182 | 539.8415 | 904.0214 | 344.0844 | 2658.6845
2027-10-17 23:00 | 12.7024 | 164.3868 | 179.1055 | 91.5762 | 204.6693 | 68.3445 | 150.2119 | 532.5241 | 892.5523 | 343.3601 | 2639.4331
2027-10-24 23:00 | 12.5713 | 168.1305 | 184.386 | 95.3605 | 202.9727 | 71.727 | 149.1799 | 550.2141 | 919.4537 | 356.1857 | 2710.1815
2027-10-31 23:00 | 13.5285 | 174.6948 | 191.5847 | 95.5082 | 209.5675 | 75.5359 | 154.0684 | 557.3322 | 925.8219 | 357.4623 | 2755.1042
2027-11-07 23:00 | 13.428 | 172.2323 | 192.4259 | 98.6107 | 213.3893 | 74.1585 | 162.4519 | 571.9708 | 948.7265 | 374.124 | 2821.5179
2027-11-14 23:00 | 13.6354 | 181.5828 | 204.4869 | 100.1671 | 217.6381 | 76.857 | 164.6205 | 580.0991 | 964.5957 | 370.8793 | 2874.5619
2027-11-21 23:00 | 13.4581 | 184.9396 | 208.6643 | 102.8493 | 227.1586 | 79.6834 | 173.7982 | 596.093 | 991.0886 | 386.5635 | 2964.2965
2027-11-28 23:00 | 14.371 | 193.1491 | 214.1231 | 106.7761 | 227.6503 | 82.6111 | 174.7667 | 606.43 | 1011.0329 | 397.3774 | 3028.2877
2027-12-05 23:00 | 16.3693 | 200.5414 | 234.95 | 105.9175 | 232.9233 | 85.5371 | 192.9408 | 612.6691 | 1021.3931 | 393.94 | 3097.1816
2027-12-12 23:00 | 17.1532 | 207.5809 | 248.1016 | 107.4875 | 243.6868 | 94.4637 | 189.7043 | 627.6876 | 1023.3903 | 394.9247 | 3154.1806
2027-12-19 23:00 | 16.9092 | 207.8143 | 247.6886 | 108.7189 | 238.1965 | 86.4859 | 198.9523 | 637.2646 | 1036.9169 | 398.5469 | 3177.4941
2027-12-26 23:00 | 17.0917 | 212.9726 | 254.9875 | 107.9346 | 245.5417 | 88.1555 | 203.0524 | 630.0791 | 1034.1694 | 394.3446 | 3188.3291
2028-01-02 23:00 | 16.4631 | 202.8083 | 249.5045 | 106.8518 | 234.0485 | 90.1293 | 185.0941 | 617.7977 | 985.2396 | 396.6263 | 3084.5632
Back to main menu

## Table 1.2 Firm
Back to main menu
Table 1.2 Firm: Forecasted Seasonal Peaks
Season | Firm Normal Weather Peak (MW) | Firm Extreme Weather Peak (MW)
Summer 2026 | 23592.6172 | 25887.8938
Winter 2026-27 | 22691.8172 | 23735.7931
Summer 2027 | 23950.1198 | 26311.387
Back to main menu

## Table 1.2 Planned
Back to main menu
Table 1.2 Planned: Forecasted Seasonal Peaks
Season | Planned Normal Weather Peak (MW) | Planned Extreme Weather Peak (MW)
Summer 2026 | 23592.6172 | 25887.8938
Winter 2026-27 | 22731.4904 | 23777.0674
Summer 2027 | 24123.2668 | 26481.5876
Back to main menu

## Table 1.3
Back to main menu
Table 1.3: Large Step Load Impacts, Firm and Planned Demand
| Firm |  | Planned
Demand Forecast | Energy (GWh) | Peak (MW) | Energy (GWh) | Peak (MW)
Summer 2026 | 278.6444 | 144.3374 | 278.6444 | 144.3374
Winter 2026-27 | 601.0349 | 349.7562 | 701.3536 | 405.4428
Summer 2027 | 1008.687 | 518.1354 | 1368.0429 | 716.8142
Back to main menu

## Table 1.4 Firm
Back to main menu
Table 1.4 Firm: Weekly Energy and Peak Demand Forecast
Week | Firm Normal Peak | Firm Extreme Peak | Load Forecast Uncertainty | Firm Normal Energy Demand
Week Ending | (MW) | (MW) | (MW) | (GWh)
2026-07-05 23:00 | 21396.806 | 24526.1213 | 1713.5289 | 2768.3044
2026-07-12 23:00 | 22068.091 | 25428.7201 | 1804.8307 | 2874.12
2026-07-19 23:00 | 22267.7409 | 25531.7583 | 1731.1839 | 2918.8318
2026-07-26 23:00 | 22247.3853 | 25538.9913 | 1785.9605 | 2917.4153
2026-08-02 23:00 | 22049.4367 | 25298.7685 | 1743.6169 | 2902.5826
2026-08-09 23:00 | 21574.2457 | 24986.479 | 1795.4011 | 2845.0833
2026-08-16 23:00 | 21548.5929 | 24621.3206 | 1632.57 | 2837.9077
2026-08-23 23:00 | 21385.3888 | 24072.6327 | 1457.2797 | 2811.3501
2026-08-30 23:00 | 21371.9894 | 23978.3225 | 1441.5837 | 2794.9288
2026-09-06 23:00 | 20980.3781 | 24315.8783 | 1788.9372 | 2733.7066
2026-09-13 23:00 | 19831.9049 | 23925.1325 | 2008.6081 | 2595.6966
2026-09-20 23:00 | 19389.5324 | 22982.5572 | 1730.6165 | 2598.7875
2026-09-27 23:00 | 18949.1082 | 22396.4312 | 1605.8954 | 2577.9067
2026-10-04 23:00 | 18599.1085 | 21371.1508 | 1285.0451 | 2546.9827
2026-10-11 23:00 | 18092.0394 | 19940.1872 | 880.7728 | 2536.1558
2026-10-18 23:00 | 18093.733 | 19290.574 | 619.7428 | 2518.8203
2026-10-25 23:00 | 18351.5744 | 19251.3849 | 473.36 | 2590.4255
2026-11-01 23:00 | 18641.0261 | 19530.0163 | 475.763 | 2639.3616
2026-11-08 23:00 | 19179.7407 | 20142.6969 | 508.4769 | 2694.6904
2026-11-15 23:00 | 19689.3124 | 20997.7089 | 673.689 | 2752.8175
2026-11-22 23:00 | 20252.4004 | 21493.5009 | 655.3915 | 2839.1983
2026-11-29 23:00 | 20763.968 | 21783.1669 | 560.7902 | 2905.5026
2026-12-06 23:00 | 21153.9501 | 22193.9261 | 571.1375 | 2976.2788
2026-12-13 23:00 | 21470.6251 | 22749.7495 | 690.9023 | 3024.1047
2026-12-20 23:00 | 21685.2389 | 23019.5116 | 716.129 | 3044.1873
2026-12-27 23:00 | 21093.1629 | 22471.8481 | 731.1707 | 2946.0318
2027-01-03 23:00 | 21065.9277 | 22456.3623 | 737.546 | 2939.1656
2027-01-10 23:00 | 21948.9109 | 23525.3016 | 836.9625 | 3117.8143
2027-01-17 23:00 | 21839.3056 | 23459.5545 | 858.1992 | 3137.0404
2027-01-24 23:00 | 21903.6033 | 23604.1317 | 893.3354 | 3163.1431
2027-01-31 23:00 | 21890.2994 | 23509.2987 | 851.2674 | 3160.7915
2027-02-07 23:00 | 21371.8652 | 22806.8782 | 768.9404 | 3094.2547
2027-02-14 23:00 | 21373.1834 | 22810.797 | 766.6268 | 3088.6008
2027-02-21 23:00 | 21085 | 22529.6675 | 772.3928 | 3026.9563
2027-02-28 23:00 | 20931.1226 | 22249.9692 | 705.8723 | 3025.9577
2027-03-07 23:00 | 20398.7084 | 21670.49 | 692.705 | 2948.9606
2027-03-14 23:00 | 19962.359 | 21206.0956 | 689.5613 | 2889.5561
2027-03-21 23:00 | 19446.3412 | 20654.0636 | 641.2432 | 2823.0494
2027-03-28 23:00 | 19023.4433 | 20000.6961 | 553.4418 | 2731.1649
2027-04-04 23:00 | 18589.3982 | 19646.2459 | 560.5975 | 2690.1834
2027-04-11 23:00 | 18231.1751 | 19274.8182 | 569.2375 | 2643.2547
2027-04-18 23:00 | 17897.2985 | 19279.7203 | 719.6402 | 2583.4256
2027-04-25 23:00 | 17644.8513 | 18867.1886 | 643.7582 | 2553.6755
2027-05-02 23:00 | 17460.0087 | 18627.7123 | 612.6004 | 2529.2832
2027-05-09 23:00 | 17377.2422 | 18859.3917 | 746.1358 | 2511.7559
2027-05-16 23:00 | 17464.2971 | 19457.9879 | 969.049 | 2508.2706
2027-05-23 23:00 | 18148.9467 | 20612.3742 | 1307.7464 | 2527.9417
2027-05-30 23:00 | 18208.8078 | 22654.2556 | 2034.8531 | 2497.6944
2027-06-06 23:00 | 19060.487 | 23686.5686 | 2183.5316 | 2621.2222
2027-06-13 23:00 | 19550.0301 | 24069.6437 | 2176.7571 | 2665.9233
2027-06-20 23:00 | 20597.4928 | 24828.2721 | 2123.8008 | 2767.4456
2027-06-27 23:00 | 21473.5568 | 24687.2453 | 1748.9026 | 2834.6447
2027-07-04 23:00 | 21490.9768 | 24657.5271 | 1720.4203 | 2834.3971
2027-07-11 23:00 | 22236.778 | 25600.9952 | 1805.392 | 2930.0568
2027-07-18 23:00 | 22448.6626 | 25730.6934 | 1776.2444 | 2988.6355
2027-07-25 23:00 | 22459.9822 | 25764.9149 | 1794.3197 | 2990.6025
2027-08-01 23:00 | 22312.64 | 25482.7345 | 1682.3722 | 2976.4618
2027-08-08 23:00 | 21860.8689 | 25250.8883 | 1789.7942 | 2924.3126
2027-08-15 23:00 | 21820.128 | 24968.7148 | 1666.1063 | 2913.585
2027-08-22 23:00 | 21614.2644 | 24385.6572 | 1493.868 | 2881.8878
2027-08-29 23:00 | 21633.9319 | 24182.2036 | 1411.3369 | 2871.6012
2027-09-05 23:00 | 21311.1592 | 24566.2498 | 1751.8942 | 2821.6047
2027-09-12 23:00 | 20203.5027 | 24226.2481 | 1994.1296 | 2681.7844
2027-09-19 23:00 | 19731.367 | 23395.8993 | 1770.1976 | 2679.0268
2027-09-26 23:00 | 19264.9503 | 22820.4837 | 1644.0278 | 2655.9217
2027-10-03 23:00 | 19178.1919 | 21499.4222 | 1232.3517 | 2632.7306
2027-10-10 23:00 | 18408.35 | 20371.4901 | 927.3887 | 2617.7591
2027-10-17 23:00 | 18398.3578 | 19657.3033 | 647.4782 | 2598.5078
2027-10-24 23:00 | 18628.2892 | 19523.3188 | 470.556 | 2669.2561
2027-10-31 23:00 | 18910.3862 | 19812.9282 | 484.7125 | 2714.1789
2027-11-07 23:00 | 19461.0074 | 20402.1127 | 498.9884 | 2775.1376
2027-11-14 23:00 | 19917.5905 | 21130.409 | 632.01 | 2828.1816
2027-11-21 23:00 | 20490.2726 | 21755.7517 | 665.8711 | 2917.9162
2027-11-28 23:00 | 21034.5501 | 22084.627 | 574.9633 | 2981.9074
2027-12-05 23:00 | 21393.8971 | 22418.7437 | 564.9823 | 3048.4828
2027-12-12 23:00 | 21756.458 | 23010.9789 | 677.5458 | 3104.5749
2027-12-19 23:00 | 21990.8301 | 23321.8414 | 712.2488 | 3127.8884
2027-12-26 23:00 | 22011.1762 | 23364.2228 | 722.5903 | 3138.7234
2028-01-02 23:00 | 21759.6694 | 23311.693 | 834.75 | 3034.9114
Back to main menu

## Table 1.4 Planned
Back to main menu
Table 1.4 Planned: Weekly Energy and Peak Demand Forecast
Week | Planned Normal Peak | Planned Extreme Peak | Load Forecast Uncertainty | Planned Normal Energy Demand
Week Ending | (MW) | (MW) | (MW) | (GWh)
2026-07-05 23:00 | 21396.3019 | 24526.9438 | 1712.9338 | 2768.3044
2026-07-12 23:00 | 22069.0917 | 25428.3953 | 1804.454 | 2874.12
2026-07-19 23:00 | 22267.2414 | 25532.3502 | 1732.3949 | 2918.8318
2026-07-26 23:00 | 22246.6329 | 25539.1888 | 1786.0592 | 2917.4153
2026-08-02 23:00 | 22049.609 | 25300.645 | 1742.6001 | 2902.5826
2026-08-09 23:00 | 21574.8785 | 24987.4127 | 1794.7044 | 2845.0833
2026-08-16 23:00 | 21548.056 | 24621.3887 | 1632.511 | 2837.9077
2026-08-23 23:00 | 21386.0604 | 24072.3907 | 1456.3156 | 2811.3501
2026-08-30 23:00 | 21370.9905 | 23977.0524 | 1442.617 | 2794.9288
2026-09-06 23:00 | 20980.3902 | 24315.7177 | 1788.81 | 2733.7066
2026-09-13 23:00 | 19832.2425 | 23922.867 | 2009.2182 | 2595.6966
2026-09-20 23:00 | 19389.5633 | 22980.1259 | 1729.8153 | 2598.7875
2026-09-27 23:00 | 18949.8784 | 22396.1702 | 1605.0828 | 2577.9067
2026-10-04 23:00 | 18598.9724 | 21372.4374 | 1285.2387 | 2546.9827
2026-10-11 23:00 | 18092.1711 | 19940.1897 | 881.1839 | 2536.1558
2026-10-18 23:00 | 18093.4519 | 19290.7106 | 619.7529 | 2518.8203
2026-10-25 23:00 | 18351.5839 | 19251.1497 | 473.5571 | 2590.4255
2026-11-01 23:00 | 18640.366 | 19531.5849 | 476.0595 | 2640.2512
2026-11-08 23:00 | 19214.4312 | 20177.036 | 508.6541 | 2700.7798
2026-11-15 23:00 | 19723.528 | 21032.126 | 673.665 | 2758.9069
2026-11-22 23:00 | 20287.2371 | 21528.4555 | 655.5649 | 2845.2877
2026-11-29 23:00 | 20798.9096 | 21817.5367 | 561.151 | 2911.592
2026-12-06 23:00 | 21194.4892 | 22234.5539 | 571.4712 | 2983.2363
2026-12-13 23:00 | 21511.2855 | 22790.1092 | 690.6589 | 3031.1886
2026-12-20 23:00 | 21726.2008 | 23060.0366 | 716.2678 | 3051.2712
2026-12-27 23:00 | 21134.078 | 22512.1199 | 731.1988 | 2953.1156
2027-01-03 23:00 | 21107.3235 | 22497.3373 | 737.7394 | 2946.2668
2027-01-10 23:00 | 21989.949 | 23565.4813 | 836.4791 | 3124.8809
2027-01-17 23:00 | 21879.5192 | 23500.9941 | 858.3034 | 3144.107
2027-01-24 23:00 | 21943.9833 | 23645.035 | 893.6936 | 3170.2097
2027-01-31 23:00 | 21930.4833 | 23550.7065 | 852.0167 | 3167.8581
2027-02-07 23:00 | 21426.1221 | 22861.7086 | 768.92 | 3103.6596
2027-02-14 23:00 | 21428.2132 | 22865.3024 | 766.9482 | 3098.0057
2027-02-21 23:00 | 21139.7187 | 22585.3056 | 772.268 | 3036.3611
2027-02-28 23:00 | 20986.0995 | 22305.3006 | 706.0873 | 3035.3626
2027-03-07 23:00 | 20458.5063 | 21729.69 | 692.8336 | 2959.1727
2027-03-14 23:00 | 20021.8661 | 21265.1255 | 689.605 | 2899.7681
2027-03-21 23:00 | 19505.5889 | 20713.6135 | 641.0788 | 2833.2614
2027-03-28 23:00 | 19082.6999 | 20059.7009 | 553.6607 | 2741.3769
2027-04-04 23:00 | 18649.738 | 19704.7212 | 559.7393 | 2701.4818
2027-04-11 23:00 | 18303.5659 | 19346.6685 | 569.6436 | 2655.4494
2027-04-18 23:00 | 17969.9654 | 19352.0362 | 719.4186 | 2595.6203
2027-04-25 23:00 | 17717.3066 | 18939.2895 | 643.76 | 2565.8702
2027-05-02 23:00 | 17532.6688 | 18699.5781 | 612.1177 | 2542.7268
2027-05-09 23:00 | 17474.3557 | 18956.2027 | 745.5743 | 2528.28
2027-05-16 23:00 | 17560.1653 | 19554.3546 | 968.794 | 2524.7948
2027-05-23 23:00 | 18246.2806 | 20708.7715 | 1306.4682 | 2544.4658
2027-05-30 23:00 | 18305.215 | 22751.4737 | 2033.3509 | 2514.2186
2027-06-06 23:00 | 19164.6692 | 23788.8907 | 2183.6641 | 2639.1202
2027-06-13 23:00 | 19654.6205 | 24177.0311 | 2178.7438 | 2684.0048
2027-06-20 23:00 | 20701.4407 | 24930.2787 | 2124.0263 | 2785.5271
2027-06-27 23:00 | 21577.7732 | 24792.5067 | 1748.7284 | 2852.7262
2027-07-04 23:00 | 21623.4266 | 24772.8308 | 1714.4683 | 2859.2809
2027-07-11 23:00 | 22409.7396 | 25771.8697 | 1804.2303 | 2960.063
2027-07-18 23:00 | 22620.5534 | 25902.1095 | 1776.1171 | 3018.6418
2027-07-25 23:00 | 22632.0086 | 25936.2865 | 1793.7347 | 3020.6087
2027-08-01 23:00 | 22485.7067 | 25654.1355 | 1681.8204 | 3006.977
2027-08-08 23:00 | 22057.3785 | 25446.383 | 1788.8375 | 2957.9575
2027-08-15 23:00 | 22016.9074 | 25165.7036 | 1665.0329 | 2947.2299
2027-08-22 23:00 | 21811.1432 | 24582.365 | 1494.1413 | 2915.5327
2027-08-29 23:00 | 21831.2348 | 24378.5907 | 1410.1769 | 2905.246
2027-09-05 23:00 | 21526.9118 | 24774.9051 | 1747.7641 | 2858.9957
2027-09-12 23:00 | 20429.6599 | 24461.2296 | 1996.5405 | 2720.7205
2027-09-19 23:00 | 19960.0465 | 23626.4245 | 1769.4741 | 2717.9629
2027-09-26 23:00 | 19494.0635 | 23048.717 | 1645.1374 | 2694.8578
2027-10-03 23:00 | 19408.0433 | 21729.0596 | 1231.4519 | 2672.5826
2027-10-10 23:00 | 18649.4485 | 20615.4064 | 927.4101 | 2658.6845
2027-10-17 23:00 | 18639.0431 | 19898.2008 | 647.3394 | 2639.4331
2027-10-24 23:00 | 18869.156 | 19764.7487 | 470.3916 | 2710.1815
2027-10-31 23:00 | 19150.589 | 20053.1874 | 484.7625 | 2755.1042
2027-11-07 23:00 | 19733.7398 | 20674.9207 | 498.8323 | 2821.5179
2027-11-14 23:00 | 20190.0441 | 21403.3655 | 632.5584 | 2874.5619
2027-11-21 23:00 | 20763.3701 | 22028.6774 | 666.1389 | 2964.2965
2027-11-28 23:00 | 21307.917 | 22357.3617 | 574.9958 | 3028.2877
2027-12-05 23:00 | 21681.4336 | 22708.5446 | 566.2123 | 3097.1816
2027-12-12 23:00 | 22049.289 | 23303.5949 | 677.9277 | 3154.1806
2027-12-19 23:00 | 22283.6768 | 23614.8017 | 712.9325 | 3177.4941
2027-12-26 23:00 | 22304.0743 | 23657.6441 | 722.998 | 3188.3291
2028-01-02 23:00 | 22055.9799 | 23608.8371 | 834.7544 | 3084.5632
Back to main menu

## Table 1.4.1
Back to main menu
Table 1.4.1: Weekly Weather and Demand History
Week Number | Week Ending | Actual Energy (GWh) | Weekly Average Temperature (°C) | Peak Day | Actual Peak (MW) | Peak Day Temperature (°C)
19 | 2003-05-11 | 2675.239 | 13.4714 | 2003-05-05 | 18741 | 13.1
20 | 2003-05-18 | 2632.509 | 11.8333 | 2003-05-12 | 18362 | 11.1
21 | 2003-05-25 | 2571.07 | 13.4762 | 2003-05-20 | 18599 | 15.7
22 | 2003-06-01 | 2649.124 | 15.0952 | 2003-05-29 | 18226 | 24.2
23 | 2003-06-08 | 2665.141 | 16.219 | 2003-06-04 | 18410 | 16.1
24 | 2003-06-15 | 2678.946 | 18.0381 | 2003-06-11 | 19042 | 24.6
25 | 2003-06-22 | 2742.722 | 19.4 | 2003-06-18 | 19935 | 22.6
26 | 2003-06-29 | 3084.92 | 25.8857 | 2003-06-26 | 24753 | 33.3
27 | 2003-07-06 | 2992.491 | 25.419 | 2003-07-04 | 23199 | 31.3
28 | 2003-07-13 | 2852.473 | 21.5524 | 2003-07-08 | 22167 | 28.6
29 | 2003-07-20 | 2847.944 | 21.2667 | 2003-07-14 | 21133 | 28
30 | 2003-07-27 | 2885.618 | 22.5905 | 2003-07-25 | 20868 | 28.7
31 | 2003-08-03 | 2897.737 | 22.3905 | 2003-07-30 | 21414 | 28.3
32 | 2003-08-10 | 3017.672 | 23.3 | 2003-08-07 | 22326 | 26.9
33 | 2003-08-17 | 2723.58 | 22.1 | 2003-08-14 | 23932 | 31
34 | 2003-08-24 | 2750.549 | 23.4048 | 2003-08-21 | 20709 | 31.7
35 | 2003-08-31 | 2853.562 | 21.7952 | 2003-08-26 | 21951 | 30
36 | 2003-09-07 | 2703.488 | 20.1095 | 2003-09-03 | 19841 | 23.2
37 | 2003-09-14 | 2870.007 | 20.7381 | 2003-09-11 | 20699 | 26.8
38 | 2003-09-21 | 2785.104 | 17.9857 | 2003-09-15 | 20233 | 19.6
39 | 2003-09-28 | 2698.174 | 15.6048 | 2003-09-22 | 19269 | 18.4
40 | 2003-10-05 | 2734.489 | 8.3905 | 2003-10-02 | 18929 | 9.4
41 | 2003-10-12 | 2696.531 | 15.3286 | 2003-10-09 | 18922 | 23.6
42 | 2003-10-19 | 2672.208 | 9.2952 | 2003-10-14 | 19092 | 16.2
43 | 2003-10-26 | 2799.532 | 7.4905 | 2003-10-23 | 19738 | 5.4
44 | 2003-11-02 | 2803.196 | 9.2762 | 2003-10-28 | 20426 | 9.7
45 | 2003-11-09 | 2900.177 | 4.019 | 2003-11-04 | 20899 | 4.7
46 | 2003-11-16 | 2927.031 | 4.5857 | 2003-11-13 | 21169 | 2
47 | 2003-11-23 | 2875.998 | 8.0048 | 2003-11-17 | 20954 | 5.3
48 | 2003-11-30 | 2975.154 | 4.1333 | 2003-11-24 | 21504 | 13.4
49 | 2003-12-07 | 2646.415 | -2.919 | 2003-12-02 | 22026 | -5.6
50 | 2003-12-14 | 3161.767 | -0.07619 | 2003-12-08 | 22584 | 1.4
51 | 2003-12-21 | 3602.808 | -0.2619 | 2003-12-15 | 22524 | 1.1
52 | 2003-12-28 | 2643.779 | 3.3333 | 2003-12-22 | 20772 | 5.9
1 | 2004-01-04 | 2717.783 | 4.4048 | 2003-12-30 | 19967 | 3
2 | 2004-01-11 | 3371.766 | -10.2286 | 2004-01-09 | 23998 | -18.3
3 | 2004-01-18 | 3441.886 | -10.7095 | 2004-01-15 | 24877 | -19.7
4 | 2004-01-25 | 3452.82 | -12.0905 | 2004-01-19 | 23728 | -8.7
5 | 2004-02-01 | 3428.432 | -8.3667 | 2004-01-26 | 24659 | -12.8
6 | 2004-02-08 | 3246.898 | -3.9905 | 2004-02-04 | 22494 | -3.9
7 | 2004-02-15 | 3235.171 | -4.1857 | 2004-02-09 | 22239 | 2.1
8 | 2004-02-22 | 3167.121 | -1.7619 | 2004-02-16 | 22792 | -5.7
9 | 2004-02-29 | 3050.511 | 0.28571 | 2004-02-23 | 21479 | -1.2
10 | 2004-03-07 | 2977.639 | 5.0048 | 2004-03-03 | 20620 | 5.8
11 | 2004-03-14 | 3038.073 | -0.10476 | 2004-03-08 | 21125 | 0.2
12 | 2004-03-21 | 3064.243 | -1.1333 | 2004-03-16 | 21476 | -3.1
13 | 2004-03-28 | 2933.927 | 5.9476 | 2004-03-22 | 21429 | -2.8
14 | 2004-04-04 | 2856.708 | 5.4857 | 2004-04-01 | 19881 | 5.2
15 | 2004-04-11 | 2757.816 | 4.5952 | 2004-04-05 | 19965 | 3.2
16 | 2004-04-18 | 2750.228 | 8.3476 | 2004-04-13 | 19339 | 4.2
17 | 2004-04-25 | 2704.802 | 10.5048 | 2004-04-21 | 18430 | 20
18 | 2004-05-02 | 2727.854 | 11.5095 | 2004-04-27 | 18771 | 5.8
19 | 2004-05-09 | 2708.043 | 9.719 | 2004-05-03 | 18664 | 8.3
20 | 2004-05-16 | 2745.619 | 18.7143 | 2004-05-13 | 20218 | 27.3
21 | 2004-05-23 | 2670.063 | 15.8571 | 2004-05-20 | 18943 | 23.6
22 | 2004-05-30 | 2605.734 | 14.3905 | 2004-05-25 | 18349 | 13.6
23 | 2004-06-06 | 2660.545 | 15.7048 | 2004-05-31 | 18508 | 13.2
24 | 2004-06-13 | 2887.122 | 20.4048 | 2004-06-09 | 23153 | 31.3
25 | 2004-06-20 | 2888.011 | 19.9476 | 2004-06-14 | 21752 | 27.3
26 | 2004-06-27 | 2761.454 | 18.481 | 2004-06-24 | 20108 | 25.8
27 | 2004-07-04 | 2745.2 | 20.8762 | 2004-06-30 | 19465 | 23.9
28 | 2004-07-11 | 2789.817 | 20.5143 | 2004-07-05 | 19911 | 20.8
29 | 2004-07-18 | 2908.264 | 22.6857 | 2004-07-12 | 22092 | 27.4
30 | 2004-07-25 | 2975.51 | 21.9143 | 2004-07-22 | 23831 | 30.1
31 | 2004-08-01 | 2924.264 | 21.5 | 2004-07-29 | 21709 | 26.7
32 | 2004-08-08 | 2841.852 | 20.7905 | 2004-08-03 | 23071 | 28.6
33 | 2004-08-15 | 2822.098 | 19.7857 | 2004-08-10 | 21120 | 26.5
34 | 2004-08-22 | 2802.037 | 19.7381 | 2004-08-18 | 20534 | 25.5
35 | 2004-08-29 | 3020.753 | 22.519 | 2004-08-27 | 22554 | 27.6
36 | 2004-09-05 | 2940.62 | 21.4238 | 2004-09-03 | 21395 | 28.4
37 | 2004-09-12 | 2839.863 | 20.6571 | 2004-09-07 | 21019 | 24.6
38 | 2004-09-19 | 2865.462 | 18.3095 | 2004-09-15 | 21740 | 25.8
39 | 2004-09-26 | 2885.929 | 20.4905 | 2004-09-23 | 21431 | 27.5
40 | 2004-10-03 | 2771.707 | 16.1 | 2004-09-27 | 19918 | 23.6
41 | 2004-10-10 | 2739.189 | 15.4238 | 2004-10-07 | 19509 | 26.8
42 | 2004-10-17 | 2707.201 | 10.481 | 2004-10-14 | 19253 | 13.4
43 | 2004-10-24 | 2819.211 | 8.4 | 2004-10-18 | 19704 | 8.8
44 | 2004-10-31 | 2793.89 | 11.381 | 2004-10-27 | 19492 | 11.4
45 | 2004-11-07 | 2855.622 | 7.7952 | 2004-11-04 | 20642 | 6.2
46 | 2004-11-14 | 2961.444 | 3.3857 | 2004-11-09 | 21076 | 1.4
47 | 2004-11-21 | 2880.44 | 8.8286 | 2004-11-15 | 20707 | 13.4
48 | 2004-11-28 | 3001.181 | 4.2905 | 2004-11-24 | 21769 | 3.4
49 | 2004-12-05 | 3085.202 | 2.0143 | 2004-12-03 | 22046 | -0.6
50 | 2004-12-12 | 3622.393 | 2.1286 | 2004-12-06 | 23352 | -1.7
51 | 2004-12-18 | 2800.887 | -3.7286 | 2004-12-14 | 23436 | -4.9
52 | 2004-12-26 | 3162.779 | -7.8762 | 2004-12-20 | 24809 | -12.3
53 | 2005-01-02 | 2907.357 | -0.25714 | 2004-12-27 | 21226 | -8.5
1 | 2005-01-09 | 3184.351 | -1.2714 | 2005-01-06 | 23183 | -2.7
2 | 2005-01-16 | 3215.38 | -1.7 | 2005-01-11 | 22615 | -1.6
3 | 2005-01-23 | 3527.552 | -13.9905 | 2005-01-18 | 24307 | -14.5
4 | 2005-01-30 | 3421.373 | -9.7857 | 2005-01-27 | 24291 | -14.6
5 | 2005-02-06 | 3165.178 | -1.5905 | 2005-01-31 | 22574 | -1.5
6 | 2005-02-13 | 3141.846 | -1.8048 | 2005-02-09 | 22244 | -3.9
7 | 2005-02-20 | 3212.867 | -2.7238 | 2005-02-18 | 22232 | -9.3
8 | 2005-02-27 | 3229.884 | -5.4238 | 2005-02-24 | 22328 | -5.7
9 | 2005-03-06 | 3169.752 | -3.019 | 2005-02-28 | 22106 | 1.8
10 | 2005-03-13 | 3205.601 | -4.2143 | 2005-03-08 | 22684 | -8.5
11 | 2005-03-20 | 3043.77 | -0.7619 | 2005-03-14 | 20989 | -0.8
12 | 2005-03-27 | 2884.713 | 2.181 | 2005-03-23 | 20899 | 1.5
13 | 2005-04-03 | 2873.583 | 6.4333 | 2005-03-28 | 19566 | 6.6
14 | 2005-04-10 | 2777.064 | 9.6524 | 2005-04-04 | 19276 | 10.9
15 | 2005-04-17 | 2705.24 | 9.9 | 2005-04-11 | 18600 | 7.9
16 | 2005-04-24 | 2733.207 | 10.4952 | 2005-04-20 | 18469 | 16.2
17 | 2005-05-01 | 2760.182 | 7.9714 | 2005-04-25 | 19320 | 6.5
18 | 2005-05-08 | 2661.14 | 10.4952 | 2005-05-02 | 18469 | 8.6
19 | 2005-05-15 | 2664.748 | 12.5952 | 2005-05-11 | 18520 | 22.6
20 | 2005-05-22 | 2633.858 | 12.9 | 2005-05-16 | 18288 | 11
21 | 2005-05-29 | 2614.715 | 16.5381 | 2005-05-26 | 18610 | 24.2
22 | 2005-06-05 | 2822.357 | 20.0714 | 2005-06-02 | 19972 | 26
23 | 2005-06-12 | 3339.343 | 26.3952 | 2005-06-10 | 24469 | 30.5
24 | 2005-06-19 | 2967.375 | 20.219 | 2005-06-14 | 24901 | 29.7
25 | 2005-06-26 | 3086.688 | 23.9857 | 2005-06-24 | 23657 | 34
26 | 2005-07-03 | 3201.62 | 25.3905 | 2005-06-27 | 25922 | 31.6
27 | 2005-07-10 | 3047.491 | 24.081 | 2005-07-04 | 23149 | 29.5
28 | 2005-07-17 | 3478.761 | 28.4 | 2005-07-13 | 25872 | 34.6
29 | 2005-07-24 | 3345.132 | 26.5381 | 2005-07-18 | 25545 | 33.3
30 | 2005-07-31 | 3059.465 | 23.3286 | 2005-07-25 | 25053 | 33.8
31 | 2005-08-07 | 3304.047 | 26.2429 | 2005-08-04 | 24979 | 32.8
32 | 2005-08-14 | 3294.582 | 25.0333 | 2005-08-09 | 25638 | 32.9
33 | 2005-08-21 | 3046.904 | 22.5143 | 2005-08-15 | 22081 | 27.6
34 | 2005-08-28 | 2960.83 | 21.0952 | 2005-08-26 | 21349 | 27.4
35 | 2005-09-04 | 3014.828 | 21.8524 | 2005-08-29 | 22761 | 28.4
36 | 2005-09-11 | 2896.404 | 20.4048 | 2005-09-07 | 22170 | 27.5
37 | 2005-09-18 | 3053.565 | 22.3429 | 2005-09-13 | 23689 | 30.1
38 | 2005-09-25 | 2907.237 | 20.0476 | 2005-09-21 | 20979 | 28.5
39 | 2005-10-02 | 2755.984 | 16.7381 | 2005-09-26 | 19927 | 22.3
40 | 2005-10-09 | 2805.329 | 16.7238 | 2005-10-04 | 20676 | 25.8
41 | 2005-10-16 | 2663.132 | 12.9905 | 2005-10-12 | 19064 | 13.2
42 | 2005-10-23 | 2759.787 | 8.8429 | 2005-10-20 | 19120 | 11.9
43 | 2005-10-30 | 2835.05 | 7.419 | 2005-10-26 | 19803 | 8.1
44 | 2005-11-06 | 2777.496 | 11.9 | 2005-11-02 | 19773 | 12.3
45 | 2005-11-13 | 2809.872 | 9.0571 | 2005-11-10 | 20392 | 5.7
46 | 2005-11-20 | 2905.28 | 4.1619 | 2005-11-17 | 21171 | 2.7
47 | 2005-11-27 | 3058.861 | -2.4381 | 2005-11-24 | 22566 | -6.3
48 | 2005-12-04 | 3000.238 | 2.119 | 2005-12-02 | 21616 | -0.8
49 | 2005-12-11 | 3199.968 | -3.7476 | 2005-12-07 | 22958 | -4.3
50 | 2005-12-17 | 2855.631 | -5.3 | 2005-12-12 | 23626 | -9.8
51 | 2005-12-25 | 3103.127 | -1.3286 | 2005-12-19 | 23257 | -4.7
52 | 2006-01-01 | 3208.112 | -1.0048 | 2005-12-29 | 20147 | 0.8
1 | 2006-01-08 | 3060.448 | -0.042857 | 2006-01-06 | 21905 | -5.2
2 | 2006-01-15 | 3046.688 | 1.5524 | 2006-01-09 | 21700 | 2.6
3 | 2006-01-22 | 3134.613 | 0.28571 | 2006-01-17 | 22861 | 0.7
4 | 2006-01-29 | 3075.232 | 0.77619 | 2006-01-26 | 22236 | -3.7
5 | 2006-02-05 | 3002.114 | 2.7476 | 2006-01-31 | 21295 | 1.3
6 | 2006-02-12 | 3166.709 | -5.3429 | 2006-02-08 | 22080 | -6.1
7 | 2006-02-19 | 3166.361 | -3.5857 | 2006-02-16 | 22079 | -0.9
8 | 2006-02-26 | 3126.432 | -2.5857 | 2006-02-20 | 21828 | -3.4
9 | 2006-03-05 | 3153.109 | -4.1429 | 2006-02-27 | 22114 | -4.1
10 | 2006-03-12 | 2943.659 | 4.2857 | 2006-03-06 | 20835 | 0.3
11 | 2006-03-19 | 2983.336 | 0.83333 | 2006-03-15 | 20716 | 2.6
12 | 2006-03-26 | 2968.069 | 0.92857 | 2006-03-20 | 21034 | -1.7
13 | 2006-04-02 | 2778.61 | 8.4048 | 2006-03-27 | 19548 | 11.5
14 | 2006-04-09 | 2829.331 | 5.1476 | 2006-04-04 | 19558 | 6.6
15 | 2006-04-16 | 2607.914 | 12.0143 | 2006-04-12 | 18530 | 16.9
16 | 2006-04-23 | 2642.006 | 11.7 | 2006-04-18 | 17818 | 15.5
17 | 2006-04-30 | 2668.331 | 9.481 | 2006-04-25 | 18633 | 7.2
18 | 2006-05-07 | 2607.266 | 14.1619 | 2006-05-04 | 18132 | 23
19 | 2006-05-14 | 2619.082 | 15.5762 | 2006-05-10 | 18225 | 23.4
20 | 2006-05-21 | 2603.746 | 12.0571 | 2006-05-16 | 17933 | 14.1
21 | 2006-05-28 | 2631.006 | 15.8857 | 2006-05-26 | 18581 | 18.8
22 | 2006-06-04 | 3030.444 | 22.6476 | 2006-05-30 | 24823 | 32.8
23 | 2006-06-11 | 2789.813 | 18.2381 | 2006-06-07 | 21130 | 27.1
24 | 2006-06-18 | 2952.481 | 22.1714 | 2006-06-17 | 21455 | 33.3
25 | 2006-06-25 | 3012.124 | 22.1429 | 2006-06-22 | 23082 | 30.6
26 | 2006-07-02 | 2974.16 | 23.3619 | 2006-06-28 | 22172 | 26.2
27 | 2006-07-09 | 2898.73 | 23.0667 | 2006-07-04 | 22330 | 28.9
28 | 2006-07-16 | 3145.2 | 24.8476 | 2006-07-14 | 23664 | 30
29 | 2006-07-23 | 3182.345 | 23.8095 | 2006-07-17 | 25658 | 33.8
30 | 2006-07-30 | 3285.355 | 25.7 | 2006-07-26 | 24177 | 30.5
31 | 2006-08-06 | 3356.688 | 26.619 | 2006-08-01 | 26768 | 36.4
32 | 2006-08-13 | 2889.38 | 21.7667 | 2006-08-09 | 21246 | 26.2
33 | 2006-08-20 | 2979.046 | 22.2429 | 2006-08-18 | 22702 | 30.4
34 | 2006-08-27 | 2879.36 | 20.9048 | 2006-08-22 | 21273 | 27.5
35 | 2006-09-03 | 2772.402 | 18.5286 | 2006-08-28 | 20529 | 23.6
36 | 2006-09-10 | 2694.952 | 18.6381 | 2006-09-08 | 19896 | 28
37 | 2006-09-17 | 2712.798 | 17.819 | 2006-09-13 | 18845 | 20.9
38 | 2006-09-24 | 2692.215 | 16.4619 | 2006-09-19 | 19775 | 18.1
39 | 2006-10-01 | 2653.947 | 13.1095 | 2006-09-27 | 18522 | 22.3
40 | 2006-10-08 | 2637.776 | 13.3524 | 2006-10-03 | 18796 | 23.3
41 | 2006-10-15 | 2621.631 | 9.7952 | 2006-10-12 | 18710 | 7.8
42 | 2006-10-22 | 2704.531 | 10.2095 | 2006-10-17 | 19000 | 12.2
43 | 2006-10-29 | 2780.566 | 5.0286 | 2006-10-25 | 19176 | 7.8
44 | 2006-11-05 | 2810.968 | 5.2762 | 2006-11-02 | 20205 | 4.4
45 | 2006-11-12 | 2770.862 | 7.5476 | 2006-11-07 | 20025 | 10.8
46 | 2006-11-19 | 2833.259 | 5.619 | 2006-11-13 | 20552 | 5.4
47 | 2006-11-26 | 2852.001 | 3.9476 | 2006-11-20 | 21129 | 1.5
48 | 2006-12-03 | 2903.458 | 6.3714 | 2006-12-01 | 20698 | 3.6
49 | 2006-12-10 | 3088.927 | -1.5333 | 2006-12-07 | 22656 | -5.5
50 | 2006-12-17 | 3355.996 | 6.6714 | 2006-12-11 | 21675 | 4.9
51 | 2006-12-23 | 2520.519 | 4.1619 | 2006-12-19 | 21351 | 4.4
52 | 2006-12-30 | 2682.677 | 0.95714 | 2006-12-29 | 19804 | -2.6
1 | 2007-01-07 | 2759.189 | 6.181 | 2007-01-03 | 20288 | 7.6
2 | 2007-01-14 | 3014.616 | 0.18095 | 2007-01-10 | 22026 | -3
3 | 2007-01-21 | 3180.515 | -5.5381 | 2007-01-16 | 22888 | -8.6
4 | 2007-01-28 | 3233.013 | -7.2095 | 2007-01-25 | 23328 | -13.1
5 | 2007-02-04 | 3255.384 | -8.5762 | 2007-01-29 | 22753 | -6.3
6 | 2007-02-11 | 3311.569 | -9.3238 | 2007-02-05 | 23640 | -10.5
7 | 2007-02-18 | 3308.032 | -10.5905 | 2007-02-13 | 23639 | -14
8 | 2007-02-25 | 3134.21 | -3.1619 | 2007-02-19 | 22345 | -5.3
9 | 2007-03-04 | 3045.905 | -1.4905 | 2007-03-01 | 21475 | -0.8
10 | 2007-03-11 | 3143.056 | -4.8762 | 2007-03-06 | 22772 | -12.5
11 | 2007-03-18 | 2924.953 | 2.9381 | 2007-03-16 | 20225 | -2.4
12 | 2007-03-25 | 2927.949 | 2.819 | 2007-03-20 | 20535 | -2.3
13 | 2007-04-01 | 2749.563 | 7.9619 | 2007-03-26 | 18807 | 19.2
14 | 2007-04-08 | 2814.703 | 0.95238 | 2007-04-05 | 19409 | -3
15 | 2007-04-15 | 2872.975 | 3.2143 | 2007-04-11 | 19680 | 4.1
16 | 2007-04-22 | 2680.61 | 11.6571 | 2007-04-16 | 19250 | 5.2
17 | 2007-04-29 | 2634.277 | 12.4524 | 2007-04-27 | 18211 | 16.8
18 | 2007-05-06 | 2572.418 | 11.681 | 2007-05-01 | 17888 | 9.7
19 | 2007-05-13 | 2603.987 | 16.381 | 2007-05-11 | 18478 | 20.5
20 | 2007-05-20 | 2605.33 | 14.1667 | 2007-05-15 | 19025 | 28.4
21 | 2007-05-27 | 2682.48 | 18.5143 | 2007-05-25 | 20875 | 27.4
22 | 2007-06-03 | 2917.633 | 21.7143 | 2007-05-31 | 21316 | 27.5
23 | 2007-06-10 | 2731.849 | 18.0048 | 2007-06-08 | 21794 | 31.2
24 | 2007-06-17 | 3052.251 | 24 | 2007-06-13 | 23299 | 29.7
25 | 2007-06-24 | 2875.267 | 21.2381 | 2007-06-18 | 22883 | 28.3
26 | 2007-07-01 | 3058.01 | 23.4048 | 2007-06-26 | 25628 | 34.2
27 | 2007-07-08 | 2763.077 | 22.1952 | 2007-07-06 | 20184 | 28.2
28 | 2007-07-15 | 2900.476 | 22.9286 | 2007-07-09 | 24173 | 33.7
29 | 2007-07-22 | 2832.297 | 22.1333 | 2007-07-18 | 21283 | 27.5
30 | 2007-07-29 | 3006.625 | 22.9667 | 2007-07-26 | 22020 | 27.5
31 | 2007-08-05 | 3270.026 | 26.6905 | 2007-08-02 | 25418 | 34.5
32 | 2007-08-12 | 3077.078 | 24.8095 | 2007-08-08 | 24012 | 31.7
33 | 2007-08-19 | 2869.053 | 21.7476 | 2007-08-16 | 22156 | 29.6
34 | 2007-08-26 | 2921.618 | 22.1381 | 2007-08-24 | 23409 | 32.8
35 | 2007-09-02 | 2932.442 | 22.4333 | 2007-08-29 | 24663 | 33.5
36 | 2007-09-09 | 2943.478 | 23.1 | 2007-09-07 | 23710 | 32.9
37 | 2007-09-16 | 2692.56 | 16.3429 | 2007-09-10 | 19512 | 23
38 | 2007-09-23 | 2761.954 | 19.4286 | 2007-09-21 | 20122 | 27.5
39 | 2007-09-30 | 2779.605 | 19.219 | 2007-09-25 | 22133 | 32.8
40 | 2007-10-07 | 2737.832 | 19.5238 | 2007-10-05 | 19206 | 24.3
41 | 2007-10-14 | 2644.804 | 14.4048 | 2007-10-09 | 18915 | 22.2
42 | 2007-10-21 | 2634.581 | 15.6286 | 2007-10-16 | 18570 | 12.8
43 | 2007-10-28 | 2652.985 | 11.981 | 2007-10-22 | 18634 | 24.8
44 | 2007-11-04 | 2684.867 | 9.0667 | 2007-11-01 | 18869 | 8.9
45 | 2007-11-11 | 2815.137 | 4.181 | 2007-11-07 | 20267 | 3.1
46 | 2007-11-18 | 2825.038 | 5.4 | 2007-11-12 | 20217 | 10.4
47 | 2007-11-25 | 2957.028 | 0.92857 | 2007-11-22 | 21494 | -3.4
48 | 2007-12-02 | 3497.435 | -0.97143 | 2007-11-28 | 21582 | -0.3
49 | 2007-12-09 | 3127.851 | -3.8143 | 2007-12-05 | 22385 | -7.9
50 | 2007-12-15 | 2735.781 | -2.8905 | 2007-12-11 | 22334 | 1.1
51 | 2007-12-23 | 2596.65 | 0.37143 | 2007-12-17 | 22585 | -3.4
52 | 2007-12-30 | 3120.152 | -0.18095 | 2007-12-27 | 19369 | 2.4
1 | 2008-01-06 | 2932.004 | -3.0143 | 2008-01-03 | 22307 | -7.7
2 | 2008-01-13 | 2878.326 | 5.8143 | 2008-01-10 | 20540 | 3.6
3 | 2008-01-20 | 3072.046 | -3.1762 | 2008-01-15 | 21303 | -0.8
4 | 2008-01-27 | 3182.096 | -5.7905 | 2008-01-21 | 22612 | -7.4
5 | 2008-02-03 | 3068.717 | -1.8905 | 2008-01-30 | 22270 | -8
6 | 2008-02-10 | 3024.216 | -1.8333 | 2008-02-06 | 21276 | -1.7
7 | 2008-02-17 | 3155.123 | -6.4333 | 2008-02-11 | 22834 | -9.3
8 | 2008-02-24 | 3046.81 | -4.7286 | 2008-02-20 | 21645 | -6.8
9 | 2008-03-02 | 3095.645 | -5.3 | 2008-02-27 | 21953 | -10.1
10 | 2008-03-09 | 2996.993 | -1.719 | 2008-03-04 | 20576 | -1.6
11 | 2008-03-16 | 2919.677 | -0.99524 | 2008-03-10 | 20185 | -0.7
12 | 2008-03-23 | 2852.89 | -0.5381 | 2008-03-18 | 19865 | 3
13 | 2008-03-30 | 2876.386 | 0.47143 | 2008-03-25 | 20067 | 2.6
14 | 2008-04-06 | 2775.843 | 5.519 | 2008-03-31 | 19196 | 5.3
15 | 2008-04-13 | 2704.624 | 8.2429 | 2008-04-11 | 19187 | 5.2
16 | 2008-04-20 | 2603.618 | 13.819 | 2008-04-14 | 18166 | 9.7
17 | 2008-04-27 | 2562.259 | 16.2286 | 2008-04-22 | 17791 | 20.9
18 | 2008-05-04 | 2615.088 | 8.1095 | 2008-04-28 | 18242 | 6.9
19 | 2008-05-11 | 2533.921 | 12.3333 | 2008-05-07 | 17750 | 15.6
20 | 2008-05-18 | 2538.939 | 13.2619 | 2008-05-14 | 17662 | 17
21 | 2008-05-25 | 2519.535 | 12.1619 | 2008-05-21 | 17701 | 9.4
22 | 2008-06-01 | 2585.264 | 16.3 | 2008-05-26 | 18453 | 26.9
23 | 2008-06-08 | 2844.201 | 22.0524 | 2008-06-06 | 21341 | 32.7
24 | 2008-06-15 | 2954.631 | 22.3952 | 2008-06-09 | 24001 | 33.1
25 | 2008-06-22 | 2684.657 | 17.0095 | 2008-06-16 | 19710 | 22.9
26 | 2008-06-29 | 2916.525 | 22.3238 | 2008-06-27 | 22302 | 27
27 | 2008-07-06 | 2712.781 | 20.6429 | 2008-07-02 | 20429 | 27.8
28 | 2008-07-13 | 3034.078 | 23.9381 | 2008-07-08 | 23224 | 30.7
29 | 2008-07-20 | 3049.678 | 23.9714 | 2008-07-17 | 23622 | 30
30 | 2008-07-27 | 2886.07 | 22.2333 | 2008-07-21 | 21078 | 24.8
31 | 2008-08-03 | 2954.73 | 23.0905 | 2008-07-31 | 21710 | 26.4
32 | 2008-08-10 | 2790.248 | 19.9571 | 2008-08-05 | 22376 | 26.1
33 | 2008-08-17 | 2764.063 | 20.4524 | 2008-08-14 | 19560 | 23.4
34 | 2008-08-24 | 2917.179 | 21.581 | 2008-08-18 | 22296 | 29.4
35 | 2008-08-31 | 2751.703 | 19.8095 | 2008-08-25 | 19101 | 20.4
36 | 2008-09-07 | 2871.959 | 21.281 | 2008-09-03 | 22900 | 30.3
37 | 2008-09-14 | 2702.472 | 18.6619 | 2008-09-14 | 18875 | 28
38 | 2008-09-21 | 2650.985 | 16.3952 | 2008-09-17 | 18274 | 23
39 | 2008-09-28 | 2666.45 | 17.1333 | 2008-09-25 | 18980 | 23.5
40 | 2008-10-05 | 2586.319 | 11.6524 | 2008-10-02 | 18029 | 12.6
41 | 2008-10-12 | 2584.606 | 13.0429 | 2008-10-08 | 18514 | 14.6
42 | 2008-10-19 | 2523.674 | 11.7952 | 2008-10-15 | 18128 | 15.9
43 | 2008-10-26 | 2640.237 | 7.7905 | 2008-10-21 | 18772 | 5.9
44 | 2008-11-02 | 2677.429 | 5.8095 | 2008-10-29 | 19171 | 3.3
45 | 2008-11-09 | 2591.332 | 10.4714 | 2008-11-03 | 18815 | 15.6
46 | 2008-11-16 | 2677.321 | 5.9429 | 2008-11-11 | 19640 | 5.6
47 | 2008-11-23 | 2922.821 | -3.3476 | 2008-11-19 | 20906 | -1.6
48 | 2008-11-30 | 2866.8 | 1.8238 | 2008-11-24 | 20878 | 3.8
49 | 2008-12-07 | 3373.616 | -1.7048 | 2008-12-04 | 20833 | 0.9
50 | 2008-12-14 | 3069.714 | -2.4048 | 2008-12-08 | 22230 | -3.7
51 | 2008-12-21 | 2183.151 | -5.1 | 2008-12-19 | 21903 | -8.9
52 | 2008-12-28 | 3488.556 | -0.44286 | 2008-12-22 | 21582 | -7.7
1 | 2009-01-04 | 2364.119 | -4.2571 | 2009-01-04 | 19721 | -2.1
2 | 2009-01-11 | 3024.795 | -5.7524 | 2009-01-08 | 21006 | -4.5
3 | 2009-01-18 | 3221.451 | -10.2429 | 2009-01-15 | 22804 | -11.3
4 | 2009-01-25 | 3120.821 | -8.0571 | 2009-01-20 | 22018 | -10.4
5 | 2009-02-01 | 3076.809 | -6.6524 | 2009-01-26 | 22003 | -8.9
6 | 2009-02-08 | 2983.238 | -5.0857 | 2009-02-04 | 21876 | -13.1
7 | 2009-02-15 | 2829.295 | 0.82857 | 2009-02-09 | 19841 | 2.6
8 | 2009-02-22 | 2852.638 | -3.1286 | 2009-02-19 | 20313 | -5.2
9 | 2009-03-01 | 2918.702 | -4.0571 | 2009-02-23 | 20882 | -6.1
10 | 2009-03-08 | 2865.83 | -0.40952 | 2009-03-02 | 21266 | -9.6
11 | 2009-03-15 | 2771.815 | 0.61429 | 2009-03-12 | 19558 | -3.4
12 | 2009-03-22 | 2607.907 | 4.3143 | 2009-03-19 | 18039 | 3.2
13 | 2009-03-29 | 2607.578 | 5.3143 | 2009-03-23 | 18345 | 1.6
14 | 2009-04-05 | 2566.444 | 6.6429 | 2009-03-30 | 18071 | 4.9
15 | 2009-04-12 | 2522.072 | 3.2905 | 2009-04-07 | 18329 | -0.5
16 | 2009-04-19 | 2427.499 | 10.4667 | 2009-04-13 | 16813 | 5.8
17 | 2009-04-26 | 2441.504 | 10.3286 | 2009-04-20 | 17644 | 5.6
18 | 2009-05-03 | 2369.714 | 13.219 | 2009-04-28 | 16573 | 10.4
19 | 2009-05-10 | 2381.014 | 14.1143 | 2009-05-07 | 16491 | 18.6
20 | 2009-05-17 | 2347.918 | 13.0524 | 2009-05-11 | 16538 | 13.2
21 | 2009-05-24 | 2324.301 | 17.9429 | 2009-05-21 | 17123 | 28.6
22 | 2009-05-31 | 2342.86 | 14.281 | 2009-05-25 | 17618 | 18.3
23 | 2009-06-07 | 2373.702 | 14.9619 | 2009-06-01 | 16474 | 15.3
24 | 2009-06-14 | 2393.083 | 16.7762 | 2009-06-11 | 16801 | 19.8
25 | 2009-06-21 | 2471.227 | 18.6476 | 2009-06-16 | 17669 | 23.4
26 | 2009-06-28 | 2827.027 | 23.3 | 2009-06-24 | 22403 | 30.7
27 | 2009-07-05 | 2429.956 | 19.0667 | 2009-06-29 | 18263 | 22.6
28 | 2009-07-12 | 2535.934 | 20.3619 | 2009-07-10 | 18804 | 25.9
29 | 2009-07-19 | 2495.28 | 19.519 | 2009-07-16 | 19044 | 27
30 | 2009-07-26 | 2542.821 | 20.1619 | 2009-07-20 | 18226 | 23.8
31 | 2009-08-02 | 2628.104 | 22.6857 | 2009-07-28 | 19678 | 27.4
32 | 2009-08-09 | 2560.875 | 20.9905 | 2009-08-04 | 20188 | 26.4
33 | 2009-08-16 | 2991.132 | 24.2952 | 2009-08-10 | 22022 | 29.9
34 | 2009-08-23 | 2953.422 | 23.9762 | 2009-08-17 | 24005 | 31.2
35 | 2009-08-30 | 2573.979 | 18.8048 | 2009-08-25 | 19558 | 25.5
36 | 2009-09-06 | 2550 | 19.1238 | 2009-09-03 | 18676 | 23.7
37 | 2009-09-13 | 2569.99 | 20.0429 | 2009-09-08 | 19551 | 25.1
38 | 2009-09-20 | 2494.128 | 16.5238 | 2009-09-14 | 18364 | 25
39 | 2009-09-27 | 2551.282 | 18.4286 | 2009-09-23 | 19258 | 27.2
40 | 2009-10-04 | 2445.95 | 11.2571 | 2009-10-01 | 17454 | 11.4
41 | 2009-10-11 | 2468.75 | 10.6286 | 2009-10-07 | 17436 | 12.4
42 | 2009-10-18 | 2540.442 | 4.7 | 2009-10-15 | 18320 | 4.1
43 | 2009-10-25 | 2553.259 | 10.3524 | 2009-10-22 | 18089 | 15.7
44 | 2009-11-01 | 2549.81 | 10.719 | 2009-10-26 | 18029 | 11.7
45 | 2009-11-08 | 2588.982 | 6.7429 | 2009-11-04 | 18972 | 5.9
46 | 2009-11-15 | 2553.776 | 8.6048 | 2009-11-09 | 18511 | 18.6
47 | 2009-11-22 | 2605.388 | 6.7571 | 2009-11-19 | 19067 | 9.6
48 | 2009-11-29 | 2640.481 | 6.1714 | 2009-11-24 | 19159 | 7.6
49 | 2009-12-06 | 2733.895 | 2.6714 | 2009-11-30 | 19685 | 3.7
50 | 2009-12-13 | 3384.411 | -1.4952 | 2009-12-10 | 21496 | -2.7
51 | 2009-12-20 | 3363.008 | -3.1857 | 2009-12-16 | 21747 | -3.8
52 | 2009-12-27 | 1989.13 | -2.0048 | 2009-12-22 | 21296 | -5.7
53 | 2010-01-03 | 2796.407 | -6.0238 | 2010-01-03 | 20770 | -8.6
1 | 2010-01-10 | 3076.419 | -7.5952 | 2010-01-04 | 21982 | -7.3
2 | 2010-01-17 | 2937.308 | -1.3429 | 2010-01-11 | 21483 | -4.7
3 | 2010-01-24 | 2897.403 | -0.53333 | 2010-01-20 | 20700 | -2.5
4 | 2010-01-31 | 3024.325 | -5.6381 | 2010-01-28 | 21864 | -7
5 | 2010-02-07 | 3008.541 | -4.8048 | 2010-02-01 | 21246 | -3.6
6 | 2010-02-14 | 2984.921 | -4.1476 | 2010-02-09 | 21018 | -3.9
7 | 2010-02-21 | 2846.377 | -0.30476 | 2010-02-17 | 20254 | 0.4
8 | 2010-02-28 | 2886.967 | -1.319 | 2010-02-25 | 20690 | -5.8
9 | 2010-03-07 | 2737.389 | 1.7714 | 2010-03-01 | 19282 | 2
10 | 2010-03-14 | 2623.207 | 6.7714 | 2010-03-08 | 18194 | 13.6
11 | 2010-03-21 | 2530.337 | 9.1429 | 2010-03-15 | 17362 | 12.1
12 | 2010-03-28 | 2652.551 | 3.4762 | 2010-03-25 | 18335 | 8.6
13 | 2010-04-04 | 2403.602 | 12.3048 | 2010-03-29 | 17597 | 8.4
14 | 2010-04-11 | 2494.844 | 10.6048 | 2010-04-09 | 17422 | 3.6
15 | 2010-04-18 | 2465.674 | 10.8905 | 2010-04-12 | 16709 | 13.1
16 | 2010-04-25 | 2447.052 | 11.5762 | 2010-04-21 | 16662 | 17.4
17 | 2010-05-02 | 2436.561 | 14.5476 | 2010-04-27 | 16607 | 9.4
18 | 2010-05-09 | 2477.159 | 13.0619 | 2010-05-05 | 17328 | 26.9
19 | 2010-05-16 | 2452.8 | 10.8143 | 2010-05-13 | 17005 | 11.3
20 | 2010-05-23 | 2470.298 | 18.5524 | 2010-05-20 | 17924 | 28.3
21 | 2010-05-30 | 2863.471 | 24.0429 | 2010-05-26 | 22806 | 31.4
22 | 2010-06-06 | 2736.188 | 20.3905 | 2010-05-31 | 20859 | 27.6
23 | 2010-06-13 | 2517.432 | 17.1 | 2010-06-11 | 17458 | 22.7
24 | 2010-06-20 | 2668.044 | 21.9286 | 2010-06-18 | 19093 | 25
25 | 2010-06-27 | 2793.61 | 22.2571 | 2010-06-23 | 21498 | 28.3
26 | 2010-07-04 | 2545.158 | 21.0905 | 2010-06-28 | 21240 | 28.9
27 | 2010-07-11 | 3196.825 | 26.9619 | 2010-07-08 | 24507 | 33.3
28 | 2010-07-18 | 3102.44 | 25.1238 | 2010-07-15 | 23587 | 28.9
29 | 2010-07-25 | 3004.401 | 24.5714 | 2010-07-21 | 22164 | 30.1
30 | 2010-08-01 | 2842.254 | 22.3952 | 2010-07-27 | 22449 | 28.3
31 | 2010-08-08 | 2931.57 | 24.3286 | 2010-08-04 | 23582 | 31.5
32 | 2010-08-15 | 3119.634 | 25.1429 | 2010-08-10 | 23426 | 29.4
33 | 2010-08-22 | 2797.864 | 22.019 | 2010-08-16 | 20994 | 27
34 | 2010-08-29 | 2729.423 | 21.1619 | 2010-08-29 | 20028 | 30.1
35 | 2010-09-05 | 3027.002 | 23.8286 | 2010-08-31 | 24566 | 32.9
36 | 2010-09-12 | 2502.796 | 18.1857 | 2010-09-07 | 19337 | 29.6
37 | 2010-09-19 | 2489.772 | 15.7571 | 2010-09-13 | 17472 | 23.6
38 | 2010-09-26 | 2539.512 | 17.6952 | 2010-09-24 | 18721 | 30.5
39 | 2010-10-03 | 2473.737 | 13.3762 | 2010-09-27 | 17513 | 15.7
40 | 2010-10-10 | 2460.436 | 14.119 | 2010-10-04 | 17452 | 12
41 | 2010-10-17 | 2431.16 | 10.9381 | 2010-10-13 | 17484 | 14.8
42 | 2010-10-24 | 2522.859 | 9.1714 | 2010-10-21 | 17759 | 7.7
43 | 2010-10-31 | 2506.893 | 11.4571 | 2010-10-26 | 17556 | 20.5
44 | 2010-11-07 | 2607.736 | 4.3 | 2010-11-05 | 18079 | 3.2
45 | 2010-11-14 | 2579.985 | 6.2429 | 2010-11-08 | 18433 | 10
46 | 2010-11-21 | 2623.409 | 5.5333 | 2010-11-18 | 18798 | 6.2
47 | 2010-11-28 | 2720.021 | 4.019 | 2010-11-25 | 19835 | 4.2
48 | 2010-12-05 | 2793.795 | 1.2 | 2010-12-02 | 20038 | 0.8
49 | 2010-12-12 | 2920.398 | -2.4 | 2010-12-08 | 21364 | -3.6
50 | 2010-12-19 | 3433.803 | -6.3476 | 2010-12-13 | 22099 | -11.6
51 | 2010-12-26 | 2822.777 | -4.6714 | 2010-12-21 | 20800 | -3.7
52 | 2011-01-02 | 2228.135 | 0.57143 | 2010-12-28 | 19037 | -0.7
1 | 2011-01-09 | 2924.562 | -4.4905 | 2011-01-06 | 20762 | -3.2
2 | 2011-01-16 | 3035.07 | -7.1476 | 2011-01-12 | 21182 | -7.7
3 | 2011-01-23 | 3110.626 | -9.0762 | 2011-01-17 | 21671 | -7.1
4 | 2011-01-30 | 3041.869 | -4.9571 | 2011-01-24 | 22531 | -9
5 | 2011-02-06 | 3045.758 | -7.2619 | 2011-01-31 | 21756 | -10.7
6 | 2011-02-13 | 2994.743 | -6.8476 | 2011-02-08 | 21510 | -9.9
7 | 2011-02-20 | 2838.845 | -0.033333 | 2011-02-15 | 20475 | -4.9
8 | 2011-02-27 | 2903.379 | -3.9714 | 2011-02-22 | 20461 | -3.9
9 | 2011-03-06 | 2872.379 | -1.1667 | 2011-03-02 | 20490 | -4.3
10 | 2011-03-13 | 2819.458 | 0.45238 | 2011-03-07 | 19974 | -2.1
11 | 2011-03-20 | 2658.262 | 4.1524 | 2011-03-14 | 18508 | 2.7
12 | 2011-03-27 | 2775.701 | -1.9524 | 2011-03-23 | 19208 | -4.5
13 | 2011-04-03 | 2648.138 | 3.5 | 2011-03-28 | 18693 | 2.2
14 | 2011-04-10 | 2564.081 | 7.4286 | 2011-04-05 | 17726 | 5.2
15 | 2011-04-17 | 2519.186 | 7.8381 | 2011-04-13 | 16945 | 11.2
16 | 2011-04-24 | 2501.655 | 6.5 | 2011-04-18 | 17763 | 3.7
17 | 2011-05-01 | 2420.774 | 10.4619 | 2011-04-26 | 16703 | 11.6
18 | 2011-05-08 | 2412.314 | 11.2286 | 2011-05-03 | 17036 | 7
19 | 2011-05-15 | 2392.347 | 14.6667 | 2011-05-13 | 16340 | 25.8
20 | 2011-05-22 | 2423.044 | 15.981 | 2011-05-16 | 16671 | 10.2
21 | 2011-05-29 | 2375.854 | 16.781 | 2011-05-26 | 16587 | 20.2
22 | 2011-06-05 | 2563.83 | 20.5857 | 2011-05-31 | 20689 | 29.3
23 | 2011-06-12 | 2660.324 | 21.2 | 2011-06-08 | 22533 | 33.3
24 | 2011-06-19 | 2568.452 | 19.8048 | 2011-06-16 | 18715 | 24.7
25 | 2011-06-26 | 2647.068 | 20.9238 | 2011-06-21 | 19867 | 25.6
26 | 2011-07-03 | 2627.884 | 22.2429 | 2011-06-28 | 19718 | 26.3
27 | 2011-07-10 | 2869.302 | 24.2762 | 2011-07-06 | 21238 | 29.2
28 | 2011-07-17 | 3001.318 | 25.819 | 2011-07-12 | 22605 | 31.7
29 | 2011-07-24 | 3340.465 | 28.8381 | 2011-07-21 | 25285 | 37.5
30 | 2011-07-31 | 2944.723 | 25.1714 | 2011-07-29 | 21553 | 31.4
31 | 2011-08-07 | 2980.877 | 24.7476 | 2011-08-02 | 21933 | 31.3
32 | 2011-08-14 | 2786.159 | 22.2286 | 2011-08-08 | 21737 | 26.2
33 | 2011-08-21 | 2857.856 | 23.8857 | 2011-08-18 | 21317 | 29.9
34 | 2011-08-28 | 2679.356 | 21.9095 | 2011-08-24 | 19849 | 27.9
35 | 2011-09-04 | 2834.56 | 23.3381 | 2011-09-02 | 21374 | 28.3
36 | 2011-09-11 | 2513.313 | 18.5333 | 2011-09-09 | 18252 | 25.2
37 | 2011-09-18 | 2549.873 | 16.4429 | 2011-09-12 | 19983 | 28.5
38 | 2011-09-25 | 2534.472 | 18.0286 | 2011-09-21 | 17934 | 21.7
39 | 2011-10-02 | 2528.475 | 15.5333 | 2011-09-26 | 18464 | 24.1
40 | 2011-10-09 | 2468.478 | 15.981 | 2011-10-03 | 17372 | 14
41 | 2011-10-16 | 2452.727 | 15.4476 | 2011-10-11 | 17674 | 22.7
42 | 2011-10-23 | 2487.87 | 9.7476 | 2011-10-19 | 17644 | 11.7
43 | 2011-10-30 | 2552.612 | 6.6667 | 2011-10-27 | 18178 | 4.7
44 | 2011-11-06 | 2534.665 | 8.0762 | 2011-11-01 | 17812 | 12.7
45 | 2011-11-13 | 2539.151 | 9.9667 | 2011-11-11 | 18180 | 5.5
46 | 2011-11-20 | 2565.766 | 7.581 | 2011-11-17 | 18729 | 4.3
47 | 2011-11-27 | 2623.685 | 6.381 | 2011-11-22 | 19370 | 1.3
48 | 2011-12-04 | 2700.273 | 4.1476 | 2011-11-29 | 19553 | 5.6
49 | 2011-12-11 | 2791.724 | 0.80476 | 2011-12-07 | 19881 | 1.2
50 | 2011-12-18 | 2774.329 | 2.681 | 2011-12-12 | 19666 | 6.5
51 | 2011-12-25 | 3136.682 | 0.8619 | 2011-12-20 | 20144 | -1.3
52 | 2012-01-01 | 2196.658 | -0.25238 | 2011-12-29 | 19407 | -2.8
1 | 2012-01-08 | 2822.035 | -1.7476 | 2012-01-03 | 21615 | -14.3
2 | 2012-01-15 | 2860.282 | -1.8952 | 2012-01-15 | 20042 | -7.5
3 | 2012-01-22 | 2975.382 | -2.3333 | 2012-01-18 | 20836 | -4.5
4 | 2012-01-29 | 2851.318 | 0.95238 | 2012-01-25 | 20096 | -0.9
5 | 2012-02-05 | 2790.934 | 1.7286 | 2012-01-30 | 20173 | -1.4
6 | 2012-02-12 | 2836.756 | -1.7524 | 2012-02-07 | 19731 | -0.3
7 | 2012-02-19 | 2774.69 | 0.64286 | 2012-02-14 | 19527 | 1
8 | 2012-02-26 | 2751.527 | 0.98095 | 2012-02-21 | 19456 | 3
9 | 2012-03-04 | 2791.485 | 1.4048 | 2012-02-29 | 19773 | 1.3
10 | 2012-03-11 | 2740.816 | 3.3857 | 2012-03-05 | 20341 | -2.8
11 | 2012-03-18 | 2477.837 | 11.5429 | 2012-03-12 | 17582 | 11.8
12 | 2012-03-25 | 2440.227 | 16.0571 | 2012-03-22 | 17270 | 23.7
13 | 2012-04-01 | 2573.313 | 3.9857 | 2012-03-26 | 17978 | 2.6
14 | 2012-04-08 | 2430.949 | 7.7857 | 2012-04-03 | 17337 | 10.7
15 | 2012-04-15 | 2487.758 | 9.9 | 2012-04-10 | 17665 | 8
16 | 2012-04-22 | 2459.347 | 11.1857 | 2012-04-17 | 16991 | 10.4
17 | 2012-04-29 | 2503.789 | 6.6048 | 2012-04-23 | 17691 | 4.1
18 | 2012-05-06 | 2429.049 | 12.8714 | 2012-04-30 | 17429 | 9.4
19 | 2012-05-13 | 2391.626 | 15.7048 | 2012-05-07 | 16606 | 15.3
20 | 2012-05-20 | 2425.019 | 17.3905 | 2012-05-15 | 16943 | 23.7
21 | 2012-05-27 | 2612.829 | 22.3619 | 2012-05-25 | 19995 | 30.7
22 | 2012-06-03 | 2571.502 | 18.3714 | 2012-05-28 | 20922 | 28.6
23 | 2012-06-10 | 2556.36 | 19.8429 | 2012-06-10 | 19088 | 29
24 | 2012-06-17 | 2718.756 | 21.6 | 2012-06-11 | 21312 | 27.7
25 | 2012-06-24 | 3033.376 | 25.3905 | 2012-06-20 | 23783 | 34.2
26 | 2012-07-01 | 2828.257 | 24.1095 | 2012-06-29 | 21988 | 32.4
27 | 2012-07-08 | 3062.451 | 26.4571 | 2012-07-04 | 23801 | 35.9
28 | 2012-07-15 | 3032.484 | 25.3476 | 2012-07-13 | 22707 | 32.3
29 | 2012-07-22 | 3051.299 | 25.5857 | 2012-07-17 | 24470 | 36.2
30 | 2012-07-29 | 2979.547 | 24.8476 | 2012-07-23 | 23530 | 34.1
31 | 2012-08-05 | 3109.533 | 25.8952 | 2012-08-03 | 23013 | 30.1
32 | 2012-08-12 | 2765.755 | 22.2143 | 2012-08-08 | 22190 | 28.2
33 | 2012-08-19 | 2704.955 | 21.1524 | 2012-08-16 | 20235 | 26.8
34 | 2012-08-26 | 2825.816 | 23.1095 | 2012-08-24 | 21121 | 28.7
35 | 2012-09-02 | 2825.634 | 23.1286 | 2012-08-31 | 21766 | 32.6
36 | 2012-09-09 | 2779.356 | 21.1286 | 2012-09-06 | 21168 | 27.1
37 | 2012-09-16 | 2571.289 | 18.7333 | 2012-09-13 | 19869 | 28.7
38 | 2012-09-23 | 2464.238 | 14.9238 | 2012-09-17 | 17723 | 23.2
39 | 2012-09-30 | 2445.948 | 13.9 | 2012-09-25 | 17165 | 22
40 | 2012-10-07 | 2466.144 | 14.5524 | 2012-10-03 | 17669 | 18.5
41 | 2012-10-14 | 2487.466 | 9.6857 | 2012-10-11 | 17849 | 12.8
42 | 2012-10-21 | 2473.934 | 11.2143 | 2012-10-15 | 17828 | 11
43 | 2012-10-28 | 2522.418 | 10.6476 | 2012-10-24 | 17874 | 11.4
44 | 2012-11-04 | 2619.849 | 5.0095 | 2012-10-29 | 18597 | 4.3
45 | 2012-11-11 | 2665.5 | 4.9714 | 2012-11-06 | 19302 | 2.7
46 | 2012-11-18 | 2623.09 | 5.5857 | 2012-11-13 | 19161 | 3
47 | 2012-11-25 | 2632.78 | 5.5667 | 2012-11-19 | 18772 | 8.4
48 | 2012-12-02 | 2803.389 | 1.6 | 2012-11-26 | 20012 | 2.5
49 | 2012-12-09 | 2345.457 | 3.6524 | 2012-12-05 | 20217 | 1.5
50 | 2012-12-16 | 3198.076 | 2.019 | 2012-12-11 | 20413 | -1
51 | 2012-12-23 | 3164.706 | 2.6952 | 2012-12-20 | 19846 | 2.6
52 | 2012-12-29 | 2659.264 | -3.1286 | 2012-12-27 | 19078 | -3.1
1 | 2013-01-06 | 2409.875 | -2.2571 | 2013-01-02 | 20601 | -2.8
2 | 2013-01-13 | 2742.03 | 4.7095 | 2013-01-07 | 20172 | 0.3
3 | 2013-01-20 | 2868.518 | -2.2524 | 2013-01-17 | 20779 | -7.3
4 | 2013-01-27 | 3164.884 | -9.9381 | 2013-01-24 | 22423 | -11.6
5 | 2013-02-03 | 2948.027 | -1.8524 | 2013-01-31 | 20602 | -2.6
6 | 2013-02-10 | 3044.013 | -6.3143 | 2013-02-04 | 21493 | -5.8
7 | 2013-02-17 | 2878.093 | -2.5857 | 2013-02-12 | 20053 | 0.6
8 | 2013-02-24 | 2887.399 | -2.9762 | 2013-02-20 | 20805 | -5.5
9 | 2013-03-03 | 2805.264 | -1.3714 | 2013-02-27 | 19831 | 1.5
10 | 2013-03-10 | 2712.272 | 1.7524 | 2013-03-04 | 19863 | -1.8
11 | 2013-03-17 | 2714.361 | 0 | 2013-03-14 | 19065 | 0.1
12 | 2013-03-24 | 2752.129 | -1.081 | 2013-03-20 | 19269 | -1.3
13 | 2013-03-31 | 2517.294 | 5.8 | 2013-03-27 | 18211 | 6.9
14 | 2013-04-07 | 2632.151 | 2.6 | 2013-04-02 | 18820 | 2.5
15 | 2013-04-14 | 2618.614 | 5.0667 | 2013-04-11 | 18375 | 0.1
16 | 2013-04-21 | 2511.671 | 9.0619 | 2013-04-15 | 17215 | 12.6
17 | 2013-04-28 | 2451.728 | 9.219 | 2013-04-24 | 17430 | 12.3
18 | 2013-05-05 | 2371.425 | 17.0143 | 2013-04-29 | 16558 | 13.1
19 | 2013-05-12 | 2398.106 | 15.1762 | 2013-05-08 | 16570 | 21.8
20 | 2013-05-19 | 2365.876 | 14.0905 | 2013-05-13 | 16480 | 10.8
21 | 2013-05-26 | 2410.307 | 15.9429 | 2013-05-21 | 18107 | 24.6
22 | 2013-06-02 | 2602.253 | 21.0667 | 2013-05-31 | 20372 | 29.9
23 | 2013-06-09 | 2403.479 | 15.5667 | 2013-06-06 | 16509 | 14.8
24 | 2013-06-16 | 2505.328 | 19.4238 | 2013-06-12 | 17635 | 22.4
25 | 2013-06-23 | 2631.536 | 20.8857 | 2013-06-23 | 20041 | 31.9
26 | 2013-06-30 | 2860.767 | 23.5286 | 2013-06-24 | 22541 | 31.6
27 | 2013-07-07 | 2765.496 | 23.0667 | 2013-07-04 | 21251 | 27.8
28 | 2013-07-14 | 2882.921 | 23.6619 | 2013-07-10 | 21645 | 30.5
29 | 2013-07-21 | 3288.153 | 27.4 | 2013-07-17 | 24708 | 34.3
30 | 2013-07-28 | 2622.999 | 20.181 | 2013-07-23 | 20105 | 27.4
31 | 2013-08-04 | 2542.321 | 20.2667 | 2013-08-01 | 18382 | 25.7
32 | 2013-08-11 | 2601.064 | 21.5238 | 2013-08-08 | 20078 | 26.5
33 | 2013-08-18 | 2565.818 | 19.9714 | 2013-08-12 | 18022 | 23
34 | 2013-08-25 | 2844.42 | 23.7048 | 2013-08-21 | 22146 | 31.4
35 | 2013-09-01 | 2990.963 | 24.1476 | 2013-08-29 | 22809 | 28.2
36 | 2013-09-08 | 2490.095 | 18.4952 | 2013-09-04 | 18164 | 25.3
37 | 2013-09-15 | 2667.838 | 18.9095 | 2013-09-10 | 22545 | 33.9
38 | 2013-09-22 | 2468.567 | 15.1048 | 2013-09-20 | 17696 | 23.5
39 | 2013-09-29 | 2439.383 | 15.6 | 2013-09-26 | 17321 | 20.5
40 | 2013-10-06 | 2523.773 | 17.9048 | 2013-10-02 | 17992 | 24.6
41 | 2013-10-13 | 2431.049 | 13.5048 | 2013-10-09 | 17386 | 17.6
42 | 2013-10-20 | 2428.382 | 12.4619 | 2013-10-15 | 17497 | 17.1
43 | 2013-10-27 | 2568.283 | 6.6905 | 2013-10-24 | 18084 | 8.3
44 | 2013-11-03 | 2575.664 | 4.3048 | 2013-10-29 | 18356 | 6.6
45 | 2013-11-10 | 2613.409 | 6.2381 | 2013-11-04 | 18791 | 5.2
46 | 2013-11-17 | 2658.795 | 5.3476 | 2013-11-12 | 19763 | 0.5
47 | 2013-11-24 | 2766.996 | 1.0286 | 2013-11-24 | 19790 | -5.2
48 | 2013-11-30 | 2510.417 | -1.4143 | 2013-11-28 | 20469 | -3.3
49 | 2013-12-08 | 2843.653 | 0.71905 | 2013-12-02 | 20029 | 2.5
50 | 2013-12-15 | 3088.18 | -7.5905 | 2013-12-12 | 21727 | -7.8
51 | 2013-12-22 | 2533.378 | -3.0143 | 2013-12-16 | 21867 | -8.3
52 | 2013-12-29 | 3428.571 | -3.4048 | 2013-12-24 | 18960 | -9.9
1 | 2014-01-05 | 2980.559 | -9.9143 | 2014-01-02 | 22342 | -17.9
2 | 2014-01-12 | 3047.657 | -6.2667 | 2014-01-07 | 22725 | -17.4
3 | 2014-01-19 | 2893.573 | -1.0524 | 2014-01-15 | 20465 | -1.2
4 | 2014-01-26 | 3255.467 | -13.2571 | 2014-01-22 | 22717 | -14.4
5 | 2014-02-02 | 3111.181 | -7.5 | 2014-01-28 | 22377 | -12.8
6 | 2014-02-09 | 3095.934 | -9.9333 | 2014-02-05 | 21296 | -6.8
7 | 2014-02-16 | 3077.107 | -8.5905 | 2014-02-11 | 21772 | -10.2
8 | 2014-02-23 | 2869.348 | -1.419 | 2014-02-18 | 20357 | -1.6
9 | 2014-03-02 | 3075.27 | -10.3714 | 2014-02-27 | 21728 | -12.2
10 | 2014-03-09 | 2981.282 | -7.2286 | 2014-03-03 | 21642 | -12.1
11 | 2014-03-16 | 2821.492 | -1.5952 | 2014-03-13 | 20245 | -8
12 | 2014-03-23 | 2834.923 | -1.3905 | 2014-03-17 | 20120 | -4.5
13 | 2014-03-30 | 2824.759 | -1.1238 | 2014-03-26 | 20046 | -5.1
14 | 2014-04-06 | 2621.434 | 4.2762 | 2014-04-03 | 18027 | 3.4
15 | 2014-04-13 | 2520.922 | 10.0714 | 2014-04-07 | 18102 | 9.1
16 | 2014-04-20 | 2506.027 | 6.0381 | 2014-04-15 | 18552 | -0.9
17 | 2014-04-27 | 2474.661 | 8.7905 | 2014-04-22 | 17253 | 11.3
18 | 2014-05-04 | 2476.605 | 9.119 | 2014-04-30 | 17633 | 6.6
19 | 2014-05-11 | 2372.395 | 14.1714 | 2014-05-07 | 16515 | 13
20 | 2014-05-18 | 2395.651 | 13.8714 | 2014-05-13 | 16859 | 20.6
21 | 2014-05-25 | 2331.344 | 17.0905 | 2014-05-21 | 16532 | 19.6
22 | 2014-06-01 | 2471.538 | 19.6524 | 2014-05-27 | 18762 | 29.4
23 | 2014-06-08 | 2515.024 | 19.8333 | 2014-06-02 | 18848 | 29.1
24 | 2014-06-15 | 2543.584 | 19.8952 | 2014-06-12 | 18594 | 26.2
25 | 2014-06-22 | 2599.973 | 21.0667 | 2014-06-17 | 19826 | 31.2
26 | 2014-06-29 | 2819.858 | 23.1095 | 2014-06-24 | 19847 | 27.9
27 | 2014-07-06 | 2714.132 | 23.3429 | 2014-06-30 | 20852 | 30.3
28 | 2014-07-13 | 2669.169 | 22.2 | 2014-07-07 | 20006 | 28.4
29 | 2014-07-20 | 2552.327 | 19.6857 | 2014-07-14 | 18418 | 22.4
30 | 2014-07-27 | 2741.847 | 22.7857 | 2014-07-22 | 21250 | 29.8
31 | 2014-08-03 | 2568.17 | 20.5286 | 2014-08-01 | 18453 | 27
32 | 2014-08-10 | 2650.137 | 21.681 | 2014-08-06 | 18833 | 24.7
33 | 2014-08-17 | 2568.169 | 19.481 | 2014-08-11 | 19849 | 27.5
34 | 2014-08-24 | 2668.166 | 20.7238 | 2014-08-21 | 19519 | 25.7
35 | 2014-08-31 | 2737.966 | 22.9857 | 2014-08-26 | 21457 | 31.3
36 | 2014-09-07 | 2734.093 | 22.9905 | 2014-09-05 | 21341 | 31.4
37 | 2014-09-14 | 2509.656 | 15.7048 | 2014-09-10 | 18939 | 22.7
38 | 2014-09-21 | 2416.075 | 15.4762 | 2014-09-15 | 17138 | 17.8
39 | 2014-09-28 | 2449.553 | 17.6095 | 2014-09-25 | 17439 | 20.9
40 | 2014-10-05 | 2455.573 | 15.6 | 2014-09-29 | 18206 | 23.9
41 | 2014-10-12 | 2413.467 | 10.8429 | 2014-10-09 | 17405 | 13.9
42 | 2014-10-19 | 2395.899 | 13.6714 | 2014-10-14 | 17562 | 22.1
43 | 2014-10-26 | 2452.995 | 10.5667 | 2014-10-20 | 17679 | 11.8
44 | 2014-11-02 | 2516.429 | 6.4143 | 2014-10-30 | 17777 | 9.1
45 | 2014-11-09 | 2562.845 | 6.1619 | 2014-11-07 | 18215 | 9
46 | 2014-11-16 | 2648.011 | 4.2238 | 2014-11-13 | 19129 | 16.5
47 | 2014-11-23 | 2821.612 | -3.4048 | 2014-11-19 | 20091 | 0.8
48 | 2014-11-30 | 2775.392 | 2.7714 | 2014-11-28 | 19823 | 1.3
49 | 2014-12-07 | 3283.115 | -0.72381 | 2014-12-02 | 20813 | -1.2
50 | 2014-12-14 | 2859.799 | 0.39048 | 2014-12-11 | 20252 | -3.9
51 | 2014-12-21 | 2411.784 | 0.33333 | 2014-12-18 | 20068 | -0.7
52 | 2014-12-28 | 2822.78 | 4.4286 | 2014-12-22 | 19495 | 1.6
1 | 2015-01-04 | 2301.463 | -3.0095 | 2014-12-30 | 19294 | -3.4
2 | 2015-01-11 | 3057.961 | -10.5857 | 2015-01-07 | 21689 | -15.7
3 | 2015-01-18 | 3017.139 | -6.4905 | 2015-01-13 | 21134 | -11.6
4 | 2015-01-25 | 2937.356 | -5.0667 | 2015-01-20 | 20704 | -6.7
5 | 2015-02-01 | 3027.87 | -7.981 | 2015-01-27 | 20823 | -6.8
6 | 2015-02-08 | 3041.641 | -8.3238 | 2015-02-02 | 20807 | -11.3
7 | 2015-02-15 | 3084.421 | -11.6714 | 2015-02-12 | 21014 | -14.5
8 | 2015-02-22 | 3132.266 | -13.0905 | 2015-02-19 | 21474 | -15.8
9 | 2015-03-01 | 3090.03 | -12.0143 | 2015-02-23 | 21440 | -15.5
10 | 2015-03-08 | 2913.928 | -5.5048 | 2015-03-05 | 20934 | -9.6
11 | 2015-03-15 | 2638.4 | 3.0333 | 2015-03-09 | 18606 | 5.4
12 | 2015-03-22 | 2632.494 | 1.0476 | 2015-03-18 | 18457 | 2
13 | 2015-03-29 | 2715.982 | -1.5143 | 2015-03-23 | 19292 | -2.9
14 | 2015-04-05 | 2505.908 | 4.6714 | 2015-03-30 | 18059 | 6.9
15 | 2015-04-12 | 2545.891 | 6.8667 | 2015-04-08 | 18322 | 2.4
16 | 2015-04-19 | 2332.075 | 12.8905 | 2015-04-16 | 16601 | 14.9
17 | 2015-04-26 | 2442.08 | 6.4 | 2015-04-23 | 17598 | 2.8
18 | 2015-05-03 | 2313.268 | 14.7286 | 2015-04-27 | 16471 | 12.1
19 | 2015-05-10 | 2410.036 | 18.5333 | 2015-05-08 | 16839 | 24.1
20 | 2015-05-17 | 2348.964 | 15.181 | 2015-05-11 | 17104 | 19.2
21 | 2015-05-24 | 2299.844 | 16.1762 | 2015-05-18 | 16442 | 28.2
22 | 2015-05-31 | 2569.175 | 21.2905 | 2015-05-26 | 19339 | 28.8
23 | 2015-06-07 | 2363.66 | 15.8952 | 2015-06-05 | 17230 | 24.3
24 | 2015-06-14 | 2485.383 | 19.8905 | 2015-06-10 | 18133 | 27.6
25 | 2015-06-21 | 2552.342 | 20.7619 | 2015-06-15 | 18899 | 24.1
26 | 2015-06-28 | 2526.585 | 19.4143 | 2015-06-22 | 19328 | 25.5
27 | 2015-07-05 | 2378.004 | 19.6 | 2015-07-05 | 17258 | 25.6
28 | 2015-07-12 | 2668.985 | 22.2762 | 2015-07-06 | 19906 | 26.6
29 | 2015-07-19 | 2745.486 | 22.7905 | 2015-07-13 | 20698 | 28.1
30 | 2015-07-26 | 2782.495 | 23.7429 | 2015-07-20 | 20434 | 28
31 | 2015-08-02 | 2964.323 | 25.6143 | 2015-07-28 | 22508 | 32.5
32 | 2015-08-09 | 2540.375 | 21.081 | 2015-08-04 | 18181 | 25.8
33 | 2015-08-16 | 2730.578 | 22.8476 | 2015-08-16 | 20595 | 30.4
34 | 2015-08-23 | 2843.997 | 23.1333 | 2015-08-17 | 22396 | 32.1
35 | 2015-08-30 | 2541.425 | 19.3762 | 2015-08-30 | 18040 | 25.4
36 | 2015-09-06 | 3001.099 | 25.8 | 2015-09-02 | 21922 | 32.6
37 | 2015-09-13 | 2697.254 | 20.5619 | 2015-09-08 | 21842 | 28.7
38 | 2015-09-20 | 2580.759 | 20.8571 | 2015-09-17 | 20119 | 27.2
39 | 2015-09-27 | 2446.319 | 17.6476 | 2015-09-24 | 17875 | 22.6
40 | 2015-10-04 | 2421.31 | 13.7714 | 2015-09-28 | 18125 | 21.7
41 | 2015-10-11 | 2401.672 | 14.2333 | 2015-10-05 | 17363 | 14.2
42 | 2015-10-18 | 2381.522 | 9.8905 | 2015-10-15 | 16920 | 17.6
43 | 2015-10-25 | 2450.749 | 11.0286 | 2015-10-21 | 17269 | 10.6
44 | 2015-11-01 | 2485.082 | 8.6429 | 2015-10-26 | 17633 | 9.7
45 | 2015-11-08 | 2402.716 | 11.919 | 2015-11-03 | 17328 | 20.6
46 | 2015-11-15 | 2469.064 | 7.5571 | 2015-11-10 | 17850 | 9.2
47 | 2015-11-22 | 2481.201 | 6.7762 | 2015-11-17 | 17754 | 7.6
48 | 2015-11-29 | 2613.703 | 4.0429 | 2015-11-23 | 19042 | 1.9
49 | 2015-12-06 | 2254.946 | 4.0333 | 2015-11-30 | 19088 | 3
50 | 2015-12-13 | 2968.924 | 6.6667 | 2015-12-07 | 19002 | 5.4
51 | 2015-12-20 | 2633.978 | 3.8429 | 2015-12-16 | 18979 | 4.3
52 | 2015-12-27 | 2384.288 | 7.0238 | 2015-12-21 | 18443 | 6.6
53 | 2016-01-03 | 2531.649 | -0.48095 | 2016-01-03 | 18387 | 1.6
1 | 2016-01-10 | 2788.552 | -1.4333 | 2016-01-04 | 20719 | -11.8
2 | 2016-01-17 | 2880.036 | -4.2095 | 2016-01-11 | 20456 | -6.6
3 | 2016-01-24 | 2913.484 | -6.3286 | 2016-01-19 | 20616 | -4.3
4 | 2016-01-31 | 2737.29 | 1.0238 | 2016-01-29 | 19334 | -5.1
5 | 2016-02-07 | 2659.753 | 2.9048 | 2016-02-04 | 18732 | 2.9
6 | 2016-02-14 | 2928.908 | -8.2524 | 2016-02-11 | 20638 | -10
7 | 2016-02-21 | 2773.267 | -0.43333 | 2016-02-17 | 19976 | -1.4
8 | 2016-02-28 | 2731.77 | 0.31905 | 2016-02-24 | 19513 | 1.7
9 | 2016-03-06 | 2774.538 | -3.5571 | 2016-03-01 | 19933 | -7.9
10 | 2016-03-13 | 2473.733 | 8.8381 | 2016-03-07 | 17751 | 11.5
11 | 2016-03-20 | 2492.021 | 4.8952 | 2016-03-14 | 17209 | 8.7
12 | 2016-03-27 | 2515.03 | 1.9524 | 2016-03-24 | 18071 | -0.2
13 | 2016-04-03 | 2481.273 | 5.0333 | 2016-03-29 | 17370 | 7.2
14 | 2016-04-10 | 2606.917 | -0.86667 | 2016-04-04 | 18021 | -2.4
15 | 2016-04-17 | 2425.388 | 8.0048 | 2016-04-12 | 17669 | 6.7
16 | 2016-04-24 | 2305.512 | 11.7 | 2016-04-18 | 16356 | 22.9
17 | 2016-05-01 | 2362.348 | 7.1381 | 2016-04-25 | 16796 | 7.4
18 | 2016-05-08 | 2270.087 | 12 | 2016-05-02 | 16020 | 12
19 | 2016-05-15 | 2270.723 | 12.219 | 2016-05-12 | 15980 | 20.5
20 | 2016-05-22 | 2256.595 | 14.8667 | 2016-05-19 | 15942 | 19.7
21 | 2016-05-29 | 2403.564 | 23.9762 | 2016-05-27 | 19637 | 28.9
22 | 2016-06-05 | 2599.792 | 21.6619 | 2016-05-30 | 19852 | 27.2
23 | 2016-06-12 | 2375.761 | 17.9857 | 2016-06-11 | 17525 | 30.2
24 | 2016-06-19 | 2588.618 | 21.9857 | 2016-06-19 | 20020 | 32.1
25 | 2016-06-26 | 2743.584 | 23.8762 | 2016-06-20 | 21673 | 34
26 | 2016-07-03 | 2563.388 | 22.3667 | 2016-06-27 | 21680 | 32.5
27 | 2016-07-10 | 2862.87 | 25.3 | 2016-07-07 | 21388 | 30.9
28 | 2016-07-17 | 2832.049 | 24.7 | 2016-07-13 | 22709 | 35
29 | 2016-07-24 | 2927.854 | 26.1476 | 2016-07-22 | 22068 | 35.1
30 | 2016-07-31 | 2899.923 | 25.7333 | 2016-07-27 | 21707 | 33.7
31 | 2016-08-07 | 2944.088 | 25.9571 | 2016-08-04 | 22364 | 31.9
32 | 2016-08-14 | 3104.654 | 27.3571 | 2016-08-10 | 23128 | 34.8
33 | 2016-08-21 | 2925.272 | 24.2952 | 2016-08-19 | 21654 | 29.3
34 | 2016-08-28 | 2849.378 | 24.3524 | 2016-08-25 | 21510 | 29.7
35 | 2016-09-04 | 2647.95 | 21.9714 | 2016-08-30 | 21380 | 30.1
36 | 2016-09-11 | 2875.792 | 25.2 | 2016-09-07 | 23106 | 34.5
37 | 2016-09-18 | 2523.08 | 20.2476 | 2016-09-13 | 18966 | 27.8
38 | 2016-09-25 | 2555.66 | 19.9476 | 2016-09-19 | 19615 | 25.6
39 | 2016-10-02 | 2370.988 | 16.3238 | 2016-09-27 | 16876 | 21.8
40 | 2016-10-09 | 2361.984 | 16.3762 | 2016-10-06 | 17376 | 23
41 | 2016-10-16 | 2300.832 | 13.8333 | 2016-10-11 | 16802 | 16.5
42 | 2016-10-23 | 2378.094 | 13.9857 | 2016-10-18 | 17360 | 25.2
43 | 2016-10-30 | 2466.419 | 7.2143 | 2016-10-27 | 18018 | 5.2
44 | 2016-11-06 | 2047.66 | 10.1714 | 2016-11-02 | 17131 | 18
45 | 2016-11-13 | 2394.658 | 7.9476 | 2016-11-08 | 17349 | 15.8
46 | 2016-11-20 | 2464.404 | 7.9143 | 2016-11-20 | 17779 | 1.4
47 | 2016-11-27 | 2658.614 | 2.5286 | 2016-11-23 | 19203 | 0.2
48 | 2016-12-04 | 2564.837 | 5.7238 | 2016-11-28 | 18210 | 7
49 | 2016-12-10 | 2332.178 | -0.48095 | 2016-12-09 | 19264 | -1.4
50 | 2016-12-18 | 2873.365 | -5.081 | 2016-12-15 | 20657 | -8.1
51 | 2016-12-25 | 3496.243 | -1.5857 | 2016-12-19 | 20592 | -7.8
52 | 2017-01-01 | 2194.803 | 0.15714 | 2016-12-28 | 17992 | -1.8
1 | 2017-01-08 | 2800.458 | -5.0571 | 2017-01-05 | 19869 | -6.6
2 | 2017-01-15 | 2791.668 | -1.5571 | 2017-01-09 | 20192 | -3.3
3 | 2017-01-22 | 2683.189 | 2.3524 | 2017-01-17 | 19118 | 1.7
4 | 2017-01-29 | 2682.02 | 0.59524 | 2017-01-24 | 18640 | 1.2
5 | 2017-02-05 | 2799.958 | -3.9333 | 2017-01-30 | 19704 | -4.9
6 | 2017-02-12 | 2791.09 | -2.3667 | 2017-02-07 | 19584 | -1.1
7 | 2017-02-19 | 2624.133 | 0.45714 | 2017-02-16 | 19189 | -3.7
8 | 2017-02-26 | 2472.737 | 4.5333 | 2017-02-21 | 17837 | 5.5
9 | 2017-03-05 | 2635.347 | -0.2381 | 2017-03-03 | 19004 | -5.6
10 | 2017-03-12 | 2648.322 | -0.27619 | 2017-03-10 | 18977 | -4.6
11 | 2017-03-19 | 2689.337 | -2.681 | 2017-03-13 | 19109 | -6.1
12 | 2017-03-26 | 2570.353 | 2.8857 | 2017-03-22 | 18574 | -2.5
13 | 2017-04-02 | 2479.132 | 6.7571 | 2017-03-30 | 17510 | 2.9
14 | 2017-04-09 | 2395.597 | 8.2048 | 2017-04-06 | 17281 | 7.3
15 | 2017-04-16 | 2228.476 | 13.0762 | 2017-04-12 | 16506 | 7.7
16 | 2017-04-23 | 2301.158 | 10.0524 | 2017-04-20 | 16381 | 5.4
17 | 2017-04-30 | 2255.022 | 11.581 | 2017-04-25 | 15935 | 9.3
18 | 2017-05-07 | 2331.499 | 8.681 | 2017-05-04 | 16227 | 10
19 | 2017-05-14 | 2283.432 | 10.1619 | 2017-05-08 | 16078 | 11.1
20 | 2017-05-21 | 2275.55 | 16.3476 | 2017-05-18 | 17704 | 29.6
21 | 2017-05-28 | 2250.356 | 16.0667 | 2017-05-25 | 15950 | 11.9
22 | 2017-06-04 | 2276.16 | 17.7857 | 2017-05-29 | 16317 | 25.1
23 | 2017-06-11 | 2391.17 | 19.9714 | 2017-06-11 | 18926 | 31.6
24 | 2017-06-18 | 2710.523 | 23.5667 | 2017-06-12 | 21165 | 32.4
25 | 2017-06-25 | 2514.885 | 20.7524 | 2017-06-19 | 18783 | 25.8
26 | 2017-07-02 | 2429.473 | 21.2333 | 2017-06-30 | 18253 | 27.9
27 | 2017-07-09 | 2564.696 | 22.919 | 2017-07-06 | 20312 | 29.6
28 | 2017-07-16 | 2641.147 | 22.4524 | 2017-07-11 | 20191 | 28.9
29 | 2017-07-23 | 2751.121 | 23.7905 | 2017-07-19 | 20580 | 31.5
30 | 2017-07-30 | 2540.604 | 21.8524 | 2017-07-27 | 19098 | 25.8
31 | 2017-08-06 | 2680.86 | 22.7905 | 2017-07-31 | 20184 | 30.8
32 | 2017-08-13 | 2550.852 | 22.0524 | 2017-08-09 | 19389 | 28.7
33 | 2017-08-20 | 2628.866 | 22.0619 | 2017-08-15 | 19198 | 27.2
34 | 2017-08-27 | 2482.693 | 19.8762 | 2017-08-21 | 20313 | 30
35 | 2017-09-03 | 2338.323 | 17.7238 | 2017-08-30 | 17703 | 23.9
36 | 2017-09-10 | 2247.089 | 16.6667 | 2017-09-05 | 16449 | 21
37 | 2017-09-17 | 2489.987 | 21.0095 | 2017-09-14 | 18415 | 27
38 | 2017-09-24 | 2771.142 | 24.2905 | 2017-09-24 | 20394 | 33.3
39 | 2017-10-01 | 2574.485 | 18.5667 | 2017-09-25 | 21682 | 31.3
40 | 2017-10-08 | 2374.265 | 19.4905 | 2017-10-04 | 17491 | 26.5
41 | 2017-10-15 | 2326.158 | 15.8048 | 2017-10-10 | 16620 | 22.9
42 | 2017-10-22 | 2276.504 | 15.0333 | 2017-10-16 | 16750 | 10.1
43 | 2017-10-29 | 2351.981 | 10.3095 | 2017-10-26 | 16698 | 10.6
44 | 2017-11-05 | 2448.709 | 8.081 | 2017-11-01 | 17664 | 6.7
45 | 2017-11-12 | 2573.358 | 2.3333 | 2017-11-10 | 18731 | -4
46 | 2017-11-19 | 2593.993 | 4.0905 | 2017-11-13 | 18616 | 5.3
47 | 2017-11-26 | 2582.342 | 4.1286 | 2017-11-22 | 18924 | 0.1
48 | 2017-12-03 | 2945.44 | 4.6762 | 2017-11-27 | 18998 | 3
49 | 2017-12-10 | 2308.909 | 1.1714 | 2017-12-07 | 19148 | 0.1
50 | 2017-12-17 | 3356.972 | -7.419 | 2017-12-13 | 20293 | -7.5
51 | 2017-12-24 | 2791.103 | -1.4714 | 2017-12-21 | 19627 | -2.9
52 | 2017-12-31 | 2472.533 | -12.5476 | 2017-12-28 | 20010 | -12.8
1 | 2018-01-07 | 3045.502 | -13.0476 | 2018-01-05 | 20747 | -15.2
2 | 2018-01-14 | 2841.975 | -1.9143 | 2018-01-14 | 19921 | -6.7
3 | 2018-01-21 | 2857.148 | -3.4571 | 2018-01-15 | 20175 | -7.3
4 | 2018-01-28 | 2752.903 | 0.21905 | 2018-01-24 | 19844 | -5.3
5 | 2018-02-04 | 2871.627 | -5.0286 | 2018-01-30 | 20211 | -8.3
6 | 2018-02-11 | 2928.324 | -6.9 | 2018-02-07 | 19913 | -5.1
7 | 2018-02-18 | 2730.743 | -0.79524 | 2018-02-13 | 19555 | -4.1
8 | 2018-02-25 | 2622.584 | 4.1095 | 2018-02-22 | 18620 | 1.4
9 | 2018-03-04 | 2536.83 | 3.9667 | 2018-02-26 | 17795 | 7
10 | 2018-03-11 | 2644.177 | -0.085714 | 2018-03-06 | 18393 | 0.2
11 | 2018-03-18 | 2611.579 | -0.17143 | 2018-03-12 | 18079 | -0.3
12 | 2018-03-25 | 2568.737 | -0.24286 | 2018-03-19 | 18015 | -0.1
13 | 2018-04-01 | 2458.085 | 3.9333 | 2018-03-27 | 17354 | 3
14 | 2018-04-08 | 2573.814 | 0.69048 | 2018-04-04 | 17882 | 2.4
15 | 2018-04-15 | 2582.041 | 2.1762 | 2018-04-09 | 17555 | 2.9
16 | 2018-04-22 | 2482.217 | 4.2286 | 2018-04-17 | 17480 | 0.7
17 | 2018-04-29 | 2319.02 | 9.6381 | 2018-04-25 | 16167 | 11
18 | 2018-05-06 | 2239.906 | 17.6238 | 2018-05-02 | 16086 | 27.5
19 | 2018-05-13 | 2234.572 | 13.9381 | 2018-05-08 | 15706 | 18.5
20 | 2018-05-20 | 2255.281 | 16.8667 | 2018-05-14 | 15980 | 24.1
21 | 2018-05-27 | 2375.999 | 20.5714 | 2018-05-25 | 17788 | 30.2
22 | 2018-06-03 | 2694.117 | 23.0476 | 2018-05-28 | 20394 | 30.7
23 | 2018-06-10 | 2332.158 | 17.3524 | 2018-06-08 | 16765 | 21.9
24 | 2018-06-17 | 2570.35 | 22.3571 | 2018-06-17 | 20161 | 31.3
25 | 2018-06-24 | 2589.977 | 20.6095 | 2018-06-18 | 20992 | 30.2
26 | 2018-07-01 | 2799.84 | 24.5 | 2018-06-29 | 21037 | 31
27 | 2018-07-08 | 2918.27 | 25.5048 | 2018-07-05 | 23374 | 33.2
28 | 2018-07-15 | 2959.067 | 25.5905 | 2018-07-15 | 21510 | 29.9
29 | 2018-07-22 | 2806.574 | 23.5857 | 2018-07-16 | 21455 | 31.5
30 | 2018-07-29 | 2804.722 | 23.5524 | 2018-07-24 | 21545 | 29.5
31 | 2018-08-05 | 2903.656 | 25.219 | 2018-08-03 | 21028 | 28.5
32 | 2018-08-12 | 2886.233 | 24.3524 | 2018-08-07 | 21190 | 27.5
33 | 2018-08-19 | 2947.795 | 24.6095 | 2018-08-15 | 21456 | 30.9
34 | 2018-08-26 | 2701.424 | 22.6238 | 2018-08-20 | 20142 | 25
35 | 2018-09-02 | 2867.372 | 23.8286 | 2018-08-28 | 22175 | 31.7
36 | 2018-09-09 | 2762.349 | 22.0048 | 2018-09-05 | 23131 | 33.9
37 | 2018-09-16 | 2678.651 | 21.0952 | 2018-09-16 | 20871 | 28.3
38 | 2018-09-23 | 2579.775 | 19.4524 | 2018-09-17 | 21233 | 26.3
39 | 2018-09-30 | 2380.053 | 15.619 | 2018-09-25 | 17419 | 20.4
40 | 2018-10-07 | 2394.01 | 12.7381 | 2018-10-02 | 16841 | 12.9
41 | 2018-10-14 | 2397.565 | 14.7 | 2018-10-09 | 18640 | 28.6
42 | 2018-10-21 | 2409.557 | 7.7714 | 2018-10-17 | 17040 | 8.5
43 | 2018-10-28 | 2514.239 | 5.3143 | 2018-10-24 | 17481 | 5.2
44 | 2018-11-04 | 2501.666 | 6.3857 | 2018-10-29 | 17267 | 8.5
45 | 2018-11-11 | 2555.529 | 5.1952 | 2018-11-09 | 18209 | 2.6
46 | 2018-11-18 | 2700.142 | 0.41905 | 2018-11-14 | 19232 | 0.3
47 | 2018-11-25 | 2739.306 | -0.68095 | 2018-11-22 | 20048 | -6.6
48 | 2018-12-02 | 2713.598 | 2.5476 | 2018-11-27 | 19248 | 1.2
49 | 2018-12-07 | 2019.62 | -1.8905 | 2018-12-07 | 19686 | -4
50 | 2018-12-16 | 3213.188 | 1.019 | 2018-12-11 | 19718 | -1.4
51 | 2018-12-23 | 2723.873 | 1.019 | 2018-12-18 | 19450 | 0.2
52 | 2018-12-30 | 2915.267 | 0.34286 | 2018-12-27 | 18108 | -0.2
1 | 2019-01-06 | 2616.032 | 0.071429 | 2019-01-02 | 19580 | -3.9
2 | 2019-01-13 | 2826.392 | -4.2524 | 2019-01-10 | 19872 | -5.1
3 | 2019-01-20 | 2947.535 | -6.981 | 2019-01-20 | 20841 | -14.5
4 | 2019-01-27 | 2983.872 | -7.0667 | 2019-01-21 | 21356 | -11.8
5 | 2019-02-03 | 3039.29 | -9.4762 | 2019-01-31 | 21174 | -14.6
6 | 2019-02-10 | 2825.025 | -1.5571 | 2019-02-06 | 19739 | -1.1
7 | 2019-02-17 | 2825.059 | -3.4714 | 2019-02-12 | 20043 | -1.2
8 | 2019-02-24 | 2768.176 | -2.0905 | 2019-02-19 | 19796 | -4.4
9 | 2019-03-03 | 2863.896 | -6.5167 | 2019-02-27 | 20436 | -7.7
10 | 2019-03-10 | 2833.518 | -6.8929 | 2019-03-05 | 20176 | -9
11 | 2019-03-17 | 2603.892 | 1.8333 | 2019-03-11 | 18103 | 2
12 | 2019-03-24 | 2559.903 | 3.1619 | 2019-03-18 | 18023 | 2.6
13 | 2019-03-31 | 2530.669 | 3.3833 | 2019-03-26 | 17633 | 3.6
14 | 2019-04-07 | 2474.168 | 5.1238 | 2019-04-01 | 17516 | 2.8
15 | 2019-04-14 | 2432.225 | 7.019 | 2019-04-11 | 17180 | 1.3
16 | 2019-04-21 | 2348.088 | 8.5762 | 2019-04-15 | 16614 | 8.3
17 | 2019-04-28 | 2332.199 | 9.1143 | 2019-04-24 | 16068 | 12.8
18 | 2019-05-05 | 2398.814 | 8.2857 | 2019-04-29 | 16946 | 6.9
19 | 2019-05-12 | 2293.824 | 11.0429 | 2019-05-09 | 15930 | 14.4
20 | 2019-05-19 | 2311.692 | 12.8381 | 2019-05-13 | 16416 | 7.2
21 | 2019-05-26 | 2263.491 | 16.2048 | 2019-05-22 | 15851 | 15.1
22 | 2019-06-02 | 2321.033 | 15.5857 | 2019-05-27 | 16051 | 22.5
23 | 2019-06-09 | 2325.469 | 17.6571 | 2019-06-07 | 16394 | 25.8
24 | 2019-06-16 | 2313.68 | 17.2286 | 2019-06-10 | 16208 | 18.4
25 | 2019-06-23 | 2433.787 | 20.3857 | 2019-06-19 | 17956 | 24.8
26 | 2019-06-30 | 2699.016 | 23.6095 | 2019-06-27 | 20178 | 28.9
27 | 2019-07-07 | 2873.591 | 24.8952 | 2019-07-05 | 21727 | 30.2
28 | 2019-07-14 | 2776.132 | 23.5 | 2019-07-10 | 21007 | 28.9
29 | 2019-07-21 | 3032.724 | 25.9286 | 2019-07-20 | 21636 | 32.4
30 | 2019-07-28 | 2840.069 | 23.9476 | 2019-07-26 | 21010 | 29.1
31 | 2019-08-04 | 2836.533 | 24.0619 | 2019-07-29 | 21614 | 31.4
32 | 2019-08-11 | 2687.182 | 23.3524 | 2019-08-07 | 20920 | 27.7
33 | 2019-08-18 | 2769.827 | 23.0143 | 2019-08-13 | 21061 | 28.1
34 | 2019-08-25 | 2679.421 | 21.9238 | 2019-08-21 | 21376 | 30.2
35 | 2019-09-01 | 2505.522 | 20.3524 | 2019-08-28 | 18637 | 26.9
36 | 2019-09-08 | 2386.035 | 18.1714 | 2019-09-03 | 17581 | 22
37 | 2019-09-15 | 2435.541 | 18.5333 | 2019-09-11 | 19703 | 28.6
38 | 2019-09-22 | 2476.362 | 20.481 | 2019-09-22 | 18758 | 30.7
39 | 2019-09-29 | 2406.897 | 18.4524 | 2019-09-23 | 17942 | 24.3
40 | 2019-10-06 | 2374.288 | 14.5905 | 2019-10-01 | 18222 | 31.2
41 | 2019-10-13 | 2286.694 | 13.2667 | 2019-10-07 | 16422 | 17.7
42 | 2019-10-20 | 2332.984 | 9.5905 | 2019-10-17 | 16740 | 8.5
43 | 2019-10-27 | 2347.65 | 11.1619 | 2019-10-24 | 16476 | 13.4
44 | 2019-11-03 | 2445.165 | 7.4762 | 2019-11-01 | 17017 | 4.6
45 | 2019-11-10 | 2561.37 | 3.1095 | 2019-11-07 | 18253 | 2.4
46 | 2019-11-17 | 2777.214 | -3.3333 | 2019-11-13 | 19534 | -4.1
47 | 2019-11-24 | 2647.337 | 2.9548 | 2019-11-18 | 19044 | 2.1
48 | 2019-12-01 | 2669.441 | 2.2167 | 2019-12-01 | 19107 | -1.3
49 | 2019-12-08 | 2792.114 | -0.61905 | 2019-12-02 | 19584 | -1.1
50 | 2019-12-15 | 2793.234 | 0.02381 | 2019-12-11 | 20228 | -3
51 | 2019-12-22 | 3251.249 | -3.519 | 2019-12-19 | 20823 | -7.8
52 | 2019-12-29 | 2108.993 | 2.5952 | 2019-12-23 | 17518 | 8.6
1 | 2020-01-05 | 2527.453 | 2.1143 | 2020-01-05 | 17946 | 0.9
2 | 2020-01-12 | 2767.482 | 0.07619 | 2020-01-08 | 19759 | -4.5
3 | 2020-01-19 | 2856.195 | -2.1476 | 2020-01-17 | 19989 | -8.5
4 | 2020-01-26 | 2801.928 | -1.3429 | 2020-01-20 | 19982 | -5.3
5 | 2020-02-02 | 2789.92 | -1.3857 | 2020-01-29 | 19370 | -2.9
6 | 2020-02-09 | 2806.795 | -3.2333 | 2020-02-06 | 19257 | -3.6
7 | 2020-02-16 | 2782.415 | -2.7 | 2020-02-14 | 19813 | -10.4
8 | 2020-02-23 | 2664.318 | -0.86667 | 2020-02-20 | 19663 | -4.7
9 | 2020-03-01 | 2716.574 | -1.5714 | 2020-02-27 | 19116 | -3.8
10 | 2020-03-08 | 2593.923 | 3.1667 | 2020-03-03 | 18046 | 3.8
11 | 2020-03-15 | 2517.192 | 4.9238 | 2020-03-11 | 17662 | 3.4
12 | 2020-03-22 | 2525.756 | 2.5286 | 2020-03-16 | 17414 | 3.9
13 | 2020-03-29 | 2381.873 | 6.3619 | 2020-03-23 | 16935 | 3.5
14 | 2020-04-05 | 2235.936 | 7.5476 | 2020-03-30 | 15763 | 8
15 | 2020-04-12 | 2142.126 | 7.8143 | 2020-04-07 | 14803 | 13.6
16 | 2020-04-19 | 2226.22 | 4.5476 | 2020-04-15 | 15450 | 4.4
17 | 2020-04-26 | 2186.118 | 5.4238 | 2020-04-21 | 15334 | 3.6
18 | 2020-05-03 | 2074.461 | 12.119 | 2020-04-30 | 14475 | 13.2
19 | 2020-05-10 | 2145.501 | 6.1286 | 2020-05-08 | 14730 | 4.8
20 | 2020-05-17 | 2135.825 | 9.4571 | 2020-05-14 | 14954 | 12.3
21 | 2020-05-24 | 2090.504 | 17.2714 | 2020-05-24 | 15545 | 25.7
22 | 2020-05-31 | 2479.051 | 20.7524 | 2020-05-26 | 20582 | 30.6
23 | 2020-06-07 | 2371.542 | 21.3762 | 2020-06-05 | 18973 | 27.6
24 | 2020-06-14 | 2372.026 | 19.4714 | 2020-06-10 | 20580 | 31.6
25 | 2020-06-21 | 2628.362 | 22.7762 | 2020-06-20 | 20024 | 30.4
26 | 2020-06-28 | 2645.033 | 23.619 | 2020-06-22 | 20415 | 29.7
27 | 2020-07-05 | 2942.976 | 27.2571 | 2020-07-02 | 22589 | 34.6
28 | 2020-07-12 | 3181.686 | 27.4905 | 2020-07-09 | 24497 | 34
29 | 2020-07-19 | 2916.228 | 25.219 | 2020-07-17 | 22195 | 30.6
30 | 2020-07-26 | 2890.849 | 24.7905 | 2020-07-26 | 22648 | 33.3
31 | 2020-08-02 | 2948.168 | 25.7048 | 2020-07-27 | 23901 | 31.3
32 | 2020-08-09 | 2606.352 | 22.0048 | 2020-08-09 | 20521 | 30.4
33 | 2020-08-16 | 2967.735 | 25.181 | 2020-08-10 | 23745 | 31.9
34 | 2020-08-23 | 2684.076 | 22.9286 | 2020-08-23 | 21353 | 31.3
35 | 2020-08-30 | 2730.506 | 22.7714 | 2020-08-24 | 23357 | 32.4
36 | 2020-09-06 | 2516.733 | 20.7857 | 2020-09-01 | 20341 | 27.4
37 | 2020-09-13 | 2345.377 | 17.7429 | 2020-09-09 | 16595 | 18.2
38 | 2020-09-20 | 2256.233 | 14.3762 | 2020-09-16 | 16056 | 24.8
39 | 2020-09-27 | 2359.117 | 19.3476 | 2020-09-24 | 16954 | 23.8
40 | 2020-10-04 | 2343.523 | 13.8238 | 2020-09-28 | 18076 | 25.9
41 | 2020-10-11 | 2269.56 | 13.3476 | 2020-10-08 | 16055 | 16
42 | 2020-10-18 | 2268.958 | 12.0095 | 2020-10-15 | 16376 | 11.9
43 | 2020-10-25 | 2387.319 | 10.081 | 2020-10-19 | 16946 | 8
44 | 2020-11-01 | 2495.502 | 5.1714 | 2020-10-27 | 17628 | 7
45 | 2020-11-08 | 2379.319 | 12.1667 | 2020-11-02 | 18169 | 4.2
46 | 2020-11-15 | 2387.329 | 10.2643 | 2020-11-13 | 17331 | 8.7
47 | 2020-11-22 | 2545.051 | 4.6367 | 2020-11-18 | 18958 | 0.2
48 | 2020-11-29 | 2573.636 | 4.75 | 2020-11-24 | 19172 | 0.1
49 | 2020-12-06 | 2264.397 | 0.91905 | 2020-12-01 | 18959 | -0.5
50 | 2020-12-13 | 3079.802 | 2.1429 | 2020-12-07 | 19403 | 0.9
51 | 2020-12-20 | 2811.958 | -2.3 | 2020-12-16 | 20675 | -6.8
52 | 2020-12-27 | 2618.5 | 0.96667 | 2020-12-22 | 19042 | 2.6
53 | 2021-01-03 | 2586.452 | 0.17143 | 2020-12-29 | 19053 | -1.8
1 | 2021-01-10 | 2748.677 | -1.0857 | 2021-01-08 | 19296 | -3.6
2 | 2021-01-17 | 2698.095 | 1.0238 | 2021-01-12 | 19427 | -1.6
3 | 2021-01-24 | 2787.687 | -2.8857 | 2021-01-20 | 19515 | -4.5
4 | 2021-01-31 | 2875.028 | -5.7286 | 2021-01-28 | 20154 | -8.4
5 | 2021-02-07 | 2822.533 | -4.7 | 2021-02-01 | 19818 | -4
6 | 2021-02-14 | 2958.496 | -8.4952 | 2021-02-08 | 20361 | -6.9
7 | 2021-02-21 | 2869.063 | -5.9714 | 2021-02-16 | 20221 | -7.1
8 | 2021-02-28 | 2677.562 | 1.9429 | 2021-02-22 | 18774 | 2.8
9 | 2021-03-07 | 2723.977 | -2.6905 | 2021-03-01 | 19485 | -0.8
10 | 2021-03-14 | 2516.079 | 5.6762 | 2021-03-08 | 18026 | 9.4
11 | 2021-03-21 | 2529.233 | 3.7143 | 2021-03-15 | 17940 | -1.4
12 | 2021-03-28 | 2386.575 | 9.9524 | 2021-03-26 | 16268 | 9.6
13 | 2021-04-04 | 2365.144 | 5.6571 | 2021-04-01 | 16767 | 1.8
14 | 2021-04-11 | 2231.181 | 13.7524 | 2021-04-05 | 15668 | 12.8
15 | 2021-04-18 | 2306.786 | 8.981 | 2021-04-15 | 15802 | 8
16 | 2021-04-25 | 2326.647 | 7.1857 | 2021-04-20 | 16402 | 4.8
17 | 2021-05-02 | 2279.233 | 9.8524 | 2021-04-29 | 15646 | 10.5
18 | 2021-05-09 | 2272.663 | 9.6667 | 2021-05-03 | 15827 | 12.4
19 | 2021-05-16 | 2202.781 | 13.3952 | 2021-05-11 | 15447 | 9.5
20 | 2021-05-23 | 2473.753 | 22.5476 | 2021-05-21 | 19259 | 31.5
21 | 2021-05-30 | 2291.647 | 15.7381 | 2021-05-25 | 19291 | 31.6
22 | 2021-06-06 | 2495.72 | 22.7 | 2021-06-06 | 20677 | 33.5
23 | 2021-06-13 | 2787.64 | 23.981 | 2021-06-07 | 21207 | 31.1
24 | 2021-06-20 | 2453.821 | 20.6667 | 2021-06-20 | 18486 | 26.1
25 | 2021-06-27 | 2575.032 | 22.3714 | 2021-06-27 | 20656 | 30.7
26 | 2021-07-04 | 2714.895 | 23.6476 | 2021-06-28 | 22193 | 31.6
27 | 2021-07-11 | 2618.1 | 21.4429 | 2021-07-06 | 21748 | 31.7
28 | 2021-07-18 | 2759.419 | 23.5571 | 2021-07-14 | 21487 | 29.2
29 | 2021-07-25 | 2705.506 | 22.7714 | 2021-07-19 | 20895 | 28.9
30 | 2021-08-01 | 2564.649 | 21.0333 | 2021-07-26 | 20858 | 30.1
31 | 2021-08-08 | 2701.63 | 23.0857 | 2021-08-05 | 20993 | 27.3
32 | 2021-08-15 | 2947.49 | 25.2476 | 2021-08-09 | 22335 | 30.6
33 | 2021-08-22 | 3002.528 | 25.2429 | 2021-08-19 | 21877 | 30.8
34 | 2021-08-29 | 3137.955 | 26.6333 | 2021-08-24 | 22909 | 33.1
35 | 2021-09-05 | 2602.69 | 21.081 | 2021-08-30 | 21570 | 28.7
36 | 2021-09-12 | 2451.704 | 20.3714 | 2021-09-07 | 18560 | 25.5
37 | 2021-09-19 | 2487.729 | 20.0381 | 2021-09-17 | 18786 | 26
38 | 2021-09-26 | 2359.527 | 16.5143 | 2021-09-21 | 17846 | 24.4
39 | 2021-10-03 | 2347.134 | 16.8976 | 2021-09-27 | 16826 | 24.2
40 | 2021-10-10 | 2423.924 | 17.619 | 2021-10-07 | 17039 | 19.8
41 | 2021-10-17 | 2367.858 | 17.0571 | 2021-10-12 | 17270 | 21.95
42 | 2021-10-24 | 2344.856 | 11.6095 | 2021-10-18 | 16337 | 13.8
43 | 2021-10-31 | 2400.534 | 9.4414 | 2021-10-25 | 16946 | 8.25
44 | 2021-11-07 | 2460.598 | 6.1143 | 2021-11-04 | 17537 | 9
45 | 2021-11-14 | 2451.66 | 8.4762 | 2021-11-14 | 17628 | 4.7
46 | 2021-11-21 | 2567.212 | 5.0238 | 2021-11-16 | 18445 | 5.5
47 | 2021-11-28 | 2679.479 | 1.0571 | 2021-11-23 | 18744 | 3.3
48 | 2021-12-05 | 2748.075 | 1.5714 | 2021-11-29 | 19612 | 0.15
49 | 2021-12-11 | 2859.142 | 1.7429 | 2021-12-08 | 20443 | -2
50 | 2021-12-19 | 2672.947 | 3.8381 | 2021-12-19 | 19133 | -3.4
51 | 2021-12-26 | 2272.806 | 0.59524 | 2021-12-22 | 19457 | -0.7
52 | 2022-01-02 | 2988.475 | 0.20476 | 2022-01-02 | 18986 | -6.3
1 | 2022-01-09 | 2867.241 | -3.8857 | 2022-01-07 | 20239 | -7
2 | 2022-01-16 | 3020.725 | -7.6524 | 2022-01-11 | 21420 | -10
3 | 2022-01-23 | 3009.042 | -7.9667 | 2022-01-20 | 21166 | -12.1
4 | 2022-01-30 | 3094.318 | -10.4095 | 2022-01-24 | 21146 | -6.1
5 | 2022-02-06 | 2960.041 | -4.6905 | 2022-02-04 | 20513 | -10.6
6 | 2022-02-13 | 2832.569 | -2.0286 | 2022-02-13 | 20058 | -9.5
7 | 2022-02-20 | 2885.157 | -3.5571 | 2022-02-14 | 20783 | -9.8
8 | 2022-02-27 | 2837.291 | -3.2381 | 2022-02-23 | 19978 | -4.8
9 | 2022-03-06 | 2781.134 | -1.0857 | 2022-02-28 | 19972 | -5.9
10 | 2022-03-13 | 2756.58 | -1.1571 | 2022-03-07 | 18836 | 1
11 | 2022-03-20 | 2567.324 | 5.881 | 2022-03-15 | 17886 | 0.7
12 | 2022-03-27 | 2584.788 | 3.4905 | 2022-03-23 | 17862 | 3.3
13 | 2022-04-03 | 2631.049 | 1.4714 | 2022-03-28 | 18833 | -5.4
14 | 2022-04-10 | 2445.197 | 7.2524 | 2022-04-04 | 16901 | 7.9
15 | 2022-04-17 | 2301.483 | 9.0905 | 2022-04-11 | 16157 | 12.1
16 | 2022-04-24 | 2395.123 | 7.9476 | 2022-04-18 | 16992 | 6.6
17 | 2022-05-01 | 2357.543 | 8.0619 | 2022-04-27 | 16727 | 3.5
18 | 2022-05-08 | 2288.564 | 11.7905 | 2022-05-03 | 16193 | 12.1
19 | 2022-05-15 | 2420.061 | 19.7 | 2022-05-15 | 18286 | 28.9
20 | 2022-05-22 | 2336.128 | 16.7381 | 2022-05-20 | 16239 | 23.6
21 | 2022-05-29 | 2332.369 | 18.0952 | 2022-05-26 | 17195 | 26.6
22 | 2022-06-05 | 2537.915 | 21.119 | 2022-05-31 | 21305 | 32.2
23 | 2022-06-12 | 2378.093 | 18.9286 | 2022-06-08 | 16558 | 22.2
24 | 2022-06-19 | 2555.752 | 21.0762 | 2022-06-16 | 21211 | 32.2
25 | 2022-06-26 | 2850.099 | 25.3667 | 2022-06-22 | 21826 | 34.6
26 | 2022-07-03 | 2545.54 | 21.8905 | 2022-06-30 | 19242 | 25.7
27 | 2022-07-10 | 2636.564 | 22.2286 | 2022-07-07 | 19479 | 25
28 | 2022-07-17 | 2778.325 | 23.5238 | 2022-07-11 | 20476 | 30.8
29 | 2022-07-24 | 3097.347 | 27.8333 | 2022-07-19 | 22713 | 34.2
30 | 2022-07-31 | 2766.036 | 22.7381 | 2022-07-28 | 20533 | 28.7
31 | 2022-08-07 | 2984.792 | 25.8476 | 2022-08-06 | 21622 | 31.1
32 | 2022-08-14 | 2741.31 | 22.4857 | 2022-08-08 | 21426 | 30.9
33 | 2022-08-21 | 2837.659 | 23.4476 | 2022-08-18 | 20733 | 27.4
34 | 2022-08-28 | 2803.392 | 22.6286 | 2022-08-24 | 21399 | 28.7
35 | 2022-09-04 | 2768.199 | 22.619 | 2022-08-29 | 21697 | 30.5
36 | 2022-09-11 | 2631.655 | 21.2905 | 2022-09-09 | 19909 | 26.5
37 | 2022-09-18 | 2530.077 | 19.6905 | 2022-09-12 | 18941 | 23.7
38 | 2022-09-25 | 2440.529 | 17.8238 | 2022-09-19 | 18808 | 27.5
39 | 2022-10-02 | 2329.524 | 13.3095 | 2022-09-27 | 16395 | 16.5
40 | 2022-10-09 | 2357.445 | 12.8333 | 2022-10-05 | 16565 | 21.6
41 | 2022-10-16 | 2313.652 | 13.2667 | 2022-10-13 | 16252 | 14.8
42 | 2022-10-23 | 2388.92 | 9.681 | 2022-10-20 | 16960 | 6.8
43 | 2022-10-30 | 2366.94 | 10.3714 | 2022-10-27 | 16629 | 9.9
44 | 2022-11-06 | 2383.733 | 13.8714 | 2022-11-02 | 16690 | 14.1
45 | 2022-11-13 | 2451.794 | 8.7333 | 2022-11-08 | 17636 | 9.1
46 | 2022-11-20 | 2743.599 | -0.90476 | 2022-11-20 | 19100 | -3.6
47 | 2022-11-27 | 2668.657 | 4.4095 | 2022-11-21 | 19219 | 7.2
48 | 2022-12-04 | 2720.887 | 2.5619 | 2022-12-01 | 19285 | 1.4
49 | 2022-12-11 | 2390.011 | 1.8667 | 2022-12-09 | 19209 | 0.5
50 | 2022-12-18 | 2877.925 | -1.3429 | 2022-12-12 | 20246 | -2
51 | 2022-12-24 | 2498.242 | -3.5286 | 2022-12-19 | 19892 | 0.8
52 | 2023-01-01 | 3352.878 | 3.9429 | 2022-12-27 | 18647 | -2.7
1 | 2023-01-08 | 2758.054 | 9.2381 | 2023-01-08 | 19145 | 10
2 | 2023-01-15 | 2902.869 | 7.1905 | 2023-01-11 | 19834 | 10
3 | 2023-01-22 | 2848.659 | 7.9524 | 2023-01-19 | 19571 | 10
4 | 2023-01-29 | 2860.668 | 8.8571 | 2023-01-25 | 19602 | 5
5 | 2023-02-05 | 3028.967 | -2.8048 | 2023-02-03 | 21301 | -15.5
6 | 2023-02-12 | 2754.954 | 2.0381 | 2023-02-06 | 19595 | -1.7
7 | 2023-02-19 | 2695.121 | 2.6905 | 2023-02-17 | 19439 | -5
8 | 2023-02-26 | 2840.656 | -2.381 | 2023-02-23 | 20084 | -4.6
9 | 2023-03-05 | 2772.582 | 0.56667 | 2023-02-27 | 19616 | -1.3
10 | 2023-03-12 | 2715.289 | -0.8381 | 2023-03-10 | 18544 | -0.1
11 | 2023-03-19 | 2703.566 | 0.76667 | 2023-03-13 | 18389 | -0.4
12 | 2023-03-26 | 2614.795 | 4.5857 | 2023-03-24 | 17653 | 2.4
13 | 2023-04-02 | 2614.37 | 3.2333 | 2023-03-29 | 17965 | 8.3
14 | 2023-04-09 | 2451.281 | 6.4557 | 2023-04-05 | 17392 | 6.95
15 | 2023-04-16 | 2319.164 | 19.8643 | 2023-04-13 | 16537 | 28.95
16 | 2023-04-23 | 2410.193 | 7.6952 | 2023-04-18 | 16640 | 4.05
17 | 2023-04-30 | 2431.248 | 7.969 | 2023-04-24 | 16656 | 9.05
18 | 2023-05-07 | 2379.279 | 9.5762 | 2023-05-02 | 16484 | 6.5
19 | 2023-05-14 | 2309.979 | 17.3333 | 2023-05-12 | 16648 | 27
20 | 2023-05-21 | 2298.549 | 14.4571 | 2023-05-17 | 15971 | 11
21 | 2023-05-28 | 2277.446 | 15.9619 | 2023-05-28 | 16518 | 27.6
22 | 2023-06-04 | 2714.703 | 23.0333 | 2023-06-02 | 21527 | 31.6
23 | 2023-06-11 | 2434.275 | 18.8905 | 2023-06-05 | 17730 | 24.3
24 | 2023-06-18 | 2430.125 | 18.0333 | 2023-06-18 | 16916 | 24.3
25 | 2023-06-25 | 2777.778 | 22.5524 | 2023-06-21 | 20337 | 26.8
26 | 2023-07-02 | 2730.731 | 22.0952 | 2023-06-30 | 19792 | 25.2
27 | 2023-07-09 | 2919.107 | 24.15 | 2023-07-05 | 22682 | 30.95
28 | 2023-07-16 | 2786.581 | 22.7476 | 2023-07-10 | 21118 | 28.35
29 | 2023-07-23 | 2788.889 | 22.8048 | 2023-07-20 | 20656 | 27
30 | 2023-07-30 | 2930.606 | 24.1381 | 2023-07-27 | 21516 | 29
31 | 2023-08-06 | 2711.472 | 22.0286 | 2023-08-03 | 21295 | 29.1
32 | 2023-08-13 | 2738.292 | 22.9905 | 2023-08-09 | 21125 | 28.2
33 | 2023-08-20 | 2677.927 | 21.3571 | 2023-08-16 | 20821 | 26.8
34 | 2023-08-27 | 2651.031 | 20.1952 | 2023-08-21 | 19471 | 24
35 | 2023-09-03 | 2592.702 | 20.0905 | 2023-09-03 | 19526 | 31.1
36 | 2023-09-10 | 2918.15 | 23.681 | 2023-09-05 | 23559 | 32.1
37 | 2023-09-17 | 2488.632 | 18.1476 | 2023-09-11 | 18965 | 23
38 | 2023-09-24 | 2424.984 | 17.5857 | 2023-09-21 | 17280 | 21.9
39 | 2023-10-01 | 2475.184 | 18.5333 | 2023-10-01 | 17311 | 26.9
40 | 2023-10-08 | 2592.116 | 19.0714 | 2023-10-03 | 20766 | 30
41 | 2023-10-15 | 2404.223 | 10.6143 | 2023-10-10 | 16894 | 12.8
42 | 2023-10-22 | 2435.498 | 11.381 | 2023-10-16 | 16869 | 11.5
43 | 2023-10-29 | 2447.685 | 14.281 | 2023-10-23 | 17013 | 13.7
44 | 2023-11-05 | 2589.671 | 6.2857 | 2023-11-01 | 18170 | 4.4
45 | 2023-11-12 | 2661.355 | 5.2762 | 2023-11-08 | 19366 | 0.6
46 | 2023-11-19 | 2605.763 | 7.1476 | 2023-11-14 | 18301 | 9.1
47 | 2023-11-26 | 2779.011 | 2.1381 | 2023-11-20 | 19479 | 0.4
48 | 2023-12-03 | 2834.018 | 1.181 | 2023-11-28 | 20269 | -1.5
49 | 2023-12-10 | 2834.801 | 3.7381 | 2023-12-06 | 19991 | 0.2
50 | 2023-12-17 | 2375.44 | 3.3714 | 2023-12-13 | 19925 | 3
51 | 2023-12-24 | 3225.166 | 1.119 | 2023-12-19 | 19702 | -0.9
52 | 2023-12-31 | 2549.777 | 4.4571 | 2023-12-30 | 18241 | 0.2
1 | 2024-01-07 | 2849.764 | -1.4905 | 2024-01-04 | 20109 | -3.1
2 | 2024-01-14 | 2902.584 | 0.1381 | 2024-01-09 | 19874 | 2.2
3 | 2024-01-21 | 3119.757 | -8.9571 | 2024-01-15 | 21081 | -9
4 | 2024-01-28 | 2918.879 | 1.0667 | 2024-01-22 | 20456 | -1.2
5 | 2024-02-04 | 2831.597 | 1.5333 | 2024-01-30 | 19523 | 1.9
6 | 2024-02-11 | 2726.211 | 3.6762 | 2024-02-05 | 19112 | 3.1
7 | 2024-02-18 | 2880.556 | -1.9381 | 2024-02-16 | 19521 | -1
8 | 2024-02-25 | 2756.548 | 0.65714 | 2024-02-20 | 19025 | 3.2
9 | 2024-03-03 | 2696.804 | 4.4714 | 2024-02-29 | 19624 | -3
10 | 2024-03-10 | 2565.62 | 7.0524 | 2024-03-10 | 17541 | -0.6
11 | 2024-03-17 | 2534.182 | 7.4952 | 2024-03-11 | 17323 | 7.4
12 | 2024-03-24 | 2779.916 | -2.0095 | 2024-03-21 | 18902 | -1.8
13 | 2024-03-31 | 2532.722 | 5.8857 | 2024-03-27 | 17508 | 10.9
14 | 2024-04-07 | 2543.842 | 6.3429 | 2024-04-03 | 17947 | 6.1
15 | 2024-04-14 | 2412.129 | 11.3762 | 2024-04-11 | 16619 | 12.9
16 | 2024-04-21 | 2435.482 | 9.7095 | 2024-04-19 | 16584 | 14.9
17 | 2024-04-28 | 2396.297 | 10.1905 | 2024-04-25 | 16506 | 7.9
18 | 2024-05-05 | 2359.978 | 14.4286 | 2024-04-29 | 16329 | 9.9
19 | 2024-05-12 | 2327.749 | 14.3762 | 2024-05-08 | 15988 | 20
20 | 2024-05-19 | 2416.477 | 18.1333 | 2024-05-16 | 16619 | 20.9
21 | 2024-05-26 | 2591.702 | 21.6048 | 2024-05-22 | 20402 | 29.1
22 | 2024-06-02 | 2405.724 | -2.25 | 2024-05-27 | 17291 | 24.2
23 | 2024-06-09 | 2598.025 | 19.8381 | 2024-06-04 | 20692 | 26.8
24 | 2024-06-16 | 2526.989 | 18.9429 | 2024-06-13 | 20220 | 30.1
25 | 2024-06-23 | 3110.749 | 25.1476 | 2024-06-19 | 23803 | 34.2
26 | 2024-06-30 | 2666.331 | 21.3905 | 2024-06-24 | 20982 | 28.1
27 | 2024-07-07 | 2847.757 | 23.4619 | 2024-07-05 | 21578 | 27.9
28 | 2024-07-14 | 3022.439 | 24.0048 | 2024-07-08 | 21979 | 29
29 | 2024-07-21 | 2875.998 | 23.0381 | 2024-07-15 | 21430 | 23.8
30 | 2024-07-28 | 2910.273 | 23.4857 | 2024-07-28 | 21710 | 28.2
31 | 2024-08-04 | 3254.234 | 26.4238 | 2024-07-31 | 23206 | 31.1
32 | 2024-08-11 | 2751.129 | 21.4048 | 2024-08-09 | 20784 | 27.2
33 | 2024-08-18 | 2901.005 | 22.8524 | 2024-08-15 | 21982 | 27.9
34 | 2024-08-25 | 2605.803 | 19.519 | 2024-08-25 | 20707 | 27.1
35 | 2024-09-01 | 2935.475 | 23.1095 | 2024-08-27 | 22503 | 31.1
36 | 2024-09-08 | 2504.95 | 17.9238 | 2024-09-05 | 19873 | 24.2
37 | 2024-09-15 | 2678.865 | 20.381 | 2024-09-15 | 20402 | 27.1
38 | 2024-09-22 | 2801.838 | 21.5381 | 2024-09-16 | 21643 | 28
39 | 2024-09-29 | 2595.066 | 20.181 | 2024-09-26 | 18357 | 24
40 | 2024-10-06 | 2493.17 | 17.5476 | 2024-09-30 | 18453 | 22.8
41 | 2024-10-13 | 2457.04 | 12.0524 | 2024-10-10 | 17159 | 14.2
42 | 2024-10-20 | 2448.06 | 10.6952 | 2024-10-16 | 17205 | 10.2
43 | 2024-10-27 | 2498.609 | 12.8571 | 2024-10-21 | 17209 | 26
44 | 2024-11-03 | 2540.856 | 11.4381 | 2024-10-28 | 17591 | 9.8
45 | 2024-11-10 | 2533.01 | 12.1333 | 2024-11-04 | 17812 | 14.1
46 | 2024-11-17 | 2641.032 | 7.1095 | 2024-11-14 | 18497 | 8.9
47 | 2024-11-24 | 2663.051 | 6.5429 | 2024-11-21 | 18481 | 5.1
48 | 2024-11-30 | 2406.491 | 1.4476 | 2024-12-01 | 19212 | 0.8
49 | 2024-12-08 | 3401.395 | -0.49048 | 2024-12-06 | 20421 | -2
50 | 2024-12-15 | 3408.632 | -0.40952 | 2024-12-12 | 20991 | -4.8
51 | 2024-12-22 | 2989.209 | -2.1143 | 2024-12-22 | 21016 | -10.5
52 | 2024-12-29 | 2783.16 | 1.2048 | 2024-12-23 | 20350 | -0.6
1 | 2025-01-05 | 2425.874 | -0.4 | 2025-01-05 | 20647 | -1
2 | 2025-01-12 | 3122.446 | -5.7095 | 2025-01-08 | 21504 | -6.6
3 | 2025-01-19 | 3073.46 | -3.7238 | 2025-01-16 | 21103 | -4.9
4 | 2025-01-26 | 3205.609 | -8.319 | 2025-01-22 | 22058 | -12
5 | 2025-02-02 | 3099.635 | -4.4762 | 2025-01-28 | 21092 | -5.1
6 | 2025-02-09 | 3112.475 | -3.5952 | 2025-02-05 | 20917 | -5.1
7 | 2025-02-16 | 3116.52 | -5.6286 | 2025-02-12 | 21115 | -6
8 | 2025-02-23 | 3096.877 | -7.2286 | 2025-02-19 | 21399 | -6.9
9 | 2025-03-02 | 2911.95 | -0.36667 | 2025-03-02 | 20232 | -5.3
10 | 2025-03-09 | 2836.548 | 1.5381 | 2025-03-03 | 19553 | 2.8
11 | 2025-03-16 | 2636.842 | 6.4333 | 2025-03-12 | 18720 | 0.9
12 | 2025-03-23 | 2626.909 | 5.7762 | 2025-03-17 | 18437 | 5.1
13 | 2025-03-30 | 2740.993 | 2.6714 | 2025-03-26 | 18565 | 3.8
14 | 2025-04-06 | 2616.332 | 5.5143 | 2025-04-02 | 19271 | 0.1
15 | 2025-04-13 | 2656.301 | 3.5143 | 2025-04-08 | 18508 | 1.1
16 | 2025-04-20 | 2463.399 | 9.6571 | 2025-04-16 | 17570 | 5.8
17 | 2025-04-27 | 2431.357 | 12.9714 | 2025-04-23 | 16501 | 15
18 | 2025-05-04 | 2422.202 | 12.2143 | 2025-05-01 | 16635 | 9.1
19 | 2025-05-11 | 2401.107 | 14.1952 | 2025-05-07 | 16320 | 23
20 | 2025-05-18 | 2500.327 | 18.5476 | 2025-05-16 | 18190 | 27.1
21 | 2025-05-25 | 2409.852 | 10.9952 | 2025-05-22 | 16664 | 10.8
22 | 2025-06-01 | 2412.068 | 15.2714 | 2025-05-28 | 16694 | 15.8
23 | 2025-06-08 | 2536.713 | 20.9333 | 2025-06-04 | 19623 | 31
24 | 2025-06-15 | 2531.677 | 19.9048 | 2025-06-11 | 18815 | 28
25 | 2025-06-22 | 2906.411 | 23.4048 | 2025-06-22 | 23182 | 34.8
26 | 2025-06-29 | 3142.408 | 25.1905 | 2025-06-24 | 24775 | 34.9
27 | 2025-07-06 | 3012.732 | 25.3048 | 2025-07-06 | 22563 | 34.2
28 | 2025-07-13 | 3222.327 | 26.0905 | 2025-07-12 | 22876 | 33.9
29 | 2025-07-20 | 3088.335 | 24.581 | 2025-07-16 | 23555 | 32.2
30 | 2025-07-27 | 3108.112 | 24.7048 | 2025-07-24 | 24399 | 33.2
31 | 2025-08-03 | 3042.594 | 24.8095 | 2025-07-28 | 24287 | 33
32 | 2025-08-10 | 3177.885 | 26.0238 | 2025-08-10 | 23996 | 32
33 | 2025-08-17 | 3311.213 | 26.2333 | 2025-08-11 | 24500 | 32.2
34 | 2025-08-24 | 2778.805 | 20.8857 | 2025-08-22 | 21032 | 26
35 | 2025-08-31 | 2507.418 | 17.1143 | 2025-08-25 | 17829 | 20.1
36 | 2025-09-07 | 2556.472 | 18.8238 | 2025-09-03 | 19590 | 26.8
37 | 2025-09-14 | 2598.283 | 19.419 | 2025-09-11 | 18587 | 24.9
38 | 2025-09-21 | 2652.341 | 19.8714 | 2025-09-18 | 19991 | 29.2
39 | 2025-09-28 | 2718.456 | 20.881 | 2025-09-23 | 19440 | 25
40 | 2025-10-05 | 2579.618 | 18.7238 | 2025-10-05 | 19379 | 26.9
41 | 2025-10-12 | 2545.678 | 14.9476 | 2025-10-06 | 20310 | 28
42 | 2025-10-19 | 2471.523 | 14.3762 | 2025-10-14 | 17088 | 21.2
43 | 2025-10-26 | 2571.18 | 9.4429 | 2025-10-23 | 17344 | 12.2
44 | 2025-11-02 | 2635.246 | 7.1714 | 2025-10-30 | 17825 | 7.9
45 | 2025-11-09 | 2719.497 | 6.3333 | 2025-11-09 | 19023 | -1.1
46 | 2025-11-16 | 2837.142 | 3.0476 | 2025-11-10 | 19827 | -2.9
47 | 2025-11-23 | 2844.141 | 3.9286 | 2025-11-17 | 19615 | 4.2
48 | 2025-11-30 | 2893.457 | -2.25 | 2025-11-27 | 19546 | 3
49 | 2025-12-07 | 3100.884 | -2.7762 | 2025-12-04 | 21541 | -4.9
50 | 2025-12-13 | 3648.047 | -5.1524 | 2025-12-08 | 21364 | -3.9
51 | 2025-12-21 | 3515.775 | -0.66667 | 2025-12-15 | 21321 | -4.8
52 | 2025-12-28 | 2119.727 | -1.6 | 2025-12-22 | 20284 | 3.2
1 | 2026-01-04 | 3046.55 | -5.1524 | 2026-01-04 | 20788 | -1.2
2 | 2026-01-11 | 3001.914 | 1.9048 | 2026-01-05 | 20994 | -0.1
3 | 2026-01-18 | 3110.401 | -2.7905 | 2026-01-15 | 21534 | -11
4 | 2026-01-25 | 3290.768 | -9.981 | 2026-01-25 | 22064 | -11
5 | 2026-02-01 | 3303.21 | -11.7571 | 2026-01-29 | 22022 | -12
6 | 2026-02-08 | 3258.679 | -9.3952 | 2026-02-08 | 21644 | -13.2
7 | 2026-02-15 | 3105.124 | -3.5476 | 2026-02-09 | 21821 | -8.1
8 | 2026-02-22 | 2957.738 | 0.87143 | 2026-02-18 | 20456 | -0.2
9 | 2026-03-01 | 3023.744 | -3.1238 | 2026-02-24 | 20716 | -8.1
10 | 2026-03-08 | 2890.177 | 2.481 | 2026-03-02 | 20333 | -0.2
11 | 2026-03-15 | 2811.66 | 4.8 | 2026-03-13 | 19212 | -4.2
12 | 2026-03-22 | 2909.909 | 1.4952 | 2026-03-17 | 20162 | -5.1
13 | 2026-03-29 | 2811.063 | 1.9667 | 2026-03-23 | 19045 | 1.2
14 | 2026-04-05 | 2632.188 | 8.681 | 2026-04-02 | 18042 | -4.3
15 | 2026-04-12 | 2675.025 | 5.0095 | 2026-04-07 | 18502 | 2.2
16 | 2026-04-19 | 2553.398 | 13.9571 | 2026-04-15 | 17292 | 3
17 | 2026-04-26 | 2530.546 | 8.8143 | 2026-04-20 | 17670 | 0.8
18 | 2026-05-03 | 2537.201 | 9.6048 | 2026-04-29 | 17131 | 18.9
19 | 2026-05-10 | 2480.511 | 11.5286 | 2026-05-05 | 16998 | 4.2
20 | 2026-05-17 | 2492.005 | 12.8381 | 2026-05-13 | 16926 | 9.8
21 | 2026-05-24 | 2548.829 | 15.881 | 2026-05-19 | 20990 | 16.1
22 | 2026-05-31 | 2541.703 | 19.4667 | 2026-05-26 | 19140 | 13.9
Back to main menu

## Table 1.4.2
Back to main menu
Table 1.4.2: Monthly Weather and Demand History
Month | Energy Demand (GWh) | Reported Embedded Generation (GWh) | Peak Demand (MW) | Average Hour (MW) | Minimum Hour (MW) | 90th Percentile (MW) | # of Hours Above 20,000MW (hrs) | Average Temperature (°C) | Weather Corrected Energy (GWh) | Forecasted Energy (GWh) | Energy Forecast MAPE | Peak Temperature (°C) | Weather Corrected Peak (MW) | Forecasted Peak (MW) | Peak Forecast MAPE
2002-05-31 | 11874.901 |  | 20068 | 15960.8884 | 12092 | 18344.4 | 1 | 12.4667 | 11661.943 | 11525.8367 | 1.167% | 27.9 | 20244.5263 | 19777 | 2.309%
2002-06-30 | 12185.238 |  | 23578 | 16923.9417 | 11537 | 20698 | 97 | 20.19 | 12055.7597 | 11830.544 | 1.868% | 30.7 | 23272.9209 | 21897 | 5.912%
2002-07-31 | 14033.343 |  | 25226 | 18862.0202 | 12348 | 23309.7 | 261 | 25.514 | 13532.3366 | 12956.0938 | 4.258% | 34.7 | 23653.7174 | 23007.2548 | 2.733%
2002-08-31 | 13748.878 |  | 25414 | 18479.6747 | 13077 | 22694.7 | 207 | 23.8785 | 13322.4613 | 12822.9862 | 3.749% | 33.4 | 24272.2514 | 22720.1818 | 6.394%
2002-09-30 | 12593.138 |  | 25062 | 17490.4694 | 12409 | 20801 | 114 | 21.43 | 12144.4221 | 11393.0328 | 6.187% | 33.5 | 21739.209 | 21099.9455 | 2.941%
2002-10-31 | 12397.839 |  | 21216 | 16663.7621 | 12244 | 19077.2 | 25 | 9.8516 | 12155.0684 | 12042.8325 | 0.9234% | 28.8 | 19901.5621 | 20319.2849 | 2.099%
2002-11-30 | 12655.667 |  | 21862 | 17577.3153 | 12709 | 20027.2 | 75 | 3.7489 | 12836.1101 | 12370.454 | 3.628% | 0.1 | 22314.4629 | 22421.8556 | 0.4813%
2002-12-31 | 13483.864 |  | 23334 | 18070.6062 | 13057 | 21021.7 | 197 | -1.2538 | 13500.9659 | 13362.8148 | 1.023% | -1.2 | 23550.9979 | 23522.7043 | 0.1201%
2003-01-31 | 14486.674 |  | 24158 | 19471.336 | 13236 | 22223.4 | 346 | -7.272 | 14211.1695 | 13919.5093 | 2.052% | -13.4 | 23893.0266 | 23850.0397 | 0.1799%
2003-02-28 | 13122.529 |  | 23469 | 19527.5729 | 14523 | 21982.3 | 315 | -6.0738 | 12808.0447 | 12426.863 | 2.976% | -10 | 22949.8962 | 23272.5444 | 1.406%
2003-03-31 | 13414.004 |  | 23117 | 18029.5753 | 13289 | 20781.2 | 142 | 0.44409 | 13159.4331 | 12901.8683 | 1.957% | -14.3 | 21751.8023 | 22090.2796 | 1.556%
2003-04-30 | 12097.332 |  | 21010 | 16801.85 | 12290 | 19540.6 | 53 | 6.7444 | 12069.9486 | 11760.2993 | 2.565% | -1.8 | 20846.9119 | 19850.9002 | 4.778%
2003-05-31 | 11627.445 |  | 18741 | 15628.2863 | 11604 | 17985.6 | 0 | 13.2559 | 11741.5567 | 11691.2195 | 0.4287% | 13.1 | 19844.7318 | 19853.0281 | 0.04181%
2003-06-30 | 11884.956 |  | 24753 | 16506.8833 | 11821 | 19404.9 | 58 | 19.6744 | 11841.7488 | 12214.3634 | 3.147% | 33.3 | 23523.3557 | 22798.6336 | 3.081%
2003-07-31 | 12897.586 |  | 23175 | 17335.4651 | 11957 | 20680.5 | 139 | 22.7849 | 12968.9604 | 13433.0128 | 3.578% | 31.3 | 23762.5491 | 23684.1903 | 0.3298%
2003-08-31 | 12514.308 |  | 23891 | 16820.3065 | 2270 | 21000.8 | 144 | 22.5495 | 12171.8874 | 13155.7383 | 8.083% | 31 | 23561.0011 | 23347.1957 | 0.9075%
2003-09-30 | 11794.469 |  | 20700 | 16381.2069 | 11802 | 19023.3 | 14 | 18.04 | 11779.2706 | 11789.027 | 0.08283% | 26.8 | 20307.2007 | 21599.7344 | 6.365%
2003-10-31 | 12159.932 |  | 20408 | 16343.9946 | 11941 | 18583.6 | 4 | 9.9935 | 12134.778 | 12368.2786 | 1.924% | 9.7 | 21259.1741 | 20666.6154 | 2.787%
2003-11-30 | 12389.858 |  | 21584 | 17208.1361 | 12724 | 19670.3 | 54 | 5.4578 | 12865.0242 | 12585.1188 | 2.176% | 13.4 | 22716.1034 | 22681.1697 | 0.1538%
2003-12-31 | 13327.663 |  | 22798 | 17779.9919 | 12550 | 20959.3 | 165 | 0.45591 | 13534.0494 | 13768.4138 | 1.732% | -5.6 | 23431.3362 | 23858.3895 | 1.823%
2004-01-31 | 14767.413 |  | 24937 | 19848.6734 | 13219 | 22977 | 399 | -8.5817 | 14323.0642 | 14191.7421 | 0.9169% | -19.7 | 24408.7438 | 24078.4061 | 1.353%
2004-02-29 | 13088.075 |  | 22608 | 18804.7055 | 14243 | 21145.5 | 249 | -2.554 | 13173.0548 | 13033.9545 | 1.056% | -3.9 | 23057.4279 | 23556.2598 | 2.163%
2004-03-31 | 13224.641 |  | 21634 | 17775.0551 | 13238 | 20123.3 | 84 | 2.9398 | 13203.0654 | 13279.366 | 0.5779% | -3.1 | 21870.1159 | 22452.4608 | 2.663%
2004-04-30 | 11792.132 |  | 19911 | 16377.9611 | 12427 | 18638.3 | 0 | 7.9389 | 11874.9664 | 11891.0349 | 0.1353% | 3.2 | 20525.8394 | 19942.5254 | 2.842%
2004-05-31 | 11835.269 |  | 20327 | 15907.6196 | 11983 | 18401.3 | 4 | 14.3634 | 11790.5055 | 11844.4455 | 0.4575% | 27.3 | 20053.0994 | 20166.6217 | 0.5661%
2004-06-30 | 12045.885 |  | 23163 | 16730.3958 | 12059 | 19989.2 | 72 | 18.8211 | 12217.9222 | 12553.0052 | 2.743% | 31.3 | 23163 | 23585.4466 | 1.824%
2004-07-31 | 12769.985 |  | 23976 | 17163.9583 | 12385 | 20583.8 | 94 | 21.7398 | 12930.3649 | 13366.3211 | 3.372% | 30.1 | 24618.2502 | 23677.3092 | 3.822%
2004-08-31 | 12746.297 |  | 23159 | 17132.1183 | 12223 | 20350.3 | 97 | 20.7581 | 12964.5229 | 13300.7716 | 2.594% | 28.6 | 23229.7881 | 23298.2624 | 0.2948%
2004-09-30 | 12369.687 |  | 21911 | 17180.1208 | 12285 | 20296.4 | 102 | 19.7733 | 12205.4933 | 11892.6387 | 2.563% | 25.8 | 20958.8749 | 21881.4147 | 4.402%
2004-10-31 | 12215.166 |  | 19829 | 16418.2339 | 12343 | 18770.5 | 0 | 11.7656 | 12456.5009 | 12357.6295 | 0.7937% | 8.8 | 20925.8279 | 21212.056 | 1.368%
2004-11-30 | 12601.008 |  | 22066 | 17501.4 | 12969 | 19980.6 | 71 | 5.8989 | 13148.5344 | 12864.0567 | 2.164% | 5 | 23333.9595 | 22748.6257 | 2.509%
2004-12-31 | 13981.717 |  | 24979 | 18705.2554 | 14169 | 21867.1 | 261 | -2.0914 | 13836.9923 | 13651.944 | 1.337% | -12.3 | 24073.4484 | 23404.0469 | 2.781%
2005-01-31 | 14619.18 |  | 24362 | 19649.4355 | 13545 | 22555.1 | 356 | -6.0849 | 14521.4247 | 14269.3901 | 1.736% | -14.5 | 24173.3301 | 23890.98 | 1.168%
2005-02-28 | 12731.835 |  | 22322 | 18946.183 | 14854 | 21241.5 | 249 | -2.7 | 12865.7476 | 12795.0929 | 0.5492% | -3.9 | 22791.1102 | 23507.03 | 3.141%
2005-03-31 | 13494.28 |  | 22724 | 18137.4731 | 13959 | 20632.1 | 143 | -0.29892 | 13288.2099 | 13401.8026 | 0.8548% | -8.5 | 22667.3301 | 22370.34 | 1.31%
2005-04-30 | 11827.861 |  | 19343 | 16427.5847 | 12279 | 18455.1 | 0 | 9.0533 | 12209.0045 | 12063.7878 | 1.189% | 10.9 | 20931.6333 | 20760.1 | 0.8195%
2005-05-31 | 11744.825 |  | 19007 | 15786.0551 | 11950 | 18139.5 | 0 | 13.2495 | 11734.2216 | 11928.3062 | 1.654% | 22.3 | 18687.7703 | 20306.03 | 8.659%
2005-06-30 | 13499.266 |  | 26157 | 18748.9806 | 12066 | 23349.8 | 260 | 23.7111 | 12679.5247 | 12284.376 | 3.116% | 31.6 | 24410.9107 | 23402.64 | 4.13%
2005-07-31 | 14094.375 |  | 26160 | 18944.0524 | 12109 | 23810.9 | 277 | 25.2505 | 13572.7661 | 13233.9731 | 2.496% | 34.6 | 25823.1716 | 23820.5 | 7.755%
2005-08-31 | 14031.29 |  | 25816 | 18859.2608 | 13487 | 22804.3 | 274 | 23.672 | 13565.2965 | 13465.8968 | 0.7327% | 32.9 | 24779.5218 | 23372.48 | 5.678%
2005-09-30 | 12552.618 |  | 23914 | 17434.1917 | 12541 | 20722.2 | 140 | 20.12 | 12367.9416 | 12151.9814 | 1.746% | 30.1 | 21719.6272 | 22078.34 | 1.652%
2005-10-31 | 12187.328 |  | 20752 | 16380.8172 | 12112 | 18944.1 | 22 | 11.9323 | 12126.6613 | 12472.8188 | 2.855% | 25.8 | 21108.1878 | 20922.81 | 0.8782%
2005-11-30 | 12440.55 |  | 22564 | 17278.5417 | 12548 | 20020.1 | 74 | 5.5967 | 12682.2654 | 12867.08 | 1.457% | -6.3 | 22614.2615 | 22937.6 | 1.43%
2005-12-31 | 13745.639 |  | 23766 | 18422.0914 | 12673 | 21484.9 | 250 | -2.7237 | 13620.1354 | 13796.3409 | 1.294% | -4.8 | 24097.0219 | 23641.84 | 1.889%
2006-01-31 | 13596.17 |  | 23052 | 18274.4207 | 13644 | 20907.3 | 189 | 0.7957 | 14274.4358 | 14424.4515 | 1.051% | -5 | 24238.2139 | 24284.96 | 0.1929%
2006-02-28 | 12568.25 | 196.7766 | 22321 | 18702.753 | 14051 | 20957.7 | 220 | -3.0024 | 12600.0722 | 12948.2914 | 2.764% | -0.9 | 22387.273 | 23800.5 | 6.313%
2006-03-31 | 13199.998 | 174.9678 | 21772 | 17741.9341 | 13274 | 20091.1 | 83 | 2.3215 | 13175.0216 | 13634.8299 | 3.49% | -2.2 | 22053.7104 | 22821.37 | 3.481%
2006-04-30 | 11512.852 | 209.6124 | 19582 | 15990.0722 | 12020 | 18469.4 | 0 | 9.45 | 11956.204 | 12047.9755 | 0.7676% | 3.7 | 20333.283 | 20910.04 | 2.837%
2006-05-31 | 11927.478 | 182.5572 | 24857 | 16031.5565 | 11812 | 18116.3 | 42 | 15.6548 | 11823.8872 | 12279.9916 | 3.857% | 32.8 | 21889.4457 | 21678.33 | 0.9645%
2006-06-30 | 12541.936 | 156.8548 | 23349 | 17419.3556 | 11957 | 20688.4 | 143 | 20.8756 | 12477.8857 | 12623.9122 | 1.17% | 30.6 | 23612.7463 | 23998.72 | 1.635%
2006-07-31 | 13853.619 | 105.9768 | 26092 | 18620.4556 | 12470 | 22948.8 | 269 | 24.6108 | 13347.7145 | 13679.2646 | 2.484% | 33.6 | 25257.3418 | 25397.46 | 0.5548%
2006-08-31 | 13308.1 | 102.0594 | 27005 | 17887.2312 | 12545 | 21104.2 | 172 | 22.2785 | 13263.4984 | 13630.8008 | 2.769% | 36.4 | 23880.5188 | 24805.29 | 3.872%
2006-09-30 | 11521.035 | 75.3164 | 19976 | 16001.4375 | 11796 | 18524.1 | 0 | 16.6411 | 11661.5416 | 12254.9406 | 5.089% | 28 | 21526.7648 | 23566.96 | 9.477%
2006-10-31 | 11962.307 | 112.2613 | 19590 | 16078.3696 | 11621 | 18409.9 | 0 | 9.7226 | 11803.3843 | 12521.8009 | 6.087% | 13.5 | 20459.0154 | 21498.15 | 5.079%
2006-11-30 | 12178.739 | 217.4506 | 21267 | 16914.9153 | 12720 | 19351.1 | 30 | 5.9711 | 12633.6484 | 12892.685 | 2.05% | 1.5 | 22968.2115 | 23080.82 | 0.4903%
2006-12-31 | 12884.176 | 213.476 | 22941 | 18010.0014 | 12246 | 20322.4 | 107 | 2.4269 | 13331.6936 | 13800.6488 | 3.518% | -5.5 | 23625.9393 | 24123.74 | 2.107%
2007-01-31 | 13758.097 | 206.1901 | 23537 | 17914.1888 | 12941 | 21448 | 243 | -2.2806 | 14060.0462 | 14347.6006 | 2.045% | -13.1 | 23776.8339 | 24407.33 | 2.652%
2007-02-28 | 13037.578 | 188.1128 | 23935 | 19401.1577 | 14894 | 21908 | 280 | -7.169 | 12657.9939 | 12799.7079 | 1.12% | -14 | 23053.0639 | 23805.23 | 3.263%
2007-03-31 | 13192.72 | 130.1285 | 22969 | 17732.1519 | 13331 | 20433.1 | 121 | 1.6097 | 13158.0262 | 13334.4268 | 1.341% | -12.5 | 22680.4017 | 22410.89 | 1.188%
2007-04-30 | 11827.647 | 154.9039 | 20016 | 16427.2875 | 11819 | 18975.2 | 1 | 7.2678 | 11883.5165 | 11833.3207 | 0.4224% | 4.1 | 21218.7001 | 20306.68 | 4.298%
2007-05-31 | 11818.634 | 186.5976 | 21490 | 15885.2608 | 11814 | 18653.5 | 33 | 15.9075 | 11715.6686 | 11997.9552 | 2.409% | 27.5 | 18881.5106 | 20882.55 | 10.6%
2007-06-30 | 12692.547 | 117.2711 | 25737 | 17628.5375 | 11699 | 21772.7 | 166 | 22.0044 | 12370.1039 | 12397.7724 | 0.2237% | 34.2 | 24968.2328 | 24501.25 | 1.87%
2007-07-31 | 12840.811 | 117.543 | 24561 | 17259.1546 | 11710 | 21065 | 133 | 22.6237 | 13020.6286 | 13470.8252 | 3.458% | 32.6 | 24937.0822 | 25524.57 | 2.356%
2007-08-31 | 13454.57 | 94.9993 | 25584 | 18084.0995 | 12293 | 22075.9 | 206 | 23.614 | 13116.9687 | 13368.0197 | 1.914% | 34.5 | 24566.9071 | 24734.55 | 0.6824%
2007-09-30 | 11916.219 | 59.8788 | 24046 | 16550.3042 | 11867 | 19637 | 51 | 19.5556 | 11730.0385 | 11853.5568 | 1.053% | 32.9 | 20976.0219 | 22636.33 | 7.915%
2007-10-31 | 11908.105 | 93.128 | 19233 | 16005.5175 | 11788 | 18411.2 | 0 | 15.0344 | 12052.1085 | 12419.5501 | 3.049% | 24.3 | 19607.6114 | 21554.34 | 9.928%
2007-11-30 | 12350.431 | 133.6983 | 21814 | 17153.3764 | 12371 | 19847.5 | 60 | 3.4744 | 12534.9107 | 12719.7604 | 1.475% | -0.3 | 22401.7023 | 22807.03 | 1.809%
2007-12-31 | 13407.761 | 151.2253 | 22935 | 17932.1102 | 13146 | 20760.6 | 189 | -1.8172 | 13302.9248 | 13588.2725 | 2.145% | -3.4 | 23142.7472 | 24122.74 | 4.235%
2008-01-31 | 13609.986 | 192.7611 | 22782 | 18292.9919 | 13556 | 20970.1 | 196 | -1.6978 | 13996.4363 | 13978.7473 | 0.1264% | -8 | 23324.016 | 23839.9286 | 2.212%
2008-02-29 | 12896.823 | 182.6809 | 23054 | 18529.9167 | 14295 | 21007 | 204 | -4.3287 | 12775.3563 | 12968.8203 | 1.514% | -9.3 | 22662.4184 | 23331.2989 | 2.951%
2008-03-31 | 13003.771 | 195.6356 | 20990 | 17478.1868 | 13902 | 19568.2 | 31 | -0.62903 | 12635.3784 | 12970.3688 | 2.651% | -1.6 | 21209.0269 | 21883.6734 | 3.181%
2008-04-30 | 11520.396 | 175.7789 | 19512 | 16000.55 | 11571 | 18116.5 | 0 | 10.6456 | 11872.3822 | 11698.943 | 1.461% | 14.1 | 21077.4953 | 20048.0315 | 4.884%
2008-05-31 | 11407.14 | 182.8544 | 18650 | 15332.1774 | 11465 | 17575.7 | 0 | 12.972 | 11443.4889 | 11735.9553 | 2.556% | 26.9 | 20139.9842 | 20210.7676 | 0.3515%
2008-06-30 | 12189.13 | 160.4473 | 24195 | 16929.3472 | 11764 | 20433.6 | 101 | 20.7033 | 11982.089 | 12103.6774 | 1.015% | 33.1 | 23724.3431 | 23892.0192 | 0.7068%
2008-07-31 | 13155.66 | 136.1417 | 23787 | 17682.3387 | 12035 | 21319.6 | 176 | 22.9054 | 13123.8184 | 13161.835 | 0.2897% | 30 | 24987.592 | 25231.8939 | 0.9777%
2008-08-31 | 12548.525 | 152.1998 | 22707 | 16866.297 | 11986 | 19786.9 | 65 | 20.6624 | 12703.1866 | 12926.0971 | 1.755% | 26.1 | 23579.6573 | 24477.7753 | 3.809%
2008-09-30 | 11793.462 | 123.1236 | 22975 | 16379.8083 | 12061 | 18964.3 | 41 | 18.1289 | 11692.7164 | 11529.5318 | 1.396% | 30.3 | 21404.2678 | 22290.904 | 4.142%
2008-10-31 | 11634.137 | 132.3682 | 19366 | 15637.2809 | 11450 | 17924.4 | 0 | 10.0656 | 11691.8059 | 12044.3073 | 3.015% | 4.8 | 19511.6562 | 20907.5479 | 7.154%
2008-11-30 | 11828.99 | 145.2536 | 21279 | 16429.1528 | 11881 | 19036.5 | 24 | 3.7756 | 12095.7719 | 12262.6183 | 1.379% | 3.8 | 22489.0231 | 22119.6095 | 1.643%
2008-12-31 | 13087.707 | 170.3211 | 22541 | 17555.7755 | 11992 | 20509.2 | 121 | -2.4763 | 12907.8943 | 13264.4707 | 2.762% | -3.7 | 22164.6447 | 23154.6001 | 4.466%
2009-01-31 | 13730.291 | 169.634 | 22983 | 18454.6922 | 13872 | 21036.7 | 199.392 | -7.6344 | 13535.4467 | 13686.8304 | 1.118% | -11.3 | 22667.0788 | 23813.0998 | 5.056%
2009-02-28 | 11697.974 | 165.2381 | 22110 | 17407.6994 | 13312 | 19675.5 | 47.712 | -2.5405 | 11749.4678 | 12296.9476 | 4.66% | -13.1 | 21808.7203 | 23220.5185 | 6.474%
2009-03-31 | 12166.882 | 173.3939 | 21466 | 16353.336 | 11855 | 18906.8 | 20.832 | 2.143 | 12165.27 | 12746.6818 | 4.779% | -9.6 | 20868.6368 | 21914.9455 | 5.014%
2009-04-30 | 10746.635 | 180.7399 | 18744 | 14925.8819 | 10790 | 17106.2 | 0 | 8.7178 | 10901.2606 | 11354.7401 | 4.16% | -0.5 | 20344.9145 | 20074.7226 | 1.328%
2009-05-31 | 10504.201 | 197.5122 | 17560 | 14118.5497 | 10794 | 16433.1 | 0 | 14.7226 | 10536.0659 | 11416.2719 | 8.354% | 28.6 | 18785.4908 | 20357.5736 | 8.369%
2009-06-30 | 10884.323 | 147.3338 | 22540 | 15117.1153 | 10678 | 17997.5 | 34.56 | 18.4178 | 11161.8895 | 11587.9581 | 3.817% | 30.7 | 23485.0159 | 23172.7205 | 1.33%
2009-07-31 | 11315.411 | 141.1481 | 20011 | 15208.8858 | 10786 | 18132.3 | 0.744 | 20.3344 | 12091.706 | 12626.1861 | 4.42% | 27.4 | 22352.287 | 24350.6569 | 8.94%
2009-08-31 | 12225.812 | 143.9902 | 24380 | 16432.543 | 11040 | 20682.7 | 122.016 | 21.8935 | 12113.2789 | 12370.0057 | 2.119% | 31.2 | 24120.5582 | 23669.6928 | 1.869%
2009-09-30 | 10931.831 | 112.68 | 19731 | 15183.0986 | 10890 | 18072.2 | 0 | 17.9767 | 10838.0625 | 10978.4771 | 1.296% | 25.1 | 19977.6676 | 21055.1421 | 5.393%
2009-10-31 | 11181.875 | 146.4268 | 18420 | 15029.4019 | 11295 | 17250.6 | 0 | 9.3043 | 11214.1928 | 11567.95 | 3.155% | 4.1 | 19464.8512 | 20214.6873 | 3.852%
2009-11-30 | 11112.909 | 186.1543 | 19710 | 15434.5958 | 11333 | 17812.7 | 0 | 6.9422 | 11605.7866 | 11858.5268 | 2.178% | 3.7 | 21501.2294 | 21361.9788 | 0.6476%
2009-12-31 | 12688.573 | 197.3074 | 21831 | 17054.5336 | 12293 | 19724.4 | 55.8 | -1.4763 | 12677.5761 | 12693.1919 | 0.1232% | -6.7 | 21730.9099 | 21919.3561 | 0.8672%
2010-01-31 | 13145.438 | 206.3791 | 22045 | 17668.5995 | 13075 | 20120.3 | 84.072 | -4.2796 | 13227.8161 | 13097.6605 | 0.984% | -7.3 | 22297.8804 | 22717.3216 | 1.881%
2010-02-28 | 11751.752 | 175.9426 | 21367 | 17487.7262 | 13243 | 19687.6 | 45.696 | -2.644 | 11777.6488 | 11804.099 | 0.2246% | -3.6 | 22020.4448 | 22459.742 | 1.995%
2010-03-31 | 11686.054 | 96.5068 | 19393 | 15707.0618 | 11951 | 17744.6 | 0 | 5.5548 | 12010.9613 | 12430.8985 | 3.496% | 2 | 21346.0734 | 21309.448 | 0.1716%
2010-04-30 | 10474.752 | 174.4465 | 17398 | 14548.2667 | 10618 | 16556.5 | 0 | 11.8533 | 10898.0905 | 10857.612 | 0.3714% | 3.6 | 19258.6821 | 18770.6298 | 2.534%
2010-05-31 | 11368.031 | 153.2328 | 22904 | 15279.6116 | 10914 | 18075.7 | 43.896 | 17.0323 | 10951.2917 | 10814.7613 | 1.247% | 31.4 | 21295.2011 | 18843.502 | 11.51%
2010-06-30 | 11555.961 | 145.4928 | 21527 | 16049.9458 | 11506 | 19165.4 | 43.92 | 20.2422 | 11538.1526 | 11411.3572 | 1.099% | 28.3 | 22474.9206 | 22550.9548 | 0.3383%
2010-07-31 | 13307.242 | 172.6285 | 25075 | 17886.078 | 11400 | 22219.6 | 223.944 | 24.5226 | 12903.2908 | 12442.4622 | 3.571% | 33.3 | 24049.6327 | 23498.3733 | 2.292%
2010-08-31 | 12921.565 | 148.0201 | 24917 | 17367.6949 | 11813 | 21949.3 | 154.752 | 23.5247 | 12462.2289 | 12301.8326 | 1.287% | 32.9 | 24202.4847 | 22972.5225 | 5.082%
2010-09-30 | 11049.081 | 177.8492 | 24444 | 15345.9458 | 11124 | 17783.9 | 34.56 | 17.6822 | 10949.8132 | 11055.5026 | 0.9652% | 32.4 | 21702.065 | 21442.7835 | 1.195%
2010-10-31 | 10929.335 | 220.7635 | 17704 | 14689.9664 | 10816 | 16634.7 | 0 | 11.3839 | 10983.9114 | 11228.8238 | 2.23% | 11.4 | 19199.6083 | 18855.0679 | 1.795%
2010-11-30 | 11303.778 | 237.219 | 19970 | 15699.6917 | 11584 | 17896.8 | 0 | 5.0711 | 11457.171 | 11620.4239 | 1.425% | 4.2 | 20712.8718 | 20717.7815 | 0.0237%
2010-12-31 | 12694.155 | 264.8843 | 22114 | 17062.0363 | 12614 | 19769 | 55.8 | -3.1946 | 12581.1214 | 12708.2117 | 1.01% | -11.6 | 21966.6139 | 21580.6272 | 1.757%
2011-01-31 | 13301.687 | 252.0926 | 22733 | 17878.6116 | 11835 | 20361.5 | 113.832 | -6.0312 | 13237.9305 | 13343.9086 | 0.8006% | -9 | 22876.7298 | 22270.5192 | 2.65%
2011-02-28 | 11775.464 | 233.9528 | 21871 | 17523.0119 | 13358 | 19879.6 | 53.088 | -4.0107 | 11710.5829 | 11979.6008 | 2.297% | -7.7 | 21660.2043 | 21982.186 | 1.487%
2011-03-31 | 12352.443 | 266.6101 | 20667 | 16602.746 | 12736 | 18528.7 | 8.184 | 0.46559 | 12318.7834 | 12467.2468 | 1.205% | -4.3 | 21179.9192 | 20550.1632 | 2.973%
2011-04-30 | 10789.012 | 282.9928 | 17945 | 14984.7389 | 11276 | 17112.6 | 0 | 7.8011 | 11022.5512 | 10965.5571 | 0.5171% | 5.2 | 19571.3477 | 18195.8466 | 7.028%
2011-05-31 | 10781.74 | 261.12 | 20847 | 14491.586 | 10799 | 16552 | 8.928 | 15.1258 | 10594.0641 | 10934.6882 | 3.215% | 29.3 | 18742.8072 | 18515.1791 | 1.214%
2011-06-30 | 11238.277 | 218.9465 | 22765 | 15608.7181 | 10890 | 18748.6 | 18 | 20.4978 | 11253.6631 | 11593.1744 | 3.017% | 33.3 | 22294.084 | 23107.108 | 3.647%
2011-07-31 | 13298.189 | 200.5274 | 25450 | 17873.9099 | 11529 | 21827.5 | 190.464 | 25.7946 | 12809.1348 | 12517.8651 | 2.274% | 37.5 | 23631.2692 | 23538.8355 | 0.3911%
2011-08-31 | 12531.706 | 189.0822 | 22051 | 16843.6909 | 12205 | 20167.4 | 84.072 | 23.0892 | 12292.4814 | 12538.1515 | 1.999% | 31.3 | 22208.747 | 23196.6756 | 4.448%
2011-09-30 | 11144.546 | 169.0598 | 21552 | 15478.5361 | 11300 | 18071.9 | 23.76 | 18.6522 | 11031.1087 | 10964.8288 | 0.6008% | 28.3 | 21317.1824 | 21238.6927 | 0.3682%
2011-10-31 | 11012.737 | 211.1046 | 18234 | 14802.0659 | 11124 | 16971.2 | 0 | 11.6097 | 10973.2195 | 11154.7901 | 1.655% | 4.7 | 18168.0995 | 18437.0481 | 1.48%
2011-11-30 | 11116.536 | 267.3446 | 19673 | 15439.6333 | 11284 | 17789 | 0 | 7.6078 | 11452.4357 | 11622.5291 | 1.485% | 5.6 | 21347.2844 | 20747.3335 | 2.81%
2011-12-31 | 12121.895 | 278.8385 | 20204 | 16292.8696 | 11974 | 18901.5 | 4.464 | 1.3043 | 12314.3757 | 12864.6619 | 4.469% | -1.3 | 20772.1165 | 21942.4375 | 5.634%
2012-01-31 | 12715.234 | 290.1431 | 21847 | 17090.3683 | 12439 | 19422.5 | 31.248 | -0.83763 | 12932.2873 | 13280.0235 | 2.689% | -14.3 | 22084.7322 | 22160.0997 | 0.3413%
2012-02-29 | 11610.18 | 259.7219 | 19956 | 16681.2931 | 13228 | 18709 | 0 | 0.41839 | 11380.2015 | 12202.5791 | 7.226% | 1.3 | 20756.8677 | 21813.8691 | 5.092%
2012-03-31 | 11487.527 | 304.436 | 20332 | 15440.2245 | 11250 | 17580.1 | 2.232 | 7.8925 | 11726.1779 | 12264.8125 | 4.593% | -2.8 | 20595.0545 | 20708.9072 | 0.5528%
2012-04-30 | 10641.371 | 287.2476 | 17874 | 14779.6819 | 11248 | 16598.3 | 0 | 8.6278 | 10883.4994 | 10866.5786 | 0.1555% | 4.1 | 19830.1533 | 18745.092 | 5.472%
2012-05-31 | 11136.995 | 273.7978 | 21106 | 14969.0793 | 10998 | 17581 | 13.392 | 18.0011 | 10838.5019 | 10943.6824 | 0.9704% | 28.6 | 19736.9901 | 19038.2309 | 3.54%
2012-06-30 | 11800.326 | 280.2738 | 24107 | 16389.3417 | 11017 | 20405.4 | 93.6 | 21.7878 | 11511.081 | 11398.2442 | 0.9802% | 34.2 | 22832.4909 | 22569.1521 | 1.153%
2012-07-31 | 13456.845 | 224.7422 | 24636 | 18087.1573 | 12425 | 22075.1 | 212.04 | 25.5516 | 13057.6199 | 12319.3311 | 5.654% | 36.2 | 23630.2664 | 23298.1422 | 1.406%
2012-08-31 | 12632.817 | 218.4517 | 23188 | 16979.5927 | 11676 | 20667.4 | 109.368 | 22.9667 | 12373.2613 | 12419.0386 | 0.37% | 30.1 | 22726.501 | 22956.5741 | 1.012%
2012-09-30 | 11040.767 | 215.7734 | 21183 | 15334.3986 | 11012 | 18710.3 | 23.04 | 17.5778 | 10900.4102 | 10811.3017 | 0.8175% | 27.1 | 20370.1157 | 20506.0631 | 0.6674%
2012-10-31 | 11141.991 | 278.1392 | 18829 | 14975.7944 | 11436 | 16974.5 | 0 | 11.0935 | 11149.8822 | 11199.8353 | 0.448% | 4.3 | 18684.153 | 18345.9037 | 1.81%
2012-11-30 | 11487.169 | 271.2616 | 20144 | 15954.4014 | 11824 | 18349.8 | 2.16 | 4.2867 | 11663.449 | 11629.6439 | 0.2898% | -3.7 | 20258.2258 | 20571.5606 | 1.547%
2012-12-29 | 12156.557 | 285.1456 | 20382 | 17466.3175 | 12670 | 18764.9 | 9.672 | 1.4419 | 12306.8289 | 12612.0073 | 2.48% | -1 | 20910.8981 | 21693.287 | 3.742%
2013-01-31 | 12889.507 | 301.2556 | 22610 | 16274.6301 | 12270 | 20123.6 | 83.328 | -1.7989 | 13061.0693 | 13314.3055 | 1.939% | -11.6 | 22610 | 22013.997 | 2.636%
2013-02-28 | 11742.246 | 289.301 | 21426 | 17473.5804 | 13638 | 19632.9 | 38.976 | -3.6452 | 11668.8474 | 11819.7381 | 1.293% | -5.8 | 21333.0082 | 21773.6201 | 2.065%
2013-03-31 | 11958.319 | 350.9198 | 19825 | 16073.0094 | 11963 | 18101.1 | 0 | 0.98602 | 11869.9986 | 12283.0437 | 3.48% | -1.8 | 20784.4526 | 20634.9497 | 0.7193%
2013-04-30 | 10944.906 | 354.007 | 18854 | 15201.2583 | 11209 | 17185.7 | 0 | 6.9567 | 11090.2932 | 11018.1303 | 0.6507% | 2.3 | 19284.8182 | 18492.3312 | 4.109%
2013-05-31 | 10785.424 | 362.6957 | 20488 | 14496.5376 | 10765 | 16610.7 | 4.464 | 16.5247 | 10533.5712 | 10932.3105 | 3.785% | 29.9 | 18341.9804 | 19100.9692 | 4.138%
2013-06-30 | 11174.679 | 290.1226 | 22662 | 15520.3875 | 10816 | 18354.4 | 43.2 | 19.9844 | 11283.4325 | 11406.4319 | 1.09% | 31.6 | 22719.4401 | 22499.2459 | 0.9692%
2013-07-31 | 12722.707 | 357.4735 | 24927 | 17100.4126 | 11506 | 21288 | 122.76 | 23.2097 | 12736.3503 | 12479.5529 | 2.016% | 34.3 | 24352.1456 | 23212.9348 | 4.678%
2013-08-31 | 12100.351 | 398.7601 | 22833 | 16263.9126 | 11139 | 20243.4 | 84.816 | 22.1183 | 12084.9413 | 12227.7513 | 1.182% | 28.2 | 23255.371 | 22359.7987 | 3.851%
2013-09-30 | 10837.167 | 336.0942 | 22682 | 15051.6208 | 11003 | 17399.6 | 20.88 | 17.26 | 10767.0057 | 11015.3041 | 2.306% | 33.9 | 20422.3176 | 20513.3592 | 0.4458%
2013-10-31 | 11135.689 | 352.2154 | 18445 | 14967.3239 | 11018 | 17040.1 | 0 | 11.7849 | 11114.0467 | 11279.1846 | 1.486% | 6.6 | 18981.007 | 18388.3002 | 3.123%
2013-11-30 | 11640.948 | 422.4146 | 20615 | 16167.9833 | 11571 | 18660.2 | 8.64 | 2.53 | 11709.7788 | 11686.9287 | 0.1951% | -3.3 | 20034.8189 | 20326.4941 | 1.456%
2013-12-31 | 12702.006 | 329.2647 | 21964 | 17072.5887 | 12626 | 19937.2 | 66.216 | -3.5086 | 12528.9266 | 12699.9803 | 1.365% | -8.3 | 21184.5386 | 21395.0558 | 0.9937%
2014-01-31 | 13613.596 | 400.6012 | 22774 | 18297.8441 | 13381 | 20167.4 | 87.048 | -7.8516 | 13409.7767 | 13356.427 | 0.3978% | -17.4 | 22043.8439 | 22319.8106 | 1.252%
2014-02-28 | 12067.276 | 336.7994 | 21905 | 17957.256 | 13981 | 20340.8 | 109.536 | -7.1464 | 11812.9441 | 11748.3799 | 0.5466% | -12.2 | 21218.2216 | 20964.0592 | 1.198%
2014-03-31 | 12672.074 | 436.3629 | 21656 | 17032.3575 | 13296 | 18156.7 | 8.928 | -2.8688 | 12242.1563 | 12054.5719 | 1.532% | -12.1 | 20728.4579 | 19906 | 3.968%
2014-04-30 | 10836.804 | 477.6859 | 18557 | 15051.1167 | 11944 | 16454 | 0 | 7.3289 | 11038.5265 | 10731.1367 | 2.785% | -0.9 | 19249.9632 | 17649 | 8.317%
2014-05-31 | 10642.583 | 485.0087 | 18844 | 14304.547 | 10719 | 16623.2 | 0 | 15.3871 | 10546.4252 | 10790.2174 | 2.312% | 29.4 | 18750.4605 | 18964 | 1.139%
2014-06-30 | 11228.548 | 467.8886 | 20807 | 15595.2056 | 10723 | 17232.9 | 0 | 21.0889 | 11140.5499 | 11346.2756 | 1.847% | 30.3 | 20705.1957 | 22469.55 | 8.521%
2014-07-31 | 11717.444 | 448.354 | 21300 | 15749.2527 | 11321 | 19790.1 | 63.984 | 21.471 | 12324.9268 | 12360.0815 | 0.2852% | 29.8 | 22294.8035 | 22948.69 | 2.933%
2014-08-31 | 11718.183 | 386.2556 | 21363 | 15750.246 | 11362 | 19044 | 47.616 | 21.3172 | 11819.2371 | 11992.5131 | 1.466% | 31.3 | 21644.3547 | 21403.44 | 1.113%
2014-09-30 | 10836.546 | 423.8321 | 21123 | 15050.7583 | 11112 | 19853.4 | 61.2 | 17.9967 | 10671.4853 | 10579.5258 | 0.8617% | 31.4 | 19449.0766 | 19023.2704 | 2.189%
2014-10-31 | 10819.853 | 438.5968 | 17784 | 14542.8132 | 10769 | 16432.6 | 0 | 11.6849 | 10814.1957 | 11126.7565 | 2.89% | 9.1 | 18447.2196 | 18638.7361 | 1.038%
2014-11-30 | 11487.634 | 407.9288 | 20102 | 15955.0472 | 12082 | 17109.3 | 0 | 2.2756 | 11410.1121 | 11497.4835 | 0.7657% | 0.8 | 19923.2587 | 20302.34 | 1.903%
2014-12-31 | 12131.525 | 425.9567 | 20938 | 16305.8132 | 11398 | 17611.5 | 0 | 0.52366 | 12256.0958 | 12769.4956 | 4.189% | -1.2 | 21582.6701 | 21237.74 | 1.598%
2015-01-31 | 13119.979 | 462.7948 | 21814 | 17634.3804 | 13344 | 19048.7 | 26.784 | -6.6624 | 12937.1182 | 13068.9431 | 1.019% | -15.7 | 21503.4489 | 22293.59 | 3.674%
2015-02-28 | 12302.278 | 399.7277 | 21494 | 18306.9613 | 14588 | 18778.7 | 5.376 | -11.4369 | 11740.7311 | 11528.5197 | 1.807% | -15.8 | 19709.6284 | 21016.81 | 6.632%
2015-03-31 | 12044.976 | 495.7729 | 20827 | 16189.4839 | 12675 | 18117.4 | 5.208 | -0.59892 | 11748.227 | 11856.8161 | 0.9243% | -9.6 | 20109.8817 | 19840.93 | 1.337%
2015-04-30 | 10404.962 | 653.4141 | 18462 | 14451.3361 | 10975 | 16390.3 | 0 | 8.6044 | 10624.618 | 10542.0267 | 0.7774% | 2.4 | 19362.8308 | 18121.2 | 6.412%
2015-05-31 | 10547.132 | 529.8747 | 19158 | 14176.2527 | 10657 | 16587.6 | 0 | 17.772 | 10231.5964 | 10635.9243 | 3.952% | 28.8 | 17881.7583 | 19370.33 | 8.325%
2015-06-30 | 10624.316 | 577.9038 | 19339 | 14755.9944 | 10804 | 17220.7 | 0 | 18.9767 | 10908.724 | 11410.2692 | 4.598% | 25.5 | 20554.6293 | 22276.64 | 8.378%
2015-07-31 | 12105.066 | 521.3404 | 22516 | 16270.25 | 11010 | 19756.8 | 61.752 | 23.0602 | 12273.6405 | 12174.2184 | 0.81% | 32.5 | 22638.5319 | 22888.49 | 1.104%
2015-08-31 | 11797.099 | 472.2223 | 22383 | 15856.3159 | 11414 | 19007.1 | 46.872 | 21.8011 | 11782.7212 | 11821.2763 | 0.3272% | 32.1 | 22383 | 21463.69 | 4.107%
2015-09-30 | 11361.901 | 503.8076 | 22063 | 15780.4181 | 10927 | 19812.8 | 61.92 | 20.7778 | 10718.9879 | 10512.648 | 1.925% | 32.6 | 19299.6325 | 18485 | 4.221%
2015-10-31 | 10687.264 | 497.6939 | 17667 | 14364.6022 | 10539 | 16384.2 | 0 | 10.829 | 10731.7474 | 11150.1256 | 3.899% | 13.1 | 18444.3181 | 18339 | 0.571%
2015-11-30 | 10681.592 | 477.3161 | 19239 | 14835.5444 | 11338 | 17157.4 | 0 | 7.5422 | 10867.5486 | 11595.0899 | 6.695% | 1.9 | 19631.9089 | 20306 | 3.434%
2015-12-31 | 11313.857 | 435.4307 | 19161 | 15206.797 | 10811 | 17642 | 0 | 4.8495 | 11784.7123 | 12611.2501 | 7.014% | 6.8 | 20418.0801 | 21160.04 | 3.634%
2016-01-31 | 12384.867 | 471.7938 | 20836 | 16646.3266 | 12116 | 19066 | 24.552 | -2.6 | 12523.599 | 12982.1466 | 3.661% | -11.8 | 21249.7402 | 22360.24 | 5.226%
2016-02-29 | 11471.763 | 474.1135 | 20766 | 16482.4181 | 12533 | 18707.5 | 4.872 | -1.2391 | 11502.97 | 11806.8997 | 2.642% | -10 | 20194.6163 | 20985.25 | 3.915%
2016-03-31 | 11302.963 | 530.5494 | 20063 | 15192.1546 | 11717 | 17387.3 | 0.744 | 3.6194 | 11445.7227 | 11758.7447 | 2.735% | -7.9 | 20324.618 | 20075.21 | 1.227%
2016-04-30 | 10409.92 | 661.3944 | 17821 | 14458.2222 | 11286 | 16583.2 | 0 | 5.97 | 10578.9099 | 10309.6515 | 2.545% | 0.6 | 18912.1728 | 17405.08 | 7.969%
2016-05-31 | 10470.808 | 665.3817 | 19885 | 14073.6667 | 10461 | 17171.1 | 0 | 15.9602 | 10115.8584 | 10530.0143 | 4.094% | 27.2 | 19707.6447 | 19235.65 | 2.395%
2016-06-30 | 11101.521 | 613.5199 | 21692 | 15418.7792 | 10596 | 18447.4 | 24.48 | 21.52 | 11141.3797 | 11378.6081 | 2.129% | 34 | 21568.912 | 22315.7305 | 3.462%
2016-07-31 | 12497.616 | 548.7117 | 22659 | 16797.871 | 10985 | 20860.1 | 143.592 | 25.0882 | 12345.0421 | 11896.1402 | 3.636% | 35 | 22288.7672 | 22599.9414 | 1.396%
2016-08-31 | 13113.359 | 534.2805 | 23100 | 17625.4825 | 12287 | 21278.8 | 183.768 | 25.4183 | 12295.9028 | 11771.834 | 4.262% | 34.8 | 22375.997 | 21440.3166 | 4.182%
2016-09-30 | 11072.26 | 523.2114 | 23213 | 15378.1389 | 10855 | 18825.3 | 42.48 | 20.6733 | 10659.2295 | 10401.8861 | 2.414% | 34.5 | 19712.7154 | 18289 | 7.222%
2016-10-31 | 10518.677 | 417.6305 | 18189 | 14138.0067 | 10663 | 16351 | 0 | 12.6344 | 10453.1463 | 10947.5325 | 4.73% | 5.2 | 18394.9922 | 18079 | 1.718%
2016-11-30 | 10697.637 | 418.8378 | 19369 | 14857.8292 | 11211 | 17154.5 | 0 | 7.5167 | 10913.6011 | 11524.026 | 5.593% | 0.2 | 19544.7667 | 20296 | 3.844%
2016-12-31 | 11978.041 | 435.9647 | 20688 | 16099.5175 | 11684 | 18666.1 | 10.416 | -1.129 | 11950.5536 | 12430.7427 | 4.018% | -8.1 | 20286.7849 | 20888 | 2.964%
2017-01-31 | 12108.005 | 463.9501 | 20372 | 16274.2003 | 12246 | 18425.1 | 2.232 | -1.1495 | 12369.7298 | 12818.8508 | 3.631% | -3.3 | 20965.9674 | 21913.73 | 4.52%
2017-02-28 | 10607.563 | 490.9519 | 19838 | 15785.064 | 11867 | 18064.6 | 0 | 0.47143 | 10787.4931 | 11294.713 | 4.702% | -1.1 | 20379.4501 | 20966.2287 | 2.879%
2017-03-31 | 11591.031 | 560.1987 | 19174 | 15579.3427 | 12158 | 17608.2 | 0 | 0.46667 | 11413.3465 | 11824.0632 | 3.599% | -8.1 | 18692.3503 | 20137.3 | 7.73%
2017-04-30 | 9788.616 | 594.6314 | 17349 | 13595.3 | 10167 | 15576.2 | 0 | 10.6278 | 10105.7565 | 10366.7129 | 2.582% | 7.3 | 18482.7844 | 17969.79 | 2.776%
2017-05-31 | 10153.182 | 619.1188 | 17738 | 13646.75 | 10249 | 15622.5 | 0 | 13.4538 | 10012.8427 | 10576.9018 | 5.633% | 29.6 | 18260.3078 | 19193.19 | 5.109%
2017-06-30 | 10657.08 | 578.0093 | 21168 | 14801.5 | 10518 | 17663.4 | 7.2 | 20.6422 | 10682.999 | 11159.3312 | 4.459% | 32.4 | 21144.8187 | 22454.87 | 6.196%
2017-07-31 | 11587.63 | 582.9578 | 20627 | 15574.7715 | 10806 | 19028.7 | 17.112 | 22.8473 | 11851.6211 | 11984.7355 | 1.123% | 31.5 | 22152.8524 | 22492.73 | 1.534%
2017-08-31 | 11350.012 | 559.5215 | 20158 | 15255.3925 | 10829 | 18577.9 | 5.208 | 21.228 | 11513.597 | 12105.5471 | 5.141% | 30 | 21323.3584 | 22376.43 | 4.939%
2017-09-30 | 10679.393 | 484.1858 | 21786 | 14832.4903 | 10487 | 18795.6 | 25.2 | 19.9789 | 10155.927 | 10494.2948 | 3.332% | 31.3 | 17821.4732 | 19490.21 | 9.364%
2017-10-31 | 10339.329 | 532.8493 | 17418 | 13896.9476 | 10534 | 15857.7 | 0 | 14.4925 | 10260.3837 | 10942.7953 | 6.651% | 26.5 | 17407.7858 | 18030.62 | 3.578%
2017-11-30 | 10955.909 | 497.8786 | 19115 | 15216.5403 | 11199 | 17381.1 | 0 | 4.6056 | 10946.7668 | 11371.7451 | 3.882% | 3 | 19195.4397 | 20230.97 | 5.395%
2017-12-31 | 12338.893 | 402.8257 | 20306 | 16584.5336 | 12093 | 18875.6 | 5.952 | -4.1731 | 12096.0133 | 12303.6865 | 1.717% | -4.1 | 21439.6493 | 20901.44 | 2.51%
2018-01-31 | 12700.826 | 533.4365 | 20906 | 17071.0027 | 12453 | 19337.8 | 14.88 | -4.6452 | 12679.8037 | 12685.9178 | 0.04822% | -15.2 | 20177.5339 | 21618.93 | 7.144%
2018-02-28 | 10951.065 | 496.4596 | 20076 | 16296.2277 | 12716 | 18608.6 | 1.344 | -0.70714 | 11081.1365 | 11074.1738 | 0.06283% | -8.2 | 20042.2165 | 20242.21 | 0.9979%
2018-03-31 | 11372.42 | 596.6609 | 18462 | 15285.5108 | 12158 | 17159.9 | 0 | 0.8828 | 11267.3415 | 11423.555 | 1.386% | 0.2 | 19330.8728 | 19551.97 | 1.144%
2018-04-30 | 10578.368 | 586.9588 | 18011 | 14692.1778 | 11497 | 16647.2 | 0 | 4.37 | 10586.2978 | 10157.8502 | 4.047% | 2.4 | 18107.9593 | 17669.81 | 2.42%
2018-05-31 | 10421.469 | 664.6636 | 20473 | 14007.3508 | 10541 | 16770.4 | 10.416 | 18.4376 | 10081.137 | 10289.6502 | 2.068% | 30.7 | 19262.1307 | 18817.47 | 2.308%
2018-06-30 | 10923.446 | 602.8769 | 21369 | 15171.4528 | 10698 | 18437.3 | 37.44 | 20.7522 | 10980.4534 | 10863.4062 | 1.066% | 30.2 | 20626.9619 | 21890.0001 | 6.123%
2018-07-31 | 12685.981 | 517.157 | 22909 | 17051.0497 | 11413 | 20705.3 | 140.616 | 24.6247 | 12483.776 | 11652.7714 | 6.657% | 33.2 | 22409.0792 | 22076.0001 | 1.486%
2018-08-31 | 12688.795 | 531.4383 | 21990 | 17054.832 | 11966 | 20622.8 | 120.528 | 24.1731 | 12040.5393 | 11685.5744 | 2.948% | 31.7 | 21385.6483 | 21946.0001 | 2.62%
2018-09-30 | 11147.31 | 480.938 | 23240 | 15482.375 | 10701 | 19596.5 | 56.88 | 19.9011 | 10579.1906 | 10189.9802 | 3.679% | 33.9 | 19505.5646 | 19019 | 2.494%
2018-10-31 | 10717.348 | 485.4689 | 18205 | 14405.0376 | 10847 | 16419.1 | 0 | 9.9258 | 10526.7735 | 10750.0648 | 2.121% | 26.1 | 17751.4152 | 17788 | 0.2061%
2018-11-30 | 11360.321 | 423.7495 | 20152 | 15778.2236 | 11765 | 17927.3 | 0.72 | 2.12 | 11184.9393 | 11170.7506 | 0.1269% | -6.6 | 19266.3918 | 19828 | 2.915%
2018-12-31 | 11938.614 | 407.6369 | 19891 | 16046.5242 | 12284 | 18215.4 | 0 | 0.47097 | 12019.553 | 12007.3958 | 0.1011% | -1.4 | 20375.1864 | 20503 | 0.6273%
2019-01-31 | 12777.216 | 463.966 | 21525 | 17173.6774 | 12291 | 19588.2 | 41.664 | -5.9118 | 12688.8389 | 12973.2132 | 2.241% | -11.8 | 21058.2817 | 21506 | 2.126%
2019-02-28 | 11291.744 | 455.9299 | 20500 | 16803.1905 | 13041 | 19051 | 8.736 | -3.4405 | 11212.4836 | 11162.2057 | 0.4484% | -10.1 | 20420.3692 | 20008 | 2.019%
2019-03-31 | 11658.678 | 588.34 | 20263 | 15670.2661 | 12210 | 17519 | 2.232 | -0.036022 | 11458.0531 | 11522.1982 | 0.5598% | -9 | 19573.6921 | 19457 | 0.5962%
2019-04-30 | 10264.505 | 597.1531 | 17645 | 14256.2569 | 11079 | 16133.5 | 0 | 7.3189 | 10432.2785 | 10252.9314 | 1.719% | 2.8 | 18796.3299 | 17548 | 6.641%
2019-05-31 | 10219.56 | 574.423 | 16784 | 13735.9677 | 10328 | 15586.7 | 0 | 13.0312 | 10218.7126 | 10412.0446 | 1.892% | 8.2 | 17977.0308 | 18663 | 3.816%
2019-06-30 | 10365.619 | 600.8034 | 20248 | 14396.6931 | 10564 | 17336.5 | 2.88 | 19.5056 | 10608.5215 | 10939.3571 | 3.119% | 28.9 | 21239.1838 | 21623 | 1.807%
2019-07-31 | 12792.766 | 606.5726 | 21791 | 17194.578 | 11565 | 20646.4 | 145.824 | 24.6344 | 12446.1887 | 11763.9974 | 5.481% | 31.4 | 21120.5208 | 22061 | 4.453%
2019-08-31 | 11825.052 | 555.2842 | 21354 | 15893.8871 | 11280 | 19305.9 | 40.92 | 22.4419 | 11798.5843 | 11598.2109 | 1.698% | 30.2 | 22490.4547 | 21200 | 5.738%
2019-09-30 | 10318.533 | 482.8673 | 19717 | 14331.2958 | 10477 | 16722 | 0 | 18.74 | 10167.6302 | 10564.4926 | 3.903% | 28.6 | 18958.9757 | 19469.84 | 2.695%
2019-10-31 | 10351.05 | 505.1513 | 18329 | 13912.7016 | 10739 | 15950.2 | 0 | 11.7903 | 10446.8836 | 10788.0047 | 3.265% | 31.2 | 18814.592 | 17559 | 6.674%
2019-11-30 | 11255.325 | 452.3729 | 19625 | 15632.3958 | 11711 | 17850 | 0 | 1.6178 | 11094.2081 | 11194.6524 | 0.9054% | -4.1 | 19001.8635 | 19597 | 3.132%
2019-12-31 | 11997.095 | 447.2177 | 20974 | 16125.1277 | 11787 | 18657.6 | 11.16 | -0.23333 | 12094.1802 | 12086.6766 | 0.06204% | -7.8 | 20974 | 20307 | 3.18%
2020-01-31 | 12178.575 | 426.7563 | 19928 | 16369.0524 | 12353 | 18557.8 | 0 | -0.75161 | 12460.9405 | 12859.4588 | 3.198% | -8.5 | 21137.8728 | 21185.0004 | 0.223%
2020-02-29 | 11239.82 | 490.212 | 19630 | 16149.1667 | 12683 | 18163 | 0 | -1.9977 | 11253.1814 | 11586.6754 | 2.964% | -10.4 | 19776.0281 | 19917.0004 | 0.7128%
2020-03-31 | 10989.389 | 585.8152 | 18183 | 14770.6841 | 11120 | 16702.6 | 0 | 4.1634 | 11058.3098 | 11522.322 | 4.196% | 5.4 | 19680.948 | 19377.0004 | 1.544%
2020-04-30 | 9282.854 | 642.7441 | 15350 | 12892.8528 | 10379 | 14231.4 | 0 | 7.01 | 9383.3554 | 10229.1483 | 9.014% | 4.4 | 16515.7848 | 17302.0004 | 4.76%
2020-05-31 | 9642.117 | 671.1773 | 20649 | 12959.8347 | 9831 | 15246.8 | 3.72 | 13.3968 | 9306.4436 | 9434.378 | 1.375% | 30.6 | 18761.2836 | 17426 | 7.117%
2020-06-30 | 10800.015 | 634.4604 | 21292 | 15000.0208 | 10340 | 18996.7 | 20.88 | 22.0667 | 10596.6512 | 10274.389 | 3.041% | 31.2 | 20741.8718 | 20034 | 3.413%
2020-07-31 | 13202.706 | 617.8423 | 24446 | 17745.5726 | 12154 | 21827.4 | 188.232 | 26.2043 | 12529.7172 | 11731.6936 | 6.369% | 34 | 24057.7367 | 22364.4404 | 7.038%
2020-08-31 | 12081.08 | 578.6123 | 23823 | 16238.0108 | 11221 | 20133.6 | 82.584 | 23.2366 | 12338.1938 | 11441.5908 | 7.267% | 31.9 | 25317.7535 | 21631.4406 | 14.56%
2020-09-30 | 10114.374 | 551.2872 | 20225 | 14047.7417 | 10834 | 16340.6 | 1.44 | 17.9378 | 10011.2355 | 10356.1124 | 3.445% | 27.4 | 19254.2062 | 20312.4408 | 5.496%
2020-10-31 | 10339.39 | 528.3272 | 17679 | 13897.0296 | 10645 | 16042.5 | 0 | 10.371 | 10349.5982 | 10040.7873 | 2.984% | 7 | 17587.3164 | 17039.9727 | 3.112%
2020-11-30 | 10529.032 | 524.2466 | 19147 | 14623.6556 | 10808 | 17008.6 | 0 | 7.763 | 10693.8532 | 10531.6058 | 1.517% | 0.1 | 19416.1975 | 18891.9134 | 2.7%
2020-12-31 | 11811.675 | 485.452 | 20738 | 15875.9073 | 12389 | 18200.4 | 3.72 | 0.31505 | 11932.8039 | 11815.0887 | 0.9865% | -6.8 | 20975.3455 | 19805.1651 | 5.579%
2021-01-31 | 12105.158 | 409.653 | 20150 | 16270.3737 | 12798 | 18344.9 | 1.488 | -1.9591 | 12307.6071 | 12539.1611 | 1.881% | -8.4 | 20951.6431 | 21176.0005 | 1.071%
2021-02-28 | 11233.123 | 456.7989 | 20318 | 16715.9568 | 13200 | 18799.9 | 3.36 | -4.306 | 11144.3783 | 11073.4765 | 0.6362% | -6.9 | 20175.4672 | 20760.0005 | 2.897%
2021-03-31 | 11101.706 | 690.6151 | 19344 | 14921.6478 | 11659 | 16933 | 0 | 4.6086 | 11249.5616 | 11497.7125 | 2.206% | -0.8 | 19868.2566 | 19384.0005 | 2.437%
2021-04-30 | 9781.57 | 596.9459 | 16644 | 13585.5139 | 10498 | 15264.1 | 0 | 8.98 | 10097.7166 | 10244.8035 | 1.457% | 4.8 | 17618.7846 | 17070.0009 | 3.115%
2021-05-31 | 10086.333 | 622.8177 | 19443 | 13556.8992 | 10782 | 15777.1 | 0 | 15.1602 | 9986.9371 | 10152.0681 | 1.653% | 31.6 | 18021.5172 | 18055.3342 | 0.1876%
2021-06-30 | 11262.474 | 611.5113 | 22258 | 15642.325 | 11304 | 19635.9 | 59.76 | 22.9889 | 10840.8856 | 10747.5852 | 0.8606% | 31.6 | 21528.4908 | 22162.0009 | 2.943%
2021-07-31 | 11636.443 | 611.3859 | 21655 | 15640.3804 | 11108 | 19487.8 | 49.848 | 22.2151 | 11970.9832 | 11806.5074 | 1.374% | 31.7 | 22251.4821 | 22413.0005 | 0.7259%
2021-08-31 | 12856.511 | 581.7597 | 22986 | 17280.2567 | 10853 | 21313.1 | 188.976 | 24.7634 | 12072.0791 | 11706.2663 | 3.03% | 33.1 | 21854.4728 | 22235.0005 | 1.741%
2021-09-30 | 10389.017 | 544.7746 | 18769 | 14429.1903 | 10426 | 16782 | 0 | 18.74 | 10401.3058 | 10472.6839 | 0.6862% | 26 | 18979.8917 | 21212.0005 | 11.76%
2021-10-31 | 10516.14 | 524.146 | 17312 | 14134.5968 | 10779 | 16116.7 | 0 | 14.3432 | 10429.4829 | 10365.0376 | 0.6179% | 21.95 | 17606.8602 | 17270.7147 | 1.909%
2021-11-30 | 10956.602 | 515.9736 | 19644 | 15217.5028 | 11605 | 17496.4 | 0 | 4.74 | 11017.3258 | 10886.7659 | 1.185% | 0.15 | 19684.7166 | 19227.38 | 2.323%
2021-12-31 | 11969.602 | 476.8031 | 20455 | 16088.1747 | 12517 | 18342.8 | 2.976 | 2.0215 | 12185.9418 | 11984.4925 | 1.653% | -2.3 | 21331.5579 | 20088.8968 | 5.825%
2022-01-31 | 13085.388 | 489.3876 | 21349 | 17587.8871 | 12491 | 19796.7 | 55.056 | -7.0054 | 12928.5532 | 12536.9576 | 3.029% | -12.1 | 21334.1018 | 20983.6671 | 1.643%
2022-02-28 | 11487.734 | 515.5153 | 20918 | 17094.8423 | 13761 | 19171.3 | 14.112 | -3.5488 | 11400.5165 | 11208.712 | 1.682% | -9.8 | 20782.3287 | 20446.0004 | 1.618%
2022-03-31 | 11816.835 | 611.8729 | 19763 | 15882.8427 | 12285 | 17932.4 | 0 | 1.929 | 11793.6956 | 11617.5125 | 1.494% | -5.2 | 19941.2707 | 19401.3338 | 2.708%
2022-04-30 | 10265.047 | 646.6282 | 17256 | 14257.0097 | 11430 | 16016.1 | 0 | 7.5244 | 10311.1592 | 10239.112 | 0.6987% | 6.6 | 17752.3935 | 17251.0005 | 2.824%
2022-05-31 | 10469.914 | 677.424 | 21292 | 14072.4651 | 10485 | 16297 | 8.928 | 17.0151 | 10137.6947 | 10372.2878 | 2.314% | 32.2 | 20136.0014 | 18269.0005 | 9.272%
2022-06-30 | 10929.858 | 654.792 | 21954 | 15180.3583 | 10627 | 18994.9 | 43.2 | 21.0744 | 11002.2267 | 10967.9836 | 0.3112% | 34.6 | 22101.7092 | 22161.0005 | 0.2683%
2022-07-31 | 12343.623 | 588.0453 | 22607 | 16590.8911 | 11449 | 20039.3 | 77.376 | 24.086 | 12411.016 | 11893.9057 | 4.167% | 34.2 | 22484.9516 | 22542.0005 | 0.2537%
2022-08-31 | 12624.254 | 603.8346 | 21871 | 16968.0833 | 11830 | 20450 | 99.696 | 23.6763 | 11998.9314 | 12028.3221 | 0.2449% | 30.5 | 23477.9346 | 22430.0005 | 4.463%
2022-09-30 | 10814.096 | 493.97 | 20350 | 15019.5778 | 11082 | 17965.3 | 2.88 | 18.7344 | 10678.4907 | 10551.0851 | 1.193% | 29.2 | 20446.2276 | 21489.0005 | 5.1%
2022-10-31 | 10384.167 | 567.3429 | 17294 | 13957.2137 | 10820 | 15961.1 | 0 | 11.6301 | 10447.0825 | 10603.0084 | 1.493% | 8.9 | 17724.6236 | 17559.0005 | 0.9344%
2022-11-30 | 11044.181 | 489.5672 | 19441 | 15339.1403 | 10931 | 17734 | 0 | 6.0933 | 11128.3255 | 11151.0711 | 0.2044% | -3.6 | 19389.6575 | 19812.0005 | 2.178%
2022-12-31 | 12273.23 | 460.9624 | 20173 | 16496.2769 | 12417 | 18629 | 2.232 | 0.16129 | 12412.7534 | 12191.9609 | 1.779% | 0.8 | 20584.5241 | 20241.0005 | 1.669%
2023-01-31 | 12519.712 | 376.932 | 20486 | 16827.5699 | 12603 | 18821.9 | 4.464 | 8.3011 | 13052.768 | 12663.6554 | 2.981% | 8 | 21435.1399 | 21170.3338 | 1.235%
2023-02-28 | 11225.17 | 505.7145 | 21388 | 16704.122 | 12990 | 19014 | 10.08 | -0.72976 | 11325.8235 | 11375.0622 | 0.4347% | -15.5 | 20433.0112 | 20892.3338 | 2.248%
2023-03-31 | 11846.269 | 623.4296 | 18811 | 15922.4046 | 12940 | 17656 | 0 | 1.6882 | 11814.7494 | 11846.6528 | 0.27% | -0.1 | 19000.8853 | 19701.0485 | 3.685%
2023-04-30 | 10271.638 | 587.4763 | 17547 | 14266.1639 | 11117 | 15920.1 | 0 | 10.0774 | 10374.8437 | 10349.2653 | 0.2465% | 5.4 | 19103.3719 | 17785.9996 | 6.896%
2023-05-31 | 10356.75 | 675.0171 | 20787 | 13920.3629 | 10859 | 15783.1 | 5.208 | 15.1742 | 10473.6584 | 10418.8057 | 0.5237% | 29.9 | 18001.5877 | 18869.9996 | 4.824%
2023-06-30 | 11119.814 | 599.2129 | 21463 | 15444.1861 | 11438 | 18666.1 | 23.04 | 20.5444 | 11230.6805 | 10652.496 | 5.148% | 31.6 | 22417.4764 | 21884.9996 | 2.375%
2023-07-31 | 12507.785 | 591.493 | 22686 | 16811.539 | 11987 | 20318.4 | 102.672 | 23.3629 | 12455.0186 | 11858.9002 | 4.786% | 30.95 | 23368.3724 | 22445.9996 | 3.947%
2023-08-31 | 11828.62 | 564.0255 | 21364 | 15898.6828 | 11629 | 18779.7 | 17.856 | 21.272 | 12005.3253 | 12249.9171 | 2.037% | 29.1 | 21865.1956 | 22396.9996 | 2.432%
2023-09-30 | 10997.556 | 494.2157 | 23713 | 15274.3833 | 11402 | 18088.3 | 43.92 | 19.6733 | 10685.1004 | 10718.9739 | 0.317% | 32.1 | 21317.3942 | 21479.9996 | 0.7628%
2023-10-31 | 10932.34 | 461.1476 | 20849 | 14694.0054 | 11260 | 16853.6 | 5.952 | 13.4688 | 10757.1302 | 10593.967 | 1.517% | 30 | 19208.5675 | 17668.0452 | 8.02%
2023-11-30 | 11456.562 | 454.778 | 20579 | 15911.8917 | 12555 | 18103 | 2.88 | 4.66 | 11478.5016 | 11007.299 | 4.105% | -1.5 | 20453.2108 | 19742.0453 | 3.477%
2023-12-31 | 12065.5 | 427.7837 | 20004 | 16217.0699 | 12029 | 18506.6 | 0.744 | 3.0699 | 12384.2261 | 12018.94 | 2.95% | 3 | 21211.1571 | 20346.0453 | 4.079%
2024-01-31 | 13036.084 | 436.2955 | 21081 | 17521.6183 | 13750 | 19526.1 | 26.04 | -1.8882 | 13208.8176 | 12929.406 | 2.115% | -9 | 21405.4347 | 21418.2553 | 0.05989%
2024-02-29 | 11516.766 | 515.0876 | 19624 | 16547.0776 | 12975 | 18418 | 0 | 1.231 | 11729.9509 | 11956.6273 | 1.932% | -3 | 20022.691 | 20987.7553 | 4.82%
2024-03-31 | 11542.29 | 590.9683 | 18902 | 15513.8306 | 12598 | 17286.8 | 0 | 4.7065 | 11632.2959 | 11836.2413 | 1.753% | -1.8 | 18939.8337 | 19645.2454 | 3.724%
2024-04-30 | 10489.417 | 651.5238 | 17947 | 14568.6347 | 11368 | 16245.8 | 0 | 9.56 | 10650.6806 | 10616.6408 | 0.3196% | 6.1 | 18586.0743 | 17839.6154 | 4.016%
2024-05-31 | 10735.152 | 649.7686 | 20402 | 14428.9677 | 11280 | 16339.7 | 6.696 | 17.5914 | 10640.585 | 10660.6544 | 0.1886% | 29.1 | 19498.7984 | 19148.7554 | 1.795%
2024-06-30 | 11566.905 | 625.1741 | 23803 | 16065.1458 | 11298 | 19934.3 | 69.84 | 21.0956 | 11334.1111 | 10892.6773 | 3.895% | 34.2 | 22585.2284 | 22502.1655 | 0.3678%
2024-07-31 | 13072.592 | 622.0428 | 23206 | 17570.6882 | 11159 | 21098.8 | 184.512 | 23.7667 | 12956.8035 | 12334.9116 | 4.8% | 31.1 | 23182.1746 | 22729.3704 | 1.953%
2024-08-31 | 12666.051 | 541.4969 | 23110 | 17024.2621 | 12063 | 20495.1 | 113.832 | 22.3538 | 12419.372 | 12432.5962 | 0.1065% | 29.1 | 22518.533 | 22592.9271 | 0.3304%
2024-09-30 | 11321.751 | 509.8347 | 21643 | 15724.6542 | 11633 | 18533 | 14.4 | 20.0589 | 10932.1478 | 11042.347 | 1.008% | 28 | 21462.7165 | 21998.022 | 2.494%
2024-10-31 | 10992.867 | 533.6771 | 18117 | 14775.3589 | 11730 | 16621.4 | 0 | 13.2301 | 11048.6213 | 11073.6096 | 0.2262% | 21.2 | 18603.2901 | 17976.8176 | 3.368%
2024-11-30 | 11312.89 | 458.6703 | 19212 | 15712.3472 | 12378 | 17631.1 | 0 | 7.1389 | 11494.5336 | 11500.099 | 0.04842% | 5.8 | 19942.2233 | 20217.9361 | 1.383%
2024-12-31 | 12959.601 | 445.067 | 21016 | 17418.8185 | 13155 | 19552.8 | 34.968 | -0.25484 | 13046.7703 | 12626.6472 | 3.22% | -10.5 | 21342.8087 | 21036.6297 | 1.435%
2025-01-31 | 13668.714 | 511.7658 | 22058 | 18371.9274 | 13626 | 20564 | 148.056 | -4.7839 | 13661.657 | 13253.9945 | 2.984% | -12 | 22379.5336 | 21835.8361 | 2.429%
2025-02-28 | 12278.547 | 424.9022 | 21399 | 16503.4234 | 14670 | 20182.3 | 96.096 | -4.2048 | 12130.7045 | 11671.9004 | 3.782% | -6.9 | 21116.0479 | 21259.4124 | 0.6789%
2025-03-31 | 12057.659 | 627.9253 | 20232 | 16206.5309 | 12515 | 18017.4 | 2.232 | 3.3323 | 12091.2745 | 12058.4394 | 0.2716% | -5.3 | 19614.4739 | 20000.0174 | 1.966%
2025-04-30 | 10837.309 | 643.6038 | 19271 | 14566.2755 | 11805 | 16902.1 | 0 | 8.5978 | 10891.1786 | 10619.601 | 2.494% | 0.1 | 19246.3001 | 18154.8411 | 5.671%
2025-05-31 | 10784.244 | 639.538 | 18190 | 14494.9516 | 11648 | 16270.8 | 0 | 14.3613 | 10886.6628 | 10649.1943 | 2.181% | 27.1 | 18891.1849 | 19064.5516 | 0.9177%
2025-06-30 | 11845.624 | 633.9965 | 24775 | 15921.5376 | 11639 | 20141.9 | 77.04 | 22.01 | 11544.6629 | 11223.7937 | 2.779% | 34.9 | 22678.4237 | 22279.0506 | 1.761%
2025-07-31 | 13905.926 | 604.4885 | 24399 | 18690.7608 | 12762 | 22537.1 | 279 | 25.4108 | 13471.3387 | 12424.9641 | 7.767% | 33.2 | 23249.8525 | 23168.1551 | 0.3514%
2025-08-31 | 12930.485 | 545.7734 | 24500 | 17379.6841 | 12184 | 22130.4 | 155.496 | 22.5892 | 12734.6294 | 12363.8608 | 2.911% | 32.2 | 23530.1953 | 22782.3554 | 3.178%
2025-09-30 | 11276.887 | 458.924 | 19991 | 15157.1062 | 12093 | 18262.3 | 0 | 19.7033 | 11125.7506 | 11069.0052 | 0.51% | 29.2 | 21192.8937 | 21288.0486 | 0.449%
2025-10-31 | 11319.417 | 481.3716 | 20310 | 15214.2702 | 11805 | 17125.2 | 1.488 | 12.943 | 11323.7934 | 11076.979 | 2.18% | 28 | 18572.3296 | 18320.7967 | 1.354%
2025-11-30 | 12026.73 | 415.8447 | 19827 | 16164.9597 | 13242 | 18499.4 | 0 | 4.2522 | 12004.1764 | 11562.3458 | 3.681% | -2.9 | 19963.3073 | 20153.1936 | 0.9512%
2025-12-31 | 13676.513 | 407.8892 | 21541 | 18382.4099 | 14548 | 20160.6 | 97.464 | -2.686 | 13529.2595 | 12900.8568 | 4.645% | -4.9 | 21487.8851 | 21447.1157 | 0.1897%
2026-01-31 | 14011.786 | 477.0403 | 22064 | 18833.0457 | 14781 | 20879.6 | 220.224 | -5.5957 | 13936.0406 | 13826.1993 | 0.7882% | -11 | 22160.5721 | 22550.57 | 1.76%
2026-02-28 | 12373.547 | 436.0513 | 21821 | 16631.1116 | 14595 | 20375.4 | 110.88 | 14.1581 | 12322.8713 | 12168.7162 | 1.251% | -8.1 | 21428.1773 | 21686.2 | 1.204%
2026-03-31 | 12605.428 | 598.4014 | 20333 | 16942.7796 | 13270 | 18781.8 | 5.952 | 3.1204 | 12592.448 | 12554.0826 | 0.3047% | -5.1 | 19889.5794 | 20412.11 | 2.627%
2026-04-30 | 11092.866 | 616.6241 | 18502 | 14909.7661 | 12434 | 17173.6 | 0 | 14.1581 | 11162.0081 | 10995.8665 | 1.488% | 0.8 | 19288.6539 | 18337.2522 | 4.932%
2026-05-31 | 11136.637 | 649.3378 | 20990 | 14968.5981 | 11893 | 16593.3 | 3.72 | 0 | 11107.4819 | 11100.8529 | 0.05968% | 30.1 | 19345.3919 | 19510.8225 | 0.8551%
Back to main menu

## Table 1.4.3
Back to main menu
Table 1.4.3: Monthly Consumption by Market Participant Type
| Monthly Energy Demand (GWh) |  |  |  |  | Monthly Peak Demand (MW)
Month | Energy Demand | LDC Consumption | Wholesale Consumption | Generator Consumption | Losses | Peak Demand | LDC Consumption | Wholesale Consumption | Generator Consumption | Losses
2002-05-31 | 11874.901 | 9466.601 | 2081.739 | 140.146 | 186.415 | 20068 | 16707.96 | 2841.338 | 157.638 | 361.064
2002-06-30 | 12185.238 | 9864.032 | 2012.067 | 134.504 | 174.635 | 23578 | 20428.91 | 2643.003 | 137.661 | 368.426
2002-07-31 | 14033.343 | 11576.297 | 2018.911 | 150.335 | 287.8 | 25226 | 22063.8 | 2415.473 | 134.548 | 612.179
2002-08-31 | 13748.878 | 11167.443 | 2096.774 | 176.548 | 308.113 | 25414 | 21694.54 | 2594.581 | 196.459 | 928.42
2002-09-30 | 12593.138 | 10114.337 | 2050.509 | 142.07 | 286.222 | 25062 | 21577.29 | 2561.387 | 144.599 | 778.724
2002-10-31 | 12397.839 | 9862.483 | 2137.213 | 149.407 | 248.736 | 21216 | 17642.04 | 2820.526 | 141.773 | 611.661
2002-11-30 | 12655.667 | 10127.444 | 2112.743 | 143.845 | 271.635 | 21862 | 18381.47 | 2755.733 | 168.79 | 556.007
2002-12-31 | 13483.864 | 11037.036 | 2023.317 | 170.222 | 253.289 | 23334 | 19815.43 | 2740.625 | 146.763 | 631.182
2003-01-31 | 14486.674 | 11888.726 | 2187.64 | 167.688 | 242.62 | 24158 | 20778.8 | 2817.494 | 154.589 | 407.117
2003-02-28 | 13122.529 | 10715.513 | 1981.331 | 156.006 | 269.679 | 23469 | 20024.81 | 2805.901 | 215.791 | 422.498
2003-03-31 | 13414.004 | 10768.113 | 2192.28 | 167.167 | 286.444 | 23117 | 19689.78 | 2885.733 | 187.437 | 354.05
2003-04-30 | 12097.332 | 9624.429 | 2088.532 | 161.837 | 222.534 | 21010 | 17771.1 | 2657.654 | 196.626 | 384.62
2003-05-31 | 11627.445 | 9165.532 | 2114.832 | 143.984 | 203.097 | 18741 | 15387.78 | 2817.187 | 186.956 | 349.077
2003-06-30 | 11884.956 | 9582.859 | 1921.764 | 167.923 | 212.41 | 24753 | 21586.53 | 2263.442 | 188.539 | 714.489
2003-07-31 | 12897.586 | 10664.835 | 1835.72 | 158.334 | 238.697 | 23175 | 20435.12 | 2212.712 | 162.441 | 364.727
2003-08-31 | 12514.308 | 10340.948 | 1783.823 | 170.359 | 219.178 | 23891 | 20915.12 | 2358.598 | 184.046 | 433.236
2003-09-30 | 11794.469 | 9431.235 | 1977.11 | 167.921 | 218.203 | 20700 | 17454.71 | 2612.308 | 163.716 | 469.266
2003-10-31 | 12159.932 | 9686.179 | 2067.456 | 198.093 | 208.204 | 20408 | 16887.17 | 2775.37 | 298.908 | 446.552
2003-11-30 | 12389.858 | 9948.111 | 2036.796 | 175.8 | 229.151 | 21584 | 17991.12 | 2782.01 | 190.243 | 620.627
2003-12-31 | 13327.663 | 10932.665 | 1969.767 | 183.865 | 241.366 | 22798 | 19265.16 | 2834.078 | 176.349 | 522.413
2004-01-31 | 14767.413 | 12198.477 | 2104.447 | 198.64 | 265.849 | 24937 | 21481.3 | 2721.368 | 264.033 | 470.299
2004-02-29 | 13088.075 | 10672.632 | 1970.306 | 177.544 | 267.593 | 22608 | 19037.09 | 2699.003 | 255.4771 | 616.4299
2004-03-31 | 13224.641 | 10655.46 | 2122.051 | 169.56 | 277.57 | 21634 | 18016.84 | 2626.161 | 277.468 | 713.531
2004-04-30 | 11792.132 | 9440.718 | 1965.52 | 135.051 | 250.843 | 19911 | 16643.61 | 2707.734 | 178.464 | 381.192
2004-05-31 | 11835.269 | 9342.564 | 2043.903 | 155.45 | 293.352 | 20327 | 17063.54 | 2516.653 | 165.742 | 581.065
2004-06-30 | 12045.885 | 9547.152 | 2052.914 | 164.35 | 281.469 | 23163 | 19707.77 | 2663.11 | 157.95 | 634.17
2004-07-31 | 12769.985 | 10306.992 | 1967.079 | 177.05 | 318.864 | 23976 | 20506.23 | 2491.816 | 166.45 | 811.504
2004-08-31 | 12746.297 | 10241.325 | 2047.405 | 178.064 | 279.503 | 23159 | 19644.67 | 2631.637 | 186.377 | 696.316
2004-09-30 | 12369.687 | 9861.224 | 2065.015 | 156.763 | 286.685 | 21911 | 18334.65 | 2713.43 | 146.421 | 716.499
2004-10-31 | 12215.166 | 9633.603 | 2153.798 | 167.2 | 260.565 | 19829 | 16245.53 | 2899.387 | 159.471 | 524.612
2004-11-30 | 12601.008 | 10046.497 | 2070.218 | 187.926 | 296.367 | 22066 | 18138.28 | 2941.28 | 297.978 | 688.462
2004-12-31 | 13981.717 | 11434.513 | 2017.175 | 194.386 | 335.643 | 24979 | 21447.05 | 2662.278 | 196.875 | 672.797
2005-01-31 | 14619.18 | 12016.966 | 2090.334 | 198.56 | 313.32 | 24362 | 21030.26 | 2558.497 | 208.777 | 564.466
2005-02-28 | 12731.835 | 10393.346 | 1913.32 | 153.437 | 271.732 | 22322 | 18828.79 | 2715.305 | 226.273 | 551.632
2005-03-31 | 13494.28 | 10952.794 | 2055.749 | 195.636 | 290.101 | 22724 | 19266.54 | 2706.327 | 202.516 | 548.617
2005-04-30 | 11827.861 | 9388.13 | 1980.341 | 188.9 | 270.49 | 19343 | 15820.59 | 2789.575 | 261.253 | 471.582
2005-05-31 | 11744.825 | 9333.369 | 1989.317 | 174.521 | 247.618 | 19007 | 15617.54 | 2700.374 | 152.414 | 536.672
2005-06-30 | 13499.266 | 11095.068 | 1907.147 | 169.877 | 327.174 | 26157 | 22535.89 | 2563.391 | 200.283 | 857.436
2005-07-31 | 14094.375 | 11641.796 | 1878.941 | 191.549 | 382.089 | 26160 | 22580.23 | 2333.553 | 242.33 | 1003.887
2005-08-31 | 14031.29 | 11407.667 | 2030.291 | 207.892 | 385.44 | 25816 | 22243.61 | 2430.247 | 216.422 | 925.721
2005-09-30 | 12552.618 | 10024.722 | 1983.19 | 197.067 | 347.639 | 23914 | 20335.88 | 2512.888 | 216.241 | 848.991
2005-10-31 | 12187.328 | 9837.039 | 1904.417 | 177.228 | 268.644 | 20752 | 17598.01 | 2427.417 | 178.481 | 548.092
2005-11-30 | 12440.55 | 10179.434 | 1831.654 | 164.858 | 264.604 | 22564 | 19415.04 | 2459.517 | 173.174 | 516.269
2005-12-31 | 13745.639 | 11400.567 | 1858.136 | 196.651 | 290.285 | 23766 | 20461.34 | 2428.282 | 252.777 | 623.601
2006-01-31 | 13596.17 | 11188.909 | 1905.583 | 187.931 | 313.747 | 23052 | 19542.59 | 2540.335 | 211.234 | 757.841
2006-02-28 | 12568.25 | 10421.74 | 1719.011 | 163.583 | 263.916 | 22321 | 18801.15 | 2538.497 | 239.103 | 742.25
2006-03-31 | 13199.998 | 10803.314 | 1939.387 | 173.782 | 283.515 | 21772 | 18543.05 | 2487.994 | 178.339 | 562.617
2006-04-30 | 11512.852 | 9215.929 | 1861.338 | 153.612 | 281.973 | 19582 | 16298.82 | 2556.562 | 160.219 | 566.399
2006-05-31 | 11927.478 | 9647.028 | 1867.851 | 176.75 | 235.849 | 24857 | 21656.22 | 2407.501 | 238.276 | 555.003
2006-06-30 | 12541.936 | 10215.528 | 1875.843 | 193.439 | 257.126 | 23349 | 20111.81 | 2383.145 | 176.614 | 677.431
2006-07-31 | 13853.619 | 11539.169 | 1830.002 | 187.291 | 297.157 | 26092 | 22600.56 | 2398.848 | 185.769 | 906.823
2006-08-31 | 13308.1 | 10969.255 | 1903.683 | 161.696 | 273.466 | 27005 | 23709.23 | 2399.945 | 170.879 | 724.946
2006-09-30 | 11521.035 | 9386.092 | 1789.232 | 159.352 | 186.359 | 19976 | 16932.17 | 2457.453 | 175.436 | 410.941
2006-10-31 | 11962.307 | 9829.599 | 1745.321 | 150.308 | 237.079 | 19590 | 16650.66 | 2371.199 | 188.448 | 379.693
2006-11-30 | 12178.739 | 10018.7 | 1734.991 | 163.953 | 261.095 | 21267 | 18187.39 | 2295.35 | 204.2 | 580.06
2006-12-31 | 12884.176 | 10733.116 | 1708.01 | 162.411 | 280.639 | 22941 | 19873.93 | 2164.479 | 207.483 | 695.108
2007-01-31 | 13758.097 | 11458.472 | 1823.005 | 161.93 | 314.69 | 23537 | 20372.37 | 2394.209 | 185.55 | 584.871
2007-02-28 | 13037.578 | 11013.358 | 1619.551 | 142.892 | 261.777 | 23935 | 20829.21 | 2384.199 | 165.209 | 556.382
2007-03-31 | 13192.72 | 10931.852 | 1833.514 | 178.988 | 248.366 | 22969 | 19865.96 | 2417.187 | 260.159 | 425.694
2007-04-30 | 11827.647 | 9668.557 | 1776.836 | 165.698 | 216.556 | 20016 | 16660.53 | 2684.113 | 161.312 | 510.045
2007-05-31 | 11818.634 | 9589.524 | 1804.081 | 202.45 | 222.579 | 21490 | 18256.83 | 2306.318 | 236.902 | 689.95
2007-06-30 | 12692.547 | 10502.573 | 1730.187 | 186.088 | 273.699 | 25737 | 22461.02 | 2385.343 | 177.232 | 713.405
2007-07-31 | 12840.811 | 10640.371 | 1719.629 | 188.169 | 292.642 | 24561 | 21500.94 | 2264.306 | 200.085 | 595.669
2007-08-31 | 13454.57 | 11202.657 | 1742.24 | 199.774 | 309.899 | 25584 | 22471.59 | 2135.841 | 233.451 | 743.118
2007-09-30 | 11916.219 | 9815.422 | 1676.489 | 184.25 | 240.058 | 24046 | 20805.99 | 2324.986 | 195.763 | 719.261
2007-10-31 | 11908.105 | 9825.783 | 1715.497 | 148.482 | 218.343 | 19233 | 16516.44 | 2203.376 | 131.916 | 381.268
2007-11-30 | 12350.431 | 10287.772 | 1677.403 | 169.532 | 215.724 | 21814 | 19071.32 | 2102.755 | 159.15 | 480.775
2007-12-31 | 13407.761 | 11284.385 | 1674.218 | 171.179 | 277.979 | 22935 | 19842.07 | 2253.562 | 206.111 | 633.257
2008-01-31 | 13609.986 | 11443.712 | 1728.704 | 166.817 | 270.753 | 22782 | 19743.18 | 2259.941 | 188.114 | 590.765
2008-02-29 | 12896.823 | 10838.401 | 1633.662 | 147.825 | 276.935 | 23054 | 19969.28 | 2349.389 | 165.128 | 570.203
2008-03-31 | 13003.771 | 10838.211 | 1720.417 | 173.083 | 272.06 | 20990 | 17994.66 | 2205.371 | 217.193 | 572.776
2008-04-30 | 11520.396 | 9367.341 | 1699.281 | 151.486 | 302.288 | 19512 | 16522.2 | 2326.748 | 194.598 | 468.454
2008-05-31 | 11407.14 | 9211.31 | 1732.848 | 162.026 | 300.956 | 18650 | 15591.79 | 2431.522 | 170.796 | 455.892
2008-06-30 | 12189.13 | 9970.632 | 1736.46 | 170.098 | 311.94 | 24195 | 21012.33 | 2343.515 | 181.583 | 657.572
2008-07-31 | 13155.66 | 10881.08 | 1770.797 | 177.722 | 326.061 | 23787 | 20810.26 | 2200.689 | 153.239 | 622.812
2008-08-31 | 12548.525 | 10286.646 | 1787.408 | 173.04 | 301.431 | 22707 | 19448.08 | 2289.167 | 231.554 | 738.199
2008-09-30 | 11793.462 | 9611.373 | 1755.254 | 170.494 | 256.341 | 22975 | 20077.14 | 2198.497 | 161.722 | 537.641
2008-10-31 | 11634.137 | 9611.594 | 1645.026 | 164.976 | 212.541 | 19366 | 16642.02 | 2071.701 | 179.135 | 473.144
2008-11-30 | 11828.99 | 9989.561 | 1418.322 | 179.317 | 241.79 | 21279 | 18309.22 | 1826.499 | 227.767 | 915.514
2008-12-31 | 13087.707 | 11170.594 | 1413.875 | 191.224 | 312.014 | 22541 | 19782.98 | 1874.284 | 198.588 | 685.148
2009-01-31 | 13730.291 | 11751.74 | 1506.224 | 184.672 | 287.655 | 22983 | 19479.27 | 1824.502 | 239.3108 | 1439.9172
2009-02-28 | 11697.974 | 10037.791 | 1242.672 | 159.759 | 257.752 | 22110 | 18884.05 | 1763.431 | 255.6966 | 1206.8224
2009-03-31 | 12166.882 | 10357.06 | 1375.926 | 158.075 | 275.821 | 21466 | 16832.38 | 1780.814 | 221.7559 | 2631.0501
2009-04-30 | 10746.635 | 9088.459 | 1224.828 | 201.2 | 232.148 | 18744 | 15030.25 | 1775.23 | 295.5305 | 1642.9895
2009-05-31 | 10504.201 | 8780.168 | 1251.811 | 206.235 | 265.987 | 17560 | 20038.81 | 1886.091 | 227.77 | -4592.671
2009-06-30 | 10884.323 | 9216.895 | 1206.297 | 188.948 | 272.183 | 22540 | 19081.86 | 1829.943 | 141.6956 | 1486.5014
2009-07-31 | 11315.411 | 9620.536 | 1210.339 | 221.321 | 263.215 | 20011 | 22713.48 | 1581.902 | 158.5048 | -4442.8868
2009-08-31 | 12225.812 | 10434.537 | 1301.835 | 211.757 | 277.683 | 24380 | 22057.34 | 1746.493 | 229.3842 | 346.7828
2009-09-30 | 10931.831 | 9277.913 | 1239.615 | 177.855 | 236.448 | 19731 | 21922.34 | 1687.679 | 239.7521 | -4118.7711
2009-10-31 | 11181.875 | 9508.079 | 1259.913 | 179.112 | 234.771 | 18420 | 15363.31 | 1932.541 | 233.1459 | 891.0031
2009-11-30 | 11112.909 | 9475.052 | 1262.265 | 173.551 | 202.041 | 19710 | 17340.45 | 1920.156 | 233.9333 | 215.4607
2009-12-31 | 12688.573 | 10946.598 | 1225.323 | 204.103 | 312.549 | 21831 | 19729.84 | 1749.27 | 252.1934 | 99.6966
2010-01-31 | 13145.438 | 11330.024 | 1308.6 | 224.973 | 281.841 | 22045 | 19479.27 | 1824.502 | 239.3108 | 501.9172
2010-02-28 | 11751.752 | 10068.441 | 1247.677 | 172.272 | 263.362 | 21367 | 18884.05 | 1763.431 | 255.6966 | 463.8224
2010-03-31 | 11686.054 | 9927.551 | 1346.685 | 178.911 | 232.907 | 19393 | 16832.38 | 1780.814 | 221.7559 | 558.0501
2010-04-30 | 10474.752 | 8748.214 | 1305.947 | 201.493 | 219.098 | 17398 | 15030.25 | 1775.23 | 295.5305 | 296.9895
2010-05-31 | 11368.031 | 9536.118 | 1350.434 | 184.847 | 296.632 | 22904 | 20038.81 | 1886.091 | 227.77 | 751.329
2010-06-30 | 11555.961 | 9797.61 | 1334.971 | 175.296 | 248.084 | 21527 | 19081.86 | 1829.943 | 141.6956 | 473.5014
2010-07-31 | 13307.242 | 11457.602 | 1358.685 | 196.219 | 294.736 | 25075 | 22713.48 | 1581.902 | 158.5048 | 621.1132
2010-08-31 | 12921.565 | 11046.524 | 1379.923 | 227.005 | 268.113 | 24917 | 22057.34 | 1746.493 | 229.3842 | 883.7828
2010-09-30 | 11049.081 | 9272.091 | 1363.8 | 223.294 | 189.896 | 24444 | 21922.34 | 1687.679 | 239.7521 | 594.2289
2010-10-31 | 10929.335 | 9166.553 | 1415.512 | 194.924 | 152.346 | 17704 | 15363.31 | 1932.541 | 233.1459 | 175.0031
2010-11-30 | 11303.778 | 9631.649 | 1343.104 | 197.012 | 132.013 | 19970 | 17340.45 | 1920.156 | 233.9333 | 475.4607
2010-12-31 | 12694.155 | 10967.855 | 1333.472 | 213.793 | 179.035 | 22114 | 19729.84 | 1749.27 | 252.1934 | 382.6966
2011-01-31 | 13301.687 | 11430.562 | 1397.349 | 228.348 | 245.428 | 22733 | 19938.47 | 1797.701 | 258.0538 | 738.7752
2011-02-28 | 11775.464 | 10128.289 | 1258.023 | 199.187 | 189.965 | 21871 | 19081.88 | 1931.922 | 277.2781 | 579.9199
2011-03-31 | 12352.443 | 10487.541 | 1406.471 | 201.955 | 256.476 | 20667 | 17995.89 | 1925.285 | 237.1581 | 508.6669
2011-04-30 | 10789.012 | 9101.443 | 1313.581 | 194.8 | 179.188 | 17945 | 15411.63 | 1836.07 | 292.9127 | 404.3873
2011-05-31 | 10781.74 | 9046.905 | 1316.588 | 204.821 | 213.426 | 20847 | 18580.71 | 1504.528 | 253.6881 | 508.0739
2011-06-30 | 11238.277 | 9544.739 | 1219.471 | 194.518 | 279.549 | 22765 | 20342.47 | 1415.288 | 252.5383 | 754.7037
2011-07-31 | 13298.189 | 11448.888 | 1312.715 | 207.837 | 328.749 | 25450 | 23322.88 | 1198.084 | 203.9427 | 725.0933
2011-08-31 | 12531.706 | 10718.286 | 1371.117 | 191.542 | 250.761 | 22051 | 19562.88 | 1720.727 | 249.3743 | 518.0187
2011-09-30 | 11144.546 | 9376.834 | 1367.366 | 174.416 | 225.93 | 21552 | 19043.84 | 1747.319 | 185.7929 | 575.0481
2011-10-31 | 11012.737 | 9287.2 | 1366.261 | 151.445 | 207.831 | 18234 | 15871.5 | 1827.09 | 177.9033 | 357.5067
2011-11-30 | 11116.536 | 9428.401 | 1307.621 | 148.173 | 232.341 | 19673 | 17154.6 | 1837.406 | 218.8018 | 462.1922
2011-12-31 | 12121.895 | 10412.869 | 1295.596 | 184.83 | 228.6 | 20204 | 17925.51 | 1726.402 | 223.1266 | 328.9614
2012-01-31 | 12715.234 | 10948.174 | 1362.721 | 185.799 | 218.54 | 21847 | 19150.62 | 1791.478 | 308.8587 | 596.0433
2012-02-29 | 11610.18 | 9922.71 | 1283.368 | 163.061 | 241.041 | 19956 | 17273.85 | 1856.136 | 237.3638 | 588.6502
2012-03-31 | 11487.527 | 9660.31 | 1405.691 | 196.881 | 224.645 | 20332 | 17720.09 | 1987.229 | 260.8596 | 363.8214
2012-04-30 | 10641.371 | 8873.913 | 1365.573 | 191.349 | 210.536 | 17874 | 15231.22 | 1915.3 | 237.3826 | 490.0974
2012-05-31 | 11136.995 | 9304.02 | 1413.625 | 203.936 | 215.414 | 21106 | 18637.39 | 1687.272 | 242.2982 | 539.0398
2012-06-30 | 11800.326 | 10038.614 | 1338.673 | 178.791 | 244.248 | 24107 | 21813.12 | 1275.996 | 181.9566 | 835.9274
2012-07-31 | 13456.845 | 11552.619 | 1422.06 | 191.485 | 290.681 | 24636 | 22490.51 | 1276.191 | 198.1912 | 671.1078
2012-08-31 | 12632.817 | 10729.711 | 1428.622 | 212.649 | 261.835 | 23188 | 20435.58 | 1870.187 | 259.9366 | 622.2964
2012-09-30 | 11040.767 | 9271.502 | 1330.396 | 211.341 | 227.528 | 21183 | 18728.86 | 1751.122 | 241.4408 | 461.5772
2012-10-31 | 11141.991 | 9297.822 | 1426.415 | 176.549 | 241.205 | 18829 | 16008.33 | 2069.298 | 235.9358 | 515.4362
2012-11-30 | 11487.169 | 9711.027 | 1408.816 | 158.8 | 208.526 | 20144 | 17569.58 | 1922.144 | 212.0993 | 440.1767
2012-12-29 | 12156.557 | 10354.012 | 1377.79 | 173.831 | 250.924 | 20382 | 18041.85 | 1839.009 | 197.6117 | 303.5293
2013-01-31 | 12889.507 | 11003.972 | 1469.787 | 173.53 | 242.218 | 22610 | 19640.28 | 2147.084 | 197.0555 | 625.5805
2013-02-28 | 11742.246 | 9983.339 | 1377.594 | 153.907 | 227.406 | 21426 | 18759.8 | 2044.78 | 262.5673 | 358.8527
2013-03-31 | 11958.319 | 10134.187 | 1438.761 | 184.656 | 200.715 | 19825 | 17448.6 | 1936.126 | 222.6267 | 217.6473
2013-04-30 | 10944.906 | 9160.548 | 1366.503 | 212.478 | 205.377 | 18854 | 16176.39 | 2065.198 | 293.6076 | 318.8044
2013-05-31 | 10785.424 | 8990.721 | 1394.035 | 183.639 | 217.029 | 20488 | 18010.02 | 1884.409 | 199.7068 | 393.8642
2013-06-30 | 11174.679 | 9355.295 | 1365.081 | 163.498 | 290.805 | 22662 | 20486.94 | 1445.578 | 196.7334 | 532.7486
2013-07-31 | 12722.707 | 10867.174 | 1383.961 | 174.841 | 296.731 | 24927 | 22682.78 | 1267.167 | 241.1029 | 735.9501
2013-08-31 | 12100.351 | 10221.728 | 1420.874 | 179.937 | 277.812 | 22833 | 20219.6 | 1889.837 | 209.7228 | 513.8402
2013-09-30 | 10837.167 | 9076.722 | 1392.777 | 156.459 | 211.209 | 22682 | 20068.89 | 1821.304 | 205.8435 | 585.9625
2013-10-31 | 11135.689 | 9198.19 | 1502.292 | 176.758 | 258.449 | 18445 | 15816.3 | 2025.741 | 254.2856 | 348.6734
2013-11-30 | 11640.948 | 9790.636 | 1461.583 | 148.408 | 240.321 | 20615 | 18030.36 | 1922.273 | 267.9082 | 394.4588
2013-12-31 | 12702.006 | 10912.622 | 1447.614 | 188.083 | 153.687 | 21964 | 19570.07 | 2142.251 | 274.6158 | -22.9368
2014-01-31 | 13613.596 | 11658.477 | 1476.947 | 190.578 | 287.594 | 22774 | 20229.64 | 1760.07 | 276.9846 | 507.3054
2014-02-28 | 12067.276 | 10225.218 | 1395.693 | 206.555 | 239.81 | 21905 | 18798.24 | 2082.484 | 434.6011 | 589.6749
2014-03-31 | 12672.074 | 10666.474 | 1546.683 | 198.863 | 260.054 | 21656 | 18943.11 | 1956.483 | 351.4494 | 404.9576
2014-04-30 | 10836.804 | 8962.645 | 1460.568 | 212.109 | 201.482 | 18557 | 15838.52 | 2088.889 | 359.4376 | 270.1534
2014-05-31 | 10642.583 | 8790.577 | 1448.055 | 189.754 | 214.197 | 18844 | 16340.76 | 1952.935 | 239.5254 | 310.7796
2014-06-30 | 11228.548 | 9412.544 | 1454.421 | 166.33 | 195.253 | 20807 | 18622.91 | 1656.722 | 247.2939 | 280.0741
2014-07-31 | 11717.444 | 9845.802 | 1478.577 | 165.739 | 227.326 | 21300 | 19331.84 | 1234.529 | 223.8554 | 509.7756
2014-08-31 | 11718.183 | 9805.466 | 1488.258 | 173.903 | 250.556 | 21363 | 19501.8 | 1280.928 | 252.222 | 328.05
2014-09-30 | 10836.546 | 9080.103 | 1437.045 | 139.093 | 180.305 | 21123 | 19361.88 | 1344.12 | 216.4065 | 200.5935
2014-10-31 | 10819.853 | 9041.876 | 1446.698 | 151.093 | 180.186 | 17784 | 15264.16 | 1959.928 | 218.3104 | 341.6016
2014-11-30 | 11487.634 | 9707.192 | 1437.231 | 142.519 | 200.692 | 20102 | 17733.74 | 1806.566 | 246.3103 | 315.3837
2014-12-31 | 12131.525 | 10359.109 | 1425.828 | 154.903 | 191.685 | 20938 | 18328.41 | 1917.17 | 241.7382 | 450.6818
2015-01-31 | 13119.979 | 11250.337 | 1432.84 | 164.562 | 272.24 | 21814 | 19647.04 | 1319.941 | 240.0045 | 607.0145
2015-02-28 | 12302.278 | 10600.396 | 1335.858 | 142.772 | 223.252 | 21494 | 19379.05 | 1447.463 | 235.947 | 431.54
2015-03-31 | 12044.976 | 10212.786 | 1453.153 | 161.032 | 218.005 | 20827 | 18298.38 | 1955.219 | 289.3311 | 284.0699
2015-04-30 | 10404.962 | 8679.37 | 1405.231 | 151.615 | 168.746 | 18462 | 15708.66 | 1925.434 | 271.1328 | 556.7732
2015-05-31 | 10547.132 | 8798.507 | 1412.842 | 170.524 | 165.259 | 19158 | 16907.98 | 1888.851 | 228.6186 | 132.5504
2015-06-30 | 10624.316 | 8942.283 | 1351.048 | 148.015 | 182.97 | 19339 | 16892.13 | 1861.715 | 253.0514 | 332.1036
2015-07-31 | 12105.066 | 10312.467 | 1395.071 | 169.088 | 228.44 | 22516 | 20656.56 | 1189.704 | 228.4097 | 441.3263
2015-08-31 | 11797.099 | 9965.934 | 1418.277 | 166.564 | 246.324 | 22383 | 20498.96 | 1201.994 | 203.3686 | 478.6774
2015-09-30 | 11361.901 | 9625.828 | 1369.332 | 184.574 | 182.167 | 22063 | 19973.68 | 1257.934 | 211.4512 | 619.9348
2015-10-31 | 10687.264 | 8878.974 | 1453.202 | 194.589 | 160.499 | 17667 | 15013.54 | 1992.14 | 298.4092 | 362.9108
2015-11-30 | 10681.592 | 8963.684 | 1381.098 | 147.434 | 189.376 | 19239 | 16530.39 | 1927.785 | 302.168 | 478.657
2015-12-31 | 11313.857 | 9546.732 | 1393.262 | 167.618 | 206.245 | 19161 | 16555.58 | 1828.622 | 286.6657 | 490.1323
2016-01-31 | 12384.867 | 10508.333 | 1440.227 | 155.238 | 281.069 | 20836 | 18202.71 | 1838.962 | 317.9757 | 476.3523
2016-02-29 | 11471.763 | 9726.471 | 1372.476 | 150.337 | 222.479 | 20766 | 18094.22 | 1993.201 | 286.9147 | 391.6643
2016-03-31 | 11302.963 | 9496.261 | 1451.793 | 148.34 | 206.569 | 20063 | 17468.06 | 1861.963 | 293.4842 | 439.4928
2016-04-30 | 10409.92 | 8680.447 | 1436.773 | 153.646 | 139.054 | 17821 | 15610.16 | 1907.108 | 284.1523 | 19.5797
2016-05-31 | 10470.808 | 8757.947 | 1400.24 | 152.605 | 160.016 | 19885 | 17239.79 | 1934.375 | 353.4562 | 357.3788
2016-06-30 | 11101.521 | 9374.678 | 1386.493 | 146.615 | 193.735 | 21692 | 19702.23 | 1369.924 | 204.5618 | 415.2842
2016-07-31 | 12497.616 | 10733.656 | 1374.658 | 138.773 | 250.529 | 22659 | 20955.64 | 1104.207 | 161.3168 | 437.8362
2016-08-31 | 13113.359 | 11248.853 | 1404.99 | 164.839 | 294.677 | 23100 | 21332.92 | 1122.548 | 195.706 | 448.826
2016-09-30 | 11072.26 | 9296.858 | 1377.715 | 140.375 | 257.312 | 23213 | 21260.85 | 1152.819 | 142.8112 | 656.5198
2016-10-31 | 10518.677 | 8755.244 | 1410.365 | 158.328 | 194.74 | 18189 | 15451.67 | 1927.67 | 270.9776 | 538.6824
2016-11-30 | 10697.637 | 8920.356 | 1404.427 | 165.552 | 207.302 | 19369 | 16599.65 | 2002.135 | 266.5365 | 500.6785
2016-12-31 | 11978.041 | 10093.776 | 1403.94 | 191.718 | 288.607 | 20688 | 18146.04 | 1877.911 | 358.1404 | 305.9086
2017-01-31 | 12108.005 | 10235.721 | 1426.113 | 167.231 | 278.94 | 20372 | 17605.02 | 1903.952 | 284.0204 | 579.0076
2017-02-28 | 10607.563 | 8932.522 | 1327.331 | 157.939 | 189.771 | 19838 | 16763.11 | 2026.818 | 334.4528 | 713.6192
2017-03-31 | 11591.031 | 9770.579 | 1477.122 | 159.279 | 184.051 | 19174 | 16538.62 | 2020.879 | 270.5038 | 343.9972
2017-04-30 | 9788.616 | 8175.766 | 1362.45 | 157.307 | 93.093 | 17349 | 14585.55 | 2041.365 | 287.8311 | 434.2539
2017-05-31 | 10153.182 | 8442.449 | 1391.732 | 178.48 | 140.521 | 17738 | 15261.02 | 1979.705 | 284.9445 | 212.3305
2017-06-30 | 10657.08 | 8977.237 | 1340.846 | 158.409 | 180.588 | 21168 | 18975.18 | 1556.569 | 230.3528 | 405.8982
2017-07-31 | 11587.63 | 9826.461 | 1377.59 | 151.2 | 232.379 | 20627 | 18563.72 | 1412.149 | 207.7732 | 443.3578
2017-08-31 | 11350.012 | 9622.113 | 1359.22 | 157.201 | 211.478 | 20158 | 18606.52 | 1077.556 | 200.8482 | 273.0758
2017-09-30 | 10679.393 | 9122.15 | 1230.396 | 145.584 | 181.263 | 21786 | 20018.32 | 1007.671 | 215.3174 | 544.6916
2017-10-31 | 10339.329 | 8601.176 | 1426.975 | 139.553 | 171.625 | 17418 | 15048.39 | 1943.664 | 223.0329 | 202.9131
2017-11-30 | 10955.909 | 9213.777 | 1408.105 | 157.772 | 176.255 | 19115 | 16384.24 | 2051.185 | 276.3474 | 403.2276
2017-12-31 | 12338.893 | 10436.662 | 1408.63 | 196.667 | 296.934 | 20306 | 17882.19 | 1752.098 | 348.8256 | 322.8864
2018-01-31 | 12700.826 | 10882.596 | 1418.086 | 184.612 | 215.532 | 20906 | 18729.15 | 1274.496 | 374.7405 | 527.6135
2018-02-28 | 10951.065 | 9286.31 | 1323.263 | 160.19 | 181.302 | 20076 | 17391.54 | 1864.722 | 311.1241 | 508.6139
2018-03-31 | 11372.42 | 9566.427 | 1481.01 | 151.405 | 173.578 | 18462 | 15935.17 | 1911.541 | 271.1181 | 344.1709
2018-04-30 | 10578.368 | 8906.101 | 1368.878 | 139.08 | 164.309 | 18011 | 15475.92 | 1864.188 | 260.0555 | 410.8365
2018-05-31 | 10421.469 | 8725.155 | 1401.01 | 144.713 | 150.591 | 20473 | 18194.47 | 1599.295 | 211.7844 | 467.4506
2018-06-30 | 10923.446 | 9205.996 | 1373.762 | 146.9 | 196.788 | 21369 | 19090.62 | 1289.531 | 204.4922 | 784.3568
2018-07-31 | 12685.981 | 10951.054 | 1361.765 | 156.277 | 216.885 | 22909 | 21057.29 | 1149.358 | 275.492 | 426.86
2018-08-31 | 12688.795 | 10901.079 | 1390.079 | 149.133 | 248.504 | 21990 | 20345.65 | 1147.967 | 182.3349 | 314.0481
2018-09-30 | 11147.31 | 9441.469 | 1367.583 | 123.823 | 214.435 | 23240 | 21307.89 | 1121.28 | 169.2054 | 641.6246
2018-10-31 | 10717.348 | 9029.399 | 1440.57 | 138.254 | 109.125 | 18205 | 16055.12 | 1996.924 | 203.89 | -50.934
2018-11-30 | 11360.321 | 9612.505 | 1412.934 | 141.553 | 193.329 | 20152 | 17440.76 | 1925.193 | 292.2894 | 493.7576
2018-12-31 | 11938.614 | 10066.572 | 1439.964 | 165.292 | 266.786 | 19891 | 17186.14 | 1853.428 | 293.5 | 557.932
2019-01-31 | 12777.216 | 10984.339 | 1424.631 | 157.579 | 210.667 | 21525 | 18834.82 | 1824.973 | 233.4161 | 631.7909
2019-02-28 | 11291.744 | 9679.029 | 1303.065 | 132.852 | 176.798 | 20500 | 17986.65 | 1882.421 | 243.2612 | 387.6678
2019-03-31 | 11658.678 | 9872.263 | 1444.563 | 151.489 | 190.363 | 20263 | 17522.65 | 2049.826 | 239.7963 | 450.7277
2019-04-30 | 10264.505 | 8608.974 | 1338.349 | 170.596 | 146.586 | 17645 | 14956.61 | 2012.241 | 273.7595 | 402.3895
2019-05-31 | 10219.56 | 8467.021 | 1405.277 | 177.012 | 170.25 | 16784 | 14068.65 | 1848.762 | 312.4022 | 554.1858
2019-06-30 | 10365.619 | 8681.844 | 1388.098 | 145.5 | 150.177 | 20248 | 18015.36 | 1545.989 | 210.2323 | 476.4187
2019-07-31 | 12792.766 | 11052.777 | 1356.389 | 147.863 | 235.737 | 21791 | 20077.9 | 1055.989 | 181.1607 | 475.9503
2019-08-31 | 11825.052 | 10103.635 | 1379.382 | 141.201 | 200.834 | 21354 | 19286.97 | 1418.286 | 163.5032 | 485.2408
2019-09-30 | 10318.533 | 8735.445 | 1286.871 | 129.154 | 167.063 | 19717 | 17232.99 | 1865.817 | 179.2536 | 438.9394
2019-10-31 | 10351.05 | 8695.342 | 1377.19 | 133.423 | 145.095 | 18329 | 15858.72 | 1799.031 | 169.3067 | 501.9423
2019-11-30 | 11255.325 | 9566.229 | 1344.964 | 144.138 | 199.994 | 19625 | 17204.45 | 1869.312 | 264.8378 | 286.4002
2019-12-31 | 11997.095 | 10167.965 | 1390.827 | 185.248 | 253.055 | 20974 | 18132.44 | 1886.516 | 329.041 | 626.003
2020-01-31 | 12178.575 | 10383.457 | 1421.435 | 154.804 | 218.879 | 19928 | 17248.55 | 2038.156 | 255.5653 | 385.7287
2020-02-29 | 11239.82 | 9622.815 | 1333.64 | 130.239 | 153.126 | 19630 | 17209.54 | 1932.968 | 256.8344 | 230.6576
2020-03-31 | 10989.389 | 9283.197 | 1393.918 | 146.703 | 165.571 | 18183 | 15475.37 | 1969.849 | 270.2771 | 467.5039
2020-04-30 | 9282.854 | 7848.11 | 1153.337 | 156.852 | 124.555 | 15350 | 13280.69 | 1582.584 | 267.4529 | 219.2731
2020-05-31 | 9642.117 | 8168.463 | 1164.589 | 179.62 | 129.445 | 20649 | 18503.86 | 1386.916 | 269.737 | 488.487
2020-06-30 | 10800.015 | 9266.452 | 1204.421 | 158.555 | 170.587 | 21292 | 19034.88 | 1670.309 | 214.578 | 372.233
2020-07-31 | 13202.706 | 11611.332 | 1217.734 | 133.797 | 239.843 | 24446 | 22412.78 | 1343.705 | 211.87 | 477.645
2020-08-31 | 12081.08 | 10404.924 | 1293.469 | 146.854 | 235.833 | 23823 | 21283.78 | 1752.135 | 160.3762 | 626.7088
2020-09-30 | 10114.374 | 8539.376 | 1272.232 | 155.933 | 146.833 | 20225 | 17908.17 | 1726.147 | 208.4155 | 382.2675
2020-10-31 | 10339.39 | 8709.182 | 1346.746 | 136.399 | 147.063 | 17679 | 15258.76 | 1701.44 | 205.3914 | 513.4086
2020-11-30 | 10529.032 | 8952.778 | 1298.175 | 117.956 | 160.123 | 19147 | 16766.96 | 1779.029 | 198.332 | 402.679
2020-12-31 | 11811.675 | 10133.006 | 1324.33 | 159.628 | 194.711 | 20738 | 18149.66 | 1713.527 | 257.8595 | 616.9535
2021-01-31 | 12105.158 | 10361.393 | 1380.422 | 146.481 | 216.862 | 20150 | 17617.05 | 1904.916 | 201.7136 | 426.3204
2021-02-28 | 11233.123 | 9628.043 | 1286.376 | 128.04 | 190.664 | 20318 | 17713.35 | 1954.603 | 223.5765 | 426.4705
2021-03-31 | 11101.706 | 9383.05 | 1403.012 | 168.316 | 147.328 | 19344 | 16809.63 | 2016.47 | 209.1617 | 308.7383
2021-04-30 | 9781.57 | 8232.163 | 1334.867 | 145.429 | 69.111 | 16644 | 14263.1 | 1961.507 | 260.3496 | 159.0434
2021-05-31 | 10086.333 | 8498.898 | 1381.951 | 153.836 | 51.648 | 19443 | 17017.05 | 1789.111 | 185.9648 | 450.8742
2021-06-30 | 11262.474 | 9735.938 | 1259.332 | 132.576 | 134.628 | 22258 | 20483.21 | 1053.779 | 173.4785 | 547.5325
2021-07-31 | 11636.443 | 10067.983 | 1281.389 | 140.02 | 147.051 | 21655 | 20129.06 | 1024.867 | 174.991 | 326.082
2021-08-31 | 12856.511 | 11257.223 | 1276.353 | 145.534 | 177.401 | 22986 | 21152.87 | 1128.732 | 185.5447 | 518.8533
2021-09-30 | 10389.017 | 8816.858 | 1282.526 | 133.464 | 156.169 | 18769 | 16537.54 | 1688.898 | 169.64 | 372.922
2021-10-31 | 10516.14 | 8812.988 | 1349.298 | 146.187 | 207.667 | 17312 | 14836.55 | 1808.165 | 181.1434 | 486.1416
2021-11-30 | 10956.602 | 9289.843 | 1330.551 | 131.91 | 204.298 | 19644 | 17057.11 | 1886.821 | 179.7903 | 520.2787
2021-12-31 | 11969.602 | 10162.622 | 1393.558 | 150.401 | 263.021 | 20455 | 17758.36 | 1898.71 | 182.8977 | 615.0323
2022-01-31 | 13085.388 | 11309.713 | 1429.374 | 141.901 | 204.4 | 21349 | 18872.96 | 1818.319 | 192.0121 | 465.7089
2022-02-28 | 11487.734 | 9868.554 | 1279.543 | 139.57 | 200.067 | 20918 | 18284.47 | 1830.206 | 189.9149 | 613.4091
2022-03-31 | 11816.835 | 10021.983 | 1420.351 | 166.958 | 207.543 | 19763 | 17226.22 | 1876.425 | 246.9115 | 413.4435
2022-04-30 | 10265.047 | 8643.765 | 1301.591 | 139.261 | 180.43 | 17256 | 14635.63 | 1914.953 | 182.8324 | 522.5846
2022-05-31 | 10469.914 | 8743.427 | 1411.702 | 163.924 | 150.861 | 21292 | 19075.72 | 1585.076 | 182.1273 | 449.0767
2022-06-30 | 10929.858 | 9321.502 | 1299.146 | 148.831 | 160.379 | 21954 | 20047.8 | 1088.784 | 246.9046 | 570.5114
2022-07-31 | 12343.623 | 10601.099 | 1341.868 | 144.639 | 256.017 | 22607 | 21008.88 | 1021.468 | 156.3699 | 420.2821
2022-08-31 | 12624.254 | 10830.757 | 1351.532 | 144.462 | 297.503 | 21871 | 19879.56 | 1139.376 | 178.3511 | 673.7129
2022-09-30 | 10814.096 | 9116.212 | 1329.888 | 135.217 | 232.779 | 20350 | 17812.02 | 1857.612 | 220.7457 | 459.6223
2022-10-31 | 10384.167 | 8716.711 | 1336.906 | 114.553 | 215.997 | 17294 | 14671.49 | 1804.303 | 147.6571 | 670.5499
2022-11-30 | 11044.181 | 9332.357 | 1358.357 | 150.022 | 203.445 | 19441 | 16685.5 | 1963.331 | 221.7309 | 570.4381
2022-12-31 | 12273.23 | 10425.209 | 1423.836 | 177.746 | 246.439 | 20173 | 17611.79 | 1854.189 | 279.0826 | 427.9384
2023-01-31 | 12519.712 | 10663.9284 | 1442.7604 | 147.6643 | 265.3589 | 20486 | 17788.22 | 1880.245 | 189.9117 | 627.6233
2023-02-28 | 11225.17 | 9600.1488 | 1293.0651 | 135.588 | 196.3681 | 21388 | 18906.97 | 1669.987 | 182.8198 | 628.2232
2023-03-31 | 11846.269 | 10020.4543 | 1460.0804 | 185.4365 | 180.2977 | 18811 | 16110.98 | 1876.802 | 245.219 | 577.999
2023-04-30 | 10271.638 | 8627.354 | 1342.3702 | 129.821 | 172.0928 | 17547 | 14996.01 | 1623.887 | 195.8285 | 731.2745
2023-05-31 | 10356.75 | 8683.1386 | 1389.07 | 150.1265 | 134.4149 | 20787 | 18609.24 | 1622.633 | 190.6279 | 364.4991
2023-06-30 | 11119.814 | 9405.7355 | 1361.0294 | 177.7235 | 175.3256 | 21463 | 19512.09 | 1275.405 | 235.6532 | 439.8518
2023-07-31 | 12507.785 | 10774.2868 | 1327.9647 | 198.4082 | 207.1253 | 22686 | 20840.57 | 904.1759 | 297.5355 | 643.7186
2023-08-31 | 11828.62 | 10023.4866 | 1395.9442 | 179.0739 | 230.1152 | 21364 | 19051.29 | 1542.652 | 220.7961 | 549.2619
2023-09-30 | 10997.556 | 9302.3516 | 1313.7649 | 153.072 | 228.3675 | 23713 | 21787.11 | 917.0429 | 198.5693 | 810.2778
2023-10-31 | 10932.34 | 9206.3755 | 1385.768 | 125.7878 | 214.4087 | 20849 | 18263.33 | 1804.525 | 147.9438 | 633.2012
2023-11-30 | 11456.562 | 9679.0271 | 1398.5566 | 132.3457 | 246.6327 | 20579 | 17750.2 | 1866.194 | 194.518 | 768.088
2023-12-31 | 12065.5 | 10241.9514 | 1447.2337 | 146.7123 | 229.6026 | 20004 | 17492.49 | 1921.522 | 198.1631 | 391.8249
2024-01-31 | 13036.084 | 11101.9147 | 1422.9814 | 144.7408 | 366.4471 | 21081 | 18633 | 1745 | 183 | 520
2024-02-29 | 11516.766 | 9706.5825 | 1363.2675 | 141.9094 | 305.0065 | 19624 | 17059 | 1856 | 158 | 551
2024-03-31 | 11542.29 | 9662.1438 | 1438.1805 | 143.1947 | 298.7711 | 18902 | 16343 | 1919 | 176 | 464
2024-04-30 | 10489.417 | 8729.9908 | 1352.5453 | 150.6011 | 256.2799 | 17947 | 15250 | 1833 | 219 | 645
2024-05-31 | 10735.152 | 8909.3306 | 1386.8118 | 153.3365 | 285.6731 | 20402 | 17955 | 1893 | 137 | 417
2024-06-30 | 11566.905 | 9793.673 | 1359.5387 | 146.7093 | 266.984 | 23803 | 21929 | 1044 | 137 | 693
2024-07-31 | 13072.592 | 11226.7543 | 1335.3985 | 156.2716 | 354.1676 | 23206 | 21321 | 1003 | 155 | 727
2024-08-31 | 12666.051 | 10757.7104 | 1389.3925 | 161.2831 | 357.6651 | 23110 | 21255 | 995 | 149 | 711
2024-09-30 | 11321.751 | 9503.6166 | 1328.4107 | 153.2011 | 336.5227 | 21643 | 18979 | 1901 | 147 | 616
2024-10-31 | 10992.867 | 9093.9808 | 1422.713 | 180.5173 | 295.6559 | 18117 | 15554 | 1936 | 161 | 466
2024-11-30 | 11312.89 | 9431.1455 | 1419.4526 | 169.3741 | 292.9179 | 19212 | 16505 | 1973 | 175 | 559
2024-12-31 | 12959.601 | 10870.5701 | 1482.7244 | 147.4629 | 458.8435 | 21016 | 18161 | 1987 | 146 | 722
2025-01-31 | 13668.714 | 11640.674 | 1492.7451 | 125.8563 | 409.4386 | 22058 | 19455.51 | 1697.669 | 126.296 | 778.525
2025-02-28 | 12278.547 | 10423.565 | 1347.7547 | 150.2559 | 356.9713 | 21399 | 18634.07 | 1887.744 | 218.4029 | 658.7831
2025-03-31 | 12057.659 | 10104.3239 | 1508.986 | 134.0913 | 310.2578 | 20232 | 17493 | 1979.753 | 136.018 | 623.229
2025-04-30 | 10837.309 | 8985.7009 | 1425.0625 | 120.9368 | 305.6088 | 19271 | 16501.89 | 1894.611 | 135.812 | 738.687
2025-05-31 | 10784.244 | 8828.1414 | 1519.7494 | 135.5994 | 300.7538 | 18190 | 15481.69 | 2102.413 | 146.2299 | 459.6671
2025-06-30 | 11845.624 | 10083.8169 | 1324.7326 | 141.1828 | 295.8917 | 24775 | 22897.3 | 1081.067 | 115.504 | 681.129
2025-07-31 | 13905.926 | 12037.1718 | 1324.2562 | 155.3669 | 389.131 | 24399 | 22476.48 | 1128.796 | 108.979 | 684.745
2025-08-31 | 12930.485 | 10968.0995 | 1432.9397 | 151.2097 | 378.2361 | 24500 | 22472.56 | 1115.856 | 113.448 | 798.136
2025-09-30 | 11276.887 | 9403.587 | 1395.6112 | 153.5059 | 324.1829 | 19991 | 17458.95 | 1835.465 | 136.7609 | 559.8241
2025-10-31 | 11319.417 | 9397.4939 | 1447.8928 | 142.6134 | 331.4169 | 20310 | 17632.92 | 2070.743 | 105.693 | 500.644
2025-11-30 | 12026.73 | 10055.8108 | 1426.7021 | 175.429 | 368.7881 | 19827 | 17341.62 | 1844.312 | 166.851 | 474.217
2025-12-31 | 13676.513 | 11575.4106 | 1419.8716 | 185.5533 | 495.6775 | 21541 | 18858.91 | 1805.179 | 174.4509 | 702.4601
2026-01-31 | 14011.786 | 11974.7559 | 1447.7435 | 166.4039 | 422.8827 | 22064 | 19398.7 | 1870.507 | 171.153 | 623.64
2026-02-28 | 12373.547 | 10534.3995 | 1293.393 | 188.1049 | 357.6496 | 21821 | 19119.72 | 1918.321 | 160.136 | 622.823
2026-03-31 | 12605.428 | 10619.5205 | 1501.3256 | 192.3092 | 292.2727 | 20333 | 17633.66 | 1999.047 | 177.854 | 522.439
2026-04-30 | 11092.866 | 9246.822 | 1403.5303 | 191.6989 | 250.8149 | 18502 | 16088.62 | 1852.766 | 161.258 | 399.356
2026-05-31 | 11136.637 | 9218.687 | 1431.0683 | 230.8475 | 256.0342 | 20990 | 18439.6 | 1901.544 | 245.3971 | 403.4589
Back to main menu

## Table 1.4.4
Back to main menu
Table 1.4.4: Economic Assumptions
Year | Ontario Employment |  | Ontario Housing Starts |  | Ontario Growth Index
| Thousands | Annual Growth (%) | Thousands | Annual Growth (%) | Index | Annual Growth (%)
2011 | 6647.6 |  | 67.801 |  | 1.0465
2012 | 6685.4083 | 0.56875 | 77.387 | 14.1384 | 1.0572 | 1.0192
2013 | 6790.8917 | 1.5778 | 61.076 | -21.0772 | 1.0715 | 1.3499
2014 | 6823.4 | 0.4787 | 58.587 | -4.0753 | 1.0797 | 0.76876
2015 | 6862.7417 | 0.57657 | 68.997 | 17.7684 | 1.0896 | 0.91341
2016 | 6934.525 | 1.046 | 74.748 | 8.3351 | 1.1026 | 1.1958
2017 | 7109.1917 | 2.5188 | 79.876 | 6.8604 | 1.1243 | 1.9702
2018 | 7240.425 | 1.846 | 79.076 | -1.0016 | 1.1425 | 1.6168
2019 | 7412.8583 | 2.3815 | 68.99 | -12.7548 | 1.1628 | 1.7793
2020 | 7043.45 | -4.9833 | 81.237 | 17.7518 | 1.1413 | -1.8483
2021 | 7404.8167 | 5.1305 | 100.425 | 23.6198 | 1.1802 | 3.4097
2022 | 7764.1 | 4.852 | 95.957 | -4.4491 | 1.2182 | 3.2167
2023 | 8006.1333 | 3.1173 | 89.726 | -6.4935 | 1.2461 | 2.2907
2024 | 8146.1417 | 1.7488 | 74.5 | -16.9694 | 1.2644 | 1.4665
2025 | 8226.9583 | 0.99209 | 65.281 | -12.3745 | 1.2771 | 1.0024
2026 (f) | 8239.984 | 0.15833 | 64.781 | -0.76592 | 1.285 | 0.62482
2027 (f) | 8292.314 | 0.63507 | 66.828 | 3.1599 | 1.2963 | 0.87517
Back to main menu

## Table 1.4.5
Back to main menu
Table 1.4.5: Estimate of Contracted Embedded Generation Capacity (MW)
| Biogas | Cogeneration | Solar | Hydro | Wind | Total
2007-01-01 | 0 | 0 | 0 | 129.3052 | 0 | 129.3052
2007-02-01 | 0 | 0 | 0 | 130.66 | 0 | 130.66
2007-03-01 | 0.90726 | 0 | 0 | 130.66 | 0 | 131.5673
2007-04-01 | 5.625 | 0 | 0 | 130.66 | 0.34201 | 136.627
2007-05-01 | 9.0176 | 0 | 0 | 132.86 | 5.3585 | 147.236
2007-06-01 | 12.91 | 0 | 0 | 133.76 | 6.5101 | 153.1801
2007-07-01 | 12.91 | 0 | 0 | 133.869 | 6.5101 | 153.2891
2007-08-01 | 12.91 | 0 | 0.031813 | 134.061 | 6.5101 | 153.5129
2007-09-01 | 13.054 | 0 | 0.051979 | 134.19 | 6.5101 | 153.8061
2007-10-01 | 14.69 | 0 | 0.053184 | 134.19 | 6.631 | 155.5642
2007-11-01 | 15.189 | 0 | 0.063105 | 134.834 | 6.7601 | 156.8462
2007-12-01 | 15.6348 | 0 | 0.14466 | 135.4645 | 6.7601 | 158.0041
2008-01-01 | 16.252 | 0 | 0.21996 | 135.859 | 8.9956 | 161.3265
2008-02-01 | 16.3348 | 0 | 0.22307 | 135.859 | 16.6601 | 169.0769
2008-03-01 | 16.352 | 1.5581 | 0.22542 | 135.859 | 22.7569 | 176.7514
2008-04-01 | 16.352 | 2.3 | 0.25899 | 135.859 | 25.6601 | 180.4301
2008-05-01 | 16.352 | 2.3 | 0.29769 | 135.859 | 25.6601 | 180.4688
2008-06-01 | 16.352 | 6.8 | 0.29769 | 135.859 | 38.2002 | 197.5089
2008-07-01 | 16.352 | 7.3 | 0.304 | 135.859 | 45.4602 | 205.2752
2008-08-01 | 16.352 | 7.3 | 0.30791 | 135.9509 | 45.4602 | 205.371
2008-09-01 | 16.352 | 7.3 | 0.31281 | 136.809 | 46.8352 | 207.609
2008-10-01 | 16.352 | 7.6645 | 0.33243 | 136.809 | 56.2651 | 217.423
2008-11-01 | 17.632 | 18.6 | 0.33409 | 140.209 | 69.2203 | 245.9954
2008-12-01 | 19.552 | 18.7129 | 3.2543 | 140.809 | 73.5103 | 255.8385
2009-01-01 | 19.552 | 22.1 | 11.616 | 140.809 | 73.5103 | 267.5873
2009-02-01 | 19.552 | 22.1 | 11.7447 | 140.809 | 73.5103 | 267.716
2009-03-01 | 19.552 | 22.1 | 11.7722 | 140.809 | 73.549 | 267.7822
2009-04-01 | 19.5981 | 22.1 | 11.774 | 140.809 | 74.1103 | 268.3914
2009-05-01 | 19.898 | 22.1 | 11.7776 | 142.68 | 74.1103 | 270.5658
2009-06-01 | 19.898 | 59.9 | 11.7776 | 146.609 | 74.1103 | 312.2949
2009-07-01 | 19.898 | 85.1 | 11.7776 | 146.609 | 74.1103 | 337.4949
2009-08-01 | 19.898 | 85.1 | 11.7776 | 146.609 | 74.1103 | 337.4949
2009-09-01 | 19.898 | 85.1 | 12.7339 | 147.7423 | 74.1103 | 339.5845
2009-10-01 | 19.898 | 85.1 | 21.3408 | 148.609 | 74.1103 | 349.058
2009-11-01 | 19.898 | 85.1 | 23.5917 | 148.609 | 74.1103 | 351.309
2009-12-01 | 19.898 | 85.1 | 33.2809 | 148.8671 | 87.5426 | 374.6885
2010-01-01 | 19.898 | 96.8 | 47.3343 | 189.759 | 104.9039 | 458.6952
2010-02-01 | 19.898 | 96.8 | 53.8468 | 190.281 | 120.7104 | 481.5363
2010-03-01 | 19.898 | 96.8 | 53.8468 | 202.197 | 120.7104 | 493.4523
2010-04-01 | 23.7224 | 96.8 | 53.8468 | 223.2703 | 120.7104 | 518.35
2010-05-01 | 26.977 | 96.8 | 53.8468 | 239.197 | 142.746 | 559.5668
2010-06-01 | 26.977 | 96.8 | 53.8629 | 240.3126 | 160.3106 | 578.2631
2010-07-01 | 28.2931 | 96.8 | 64.8303 | 240.7634 | 160.3106 | 590.9974
2010-08-01 | 33.8764 | 96.8 | 104.3249 | 240.815 | 160.3106 | 636.1268
2010-09-01 | 38.9911 | 96.8 | 121.7581 | 241.505 | 160.3106 | 659.3648
2010-10-01 | 39.224 | 96.8 | 130.6526 | 243.47 | 162.4138 | 672.5603
2010-11-01 | 39.224 | 96.8 | 151.1879 | 243.62 | 175.1106 | 705.9425
2010-12-01 | 39.224 | 96.8 | 166.5989 | 244.22 | 186.9171 | 733.7599
2011-01-01 | 40.1763 | 96.8 | 195.2485 | 248.52 | 204.3365 | 785.0812
2011-02-01 | 40.864 | 96.8 | 209.3405 | 248.52 | 221.1107 | 816.6352
2011-03-01 | 40.864 | 96.8 | 215.1702 | 249.638 | 221.1107 | 823.5829
2011-04-01 | 40.864 | 96.8 | 223.6972 | 249.638 | 221.1107 | 832.1099
2011-05-01 | 40.9608 | 96.8 | 226.8121 | 249.638 | 234.014 | 848.2249
2011-06-01 | 40.964 | 96.8 | 230.5228 | 250.758 | 241.1108 | 860.1556
2011-07-01 | 40.964 | 96.8 | 262.2795 | 250.758 | 241.1108 | 891.9123
2011-08-01 | 40.964 | 96.8 | 289.5469 | 250.758 | 241.1108 | 919.1797
2011-09-01 | 40.9889 | 96.8 | 317.93 | 250.758 | 241.1108 | 947.5877
2011-10-01 | 41.338 | 96.8 | 325.5028 | 250.758 | 241.1108 | 955.5096
2011-11-01 | 41.363 | 96.8 | 330.6216 | 251.223 | 241.1108 | 961.1184
2011-12-01 | 41.6799 | 96.8 | 359.6279 | 251.223 | 241.1108 | 990.4416
2012-01-01 | 44.4734 | 96.8 | 378.2799 | 251.223 | 242.8527 | 1013.629
2012-02-01 | 44.575 | 96.8 | 384.5041 | 251.223 | 250.1108 | 1027.213
2012-03-01 | 44.575 | 96.8 | 442.107 | 251.223 | 265.9625 | 1100.6675
2012-04-01 | 45.8414 | 96.8 | 463.5679 | 251.223 | 287.9109 | 1145.3432
2012-05-01 | 46.4559 | 96.8 | 490.28 | 251.223 | 293.3948 | 1178.1537
2012-06-01 | 47.5397 | 96.8 | 521.2308 | 251.223 | 297.911 | 1214.7045
2012-07-01 | 48.4584 | 96.8 | 526.8559 | 251.223 | 297.911 | 1221.2482
2012-08-01 | 49.1175 | 96.8 | 538.457 | 251.473 | 297.911 | 1233.7585
2012-09-01 | 49.728 | 96.8 | 547.7075 | 251.473 | 301.511 | 1247.2195
2012-10-01 | 49.8409 | 96.8 | 558.4193 | 251.473 | 301.911 | 1258.4442
2012-11-01 | 49.978 | 96.8 | 577.3481 | 251.473 | 301.911 | 1277.5101
2012-12-01 | 50.3167 | 96.8 | 589.1998 | 251.473 | 310.8142 | 1298.6037
2013-01-01 | 51.5379 | 96.8 | 605.9954 | 252.048 | 327.8143 | 1334.1956
2013-02-01 | 54.923 | 96.8 | 649.91 | 254.0123 | 334.9111 | 1390.5563
2013-03-01 | 54.923 | 96.8 | 710.9791 | 259.6581 | 334.9111 | 1457.2713
2013-04-01 | 55.172 | 96.8 | 746.9822 | 260.051 | 334.9111 | 1493.9163
2013-05-01 | 56.6655 | 96.8 | 765.6521 | 265.551 | 334.9111 | 1519.5797
2013-06-01 | 58.1607 | 96.8 | 797.9923 | 271.451 | 334.9111 | 1559.3151
2013-07-01 | 58.269 | 96.8 | 833.6291 | 274.9494 | 334.9111 | 1598.5586
2013-08-01 | 58.269 | 96.8 | 857.21 | 279.901 | 334.9111 | 1627.0911
2013-09-01 | 58.269 | 96.8 | 883.7393 | 280.501 | 334.9111 | 1654.2204
2013-10-01 | 58.4625 | 96.8 | 907.9225 | 285.4687 | 335.0401 | 1683.6939
2013-11-01 | 58.519 | 96.9167 | 917.6386 | 292.601 | 335.4111 | 1701.0864
2013-12-01 | 58.519 | 97.006 | 956.7308 | 292.601 | 335.4111 | 1740.2679
2014-01-01 | 63.76 | 97.006 | 996.6295 | 292.601 | 335.4111 | 1785.4076
2014-02-01 | 68.017 | 97.006 | 1052.981 | 292.601 | 339.9111 | 1850.5161
2014-03-01 | 72.017 | 97.006 | 1131.5585 | 292.601 | 368.5134 | 1961.6959
2014-04-01 | 74.2035 | 97.006 | 1166.2717 | 292.601 | 371.4172 | 2001.4995
2014-05-01 | 74.869 | 97.006 | 1192.1372 | 292.601 | 371.4172 | 2028.0304
2014-06-01 | 74.869 | 97.006 | 1208.0346 | 292.601 | 373.4172 | 2045.9278
2014-07-01 | 74.869 | 97.006 | 1228.7427 | 294.251 | 381.4172 | 2076.2859
2014-08-01 | 74.9013 | 97.006 | 1281.9536 | 294.251 | 386.9218 | 2135.0336
2014-09-01 | 75.119 | 97.006 | 1325.7176 | 294.251 | 395.8973 | 2187.9909
2014-10-01 | 75.119 | 97.006 | 1406.5719 | 294.251 | 410.8993 | 2283.8472
2014-11-01 | 75.119 | 97.006 | 1471.3142 | 294.251 | 415.6827 | 2353.3729
2014-12-01 | 75.119 | 97.006 | 1508.8385 | 294.251 | 425.2494 | 2400.4638
2015-01-01 | 75.119 | 97.006 | 1534.8037 | 294.251 | 425.2494 | 2426.4291
2015-02-01 | 75.119 | 97.006 | 1590.2363 | 294.251 | 425.2494 | 2481.8616
2015-03-01 | 75.119 | 97.006 | 1635.3113 | 294.251 | 425.2494 | 2526.9366
2015-04-01 | 75.269 | 97.006 | 1661.6364 | 294.251 | 425.2494 | 2553.4118
2015-05-01 | 75.369 | 97.006 | 1678.9824 | 294.251 | 425.2494 | 2570.8577
2015-06-01 | 86.6499 | 97.006 | 1702.0977 | 301.513 | 429.7494 | 2617.016
2015-07-01 | 93.7858 | 97.006 | 1725.7316 | 304.762 | 449.5398 | 2670.8252
2015-08-01 | 93.931 | 97.006 | 1747.3995 | 312.373 | 470.714 | 2721.4235
2015-09-01 | 93.931 | 97.006 | 1776.4149 | 312.373 | 483.5495 | 2763.2745
2015-10-01 | 101.1052 | 97.006 | 1800.8333 | 312.373 | 483.5495 | 2794.867
2015-11-01 | 108.049 | 99.4861 | 1828.845 | 312.373 | 483.5495 | 2832.3027
2015-12-01 | 108.966 | 100.922 | 1862.1998 | 313.9214 | 485.0044 | 2871.0135
2016-01-01 | 108.966 | 100.922 | 1873.9655 | 313.973 | 487.6495 | 2885.476
2016-02-01 | 108.966 | 100.922 | 1880.6538 | 313.973 | 489.0289 | 2893.5437
2016-03-01 | 108.966 | 100.922 | 1888.5229 | 313.973 | 497.6496 | 2910.0335
2016-04-01 | 108.966 | 100.922 | 1895.2354 | 313.973 | 497.6496 | 2916.7459
2016-05-01 | 108.966 | 100.922 | 1898.972 | 313.973 | 512.4121 | 2935.2451
2016-06-01 | 108.966 | 100.922 | 1901.0536 | 313.973 | 515.2511 | 2940.1657
2016-07-01 | 108.966 | 100.922 | 1906.6903 | 313.973 | 515.2511 | 2945.8024
2016-08-01 | 109.1621 | 100.922 | 1916.1575 | 313.973 | 515.2511 | 2955.4657
2016-09-01 | 109.346 | 100.922 | 1932.2473 | 313.973 | 521.4011 | 2977.8894
2016-10-01 | 109.3541 | 100.922 | 1940.6332 | 313.973 | 542.4126 | 3007.2948
2016-11-01 | 109.596 | 100.922 | 1948.1572 | 313.973 | 553.9032 | 3026.5514
2016-12-01 | 109.596 | 100.922 | 1956.2489 | 314.038 | 569.1226 | 3049.9275
2017-01-01 | 109.596 | 100.922 | 1960.8591 | 314.038 | 571.7032 | 3057.1183
2017-02-01 | 109.596 | 100.922 | 1965.8379 | 314.038 | 571.7032 | 3062.0972
2017-03-01 | 109.596 | 103.1546 | 1973.0946 | 314.038 | 571.7032 | 3071.5864
2017-04-01 | 109.596 | 104.767 | 1988.9948 | 314.038 | 578.6372 | 3096.033
2017-05-01 | 109.596 | 105.0799 | 2002.7135 | 314.3138 | 579.962 | 3111.6652
2017-06-01 | 109.596 | 108 | 2007.9013 | 315.2713 | 580.2039 | 3120.9725
2017-07-01 | 109.596 | 108 | 2009.7802 | 315.488 | 580.2039 | 3123.0681
2017-08-01 | 109.596 | 109.1472 | 2012.9963 | 328.7428 | 580.2039 | 3140.6863
2017-09-01 | 109.596 | 111.233 | 2018.8565 | 344.838 | 580.2039 | 3164.7274
2017-10-01 | 109.596 | 111.233 | 2023.9425 | 344.838 | 580.2039 | 3169.8134
2017-11-01 | 109.596 | 111.4908 | 2029.5095 | 344.838 | 587.7212 | 3183.1555
2017-12-01 | 109.596 | 113.811 | 2033.6045 | 344.838 | 590.4548 | 3192.3043
2018-01-01 | 109.596 | 113.811 | 2039.7298 | 344.838 | 590.4548 | 3198.4296
2018-02-01 | 109.596 | 113.811 | 2048.0224 | 344.838 | 590.4548 | 3206.7222
2018-03-01 | 109.596 | 113.811 | 2056.2911 | 344.838 | 590.4548 | 3214.9909
2018-04-01 | 109.7793 | 113.811 | 2060.9914 | 344.838 | 590.4548 | 3219.8745
2018-05-01 | 109.846 | 113.811 | 2063.6322 | 344.838 | 590.4548 | 3222.582
2018-06-01 | 109.846 | 113.811 | 2070.0079 | 344.838 | 590.4548 | 3228.9577
2018-07-01 | 110.0718 | 113.811 | 2077.1555 | 344.838 | 590.4548 | 3236.3311
2018-08-01 | 110.596 | 113.811 | 2090.4804 | 344.838 | 590.4548 | 3250.1802
2018-09-01 | 110.671 | 113.811 | 2098.359 | 344.838 | 590.4548 | 3258.1338
2018-10-01 | 110.846 | 113.811 | 2104.2416 | 344.838 | 590.4548 | 3264.1914
2018-11-01 | 110.941 | 113.811 | 2104.8686 | 344.838 | 590.4548 | 3264.9134
2018-12-01 | 111.196 | 113.811 | 2105.7477 | 344.838 | 590.4548 | 3266.0475
2019-01-01 | 111.196 | 113.811 | 2128.1496 | 347.438 | 590.4548 | 3291.0494
2019-02-01 | 111.196 | 113.811 | 2138.3452 | 347.438 | 590.4548 | 3301.245
2019-03-01 | 111.446 | 113.811 | 2145.193 | 347.438 | 590.4548 | 3308.3428
2019-04-01 | 111.6627 | 115.263 | 2148.4854 | 347.438 | 590.4548 | 3313.3039
2019-05-01 | 111.9299 | 115.791 | 2150.6741 | 347.438 | 590.4548 | 3316.2878
2019-06-01 | 111.946 | 115.791 | 2152.1248 | 347.438 | 590.4548 | 3317.7546
2019-07-01 | 111.946 | 115.791 | 2153.0123 | 347.438 | 590.4548 | 3318.6421
2019-08-01 | 111.9702 | 115.791 | 2154.7448 | 347.438 | 590.4548 | 3320.3988
2019-09-01 | 112.3043 | 116.883 | 2157.8404 | 347.438 | 590.4548 | 3324.9205
2019-10-01 | 112.446 | 118.521 | 2158.9011 | 347.438 | 590.4548 | 3327.7609
2019-11-01 | 112.446 | 118.521 | 2160.0341 | 347.438 | 590.4548 | 3328.8939
2019-12-01 | 112.446 | 118.521 | 2160.2149 | 347.438 | 590.4548 | 3329.0747
2020-01-01 | 112.446 | 118.521 | 2160.2149 | 347.438 | 590.4548 | 3329.0747
2020-02-01 | 112.446 | 119.4101 | 2160.2149 | 347.438 | 590.4548 | 3329.9639
2020-03-01 | 112.446 | 123.678 | 2160.2835 | 350.5348 | 590.4548 | 3337.3971
2020-04-01 | 112.446 | 123.678 | 2160.7462 | 351.438 | 590.4548 | 3338.763
2020-05-01 | 112.446 | 123.678 | 2160.7462 | 351.438 | 590.4548 | 3338.763
2020-06-01 | 112.446 | 136.4009 | 2160.7462 | 351.438 | 590.4548 | 3351.4859
2020-07-01 | 112.446 | 151.465 | 2160.7462 | 351.438 | 590.4548 | 3366.55
2020-08-01 | 112.446 | 151.465 | 2160.7462 | 351.438 | 590.4548 | 3366.55
2020-09-01 | 112.446 | 151.465 | 2160.7689 | 351.438 | 590.4548 | 3366.5727
2020-10-01 | 112.6799 | 151.465 | 2165.9933 | 351.438 | 590.4548 | 3372.031
2020-11-01 | 112.696 | 151.465 | 2168.3075 | 356.288 | 590.4548 | 3379.2113
2020-12-01 | 112.696 | 151.465 | 2168.3075 | 356.8364 | 590.4548 | 3379.7597
2021-01-01 | 112.696 | 151.465 | 2170.1708 | 373.288 | 590.4548 | 3398.0746
2021-02-01 | 112.696 | 151.465 | 2170.4665 | 373.288 | 590.4548 | 3398.3703
2021-03-01 | 112.696 | 151.465 | 2170.4665 | 373.288 | 590.4548 | 3398.3703
2021-04-01 | 112.696 | 151.465 | 2170.4665 | 373.288 | 590.4548 | 3398.3703
2021-05-01 | 112.696 | 151.465 | 2170.4665 | 393.3203 | 590.4548 | 3418.4026
2021-06-01 | 112.696 | 151.465 | 2170.4665 | 400.288 | 590.4548 | 3425.3703
2021-07-01 | 112.696 | 151.465 | 2170.4665 | 400.288 | 590.4548 | 3425.3703
2021-08-01 | 112.696 | 151.465 | 2170.4665 | 400.288 | 590.4548 | 3425.3703
2021-09-01 | 112.696 | 151.465 | 2170.4665 | 400.288 | 590.4548 | 3425.3703
2021-10-01 | 112.696 | 151.465 | 2170.4665 | 400.288 | 590.4548 | 3425.3703
2021-11-01 | 112.696 | 151.465 | 2170.4665 | 400.288 | 590.4548 | 3425.3703
2021-12-01 | 112.696 | 151.465 | 2170.4665 | 400.288 | 590.4548 | 3425.3703
2022-01-01 | 112.696 | 151.465 | 2170.4665 | 400.288 | 590.4548 | 3425.3703
2022-02-01 | 112.696 | 151.465 | 2170.4665 | 400.288 | 590.4548 | 3425.3703
2022-03-01 | 112.696 | 151.465 | 2170.4665 | 400.288 | 590.4548 | 3425.3703
2022-04-01 | 112.696 | 151.465 | 2170.4665 | 400.288 | 590.4548 | 3425.3703
2022-05-01 | 112.696 | 151.465 | 2170.4665 | 400.288 | 590.4548 | 3425.3703
2022-06-01 | 112.696 | 151.465 | 2170.4665 | 400.288 | 590.4548 | 3425.3703
2022-07-01 | 112.696 | 151.465 | 2170.4665 | 400.288 | 590.4548 | 3425.3703
2022-08-01 | 112.696 | 151.465 | 2170.4665 | 400.288 | 590.4548 | 3425.3703
2022-09-01 | 112.696 | 151.465 | 2170.4665 | 400.288 | 590.4548 | 3425.3703
2022-10-01 | 112.696 | 151.465 | 2170.4665 | 400.288 | 590.4548 | 3425.3703
2022-11-01 | 112.696 | 151.465 | 2170.4665 | 400.288 | 590.4548 | 3425.3703
2022-12-01 | 112.696 | 151.465 | 2170.4665 | 400.288 | 590.4548 | 3425.3703
2023-01-01 | 112.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3435.3703
2023-02-01 | 112.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3435.3703
2023-03-01 | 112.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3435.3703
2023-04-01 | 112.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3435.3703
2023-05-01 | 112.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3435.3703
2023-06-01 | 112.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3435.3703
2023-07-01 | 112.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3435.3703
2023-08-01 | 112.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3435.3703
2023-09-01 | 112.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3435.3703
2023-10-01 | 112.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3435.3703
2023-11-01 | 112.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3435.3703
2023-12-01 | 112.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3435.3703
2024-01-01 | 112.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3435.3703
2024-02-01 | 112.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3435.3703
2024-03-01 | 112.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3435.3703
2024-04-01 | 112.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3435.3703
2024-05-01 | 117.3412 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3440.0155
2024-06-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2024-07-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2024-08-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2024-09-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2024-10-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2024-11-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2024-12-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2025-01-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2025-02-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2025-03-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2025-04-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2025-05-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2025-06-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2025-07-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2025-08-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2025-09-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2025-10-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2025-11-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2025-12-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2026-01-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2026-02-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2026-03-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2026-04-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2026-05-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2026-06-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2026-07-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2026-08-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2026-09-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2026-10-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2026-11-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2026-12-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2027-01-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2027-02-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2027-03-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2027-04-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2027-05-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2027-06-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2027-07-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2027-08-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2027-09-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2027-10-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2027-11-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2027-12-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
Back to main menu

## Table 2.1
Back to main menu
Table 2.1: Existing Grid-Connected Resource Capacity
Fuel Type | Total Installed Capacity (MW) | Forecast Capability at 2026 Summer Peak [Firm] (MW) | Forecast Capability at 2026 Summer Peak [Planned] (MW) | Number of Stations | Change in Number of Stations | Change in Installed Capacity (MW)
Nuclear | 12196.2 | 10309 | 10309 | 4 | 0 | 12
Hydroelectric | 8864.3044 | 5192.8151 | 5192.8151 | 76 | 0 | -1.6
Gas/Oil | 11100.29 | 10012.73 | 9986.33 | 30 | 0 | 549.5667
Wind | 4942.811 | 751.7428 | 751.7428 | 42 | 0 | 0
Biofuel | 286.8 | 205 | 205 | 4 | 0 | 0
Solar | 478.04 | 94.6283 | 94.6283 | 10 | 0 | 0
Storage | 1163.547 | 769.965 | 841.575 | 10 | 6 | 712.3
Demand Measures | - | 1148.923 | 1148.923 | - | - | -
Firm Imports (+) / Exports (-) (MW) | - | 900 | 900 | - | - | -
Total | 39031.9924 | 29384.8042 | 29430.0142 | 176 | 6 | 1272.2667
Back to main menu

## Table 2.2
Back to main menu
Table 2.2: Committed Generation and Electricity Storage Resources Status over the 18-month Reliability Outlook Period
|  |  | Estimated |  | Capacity Considered
Project Name | Zone | Fuel Type | Effective Date | Project Status | Firm (MW) | Planned (MW)
E-LT1 Projects (Within next 18MN) | Various | Various | 2026-Q2 to 2027-Q2 | Under Development | 0 | 246
LT1 Projects (Within next 18MN) | Various | Various | 2026-Q2 | Under Development | 0 | 22
Pickering B | Toronto | Nuclear | 2026-Q4 | Facility OOS | -2064 | -2064
Total | 0 | 0 | 0 | 0 | -2064 | -1796
Back to main menu

## Table 2.3
Back to main menu
Table 2.3: Monthly Historical Hydroelectric Median Values for Expected Weather Conditions
Month | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Historical Hydroelectric Median Contribution (MW) | 6050.6093 | 5971.1694 | 5770.3863 | 5852.8357 | 5923.069 | 5627.4545 | 5524.8502 | 5215.6997 | 4966.5184 | 5306.8601 | 5581.4618 | 6050.0874
Historical Hydroelectric Median Contribution without Planned Outages (MW) | 6596.6933 | 6539.4715 | 6341.7407 | 6370.8662 | 6398.8543 | 6196.0154 | 6091.866 | 5882.3025 | 5896.4712 | 6156.349 | 6377.987 | 6574.8872
Back to main menu

## Table 2.4
Back to main menu
Table 2.4: Monthly Wind Capacity Contribution Values
Month | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Wind Capacity Contribution (% of Installed Capacity) | 39.82% | 39.82% | 40.77% | 28.93% | 21.65% | 15.21% | 15.21% | 15.21% | 14.96% | 30.7% | 42.12% | 39.82%
Back to main menu

## Table 2.5
Back to main menu
Table 2.5: Monthly Solar Capacity Contribution Values
Month | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Solar Capacity Contribution (% of Installed Capacity) | 0% | 0% | 0.1654% | 2.048% | 5.581% | 19.8% | 19.8% | 19.8% | 7.768% | 0% | 0% | 0%
Back to main menu

## Table 2.6
Back to main menu
Table 2.6: Monthly Off-Peak Wind Capacity Contribution Values
Month | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Off-Peak WCC (% of Installed Capacity) | 39.82% | 39.82% | 40.77% | 28.93% | 21.65% | 15.21% | 15.21% | 15.21% | 14.96% | 30.7% | 42.12% | 39.82%
Back to main menu

## Table 2.7
Back to main menu
Table 2.7: Summary of Available Resources under Expected Weather
| Description [Normal] | Summer Peak 2026 |  | Winter Peak 2027 |  | Summer Peak 2027
# |  | Firm Scenario | Planned Scenario | Firm Scenario | Planned Scenario | Firm Scenario | Planned Scenario
1 | Installed Resources (MW) | 39032 | 39134.29 | 36968 | 37176.29 | 36968 | 37186.27
2 | Total Reductions in Resources (MW) | 11696 | 11753 | 11046 | 11135 | 12730 | 12820
3 | Demand Measures (MW) | 1148.923 | 1148.923 | 715.7142 | 715.7142 | 2361.9961 | 2361.9961
4 | Firm Imports (+) / Exports (-) (MW) | 900 | 900 | 0 | 0 | 600 | 600
5 | Available Resources (MW) | 29384.923 | 29430.213 | 26637.7143 | 26757.0043 | 27199.9961 | 27328.2661
6 | Bottling | 0 | 0 | 232.9052 | 232.9052 | 0 | 0
7 | Available Resources without Bottling (MW) | 29384.923 | 29430.213 | 26870.6194 | 26989.9094 | 27199.9961 | 27328.2661
Back to main menu

## Table 3.1
Back to main menu
Table 3.1 Firm: Summary of Zonal Energy for Firm Scenario, Expected Weather
| 18-Month Energy Demand |  | 18-Month Energy Production |  | Net Inter-Zonal Energy Transfer | Zonal Energy Demand on Peak Day of 18-Month Period | Available Energy on Peak Day of 18 Month Period
| TWh | Average MW | TWh | Average MW | TWh | GWh | GWh
Ontario | 222 | 16849 | 222.9 | 16916 | 0.9 | 485.4 | 7.3
Bruce | 1.1 | 83 | 64.9 | 4929 | 63.8 | 1.7 | 0.1
East | 13.9 | 1052 | 29.8 | 2259 | 15.9 | 28.3 | 0.5
Essa | 16.1 | 1221 | 6.8 | 517 | -9.3 | 34.3 | 0.1
Niagara | 7.8 | 594 | 21.5 | 1634 | 13.7 | 17.3 | 0.7
Northeast | 16.7 | 1267 | 12.1 | 918 | -4.6 | 28.7 | 0.3
Northwest | 5.6 | 426 | 6.8 | 514 | 1.2 | 9.5 | 0.1
Ottawa | 13.4 | 1015 | 1 | 75 | -12.4 | 29.8 | 0.3
Southwest | 44.1 | 3349 | 12.5 | 950 | -31.6 | 97 | 2.6
Toronto | 77 | 5844 | 42.3 | 3210 | -34.7 | 185.8 | 2.2
West | 26.3 | 1998 | 25.1 | 1909 | -1.2 | 53 | 0.4
Back to main menu

## Table 3.2
Back to main menu
Table 3.2 Planned: Summary of Zonal Energy for Planned Scenario, Expected Weather
| 18-Month Energy Demand |  | 18-Month Energy Production |  | Net Inter-Zonal Energy Transfer | Zonal Energy Demand on Peak Day of 18-Month Period | Available Energy on Peak Day of 18 Month Period
| TWh | Average MW | TWh | Average MW | TWh | GWh | GWh
Ontario | 223.4 | 16958 | 224.3 | 17024 | 0.9 | 485.4 | 620.5
Bruce | 1.1 | 83 | 65 | 4930 | 63.9 | 1.7 | 137.5
East | 13.9 | 1052 | 30.3 | 2297 | 16.4 | 28.3 | 99.8
Essa | 16.1 | 1221 | 6.9 | 522 | -9.2 | 34.3 | 19
Niagara | 7.8 | 594 | 21.6 | 1636 | 13.8 | 17.3 | 54.3
Northeast | 16.7 | 1266 | 12.1 | 918 | -4.6 | 28.7 | 28.8
Northwest | 5.6 | 426 | 6.8 | 515 | 1.2 | 9.5 | 19.8
Ottawa | 13.4 | 1015 | 1 | 75 | -12.4 | 29.8 | 3.2
Southwest | 45.3 | 3437 | 12.6 | 953 | -32.7 | 97 | 25.9
Toronto | 77 | 5844 | 42.4 | 3219 | -34.6 | 185.8 | 146.3
West | 26.6 | 2019 | 25.8 | 1959 | -0.8 | 53 | 86
Back to main menu

## Table 3.3
Back to main menu
Table 3.3 Firm: Ontario Energy Production by Fuel Type for the Firm Scenario, Expected Weather
Fuel Type (Grid Connected) | 2026 | 2027 | Total
Nuclear | 37792.4 | 58173.88 | 95966.28
Hydro | 16295.45 | 33782.76 | 50078.21
Gas & Oil | 12923.95 | 42862.03 | 55785.98
Wind | 5792.16 | 13003.88 | 18796.04
Bio Fuel | 201.06 | 451.69 | 652.75
Storage | 84.32 | 526.68 | 611
Other | 267.72 | 721.95 | 989.67
Total | 73357.06 | 149522.87 | 222879.93
Back to main menu

## Table 3.4
Back to main menu
Table 3.4 Planned: Ontario Energy Production by Fuel Type for the Planned Scenario, Expected Weather
Fuel Type (Grid Connected) | 2026 | 2027 | Total
Nuclear | 37794.45 | 58173.8 | 95968.25
Hydro | 16295.43 | 33782.99 | 50078.42
Gas & Oil | 12978.47 | 44198.76 | 57177.23
Wind | 5792.25 | 13025.14 | 18817.39
Bio Fuel | 201.03 | 456.86 | 657.89
Storge | 80.2 | 536.66 | 616.86
Other | 267.83 | 726.53 | 994.36
Total | 73409.66 | 150900.74 | 224310.4
Back to main menu

## Table 3.5
Back to main menu
Table 3.5: Assessment of Resource Adequacy: Expected Weather, Firm Scenario
Week | Ontario | Total Installed | Total Reductions | Demand | Firm Imports (+) | Total Available | Required | Available | Available | Required | Required | Reserve Above
Ending | Demand | Capacity | in Resources | Measures | Exports (-) | Resources | Resources | Reserve | Reserve | Reserve | Reserve | Requirement
Day | MW | MW | MW | MW | MW | MW | MW | % | MW | % | MW | MW
2026-07-05 | 21397 | 39032 | 13295 | 1148.923 | 896.1 | 26882.023 | 27179 | 25.63 | 5485 | 27.02 | 5782 | -297
2026-07-12 | 22068 | 39032 | 12530 | 1148.923 | 900 | 27650.923 | 27986 | 25.3 | 5583 | 26.82 | 5918 | -335
2026-07-19 | 22268 | 39032 | 11696 | 1148.923 | 900 | 28484.923 | 28167 | 27.92 | 6217 | 26.49 | 5899 | 318
2026-07-26 | 22247 | 39032 | 11664 | 1148.923 | 900 | 28516.923 | 28185 | 28.18 | 6270 | 26.69 | 5938 | 332
2026-08-02 | 22049 | 39032 | 11679 | 1148.923 | 900 | 28501.923 | 28104 | 29.27 | 6453 | 27.46 | 6055 | 398
2026-08-09 | 21574 | 39032 | 11852 | 1148.923 | 896.1 | 28325.023 | 27785 | 31.29 | 6751 | 28.79 | 6211 | 540
2026-08-16 | 21549 | 39032 | 12057 | 1148.923 | 896.1 | 28120.023 | 27213 | 30.49 | 6571 | 26.28 | 5664 | 907
2026-08-23 | 21385 | 39032 | 12314 | 1148.923 | 896.1 | 27863.023 | 26424 | 30.29 | 6478 | 23.56 | 5039 | 1439
2026-08-30 | 21372 | 39032 | 12491 | 1148.923 | 896.1 | 27686.023 | 26158 | 29.54 | 6314 | 22.39 | 4786 | 1528
2026-09-06 | 20980 | 39032 | 12410 | 1148.923 | 896.1 | 27767.023 | 26782 | 32.35 | 6787 | 27.65 | 5802 | 985
2026-09-13 | 19832 | 39032 | 12386 | 1148.923 | 896.1 | 27791.023 | 26688 | 40.13 | 7959 | 34.57 | 6856 | 1103
2026-09-20 | 19390 | 39032 | 12631 | 1148.923 | 896.1 | 27546.023 | 25640 | 42.06 | 8156 | 32.23 | 6250 | 1906
2026-09-27 | 18949 | 39032 | 15193 | 1148.923 | 896.1 | 24984.023 | 24965 | 31.85 | 6035 | 31.75 | 6016 | 19
2026-10-04 | 18599 | 36968 | 15275 | 1148.923 | 896.1 | 22838.023 | 23813 | 22.79 | 4239 | 28.03 | 5214 | -975
2026-10-11 | 18092 | 36968 | 15761 | 872.1728 | 596.1 | 22075.2728 | 22340 | 22.02 | 3983 | 23.48 | 4248 | -265
2026-10-18 | 18094 | 36968 | 14139 | 872.1728 | 596.1 | 23697.2728 | 22117 | 30.97 | 5603 | 22.23 | 4023 | 1580
2026-10-25 | 18352 | 36968 | 15227 | 872.1728 | 596.1 | 22609.2728 | 21926 | 23.2 | 4257 | 19.47 | 3574 | 683
2026-11-01 | 18641 | 36968 | 14825 | 872.1728 | 596.1 | 23011.2728 | 22279 | 23.44 | 4370 | 19.52 | 3638 | 732
2026-11-08 | 19180 | 36968 | 13288 | 828.4437 | 0 | 24508.4437 | 22822 | 27.78 | 5328 | 18.99 | 3642 | 1686
2026-11-15 | 19689 | 36968 | 12862 | 828.4437 | 0 | 24934.4437 | 23839 | 26.64 | 5245 | 21.08 | 4150 | 1095
2026-11-22 | 20252 | 36968 | 12088 | 828.4437 | 0 | 25708.4437 | 24348 | 26.94 | 5456 | 20.23 | 4096 | 1360
2026-11-29 | 20764 | 36968 | 11673 | 828.4437 | 0 | 26123.4437 | 24758 | 25.81 | 5359 | 19.24 | 3994 | 1365
2026-12-06 | 21154 | 36968 | 11505 | 828.4437 | 0 | 26291.4437 | 25186 | 24.28 | 5137 | 19.06 | 4032 | 1105
2026-12-13 | 21471 | 36968 | 10930 | 828.4437 | 0 | 26866.4437 | 25596 | 25.13 | 5395 | 19.21 | 4125 | 1270
2026-12-20 | 21685 | 36968 | 10900 | 828.4437 | 0 | 26896.4437 | 25800 | 24.03 | 5211 | 18.98 | 4115 | 1096
2026-12-27 | 21093 | 36968 | 10888 | 828.4437 | 0 | 26908.4437 | 25522 | 27.57 | 5815 | 21 | 4429 | 1386
2027-01-03 | 21066 | 36968 | 9938 | 828.4437 | 0 | 27858.4437 | 25774 | 32.24 | 6792 | 22.35 | 4708 | 2084
2027-01-10 | 21949 | 36968 | 11046 | 715.7142 | 0 | 26637.7143 | 26476 | 21.36 | 4689 | 20.63 | 4527 | 162
2027-01-17 | 21839 | 36968 | 11862 | 737.9142 | 0 | 25843.9143 | 26145 | 18.34 | 4005 | 19.72 | 4306 | -301
2027-01-24 | 21904 | 36968 | 11911 | 715.7142 | 0 | 25772.7143 | 26240 | 17.66 | 3869 | 19.8 | 4336 | -467
2027-01-31 | 21890 | 36968 | 11956 | 715.7142 | 0 | 25727.7143 | 26118 | 17.53 | 3838 | 19.31 | 4228 | -390
2027-02-07 | 21372 | 36968 | 12177 | 828.4437 | 0 | 25619.4437 | 25551 | 19.87 | 4247 | 19.55 | 4179 | 68
2027-02-14 | 21373 | 36968 | 12026 | 828.4437 | 0 | 25770.4437 | 25518 | 20.57 | 4397 | 19.39 | 4145 | 252
2027-02-21 | 21085 | 36968 | 11946 | 828.4437 | 0 | 25850.4437 | 25381 | 22.6 | 4765 | 20.37 | 4296 | 469
2027-02-28 | 20931 | 36968 | 12314 | 828.4437 | 0 | 25482.4437 | 25134 | 21.74 | 4551 | 20.08 | 4203 | 348
2027-03-07 | 20399 | 36968 | 12143 | 828.4437 | 0 | 25653.4437 | 24602 | 25.76 | 5254 | 20.6 | 4203 | 1051
2027-03-14 | 19962 | 36968 | 12077 | 828.4437 | 0 | 25719.4437 | 24233 | 28.84 | 5757 | 21.4 | 4271 | 1486
2027-03-21 | 19446 | 36968 | 11939 | 828.4437 | 0 | 25857.4437 | 23523 | 32.97 | 6411 | 20.97 | 4077 | 2334
2027-03-28 | 19023 | 36968 | 11915 | 828.4437 | 0 | 25881.4437 | 23251 | 36.05 | 6858 | 22.23 | 4228 | 2630
2027-04-04 | 18589 | 36968 | 14621 | 828.4437 | 0 | 23175.4437 | 21901 | 24.67 | 4586 | 17.82 | 3312 | 1274
2027-04-11 | 18231 | 36968 | 15035 | 828.4437 | 0 | 22761.4437 | 21635 | 24.85 | 4530 | 18.67 | 3404 | 1126
2027-04-18 | 17897 | 36968 | 18152 | 828.4437 | 0 | 19644.4437 | 20899 | 9.76 | 1747 | 16.77 | 3002 | -1255
2027-04-25 | 17645 | 36968 | 18399 | 828.4437 | 0 | 19397.4437 | 20726 | 9.93 | 1752 | 17.46 | 3081 | -1329
2027-05-02 | 17460 | 36968 | 16836 | 828.4437 | 0 | 20960.4437 | 20634 | 20.05 | 3500 | 18.18 | 3174 | 326
2027-05-09 | 17377 | 36968 | 17210 | 1934.9294 | 600 | 21692.9294 | 20717 | 24.84 | 4316 | 19.22 | 3340 | 976
2027-05-16 | 17464 | 36968 | 16747 | 1934.9294 | 600 | 22155.9294 | 21253 | 26.87 | 4692 | 21.7 | 3789 | 903
2027-05-23 | 18149 | 36968 | 15851 | 1934.9294 | 600 | 23051.9294 | 22445 | 27.02 | 4903 | 23.67 | 4296 | 607
2027-05-30 | 18209 | 36968 | 15570 | 1934.9294 | 600 | 23332.9294 | 24927 | 28.14 | 5124 | 36.89 | 6718 | -1594
2027-06-06 | 19060 | 36968 | 12132 | 2361.9961 | 600 | 27197.9961 | 25836 | 42.7 | 8138 | 35.55 | 6776 | 1362
2027-06-13 | 19550 | 36968 | 12163 | 2361.9961 | 600 | 27166.9961 | 26346 | 38.96 | 7617 | 34.76 | 6796 | 821
2027-06-20 | 20597 | 36968 | 12237 | 2361.9961 | 600 | 27092.9961 | 26886 | 31.54 | 6496 | 30.53 | 6289 | 207
2027-06-27 | 21474 | 36968 | 12260 | 2361.9961 | 600 | 27069.9961 | 26610 | 26.06 | 5596 | 23.92 | 5136 | 460
2027-07-04 | 21491 | 36968 | 12026 | 2361.9961 | 600 | 27303.9961 | 27097 | 27.05 | 5813 | 26.09 | 5606 | 207
2027-07-11 | 22237 | 36968 | 12511 | 2361.9961 | 600 | 26818.9961 | 27763 | 20.61 | 4582 | 24.85 | 5526 | -944
2027-07-18 | 22449 | 36968 | 12547 | 2361.9961 | 600 | 26782.9961 | 27819 | 19.31 | 4334 | 23.92 | 5370 | -1036
2027-07-25 | 22460 | 36968 | 12730 | 2361.9961 | 600 | 26599.9961 | 27655 | 18.43 | 4140 | 23.13 | 5195 | -1055
2027-08-01 | 22313 | 36968 | 12609 | 2361.9961 | 600 | 26720.9961 | 27713 | 19.76 | 4408 | 24.2 | 5400 | -992
2027-08-08 | 21861 | 36968 | 12854 | 2361.9961 | 600 | 26475.9961 | 27387 | 21.11 | 4615 | 25.28 | 5526 | -911
2027-08-15 | 21820 | 36968 | 13314 | 2361.9961 | 600 | 26015.9961 | 26664 | 19.23 | 4196 | 22.2 | 4844 | -648
2027-08-22 | 21614 | 36968 | 13255 | 2361.9961 | 600 | 26074.9961 | 26126 | 20.64 | 4461 | 20.88 | 4512 | -51
2027-08-29 | 21634 | 36968 | 13226 | 2361.9961 | 600 | 26103.9961 | 25970 | 20.66 | 4470 | 20.04 | 4336 | 134
2027-09-05 | 21311 | 36968 | 12775 | 2361.9961 | 600 | 26554.9961 | 26837 | 24.61 | 5244 | 25.93 | 5526 | -282
2027-09-12 | 20204 | 36968 | 12952 | 2361.9961 | 600 | 26377.9961 | 26552 | 30.56 | 6174 | 31.42 | 6348 | -174
2027-09-19 | 19731 | 36968 | 12744 | 2361.9961 | 600 | 26585.9961 | 25903 | 34.74 | 6855 | 31.28 | 6172 | 683
2027-09-26 | 19265 | 36968 | 14127 | 2361.9961 | 600 | 25202.9961 | 25183 | 30.82 | 5938 | 30.72 | 5918 | 20
2027-10-03 | 19178 | 36968 | 14633 | 2361.9961 | 600 | 24696.9961 | 23827 | 28.78 | 5519 | 24.24 | 4649 | 870
2027-10-10 | 18408 | 36968 | 15381 | 1934.9294 | 600 | 23521.9294 | 22626 | 27.78 | 5114 | 22.91 | 4218 | 896
2027-10-17 | 18398 | 36968 | 14218 | 1934.9294 | 600 | 24684.9294 | 22128 | 34.17 | 6287 | 20.27 | 3730 | 2557
2027-10-24 | 18628 | 36968 | 14896 | 1934.9294 | 600 | 24006.9294 | 22076 | 28.88 | 5379 | 18.51 | 3448 | 1931
2027-10-31 | 18910 | 36968 | 13536 | 1934.9294 | 600 | 25366.9294 | 22426 | 34.15 | 6457 | 18.59 | 3516 | 2941
2027-11-07 | 19461 | 36968 | 12058 | 1334.9294 | -600 | 25644.9294 | 23543 | 31.78 | 6184 | 20.98 | 4082 | 2102
2027-11-14 | 19918 | 36968 | 12856 | 1334.9294 | -600 | 24846.9294 | 23824 | 24.75 | 4929 | 19.61 | 3906 | 1023
2027-11-21 | 20490 | 36968 | 11737 | 1334.9294 | -600 | 25965.9294 | 24454 | 26.73 | 5476 | 19.35 | 3964 | 1512
2027-11-28 | 21035 | 36968 | 11417 | 1334.9294 | -600 | 26285.9294 | 25102 | 24.96 | 5251 | 19.33 | 4067 | 1184
2027-12-05 | 21394 | 36968 | 11247 | 1334.9294 | -600 | 26455.9294 | 25290 | 23.66 | 5062 | 18.21 | 3896 | 1166
2027-12-12 | 21756 | 36968 | 10948 | 1334.9294 | -600 | 26754.9294 | 25667 | 22.98 | 4999 | 17.98 | 3911 | 1088
2027-12-19 | 21991 | 36968 | 10678 | 1334.9294 | -600 | 27024.9294 | 26179 | 22.89 | 5034 | 19.04 | 4188 | 846
2027-12-26 | 22011 | 36968 | 10464 | 1334.9294 | -600 | 27238.9294 | 26445 | 23.75 | 5228 | 20.14 | 4434 | 794
2028-01-02 | 21760 | 36968 | 10401 | 1334.9294 | -600 | 27301.9294 | 26360 | 25.47 | 5542 | 21.14 | 4600 | 942
Note: The reader should be aware that security and adequacy assessments are published on the IESO web site on a daily basis that progressively supersedes information presented
in this report.
Back to main menu

## Table 3.6
Back to main menu
Table 3.6: Assessment of Resource Adequacy: Expected Weather, Planned Scenario
Week | Ontario | Total Installed | Total Reductions | Demand | Firm Imports (+) | Total Available | Required | Available | Available | Required | Required | Reserve Above
Ending | Demand | Capacity | in Resources | Measures | Exports (-) | Resources | Resources | Reserve | Reserve | Reserve | Reserve | Requirement
Day | MW | MW | MW | MW | MW | MW | MW | % | MW | % | MW | MW
2026-07-05 | 21396 | 39134.29 | 13326 | 1148.923 | 896.1 | 26953.313 | 27178 | 25.97 | 5557 | 27.02 | 5782 | -225
2026-07-12 | 22069 | 39134.29 | 12587 | 1148.923 | 900 | 27696.213 | 27987 | 25.5 | 5627 | 26.82 | 5918 | -291
2026-07-19 | 22267 | 39134.29 | 11753 | 1148.923 | 900 | 28530.213 | 28166 | 28.13 | 6263 | 26.49 | 5899 | 364
2026-07-26 | 22247 | 39134.29 | 11722 | 1148.923 | 900 | 28561.213 | 28185 | 28.38 | 6314 | 26.69 | 5938 | 376
2026-08-02 | 22050 | 39134.29 | 11737 | 1148.923 | 900 | 28546.213 | 28105 | 29.46 | 6496 | 27.46 | 6055 | 441
2026-08-09 | 21575 | 39134.29 | 11909 | 1148.923 | 896.1 | 28370.313 | 27786 | 31.49 | 6795 | 28.79 | 6211 | 584
2026-08-16 | 21548 | 39134.29 | 12114 | 1148.923 | 896.1 | 28165.313 | 27212 | 30.71 | 6617 | 26.29 | 5664 | 953
2026-08-23 | 21386 | 39134.29 | 12371 | 1148.923 | 896.1 | 27908.313 | 26425 | 30.5 | 6522 | 23.56 | 5039 | 1483
2026-08-30 | 21371 | 39134.29 | 12548 | 1148.923 | 896.1 | 27731.313 | 26157 | 29.76 | 6360 | 22.39 | 4786 | 1574
2026-09-06 | 20980 | 39134.29 | 12467 | 1148.923 | 896.1 | 27812.313 | 26782 | 32.56 | 6832 | 27.65 | 5802 | 1030
2026-09-13 | 19832 | 39134.29 | 12443 | 1148.923 | 896.1 | 27836.313 | 26688 | 40.36 | 8004 | 34.57 | 6856 | 1148
2026-09-20 | 19390 | 39134.29 | 12688 | 1148.923 | 896.1 | 27591.313 | 25640 | 42.29 | 8201 | 32.23 | 6250 | 1951
2026-09-27 | 18950 | 39134.29 | 15250 | 1148.923 | 896.1 | 25029.313 | 24966 | 32.08 | 6079 | 31.75 | 6016 | 63
2026-10-04 | 18599 | 37176.29 | 15438 | 1148.923 | 896.1 | 22883.313 | 23813 | 23.03 | 4284 | 28.03 | 5214 | -930
2026-10-11 | 18092 | 37176.29 | 15847 | 872.1728 | 596.1 | 22197.5628 | 22340 | 22.7 | 4106 | 23.48 | 4248 | -142
2026-10-18 | 18093 | 37176.29 | 14225 | 872.1728 | 596.1 | 23819.5628 | 22116 | 31.65 | 5727 | 22.24 | 4023 | 1704
2026-10-25 | 18352 | 37176.29 | 15314 | 872.1728 | 596.1 | 22730.5628 | 21926 | 23.86 | 4379 | 19.47 | 3574 | 805
2026-11-01 | 18640 | 37176.29 | 14932 | 872.1728 | 596.1 | 23112.5628 | 22278 | 24 | 4473 | 19.52 | 3638 | 835
2026-11-08 | 19214 | 37176.29 | 13378 | 828.4437 | 0 | 24626.7337 | 22856 | 28.17 | 5413 | 18.95 | 3642 | 1771
2026-11-15 | 19724 | 37176.29 | 12952 | 828.4437 | 0 | 25052.7337 | 23874 | 27.02 | 5329 | 21.04 | 4150 | 1179
2026-11-22 | 20287 | 37176.29 | 12178 | 828.4437 | 0 | 25826.7337 | 24383 | 27.31 | 5540 | 20.19 | 4096 | 1444
2026-11-29 | 20799 | 37176.29 | 11763 | 828.4437 | 0 | 26241.7337 | 24793 | 26.17 | 5443 | 19.2 | 3994 | 1449
2026-12-06 | 21194 | 37176.29 | 11595 | 828.4437 | 0 | 26409.7337 | 25226 | 24.61 | 5216 | 19.02 | 4032 | 1184
2026-12-13 | 21511 | 37176.29 | 11020 | 828.4437 | 0 | 26984.7337 | 25636 | 25.45 | 5474 | 19.18 | 4125 | 1349
2026-12-20 | 21726 | 37176.29 | 10990 | 828.4437 | 0 | 27014.7337 | 25841 | 24.34 | 5289 | 18.94 | 4115 | 1174
2026-12-27 | 21134 | 37176.29 | 10978 | 828.4437 | 0 | 27026.7337 | 25563 | 27.88 | 5893 | 20.96 | 4429 | 1464
2027-01-03 | 21107 | 37176.29 | 10028 | 828.4437 | 0 | 27976.7337 | 25815 | 32.55 | 6870 | 22.31 | 4708 | 2162
2027-01-10 | 21990 | 37176.29 | 11135 | 715.7142 | 0 | 26757.0043 | 26517 | 21.68 | 4767 | 20.59 | 4527 | 240
2027-01-17 | 21880 | 37176.29 | 11950 | 737.9142 | 0 | 25964.2043 | 26186 | 18.67 | 4084 | 19.68 | 4306 | -222
2027-01-24 | 21944 | 37176.29 | 11999 | 715.7142 | 0 | 25893.0043 | 26280 | 18 | 3949 | 19.76 | 4336 | -387
2027-01-31 | 21930 | 37176.29 | 12044 | 715.7142 | 0 | 25848.0043 | 26158 | 17.87 | 3918 | 19.28 | 4228 | -310
2027-02-07 | 21426 | 37176.29 | 12265 | 828.4437 | 0 | 25739.7337 | 25605 | 20.13 | 4314 | 19.5 | 4179 | 135
2027-02-14 | 21428 | 37176.29 | 12115 | 828.4437 | 0 | 25889.7337 | 25573 | 20.82 | 4462 | 19.34 | 4145 | 317
2027-02-21 | 21140 | 37176.29 | 12035 | 828.4437 | 0 | 25969.7337 | 25436 | 22.85 | 4830 | 20.32 | 4296 | 534
2027-02-28 | 20986 | 37176.29 | 12402 | 828.4437 | 0 | 25602.7337 | 25189 | 22 | 4617 | 20.03 | 4203 | 414
2027-03-07 | 20459 | 37176.29 | 12231 | 828.4437 | 0 | 25773.7337 | 24662 | 25.98 | 5315 | 20.54 | 4203 | 1112
2027-03-14 | 20022 | 37176.29 | 12165 | 828.4437 | 0 | 25839.7337 | 24293 | 29.06 | 5818 | 21.33 | 4271 | 1547
2027-03-21 | 19506 | 37176.29 | 12027 | 828.4437 | 0 | 25977.7337 | 23583 | 33.18 | 6472 | 20.9 | 4077 | 2395
2027-03-28 | 19083 | 37176.29 | 12003 | 828.4437 | 0 | 26001.7337 | 23311 | 36.26 | 6919 | 22.16 | 4228 | 2691
2027-04-04 | 18650 | 37176.29 | 14709 | 828.4437 | 0 | 23295.7337 | 21962 | 24.91 | 4646 | 17.76 | 3312 | 1334
2027-04-11 | 18304 | 37176.29 | 15124 | 828.4437 | 0 | 22880.7337 | 21708 | 25.01 | 4577 | 18.6 | 3404 | 1173
2027-04-18 | 17970 | 37176.29 | 18240 | 828.4437 | 0 | 19764.7337 | 20972 | 9.99 | 1795 | 16.71 | 3002 | -1207
2027-04-25 | 17717 | 37176.29 | 18487 | 828.4437 | 0 | 19517.7337 | 20798 | 10.17 | 1801 | 17.39 | 3081 | -1280
2027-05-02 | 17533 | 37176.29 | 16904 | 828.4437 | 0 | 21100.7337 | 20707 | 20.35 | 3568 | 18.1 | 3174 | 394
2027-05-09 | 17474 | 37176.29 | 17296 | 1934.9294 | 600 | 21815.2194 | 20814 | 24.84 | 4341 | 19.11 | 3340 | 1001
2027-05-16 | 17560 | 37176.29 | 16833 | 1934.9294 | 600 | 22278.2194 | 21349 | 26.87 | 4718 | 21.58 | 3789 | 929
2027-05-23 | 18246 | 37176.29 | 15865 | 1934.9294 | 600 | 23246.2194 | 22542 | 27.4 | 5000 | 23.54 | 4296 | 704
2027-05-30 | 18305 | 37176.29 | 15657 | 1934.9294 | 600 | 23454.2194 | 25023 | 28.13 | 5149 | 36.7 | 6718 | -1569
2027-06-06 | 19165 | 37186.27 | 12221 | 2361.9961 | 600 | 27327.2661 | 25941 | 42.59 | 8162 | 35.36 | 6776 | 1386
2027-06-13 | 19655 | 37186.27 | 12252 | 2361.9961 | 600 | 27296.2661 | 26451 | 38.88 | 7641 | 34.58 | 6796 | 845
2027-06-20 | 20701 | 37186.27 | 12327 | 2361.9961 | 600 | 27221.2661 | 26990 | 31.5 | 6520 | 30.38 | 6289 | 231
2027-06-27 | 21578 | 37186.27 | 12349 | 2361.9961 | 600 | 27199.2661 | 26714 | 26.05 | 5621 | 23.8 | 5136 | 485
2027-07-04 | 21623 | 37186.27 | 12142 | 2361.9961 | 600 | 27406.2661 | 27229 | 26.74 | 5783 | 25.93 | 5606 | 177
2027-07-11 | 22410 | 37186.27 | 12600 | 2361.9961 | 600 | 26948.2661 | 27936 | 20.25 | 4538 | 24.66 | 5526 | -988
2027-07-18 | 22621 | 37186.27 | 12636 | 2361.9961 | 600 | 26912.2661 | 27991 | 18.97 | 4291 | 23.74 | 5370 | -1079
2027-07-25 | 22632 | 37186.27 | 12820 | 2361.9961 | 600 | 26728.2661 | 27827 | 18.1 | 4096 | 22.95 | 5195 | -1099
2027-08-01 | 22486 | 37186.27 | 12699 | 2361.9961 | 600 | 26849.2661 | 27886 | 19.4 | 4363 | 24.01 | 5400 | -1037
2027-08-08 | 22057 | 37186.27 | 12943 | 2361.9961 | 600 | 26605.2661 | 27583 | 20.62 | 4548 | 25.05 | 5526 | -978
2027-08-15 | 22017 | 37186.27 | 13403 | 2361.9961 | 600 | 26145.2661 | 26861 | 18.75 | 4128 | 22 | 4844 | -716
2027-08-22 | 21811 | 37186.27 | 13344 | 2361.9961 | 600 | 26204.2661 | 26323 | 20.14 | 4393 | 20.69 | 4512 | -119
2027-08-29 | 21831 | 37186.27 | 13316 | 2361.9961 | 600 | 26232.2661 | 26167 | 20.16 | 4401 | 19.86 | 4336 | 65
2027-09-05 | 21527 | 37186.27 | 12864 | 2361.9961 | 600 | 26684.2661 | 27053 | 23.96 | 5157 | 25.67 | 5526 | -369
2027-09-12 | 20430 | 37186.27 | 13041 | 2361.9961 | 600 | 26507.2661 | 26778 | 29.75 | 6077 | 31.07 | 6348 | -271
2027-09-19 | 19960 | 37186.27 | 12833 | 2361.9961 | 600 | 26715.2661 | 26132 | 33.84 | 6755 | 30.92 | 6172 | 583
2027-09-26 | 19494 | 37186.27 | 14216 | 2361.9961 | 600 | 25332.2661 | 25412 | 29.95 | 5838 | 30.36 | 5918 | -80
2027-10-03 | 19408 | 37186.27 | 14722 | 2361.9961 | 600 | 24826.2661 | 24057 | 27.92 | 5418 | 23.95 | 4649 | 769
2027-10-10 | 18649 | 37186.27 | 15470 | 1934.9294 | 600 | 23651.1994 | 22867 | 26.82 | 5002 | 22.62 | 4218 | 784
2027-10-17 | 18639 | 37186.27 | 14307 | 1934.9294 | 600 | 24814.1994 | 22369 | 33.13 | 6175 | 20.01 | 3730 | 2445
2027-10-24 | 18869 | 37186.27 | 14986 | 1934.9294 | 600 | 24135.1994 | 22317 | 27.91 | 5266 | 18.27 | 3448 | 1818
2027-10-31 | 19151 | 37186.27 | 13625 | 1934.9294 | 600 | 25496.1994 | 22667 | 33.13 | 6345 | 18.36 | 3516 | 2829
2027-11-07 | 19734 | 37186.27 | 12153 | 1334.9294 | -600 | 25768.1994 | 23816 | 30.58 | 6034 | 20.69 | 4082 | 1952
2027-11-14 | 20190 | 37186.27 | 12951 | 1334.9294 | -600 | 24970.1994 | 24096 | 23.68 | 4780 | 19.35 | 3906 | 874
2027-11-21 | 20763 | 37186.27 | 11832 | 1334.9294 | -600 | 26089.1994 | 24727 | 25.65 | 5326 | 19.09 | 3964 | 1362
2027-11-28 | 21308 | 37186.27 | 11512 | 1334.9294 | -600 | 26409.1994 | 25375 | 23.94 | 5101 | 19.09 | 4067 | 1034
2027-12-05 | 21681 | 37186.27 | 11342 | 1334.9294 | -600 | 26579.1994 | 25577 | 22.59 | 4898 | 17.97 | 3896 | 1002
2027-12-12 | 22049 | 37186.27 | 11043 | 1334.9294 | -600 | 26878.1994 | 25960 | 21.9 | 4829 | 17.74 | 3911 | 918
2027-12-19 | 22284 | 37186.27 | 10773 | 1334.9294 | -600 | 27148.1994 | 26472 | 21.83 | 4864 | 18.79 | 4188 | 676
2027-12-26 | 22304 | 37186.27 | 10559 | 1334.9294 | -600 | 27362.1994 | 26738 | 22.68 | 5058 | 19.88 | 4434 | 624
2028-01-02 | 22056 | 37186.27 | 10496 | 1334.9294 | -600 | 27425.1994 | 26656 | 24.34 | 5369 | 20.86 | 4600 | 769
Note: The reader should be aware that security and adequacy assessments are published on the IESO web site on a daily basis that progressively supersedes
information presented in this report.
Back to main menu

## Table 3.7
Back to main menu
Table 3.7: Zonal Bottled Generation: Expected Weather, Both Scenarios
Week | Firm Scenario | Firm Scenario | Firm Scenario | Planned Scenario | Planned Scenario | Planned Scenario
Ending | Bruce & West | Northeast | Northwest | Bruce & West | Northeast | Northwest
Day | MW | MW | MW | MW | MW | MW
2026-07-05 | 0 | 316.3578 | 45.642 | 0 | 289.9578 | 45.6511
2026-07-12 | 0 | 0 | 8.7562 | 0 | 0 | 8.7378
2026-07-19 | 0 | 0 | 0 | 0 | 0 | 0
2026-07-26 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-02 | 0 | 0 | 23.04 | 0 | 0 | 23.0369
2026-08-09 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-16 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-23 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-30 | 0 | 0 | 0 | 0 | 0 | 0
2026-09-06 | 0 | 0 | 0 | 0 | 0 | 0
2026-09-13 | 278.8271 | 0 | 0 | 278.8271 | 0 | 0
2026-09-20 | 374.9547 | 0 | 0 | 374.9547 | 0 | 0
2026-09-27 | 0 | 0 | 0 | 0 | 0 | 0
2026-10-04 | 116.1825 | 0 | 0 | 116.1825 | 0 | 0
2026-10-11 | 0 | 0 | 0 | 0 | 0 | 0
2026-10-18 | 593.1944 | 0 | 0 | 593.1944 | 0 | 0
2026-10-25 | 500.2909 | 0 | 0 | 500.2909 | 0 | 0
2026-11-01 | 389.1155 | 0 | 0 | 389.1155 | 0 | 0
2026-11-08 | 48.7321 | 0 | 0 | 48.7321 | 0 | 0
2026-11-15 | 0 | 0 | 0 | 0 | 0 | 0
2026-11-22 | 643.369 | 0 | 0 | 643.369 | 0 | 0
2026-11-29 | 228.2524 | 0 | 0 | 228.2524 | 0 | 0
2026-12-06 | 317.7308 | 0 | 0 | 317.7308 | 0 | 0
2026-12-13 | 206.1113 | 0 | 0 | 206.1113 | 0 | 0
2026-12-20 | 136.5911 | 0 | 0 | 136.5911 | 0 | 0
2026-12-27 | 418.8247 | 0 | 0 | 418.8247 | 0 | 0
2027-01-03 | 403.1772 | 0 | 0 | 403.1772 | 0 | 0
2027-01-10 | 232.9052 | 0 | 0 | 232.9052 | 0 | 0
2027-01-17 | 14.5002 | 0 | 0 | 14.5002 | 0 | 0
2027-01-24 | 46.1651 | 0 | 0 | 46.1651 | 0 | 0
2027-01-31 | 0 | 0 | 0 | 0 | 0 | 0
2027-02-07 | 35.5463 | 0 | 0 | 35.5463 | 0 | 0
2027-02-14 | 0 | 0 | 0 | 0 | 0 | 0
2027-02-21 | 68.8136 | 0 | 0 | 68.8136 | 0 | 0
2027-02-28 | 412.5075 | 0 | 0 | 412.5075 | 0 | 0
2027-03-07 | 494.8481 | 0 | 0 | 494.8481 | 0 | 0
2027-03-14 | 508.0836 | 0 | 0 | 508.0836 | 0 | 0
2027-03-21 | 995.9125 | 0 | 0 | 995.9125 | 0 | 0
2027-03-28 | 1226.1839 | 0 | 0 | 1226.1839 | 0 | 0
2027-04-04 | 357.4207 | 0 | 53.4487 | 357.4207 | 0 | 53.4463
2027-04-11 | 709.9705 | 0 | 0 | 709.9705 | 0 | 0
2027-04-18 | 960.715 | 0 | 0 | 960.715 | 0 | 0
2027-04-25 | 1373.4596 | 0 | 0 | 1373.4596 | 0 | 0
2027-05-02 | 2012.3068 | 0 | 0 | 2012.3068 | 0 | 0
2027-05-09 | 2041.0509 | 0 | 0 | 2041.0509 | 0 | 0
2027-05-16 | 1758.9201 | 0 | 93.1014 | 1758.9201 | 0 | 93.1285
2027-05-23 | 939.5001 | 0 | 91.3935 | 939.5001 | 0 | 18.5463
2027-05-30 | 1471.8255 | 0 | 90.3799 | 1471.8255 | 0 | 90.4621
2027-06-06 | 0 | 0 | 73.9666 | 0 | 0 | 73.9789
2027-06-13 | 0 | 0 | 82.3475 | 0 | 0 | 82.4118
2027-06-20 | 0 | 0 | 68.689 | 0 | 0 | 68.7616
2027-06-27 | 0 | 0 | 53.7981 | 0 | 0 | 53.8685
2027-07-04 | 0 | 0 | 24.8229 | 0 | 0 | 51.4227
2027-07-11 | 0 | 0 | 49.8985 | 0 | 0 | 49.9497
2027-07-18 | 0 | 0 | 0 | 0 | 0 | 0
2027-07-25 | 0 | 0 | 0 | 0 | 0 | 0
2027-08-01 | 0 | 0 | 0 | 0 | 0 | 0
2027-08-08 | 0 | 0 | 0 | 0 | 0 | 0
2027-08-15 | 0 | 0 | 0 | 0 | 0 | 0
2027-08-22 | 0 | 0 | 0 | 0 | 0 | 0
2027-08-29 | 0 | 0 | 0 | 0 | 0 | 0
2027-09-05 | 0 | 0 | 0 | 0 | 0 | 0
2027-09-12 | 0 | 0 | 0 | 0 | 0 | 0
2027-09-19 | 0 | 0 | 0 | 0 | 0 | 0
2027-09-26 | 0 | 0 | 0 | 0 | 0 | 0
2027-10-03 | 0 | 0 | 0 | 0 | 0 | 0
2027-10-10 | 0 | 0 | 0 | 0 | 0 | 0
2027-10-17 | 0 | 0 | 0 | 0 | 0 | 0
2027-10-24 | 0 | 0 | 0 | 0 | 0 | 0
2027-10-31 | 0 | 0 | 0 | 0 | 0 | 0
2027-11-07 | 0 | 0 | 0 | 0 | 0 | 0
2027-11-14 | 398.3131 | 0 | 0 | 398.3131 | 0 | 0
2027-11-21 | 116.299 | 0 | 0 | 116.299 | 0 | 0
2027-11-28 | 0 | 0 | 0 | 0 | 0 | 0
2027-12-05 | 0 | 0 | 0 | 0 | 0 | 0
2027-12-12 | 80.4979 | 0 | 0 | 80.4979 | 0 | 0
2027-12-19 | 43.3255 | 0 | 0 | 43.3255 | 0 | 0
2027-12-26 | 65.4866 | 0 | 0 | 65.4866 | 0 | 0
2028-01-02 | 3.069 | 0 | 0 | 3.069 | 0 | 0
Back to main menu

## Table 3.8
Back to main menu
Table 3.8: Energy Production Capability Forecast
Month | Firm Scenario Forecast Energy Production Capability (GWh) | Planned Scenario Forecast Energy Production Capability (GWh)
2026-07-01 | 18897.1738 | 18463.459
2026-08-01 | 18894.0338 | 18460.319
2026-09-01 | 17558.374 | 17143.459
2026-10-01 | 15339.9138 | 14958.409
2026-11-01 | 15926.834 | 16012.099
2026-12-01 | 16980.5838 | 17063.629
2027-01-01 | 16348.1938 | 16430.879
2027-02-01 | 14773.2544 | 14862.319
2027-03-01 | 16650.4138 | 16732.029
2027-04-01 | 14099.574 | 14187.529
2027-05-01 | 15329.2138 | 15391.869
2027-06-01 | 16008.864 | 16078.3265
2027-07-01 | 16035.9938 | 16104.2465
2027-08-01 | 15817.6138 | 15886.9265
2027-09-01 | 15039.564 | 15109.8365
2027-10-01 | 15031.4938 | 15102.6665
2027-11-01 | 15988.214 | 16072.5565
2027-12-01 | 16926.5538 | 17006.7165
Back to main menu

## Table 3.9
Back to main menu
Table 3.9: Reductions by Fuel Type: Expected Weather, Firm Scenario
Week | Ontario | Total Internal | Total Reductions | Nuclear | Biomass, Oil & Gas | Hydro, Wind, Solar & Storage | Total Bottled
Ending | Demand | Resources | in Resources | Reductions | Reductions | Capacity Unavailable | Generation
Day | MW | MW | MW | MW | MW | MW | MW
2026-07-05 | 21397 | 39032 | 13295 | 2665.2 | 1902.52 | 8365.2894 | 361.9998
2026-07-12 | 22068 | 39032 | 12530 | 1887.2 | 2145.43 | 8488.6085 | 8.7562
2026-07-19 | 22268 | 39032 | 11696 | 1887.2 | 1169.36 | 8639.5512 | 0
2026-07-26 | 22247 | 39032 | 11664 | 1887.2 | 1207.2 | 8570.0623 | 0
2026-08-02 | 22049 | 39032 | 11679 | 1887.2 | 1169.36 | 8599.8773 | 23.04
2026-08-09 | 21574 | 39032 | 11852 | 1922.2 | 1103.78 | 8825.938 | 0
2026-08-16 | 21549 | 39032 | 12057 | 1922.2 | 1103.78 | 9030.7909 | 0
2026-08-23 | 21385 | 39032 | 12314 | 1922.2 | 1103.78 | 9288.0017 | 0
2026-08-30 | 21372 | 39032 | 12491 | 1922.2 | 1103.78 | 9465.26 | 0
2026-09-06 | 20980 | 39032 | 12410 | 1922.2 | 1103.78 | 9384.0158 | 0
2026-09-13 | 19832 | 39032 | 12386 | 1891.2 | 1069.91 | 9145.9069 | 278.8271
2026-09-20 | 19390 | 39032 | 12631 | 1891.2 | 1161.72 | 9202.6505 | 374.9547
2026-09-27 | 18949 | 39032 | 15193 | 4545.2 | 1609.68 | 9038.0543 | 0
2026-10-04 | 18599 | 36968 | 15275 | 3509.2 | 2655.35 | 8994.0729 | 116.1825
2026-10-11 | 18092 | 36968 | 15761 | 2678.2 | 5041.99 | 8040.4111 | 0
2026-10-18 | 18094 | 36968 | 14139 | 2678.2 | 2891.64 | 7975.8969 | 593.1944
2026-10-25 | 18352 | 36968 | 15227 | 2678.2 | 3858.71 | 8190.2146 | 500.2909
2026-11-01 | 18641 | 36968 | 14825 | 2678.2 | 3533.97 | 8223.8224 | 389.1155
2026-11-08 | 19180 | 36968 | 13288 | 3487.2 | 1917.62 | 7834.4837 | 48.7321
2026-11-15 | 19689 | 36968 | 12862 | 3487.2 | 1887.3 | 7487.1698 | 0
2026-11-22 | 20252 | 36968 | 12088 | 2670.2 | 1178.38 | 7596.3917 | 643.369
2026-11-29 | 20764 | 36968 | 11673 | 2670.2 | 1178.38 | 7596.3917 | 228.2524
2026-12-06 | 21154 | 36968 | 11505 | 2670.2 | 1178.38 | 7338.4995 | 317.7308
2026-12-13 | 21471 | 36968 | 10930 | 2662.2 | 889.84 | 7171.4594 | 206.1113
2026-12-20 | 21685 | 36968 | 10900 | 2662.2 | 889.84 | 7211.1988 | 136.5911
2026-12-27 | 21093 | 36968 | 10888 | 2662.2 | 889.84 | 6917.1056 | 418.8247
2027-01-03 | 21066 | 36968 | 9938 | 1784.2 | 889.84 | 6860.4415 | 403.1772
2027-01-10 | 21949 | 36968 | 11046 | 2584.2 | 1356.08 | 6873.0967 | 232.9052
2027-01-17 | 21839 | 36968 | 11862 | 3402.2 | 1356.08 | 7088.9805 | 14.5002
2027-01-24 | 21904 | 36968 | 11911 | 3402.2 | 1356.08 | 7106.6743 | 46.1651
2027-01-31 | 21890 | 36968 | 11956 | 3402.2 | 1400.08 | 7153.5484 | 0
2027-02-07 | 21372 | 36968 | 12177 | 3402.2 | 1553.66 | 7185.2979 | 35.5463
2027-02-14 | 21373 | 36968 | 12026 | 3402.2 | 1373.66 | 7250.5158 | 0
2027-02-21 | 21085 | 36968 | 11946 | 3402.2 | 1373.66 | 7101.7574 | 68.8136
2027-02-28 | 20931 | 36968 | 12314 | 3402.2 | 1373.66 | 7125.5105 | 412.5075
2027-03-07 | 20399 | 36968 | 12143 | 3397.2 | 933.32 | 7317.5476 | 494.8481
2027-03-14 | 19962 | 36968 | 12077 | 3397.2 | 933.32 | 7238.6292 | 508.0836
2027-03-21 | 19446 | 36968 | 11939 | 2564.2 | 933.32 | 7445.087 | 995.9125
2027-03-28 | 19023 | 36968 | 11915 | 2564.2 | 933.32 | 7191.3325 | 1226.1839
2027-04-04 | 18589 | 36968 | 14621 | 2564.2 | 3641.21 | 8004.9236 | 410.8694
2027-04-11 | 18231 | 36968 | 15035 | 2545.2 | 3901.79 | 7878.311 | 709.9705
2027-04-18 | 17897 | 36968 | 18152 | 5179.2 | 3829.77 | 8182.2947 | 960.715
2027-04-25 | 17645 | 36968 | 18399 | 5179.2 | 3829.77 | 8016.7517 | 1373.4596
2027-05-02 | 17460 | 36968 | 16836 | 5179.2 | 1891.82 | 7753.1201 | 2012.3068
2027-05-09 | 17377 | 36968 | 17210 | 5178.2 | 1807.19 | 8183.5903 | 2041.0509
2027-05-16 | 17464 | 36968 | 16747 | 5178.2 | 1509.69 | 8207.2883 | 1852.0215
2027-05-23 | 18149 | 36968 | 15851 | 5178.2 | 1502.17 | 8140.1967 | 1030.8935
2027-05-30 | 18209 | 36968 | 15570 | 5178.2 | 794.98 | 8035.024 | 1562.2054
2027-06-06 | 19060 | 36968 | 12132 | 2544.2 | 794.98 | 8719.0171 | 73.9666
2027-06-13 | 19550 | 36968 | 12163 | 2549.2 | 989.51 | 8541.6132 | 82.3475
2027-06-20 | 20597 | 36968 | 12237 | 2549.2 | 989.51 | 8630.0814 | 68.689
2027-06-27 | 21474 | 36968 | 12260 | 2549.2 | 989.51 | 8667.3085 | 53.7981
2027-07-04 | 21491 | 36968 | 12026 | 2549.2 | 989.51 | 8462.8383 | 24.8229
2027-07-11 | 22237 | 36968 | 12511 | 2618.2 | 1106.51 | 8736.319 | 49.8985
2027-07-18 | 22449 | 36968 | 12547 | 2618.2 | 1106.51 | 8822.3214 | 0
2027-07-25 | 22460 | 36968 | 12730 | 2618.2 | 1106.51 | 9005.7008 | 0
2027-08-01 | 22313 | 36968 | 12609 | 2618.2 | 1106.51 | 8884.6687 | 0
2027-08-08 | 21861 | 36968 | 12854 | 2645.2 | 1052.38 | 9156.0266 | 0
2027-08-15 | 21820 | 36968 | 13314 | 2645.2 | 1052.38 | 9616.5257 | 0
2027-08-22 | 21614 | 36968 | 13255 | 2645.2 | 1052.38 | 9557.392 | 0
2027-08-29 | 21634 | 36968 | 13226 | 2645.2 | 1052.38 | 9528.8983 | 0
2027-09-05 | 21311 | 36968 | 12775 | 2619.2 | 898.28 | 9257.0225 | 0
2027-09-12 | 20204 | 36968 | 12952 | 2619.2 | 1078.28 | 9254.3632 | 0
2027-09-19 | 19731 | 36968 | 12744 | 2619.2 | 1078.28 | 9046.2025 | 0
2027-09-26 | 19265 | 36968 | 14127 | 3434.2 | 1603.28 | 9089.1343 | 0
2027-10-03 | 19178 | 36968 | 14633 | 3424.2 | 1933.61 | 9275.4788 | 0
2027-10-10 | 18408 | 36968 | 15381 | 3424.2 | 3680.71 | 8275.8828 | 0
2027-10-17 | 18398 | 36968 | 14218 | 3424.2 | 2461.85 | 8331.4792 | 0
2027-10-24 | 18628 | 36968 | 14896 | 3424.2 | 3021.17 | 8451.1163 | 0
2027-10-31 | 18910 | 36968 | 13536 | 3424.2 | 2081.53 | 8030.3579 | 0
2027-11-07 | 19461 | 36968 | 12058 | 3414.2 | 1189.58 | 7453.7845 | 0
2027-11-14 | 19918 | 36968 | 12856 | 2591.2 | 2150.62 | 7716.2104 | 398.3131
2027-11-21 | 20490 | 36968 | 11737 | 2591.2 | 1282.36 | 7746.8336 | 116.299
2027-11-28 | 21035 | 36968 | 11417 | 2591.2 | 1282.36 | 7543.7799 | 0
2027-12-05 | 21394 | 36968 | 11247 | 2591.2 | 1169.58 | 7486.2085 | 0
2027-12-12 | 21756 | 36968 | 10948 | 2583.2 | 894.04 | 7390.53 | 80.4979
2027-12-19 | 21991 | 36968 | 10678 | 2583.2 | 894.04 | 7157.1418 | 43.3255
2027-12-26 | 22011 | 36968 | 10464 | 2583.2 | 894.04 | 6920.8186 | 65.4866
2028-01-02 | 21760 | 36968 | 10401 | 2583.2 | 894.04 | 6920.8186 | 3.069
Back to main menu

## Table 3.10
Back to main menu
Table 3.10: Reductions by Fuel Type: Expected Weather, Planned Scenario
Week | Ontario | Total Internal | Total Reductions | Nuclear | Biomass, Oil & Gas | Hydro, Wind, Solar & Storage | Total Bottled
Ending | Demand | Resources | in Resources | Reductions | Reductions | Capacity Unavailable | Generation
Day | MW | MW | MW | MW | MW | MW | MW
2026-07-05 | 21396 | 39134.29 | 13326 | 2665.2 | 1928.92 | 8395.9694 | 335.6089
2026-07-12 | 22069 | 39134.29 | 12587 | 1887.2 | 2171.83 | 8519.2885 | 8.7378
2026-07-19 | 22267 | 39134.29 | 11753 | 1887.2 | 1195.76 | 8670.2312 | 0
2026-07-26 | 22247 | 39134.29 | 11722 | 1887.2 | 1233.6 | 8600.7423 | 0
2026-08-02 | 22050 | 39134.29 | 11737 | 1887.2 | 1195.76 | 8630.5573 | 23.0369
2026-08-09 | 21575 | 39134.29 | 11909 | 1922.2 | 1130.18 | 8856.618 | 0
2026-08-16 | 21548 | 39134.29 | 12114 | 1922.2 | 1130.18 | 9061.4709 | 0
2026-08-23 | 21386 | 39134.29 | 12371 | 1922.2 | 1130.18 | 9318.6817 | 0
2026-08-30 | 21371 | 39134.29 | 12548 | 1922.2 | 1130.18 | 9495.94 | 0
2026-09-06 | 20980 | 39134.29 | 12467 | 1922.2 | 1130.18 | 9414.6958 | 0
2026-09-13 | 19832 | 39134.29 | 12443 | 1891.2 | 1096.31 | 9176.5869 | 278.8271
2026-09-20 | 19390 | 39134.29 | 12688 | 1891.2 | 1188.12 | 9233.3305 | 374.9547
2026-09-27 | 18950 | 39134.29 | 15250 | 4545.2 | 1636.08 | 9068.7343 | 0
2026-10-04 | 18599 | 37176.29 | 15438 | 3509.2 | 2787.75 | 9024.7529 | 116.1825
2026-10-11 | 18092 | 37176.29 | 15847 | 2678.2 | 5097.44 | 8071.0911 | 0
2026-10-18 | 18093 | 37176.29 | 14225 | 2678.2 | 2947.09 | 8006.5769 | 593.1944
2026-10-25 | 18352 | 37176.29 | 15314 | 2678.2 | 3914.16 | 8220.8946 | 500.2909
2026-11-01 | 18640 | 37176.29 | 14932 | 2678.2 | 3589.42 | 8274.9624 | 389.1155
2026-11-08 | 19214 | 37176.29 | 13378 | 3487.2 | 1956.52 | 7885.6237 | 48.7321
2026-11-15 | 19724 | 37176.29 | 12952 | 3487.2 | 1926.2 | 7538.3098 | 0
2026-11-22 | 20287 | 37176.29 | 12178 | 2670.2 | 1217.28 | 7647.5317 | 643.369
2026-11-29 | 20799 | 37176.29 | 11763 | 2670.2 | 1217.28 | 7647.5317 | 228.2524
2026-12-06 | 21194 | 37176.29 | 11595 | 2670.2 | 1217.28 | 7389.6395 | 317.7308
2026-12-13 | 21511 | 37176.29 | 11020 | 2662.2 | 928.74 | 7222.5994 | 206.1113
2026-12-20 | 21726 | 37176.29 | 10990 | 2662.2 | 928.74 | 7262.3388 | 136.5911
2026-12-27 | 21134 | 37176.29 | 10978 | 2662.2 | 928.74 | 6968.2456 | 418.8247
2027-01-03 | 21107 | 37176.29 | 10028 | 1784.2 | 928.74 | 6911.5815 | 403.1772
2027-01-10 | 21990 | 37176.29 | 11135 | 2584.2 | 1393.18 | 6924.2367 | 232.9052
2027-01-17 | 21880 | 37176.29 | 11950 | 3402.2 | 1393.18 | 7140.1205 | 14.5002
2027-01-24 | 21944 | 37176.29 | 11999 | 3402.2 | 1393.18 | 7157.8143 | 46.1651
2027-01-31 | 21930 | 37176.29 | 12044 | 3402.2 | 1437.18 | 7204.6884 | 0
2027-02-07 | 21426 | 37176.29 | 12265 | 3402.2 | 1590.76 | 7236.4379 | 35.5463
2027-02-14 | 21428 | 37176.29 | 12115 | 3402.2 | 1410.76 | 7301.6558 | 0
2027-02-21 | 21140 | 37176.29 | 12035 | 3402.2 | 1410.76 | 7152.8974 | 68.8136
2027-02-28 | 20986 | 37176.29 | 12402 | 3402.2 | 1410.76 | 7176.6505 | 412.5075
2027-03-07 | 20459 | 37176.29 | 12231 | 3397.2 | 970.42 | 7368.6876 | 494.8481
2027-03-14 | 20022 | 37176.29 | 12165 | 3397.2 | 970.42 | 7289.7692 | 508.0836
2027-03-21 | 19506 | 37176.29 | 12027 | 2564.2 | 970.42 | 7496.227 | 995.9125
2027-03-28 | 19083 | 37176.29 | 12003 | 2564.2 | 970.42 | 7242.4725 | 1226.1839
2027-04-04 | 18650 | 37176.29 | 14709 | 2564.2 | 3678.31 | 8056.0636 | 410.867
2027-04-11 | 18304 | 37176.29 | 15124 | 2545.2 | 3938.89 | 7929.451 | 709.9705
2027-04-18 | 17970 | 37176.29 | 18240 | 5179.2 | 3866.87 | 8233.4347 | 960.715
2027-04-25 | 17717 | 37176.29 | 18487 | 5179.2 | 3866.87 | 8067.8917 | 1373.4596
2027-05-02 | 17533 | 37176.29 | 16904 | 5179.2 | 1928.92 | 7783.8001 | 2012.3068
2027-05-09 | 17474 | 37176.29 | 17296 | 5178.2 | 1862.64 | 8214.2703 | 2041.0509
2027-05-16 | 17560 | 37176.29 | 16833 | 5178.2 | 1565.14 | 8237.9683 | 1852.0487
2027-05-23 | 18246 | 37176.29 | 15865 | 5178.2 | 1557.62 | 8170.8767 | 958.0464
2027-05-30 | 18305 | 37176.29 | 15657 | 5178.2 | 850.43 | 8065.704 | 1562.2876
2027-06-06 | 19165 | 37186.27 | 12221 | 2544.2 | 850.43 | 8752.6911 | 73.9789
2027-06-13 | 19655 | 37186.27 | 12252 | 2549.2 | 1044.96 | 8575.2872 | 82.4118
2027-06-20 | 20701 | 37186.27 | 12327 | 2549.2 | 1044.96 | 8663.7554 | 68.7616
2027-06-27 | 21578 | 37186.27 | 12349 | 2549.2 | 1044.96 | 8700.9825 | 53.8685
2027-07-04 | 21623 | 37186.27 | 12142 | 2549.2 | 1044.96 | 8496.5123 | 51.4227
2027-07-11 | 22410 | 37186.27 | 12600 | 2618.2 | 1161.96 | 8769.993 | 49.9497
2027-07-18 | 22621 | 37186.27 | 12636 | 2618.2 | 1161.96 | 8855.9954 | 0
2027-07-25 | 22632 | 37186.27 | 12820 | 2618.2 | 1161.96 | 9039.3748 | 0
2027-08-01 | 22486 | 37186.27 | 12699 | 2618.2 | 1161.96 | 8918.3427 | 0
2027-08-08 | 22057 | 37186.27 | 12943 | 2645.2 | 1107.83 | 9189.7006 | 0
2027-08-15 | 22017 | 37186.27 | 13403 | 2645.2 | 1107.83 | 9650.1997 | 0
2027-08-22 | 21811 | 37186.27 | 13344 | 2645.2 | 1107.83 | 9591.066 | 0
2027-08-29 | 21831 | 37186.27 | 13316 | 2645.2 | 1107.83 | 9562.5723 | 0
2027-09-05 | 21527 | 37186.27 | 12864 | 2619.2 | 953.73 | 9290.6965 | 0
2027-09-12 | 20430 | 37186.27 | 13041 | 2619.2 | 1133.73 | 9288.0372 | 0
2027-09-19 | 19960 | 37186.27 | 12833 | 2619.2 | 1133.73 | 9079.8765 | 0
2027-09-26 | 19494 | 37186.27 | 14216 | 3434.2 | 1658.73 | 9122.8083 | 0
2027-10-03 | 19408 | 37186.27 | 14722 | 3424.2 | 1989.06 | 9309.1528 | 0
2027-10-10 | 18649 | 37186.27 | 15470 | 3424.2 | 3736.16 | 8309.5568 | 0
2027-10-17 | 18639 | 37186.27 | 14307 | 3424.2 | 2517.3 | 8365.1532 | 0
2027-10-24 | 18869 | 37186.27 | 14986 | 3424.2 | 3076.62 | 8484.7903 | 0
2027-10-31 | 19151 | 37186.27 | 13625 | 3424.2 | 2136.98 | 8064.0319 | 0
2027-11-07 | 19734 | 37186.27 | 12153 | 3414.2 | 1228.48 | 7509.9145 | 0
2027-11-14 | 20190 | 37186.27 | 12951 | 2591.2 | 2189.52 | 7772.3404 | 398.3131
2027-11-21 | 20763 | 37186.27 | 11832 | 2591.2 | 1321.26 | 7802.9636 | 116.299
2027-11-28 | 21308 | 37186.27 | 11512 | 2591.2 | 1321.26 | 7599.9099 | 0
2027-12-05 | 21681 | 37186.27 | 11342 | 2591.2 | 1208.48 | 7542.3385 | 0
2027-12-12 | 22049 | 37186.27 | 11043 | 2583.2 | 932.94 | 7446.66 | 80.4979
2027-12-19 | 22284 | 37186.27 | 10773 | 2583.2 | 932.94 | 7213.2718 | 43.3255
2027-12-26 | 22304 | 37186.27 | 10559 | 2583.2 | 932.94 | 6976.9486 | 65.4866
2028-01-02 | 22056 | 37186.27 | 10496 | 2583.2 | 932.94 | 6976.9486 | 3.069
Back to main menu

## Table 3.11
Back to main menu
Table 3.11: Firm Scenario - Expected Weather: Ontario Monthly Energy Production by Fuel Type
Month | Year | Nuclear (GWh) | Hydro (GWh) | Gas & Oil (GWh) | Wind (GWh) | Biofuel (GWh) | Storage (GWh) | Other (GWh) | Total (GWh)
Jul | 2026 | 7524.99 | 2844.08 | 1829.31 | 545.59 | 37.76 | 3.15 | 65.81 | 12850.69
Aug | 2026 | 7534.77 | 2594.22 | 1771.18 | 543.56 | 39.79 | 0.85 | 60.2 | 12544.57
Sep | 2026 | 6729.25 | 2416.36 | 1441.54 | 647.37 | 34.39 | 6.27 | 51.24 | 11326.42
Oct | 2026 | 5481.24 | 2611.14 | 1947.3 | 1267.78 | 19.11 | 32.92 | 42.48 | 11401.97
Nov | 2026 | 5050.37 | 2808.45 | 2682.43 | 1357.78 | 19.43 | 23.53 | 30.45 | 11972.44
Dec | 2026 | 5471.78 | 3021.2 | 3252.19 | 1430.08 | 50.58 | 17.6 | 17.54 | 13260.97
Jan | 2027 | 4898.04 | 3038.77 | 4259.87 | 1480.23 | 84.71 | 56.76 | 32.31 | 13850.69
Feb | 2027 | 4341.89 | 2823.49 | 3727.11 | 1235.08 | 46.15 | 42.82 | 44.25 | 12260.79
Mar | 2027 | 5170.87 | 3015.05 | 3096.08 | 1237.59 | 26.37 | 33.43 | 59.94 | 12639.33
Apr | 2027 | 4092.46 | 2924.99 | 2859.97 | 1212.1 | 23.63 | 33.66 | 67.5 | 11214.31
May | 2027 | 3941.5 | 3183.62 | 3010.06 | 956.38 | 26.14 | 31.69 | 69.77 | 11219.16
Jun | 2027 | 5185.86 | 2979.38 | 2862.77 | 728.21 | 24.06 | 26.71 | 75.44 | 11882.43
Jul | 2027 | 5304.88 | 2751.86 | 4143.37 | 603.62 | 36.92 | 59.89 | 133.51 | 13034.05
Aug | 2027 | 5308.51 | 2460.09 | 4384.5 | 634.25 | 44.51 | 65.64 | 86.18 | 12983.68
Sep | 2027 | 5008.9 | 2376.22 | 3348.11 | 826.99 | 28.23 | 49.6 | 61.47 | 11699.52
Oct | 2027 | 4852.67 | 2486.01 | 3005.04 | 1297.61 | 20.56 | 47.56 | 42.81 | 11752.26
Nov | 2027 | 5010.98 | 2739.79 | 3621.62 | 1361.73 | 23.9 | 38.05 | 30.46 | 12826.53
Dec | 2027 | 5057.32 | 3003.49 | 4543.53 | 1430.09 | 66.51 | 40.87 | 18.31 | 14160.12
Back to main menu

## Table 3.12
Back to main menu
Table 3.12: Planned Scenario - Expected Weather: Ontario Monthly Energy Production by Fuel Type
Month | Year | Nuclear (GWh) | Hydro (GWh) | Gas & Oil (GWh) | Wind (GWh) | Biofuel (GWh) | Storage (GWh) | Other (GWh) | Total (GWh)
2026-07-01 | 2026 | 7525 | 2844.08 | 1829.24 | 545.52 | 37.75 | 3.14 | 65.94 | 12850.67
2026-08-01 | 2026 | 7536.84 | 2594.22 | 1769.3 | 543.35 | 39.78 | 0.85 | 60.22 | 12544.56
2026-09-01 | 2026 | 6729.22 | 2416.34 | 1441.46 | 647.47 | 34.39 | 6.15 | 51.25 | 11326.28
2026-10-01 | 2026 | 5481.24 | 2611.14 | 1947.3 | 1267.54 | 19.11 | 31.6 | 42.51 | 11400.44
2026-11-01 | 2026 | 5050.37 | 2808.45 | 2707.83 | 1358.29 | 19.43 | 22.35 | 30.45 | 11997.17
2026-12-01 | 2026 | 5471.78 | 3021.2 | 3283.34 | 1430.08 | 50.57 | 16.11 | 17.46 | 13290.54
2027-01-01 | 2027 | 4898.04 | 3038.77 | 4294.45 | 1480.23 | 82.82 | 55.17 | 31.17 | 13880.65
2027-02-01 | 2027 | 4341.89 | 2823.5 | 3765.34 | 1235.09 | 45.88 | 41.61 | 44.02 | 12297.33
2027-03-01 | 2027 | 5170.87 | 3015.06 | 3140.69 | 1238.11 | 26.18 | 32.23 | 59.94 | 12683.08
2027-04-01 | 2027 | 4092.38 | 2925.01 | 2902.63 | 1221.79 | 23.63 | 33.59 | 67.67 | 11266.7
2027-05-01 | 2027 | 3941.5 | 3183.65 | 3078.26 | 963.25 | 24.34 | 32.31 | 69.81 | 11293.12
2027-06-01 | 2027 | 5185.86 | 2979.39 | 2938.94 | 729.8 | 24.07 | 28.18 | 75.32 | 11961.56
Jul | 2027 | 5304.88 | 2752.01 | 4273.72 | 603.69 | 38.73 | 63.84 | 134.7 | 13171.57
Aug | 2027 | 5308.51 | 2460.09 | 4529.45 | 634.25 | 46.38 | 69.83 | 88.58 | 13137.09
Sep | 2027 | 5008.9 | 2376.22 | 3512.06 | 827.71 | 29.6 | 51.25 | 62.52 | 11868.26
Oct | 2027 | 4852.67 | 2486.01 | 3184.73 | 1299.29 | 20.56 | 49.58 | 43.13 | 11935.97
Nov | 2027 | 5010.98 | 2739.79 | 3820.29 | 1361.84 | 24.03 | 38.35 | 30.46 | 13025.74
Dec | 2027 | 5057.32 | 3003.49 | 4758.2 | 1430.09 | 70.64 | 40.72 | 19.21 | 14379.67
Back to main menu

## Figure 3.1
Back to main menu
Figure 3.1: Reserve above Requirement
Back to main menu

## Table 4.1
Back to main menu
Table 4.1: Transmission Projects
Zone | ID | Transmitter | Description | Proposed I/S Date
Bruce | N/A | Hydro-One | Tara Battery Storage 230kV LT1 Connection | 2027 Q2
Bruce | 2021-698 | Hydro-One | Bruce A Transformer Station 500 kV Switchyard Rep | 2027 Q4
East | 2024-800 | Hydro-One | Connect Skyview BESS | 2026 Q4
East | 2023-758 | Hydro-One | Belleville TS: Build 75/125 MVA, 230/44 kV DESN | 2026 Q4
East | 2023-761 | Hydro-One | Gardiner TS: T1/T2 PCT Component Replacement | 2026 Q4
East | 2020-EX1089 | Hydro-One | Lennox TS BULK: ABCB component replacement | 2026 Q4
East | N/A | Hydro-One | Picton TS - T1/T2 Transformer Replacement | 2026 Q4
East | 2024-774 | Hydro-One | Connect Napanee Generating Station Expansion | 2027 Q1
East | N/A | Hydro-One | Lennox TS - Replace 500kV Breaker KL526 | 2027 Q1
East | 2024-793 | Hydro-One | Connect Trailroad BESS | 2027 Q2
East | 2024-799 | Hydro-One | Connect Fitzroy BESS | 2027 Q2
East | N/A | Hydro-One | Kingston area: Build new DESN | 2027 Q4
East | 2026-EX1314 | Hydro-One | D6, Des Joachims TS X Petawawa DS, Tx Line Refur | 2027 Q4
Essa | 2016-EX886 | Hydro-One | Orillia TS: T2 Transformer Replacement | 2026 Q4
Essa | 2026-868 | Hydro-One | Connect New Chalk River CTS | 2027 Q4
Niagara | 2016-EX862 | Hydro-One | Beck 1 SS 115kV ABCB Replacement | 2026 Q3
Niagara | N/A | Hydro-One | Temporary A6C 115kV Line Tap | 2026 Q4
Niagara | N/A | Hydro-One | Q28A (Beck2 X Abitibi Jct): 230kV Line Section Upr | 2026 Q4
Niagara | 2024-791 | Hydro-One | Spring Creek MTS Tap | 2027 Q3
Northeast | 2020-EX115 | Hydro-One | HOSSM Tx Lines Sault #3 Line Refurbishment | 2026 Q3
Northeast | 2023-EX1230 | Hydro-One | HOSSM Thirdline T2 Replacement | 2026 Q3
Northeast | 2023-749 | Hydro-One | HOSSM Hollingsworth Circuit - Connection of Hollin | 2026 Q4
Northeast | 2020-EX1106 | Hydro-One | Porcupine TS: Component Replacement | 2026 Q4
Northeast | 2022-EX1196 | Hydro-One | Elliot Lake TS: Component Replacement | 2026 Q4
Northeast | 2020-676 | Hydro-One | Wikwemikong Pellet Plant Connection | 2026 Q4
Northeast | N/A | Hydro-One | A4H/A5H, Tunis JCT-Fournier JCT, Tx Line Refurb. | 2027 Q1
Northeast | 2021-707 | Hydro-One | CNC Crawford Mine Connection | 2027 Q2
Northeast | 2021-704 | Hydro-One | HOSSM Third Line TS PUC 230kV Connections | 2027 Q2
Northeast | 2020-EX1114 | Hydro-One | Kirkland Lake TS: Component Replacement | 2027 Q3
Northeast | 2020-EX1114 | Hydro-One | K1/K2, Krklnd Lk- A. Barrick, Tx Line Refurb (Cu) | 2027 Q3
Northeast | 2025-860 | Hydro-One | Porcupine TS: SVC Refurbishment | 2027 Q4
Northwest | N/A | Hydro-One | Mackenzie TS: 230kV Brownfield Refurb | 2026 Q4
Northwest | N/A | Hydro-One | 115kV E2R GBR CTS Connection | 2027 Q1
Northwest | N/A | Hydro-One | Ear Falls TS, EOL T5, Asset Replacement Project | 2027 Q4
Northwest | 2022-732 | Hydro-One | Waasigan Transmission Line - Development | 2027 Q4
Northwest | 2022-732 | Hydro-One | Waasigan Transmission Line Project - Station Work | 2027 Q4
Northwest | 2021-EX1156 | Hydro-One | Rabbit Lake SS: Component Replacement | 2027 Q4
Ottawa | N/A | Hydro-One | Longueuil TS: T3/T4 Replacement | 2026 Q4
Ottawa | 2024-EX1280 | Hydro-One | Russell TS - T1/T2 & Comp Replacement | 2027 Q2
Ottawa | 2023-EX1243 | Hydro-One | Merivale TS Add 230/115kV Autotransformers | 2027 Q4
Southwest | 2024-776 | Hydro-One | Elora BESS LP1 Connection | 2026 Q3
Southwest | N/A | Hydro-One | B5/6C, BurlingtonTS X WestoverCTS, Tx Line Refurb. | 2026 Q3
Southwest | 2018-EX980 | Hydro-One | Middleport ABCB Replacement Project | 2026 Q4
Southwest | 2024-780 | Hydro-One | Oxford Battery Energy Storage Project | 2026 Q4
Southwest | 2024-EX1285 | Hydro-One | M31W: Reinforce Buchanan x St Thomas Line Tap Point | 2027 Q1
Southwest | 2022-EX1217 | Hydro-One | Nanticoke TS; ABCB Project | 2027 Q1
Southwest | N/A | Hydro-One | Preston TS: T3, T4 & Component Replacement | 2027 Q2
Southwest | 2020-EX1142 | Hydro-One | Seaforth TS: T1, T2, T5, T6, PCT & Component Repl. | 2027 Q3
Southwest | 2025-862 | Hydro-One | GrandBridge Energy Inc. Municipal Transformer Stat | 2027 Q4
Southwest | 2024-818 | Hydro-One | Palermo TS: T3, T4 Replacement & Station Expansion | 2027 Q4
Southwest | N/A | Hydro-One | Build 230kV Switching Station Q24/29HM | 2027 Q4
Toronto | N/A | Hydro-One | Clarington TS: Install Surge Capacitors | 2026 Q3
Toronto | 2019-EX1034 | Hydro-One | Claireville TS: Component Replacements | 2026 Q3
Toronto | N/A | Hydro-One | Scarboro TS:T23 & Component Replacements | 2026 Q4
Toronto | 2020-EX1104 | Hydro-One | HV UG Cable - Replace C5E/C7E | 2026 Q4
Toronto | 2016-EX869 | Hydro-One | Main TS: T3, T4 & Component Replacement | 2026 Q4
Toronto | N/A | Hydro-One | Malvern T3 EOL Replacement | 2027 Q1
Toronto | 2022-738 | Hydro-One | Connect Darlington SMR GS | 2027 Q1
Toronto | 2019-EX1083 | Hydro-One | Strachan TS: T14 & Component Replacement | 2027 Q2
Toronto | 2022-735 | Hydro-One | Vaughan MTS6 –Provide 230 kV Connection to new TS | 2027 Q3
Toronto | N/A | Hydro-One | Bowmanville 500kV Breaker Protection Replacement | 2027 Q4
Toronto | N/A | Hydro-One | Charles TS: T3, T4 & Component Replacements | 2027 Q4
Toronto | 2023-EX1253 | Hydro-One | Cherrywood TS 230kV BULK; ABCB Rep Phase 3-2 | 2027 Q4
Toronto | 2024-EX1275 | Hydro-One | Claireville TS: T13 & Component Replacements | 2027 Q4
Toronto | 2022-738 | Hydro-One | Holt Switching Station SMR Connection | 2027 Q4
Toronto | 2018-637 | Hydro-One | Richview Manby Transmission Reinforcement - Line | 2027 Q4
West | 2022-718 | Hydro-One | Connect East Windsor (Expansion) L.P. ELT1 | 2026 Q4
West | N/A | Hydro-One | St. Andrews TS: T3, T4 & Switchyard Refurbishment | 2026 Q4
West | 2021-EX1166 | Hydro-One | Lauzon TS: T6, T5 & Component Replacement | 2026 Q4
West | 2023-766 | Hydro-One | Centennial TS: Project Connect PowerCo | 2027 Q3
Back to main menu
Back to main menu

## Table 4.2
Back to main menu
Table 4.2: Interface Limits with All Elements in Service
Interface | Limit (MW) | Notes
BLIP | 3000
NBLIP | 1800
QFW | 2000 | ****
FABCW | 7500 | *
FETT | 5000 / 3500 | **
CLAN | 2000
FIO | 2900
SLW | 1350
FN | 1500 | ***
FS | 1750
P502X South | 1000
EWTE | 500
EWTW | 500
(*) FABCW limit varies according to BLIP flow.
For each recognized contingency, separate voltage and stability limit ranges are defined.
Published limit range based on the most restrictive contigency under optimal
Bruce System Conditions in SCO-South Tab1.
(**) FETT is a fixed boundary condition limit. FETT interface changes from 5000 MW to 3500 MW only during the Darlington VBO.
(***) FN is a fixed boundary condition limit.
(****) With Q26M and Q35M being 3-ended circuits (connected to Middleport TS), the
QFW limit is improved to the boundary limit of 2000 MW.
Back to main menu

## Table 4.3
Back to main menu
Table 4.3: Interconnection Flow Limits
Interconnection | Limit - Flows Out of Ontario (MW) |  | Limit - Flows Into Ontario (MW)
Manitoba – Summer* | 246 | 255 | 260 | (3,6)325
Manitoba – Winter* | 300 | (3) | 300 | (3,6)
Minnesota | 150 |  | 100 | (3)
Quebec North (Northeast) – Summer* | 105 |  | 65
D4Z | 0 | (5) | 65
H4Z | 105 | (5) | 0
Quebec North (Northeast)– Winter* | 105 |  | 85
D4Z | 0 |  | 85
H4Z | 105 |  | 0
Quebec South (Ottawa) – Summer* | 1570 |  | 1865
X2Y | 0 |  | 65
Q4C | 120 |  | not of concern
P33C | 0 | 60 | 300
D5A | 200 |  | 250
H9A | 0 |  | 0
HVDC | 1250 |  | 1250
Quebec South (Ottawa) – Winter* | 1590 |  | 1865
X2Y | 0 |  | 65
Q4C | 140 |  | not of concern
P33C | 0 |  | 300
D5A | 200 |  | 250
H9A | 0 |  | 0
HVDC | 1250 |  | 1250
Quebec South (East) – Summer* | 470 |  | 400
B31L + B5D | 470 |  | 400
Quebec South (East) – Winter* | 470 |  | 400
B31L + B5D | 470 |  | 400
New York St. Lawrence – Summer* | 300 |  | 300
New York St. Lawrence – Winter* | 300 |  | 300
New York Niagara – Summer* | 1500 | (1) | 1200 | (1,7)
Emergency Transfer Limit - Summer* | 2160 | (1) | 1860 | (1,7)
New York Niagara – Winter* | 1800 | (1) | 1600 | (1,7)
Emergency Transfer Limit - Winter* | 2200 | (1) | 2200 | (1,7)
Michigan – Summer* | 1650 | (2,3) | 1550 | (2,3)
Emergency Transfer Limit - Summer* | N/A | (2,3) | N/A | (2,3)
Michigan – Winter* | 1650 | (2,3) | 1700 | (2,3)
Emergency Transfer Limit - Winter* | N/A | (2,3) | N/A | (2,3)
* Summer Limits apply from May 1 to October 31. Winter Limits apply from November 1 to April 30.
(1) Flow limits depend on generation dispatch outside Ontario.
(2) Normal limits are based on LT ratings and phase shifters bypassed and Emergency limits are based on
ST ratings and phase shifters regulating. Flow limits vary depending on the generation dispatch
within Ontario.
(3) For real time operation of the interconnection, limits are based on ambient conditions.
(5) Limit based on 0 to 4 km/h wind speed and 30˚C ambient temperature.
(6) Flows into Ontario include flows on circuit SK1.
(7) Flow limits into Ontario are shown without considering QFW transmission constraints within Ontario.
Back to main menu

## Table 4.4
Back to main menu
Table 4.4: Bruce Zone Transmission Outages
Planned Start | Planned End | Duration (Days) | Station | Equipment Name | Outage ID | Max Recall | Major Transmission Interface Impacted | Reduction in Limit
2027-02-28 10:00 | 2027-03-11 18:00 | 11 | BRUCE A TS | K1K2, K1L24, K1_BUS, K1L22 | 1-00309650 Rev. #2 | Non-recallable | No Impact | #N/A
2027-06-20 10:00 | 2027-06-25 18:00 | 5 | BRUCE A TS | K1K2, K1L24, K1_BUS, K1L22 | 1-00312390 Rev. #1 | Non-recallable | No Impact | #N/A
2026-06-05 09:00 | 2026-07-27 06:00 | 51 | BRUCE A TS | OLDAL562, HT28L562, L560L569, OLDT3E, OLDT3T28, OLD21-B560V, OLD21-B562E, OLD21-B569B, HT28_BUS, HT3_BUS, OLDAL560, OLDEL569, OLDL560_BUS, OLDL569_BUS, OLDL562_BUS | 1-00312746 Rev. #1 | Non-recallable | FABCW NBLIP BLIP | 0 0 0
2026-06-15 07:00 | 2026-07-03 16:00 | 18 | EVERGREEN SS | L562L564 | 1-00310106 Rev. #2 | 10 Hour(s) | No Impact | #N/A
2026-07-20 06:15 | 2026-08-28 16:00 | 39 | BRUCE B SS, MILTON SS, BRUCE JCT, WILLOW CREEK JCT | B561M.BBXBR, B561M.BRXWI, B561M.WIXMI, 40-B561M, L501L563, 29-B561M | 1-00293589 Rev. #9 | 4 Hour(s) | FABCW NBLIP BLIP | 1750 300 300
2026-08-30 08:00 | 2026-09-11 16:00 | 12 | WILLOW CREEK JCT, MILTON SS, BRUCE B SS, BRUCE JCT | B501M.BBXBJ, B501M.BJXWJ, B501M.WJXMI, 40-B501M, 29-B501M | 1-00293593 Rev. #9 | 4 Hour(s) | FABCW NBLIP BLIP | 1750 300 300
2026-08-30 08:00 | 2026-09-11 16:00 | 12 | WILLOW CREEK JCT, MILTON SS, BRUCE B SS, BRUCE JCT | B501M.BBXBJ, B501M.BJXWJ, B501M.WJXMI, HL501, L501L570, 40-B501M, 29-B501M | 1-00295573 Rev. #10 | 4 Hour(s) | FABCW NBLIP BLIP | 1750 300 300
2026-06-05 09:00 | 2026-07-27 06:00 | 51 | BRUCE A TS | OLDAL562, HT28L562, L560L569, OLDT3E, OLDT3T28, OLD21-B560V, OLD21-B562E, OLD21-B569B, HT28_BUS, HT3_BUS, OLDAL560, OLDEL569, OLDL560_BUS, OLDL569_BUS, OLDL562_BUS | 1-00312746 Rev. #1 | Non-recallable | FABCW NBLIP BLIP | 0 0 0
2026-08-30 08:00 | 2026-09-11 16:00 | 12 | WILLOW CREEK JCT, MILTON SS, BRUCE B SS, BRUCE JCT | B501M.BBXBJ, B501M.BJXWJ, B501M.WJXMI, 40-B501M, 29-B501M | 1-00293593 Rev. #9 | 4 Hour(s) | FABCW NBLIP BLIP | 1750 300 300
2026-08-30 08:00 | 2026-09-11 16:00 | 12 | WILLOW CREEK JCT, MILTON SS, BRUCE B SS, BRUCE JCT | B501M.BBXBJ, B501M.BJXWJ, B501M.WJXMI, HL501, L501L570, 40-B501M, 29-B501M | 1-00295573 Rev. #10 | 4 Hour(s) | FABCW NBLIP BLIP | 1750 300 300
2026-06-05 09:00 | 2026-07-27 06:00 | 51 | BRUCE A TS | OLDAL562, HT28L562, L560L569, OLDT3E, OLDT3T28, OLD21-B560V, OLD21-B562E, OLD21-B569B, HT28_BUS, HT3_BUS, OLDAL560, OLDEL569, OLDL560_BUS, OLDL569_BUS, OLDL562_BUS | 1-00312746 Rev. #1 | Non-recallable | FABCW NBLIP BLIP | 0 0 0
2026-07-20 06:15 | 2026-08-28 16:00 | 39 | BRUCE B SS, MILTON SS, BRUCE JCT, WILLOW CREEK JCT | B561M.BBXBR, B561M.BRXWI, B561M.WIXMI, 40-B561M, L501L563, 29-B561M | 1-00293589 Rev. #9 | 4 Hour(s) | FABCW NBLIP BLIP | 1750 300 300
2025-11-12 11:00 | 2026-11-23 07:00 | 375 | BRUCE A TS | T27-WT27 | 1-00283777 Rev. #14 | Non-recallable | FABCW NBLIP BLIP | 150 0 0
2026-01-27 09:00 | 2026-11-23 07:00 | 299 | BRUCE A TS | T27-WT27 | 1-00301875 Rev. #8 | Non-recallable | FABCW NBLIP BLIP | 150 0 0
2026-07-19 12:15 | 2026-10-02 13:00 | 75 | BRUCE B SS | P-P5 | 1-00295508 Rev. #8 | Non-recallable | No Impact | #N/A
2026-09-21 07:00 | 2026-09-28 | 6 | BRUCE A TS | HT1_BUS, HT1L22, HT1L20 | 1-00295500 Rev. #10 | 4 Hour(s) | No Impact | #N/A
2027-02-23 07:00 | 2027-03-04 18:00 | 9 | BRUCE B SS | P-P5 | 1-00308922 Rev. #1 | 6 Hour(s) | No Impact | #N/A
2027-09-20 07:00 | 2027-09-30 19:00 | 10 | BRUCE B SS | P-P7 | 1-00252425 Rev. #3 | 6 Hour(s) | No Impact | #N/A
Back to main menu

## Table 4.5
Back to main menu
Table 4.5: East Zone Transmission Outages
Planned Start | Planned End | Duration (Days) | Station | Equipment Name | Outage ID | Max Recall | Major Transmission Interface Impacted | Reduction in Limit (MW)
2026-09-28 08:00 | 2026-10-09 16:00 | 11 | ST. LAWRENCE TS, MASSENA JCT | L33P.ROXLA, 49-L33P | 1-00275118 Rev. #9 | 4 Hour(s) | No Impact | #N/A
2026-10-29 08:00 | 2026-11-13 16:00 | 15 | ST. LAWRENCE TS, MASSENA JCT | L34P.ROXLA, 49-L34P | 1-00275119 Rev. #10 | 4 Hour(s) | No Impact | #N/A
2027-05-31 03:30 | 2027-06-11 16:00 | 11 | HAWTHORNE TS, MASSON GS, IPB MASSON JCT, ST. ISIDORE TS, ORLEANS JCT 2, ORLEANS TS, CUMBERLAND JCT, LONGUEUIL JCT, LONGUEUIL TS | D5A.CUXGA, D5A.CUXIS, D5A.CUXO2, D5A.HAXO2, D5A.IPXMA, D5A.LOXIS, D5A.LOXLO, D5A.O2XOR, A1A2, HT5L5, KL5, 325T2-D5A, 48-D5A, 62D5A-26, T3-D5A, T1-A1, 62D5A-625 | 1-00296584 Rev. #3 | 6 Hour(s) | D5A | 250
2026-03-31 08:00 | 2026-11-15 16:00 | 229 | BOWMANVILLE SS | H3E, H3L521, H3_BUS | 1-00285558 Rev. #17 | 8 Hour(s) | No Impact | #N/A
2026-07-19 07:00 | 2026-08-28 09:00 | 40 | LENNOX TS, BOWMANVILLE SS | X521B.BOXLE, H3L521, L21L41, PL521, X4L521 | 1-00285555 Rev. #13 | 8 Hour(s) | No Impact | #N/A
2026-10-22 08:00 | 2026-10-29 16:00 | 7 | BOWMANVILLE SS | H3E, H3L521, H3_BUS | 1-00292311 Rev. #5 | 4 Hour(s) | No Impact | #N/A
2027-05-30 07:00 | 2027-07-09 09:00 | 40 | LENNOX TS, BOWMANVILLE SS | X520B.BOXLE, H2L520, KL520, L20L42, X3L520 | 1-00276876 Rev. #12 | 8 Hour(s) | No Impact | #N/A
2027-07-11 07:00 | 2027-07-30 08:01 | 19 | LENNOX TS, BOWMANVILLE SS | X521B.BOXLE, H3L521, L21L41, PL521, X4L521 | 1-00311127 Rev. #1 | 8 Hour(s) | No Impact | #N/A
2026-10-13 08:00 | 2026-11-04 16:00 | 22 | CLARINGTON TS, HAVELOCK TS, MARINE JCT, OTONABEE TS, DUFFIN JCT, OSHAWA WILSON TS, CHERRYWOOD TS, WHITBY TS, WILSON JCT, WHITBY JCT, B23C H26C TIE JCT | 81-T23C, 81-T28C, 128T1-T31H, 54T2-T23C, 40T3-T23C, 54T4-T23C, K2L28, L23L28, L23L31, P2L31, 296-T23C, 296-T28C, 296-T31H, L28_BUS, L31_BUS, T28C.CLXDJ, T31H.HAXMJ, T31H.MJXCL, T31H.MJXOT, T23C.BJXCH, T23C.CLXWJ, T23C.WJXBJ, T23C.WJXWH, T23C.WJXWI, T23C.WJXWY, 57-T31H, 54T7-T23C, L23_BUS | 1-00295709 Rev. #4 | 12 Hour(s) | No Impact | #N/A
2026-11-16 06:30 | 2026-11-27 16:30 | 11 | CHATS FALLS TS, SOUTH MARCH TS | C3S.CFXSO, A1A2, 2-C3S, A9-C3S, A2_BUS, T2-A | 1-00196163 Rev. #50 | 6 Hour(s) | FIO BEAU P33C | 500 0 150
2026-11-16 06:30 | 2026-11-27 16:30 | 11 | CHATS FALLS TS, SOUTH MARCH TS | C3S.CFXSO, 2-C3S, A9-C3S | 1-00299033 Rev. #3 | 4 Hour(s) | FIO BEAU P33C | 500 0 150
2026-11-16 06:30 | 2026-11-27 16:30 | 11 | CHATS FALLS TS, SOUTH MARCH TS | C3S.CFXSO, DL3, HL3, 2-C3S, A9-C3S | 1-00299036 Rev. #3 | 8 Hour(s) | FIO BEAU P33C | 500 0 150
2026-08-10 07:00 | 2026-10-26 16:00 | 77 | CHENAUX TS | A1A2 | 1-00313118 Rev. #1 | 20 Day(s) | No Impact | #N/A
2026-09-14 06:30 | 2026-09-29 16:00 | 15 | DOBBIN TS | DL3, DL4, KL4, 20-P4S, D_BUS, T5-D | 1-00290612 Rev. #4 | 4 Hour(s) | No Impact | #N/A
2026-09-30 06:30 | 2026-10-14 16:00 | 14 | DOBBIN TS, DALE JCT, DOBBIN JCT | P4S.DOXDA, DL4, KL3, KL4, 20-P4S, 65P4S-52, K_BUS, T1-K, T2-K, P4S-2001 | 1-00290615 Rev. #4 | 8 Hour(s) | No Impact | #N/A
2026-10-18 06:30 | 2026-11-02 16:00 | 15 | DOBBIN TS | DL3, DL4, KL3, 20-P3S, D_BUS, P3-P, T5-D | 1-00290621 Rev. #8 | 4 Hour(s) | No Impact | #N/A
2026-11-04 06:30 | 2026-11-17 16:00 | 13 | DOBBIN TS, DALE JCT | P3S.DOXPO, DL3, KL3, KL4, 20-P3S, 65P3S-2, K_BUS, P3-P, T1-K, T2-K | 1-00290627 Rev. #6 | 4 Hour(s) | No Impact | #N/A
2026-11-28 08:00 | 2026-12-23 16:00 | 25 | NORTHBROOKE DS, LODGEROOM DS | B1S.LOXNO, 74B1S-12, Q38B1S-14 | 1-00297913 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2026-07-17 06:00 | 2026-07-28 16:00 | 11 | CLARINGTON TS, HAVELOCK TS, MARINE JCT, OTONABEE TS | 128T1-T31H, L23L31, P2L31, 296-T31H, L31_BUS, T31H.HAXMJ, T31H.MJXCL, T31H.MJXOT, 57-T31H | 1-00289102 Rev. #31 | 34 Hour(s) | No Impact | #N/A
2026-09-14 06:30 | 2026-09-25 16:00 | 11 | MERIVALE TS, TERRY FOX JCT | 319E34M-6, 6-E34M | 1-00295134 Rev. #3 | 6 Hour(s) | No Impact | #N/A
2026-10-13 08:00 | 2026-11-04 16:00 | 22 | CLARINGTON TS, HAVELOCK TS, MARINE JCT, OTONABEE TS, DUFFIN JCT, OSHAWA WILSON TS, CHERRYWOOD TS, WHITBY TS, WILSON JCT, WHITBY JCT, B23C H26C TIE JCT | 81-T23C, 81-T28C, 128T1-T31H, 54T2-T23C, 40T3-T23C, 54T4-T23C, K2L28, L23L28, L23L31, P2L31, 296-T23C, 296-T28C, 296-T31H, L28_BUS, L31_BUS, T28C.CLXDJ, T31H.HAXMJ, T31H.MJXCL, T31H.MJXOT, T23C.BJXCH, T23C.CLXWJ, T23C.WJXBJ, T23C.WJXWH, T23C.WJXWI, T23C.WJXWY, 57-T31H, 54T7-T23C, L23_BUS | 1-00295709 Rev. #4 | 12 Hour(s) | No Impact | #N/A
2026-11-16 06:30 | 2026-11-27 16:30 | 11 | CHATS FALLS TS, SOUTH MARCH TS | C3S.CFXSO, A1A2, 2-C3S, A9-C3S, A2_BUS, T2-A | 1-00196163 Rev. #50 | 6 Hour(s) | FIO BEAU P33C | 500 0 150
2026-11-16 06:30 | 2026-11-27 16:30 | 11 | CHATS FALLS TS, SOUTH MARCH TS | C3S.CFXSO, 2-C3S, A9-C3S | 1-00299033 Rev. #3 | 4 Hour(s) | FIO BEAU P33C | 500 0 150
2026-11-16 06:30 | 2026-11-27 16:30 | 11 | CHATS FALLS TS, SOUTH MARCH TS | C3S.CFXSO, DL3, HL3, 2-C3S, A9-C3S | 1-00299036 Rev. #3 | 8 Hour(s) | FIO BEAU P33C | 500 0 150
2027-05-31 03:30 | 2027-06-11 16:00 | 11 | HAWTHORNE TS, MASSON GS, IPB MASSON JCT, ST. ISIDORE TS, ORLEANS JCT 2, ORLEANS TS, CUMBERLAND JCT, LONGUEUIL JCT, LONGUEUIL TS | D5A.CUXGA, D5A.CUXIS, D5A.CUXO2, D5A.HAXO2, D5A.IPXMA, D5A.LOXIS, D5A.LOXLO, D5A.O2XOR, A1A2, HT5L5, KL5, 325T2-D5A, 48-D5A, 62D5A-26, T3-D5A, T1-A1, 62D5A-625 | 1-00296584 Rev. #3 | 6 Hour(s) | D5A | 250
2026-06-14 12:00 | 2026-07-24 12:00 | 40 | CATARAQUI TS, HINCHINBROOKE SS, KINGSTON SOLAR JCT | X3H.CAXHI, HL3, L3L23, 10-X3H, T2-X3H, 371X3H-BO2 | 1-00302305 Rev. #9 | 6 Hour(s) | No Impact | #N/A
2026-09-01 08:00 | 2026-12-13 23:00 | 103 | HINCHINBROOKE SS, CATARAQUI TS, LENNOX TS, LAFARGE JCT, GARDINER TS, GARDINER STR 44 JCT, WESTBROOK JCT, NPIF KINGSTON JCT | X2H.DEXWE, X2H.HIXCA, X2H.LAXDE, X2H.LAXLE, X2H.WEXGA, 10-X2H, 12-X2H, 1A-X2H, 1T3-X2H, H1T2-X2H | 1-00292309 Rev. #4 | 4 Hour(s) | No Impact | #N/A
2027-05-31 03:30 | 2027-06-11 16:00 | 11 | HAWTHORNE TS, MASSON GS, IPB MASSON JCT, ST. ISIDORE TS, ORLEANS JCT 2, ORLEANS TS, CUMBERLAND JCT, LONGUEUIL JCT, LONGUEUIL TS | D5A.CUXGA, D5A.CUXIS, D5A.CUXO2, D5A.HAXO2, D5A.IPXMA, D5A.LOXIS, D5A.LOXLO, D5A.O2XOR, A1A2, HT5L5, KL5, 325T2-D5A, 48-D5A, 62D5A-26, T3-D5A, T1-A1, 62D5A-625 | 1-00296584 Rev. #3 | 6 Hour(s) | No Impact | 250
2026-07-05 08:00 | 2026-07-24 16:00 | 19 | ARNPRIOR TS, ARNPRIOR JCT, MARCHWOOD JCT, MISSISSIPPI JCT, CHATS FALLS TS, STEWARTVILLE TS | W6CS.ARXAR, W6CS.ARXMI, W6CS.ARXST, W6CS.CHXMI, W6CS.MIXMA, 10-W6CS, 59W6CS-58, 61W6CS-ILS2, 61W6CS-LC2, 2W6CS-L | 1-00312236 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2026-11-28 08:00 | 2026-12-23 16:00 | 25 | NORTHBROOKE DS, LODGEROOM DS | B1S.LOXNO, 74B1S-12, Q38B1S-14 | 1-00297913 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2026-09-28 08:00 | 2026-10-09 16:00 | 11 | ST. LAWRENCE TS, MASSENA JCT | L33P.ROXLA, 49-L33P | 1-00275118 Rev. #9 | 4 Hour(s) | No Impact | #N/A
2026-10-29 08:00 | 2026-11-13 16:00 | 15 | ST. LAWRENCE TS, MASSENA JCT | L34P.ROXLA, 49-L34P | 1-00275119 Rev. #10 | 4 Hour(s) | No Impact | #N/A
2025-11-25 08:00 | 2031-12-31 16:00 | 2227 | ST. LAWRENCE TS | 49-L5C | 1-00301379 Rev. #1 | 2 Hour(s) | No Impact | #N/A
2026-03-17 15:30 | 2026-11-11 16:00 | 239 | PICTON TS | OLDT1, OLD28T1-X21 | 1-00304973 Rev. #23 | Immediate | No Impact | #N/A
2026-05-08 08:00 | 2026-10-16 08:00 | 161 | PIPERVILLE JCT | 644L24A-48, 644L24A-MSO6, 644L24A-MSO7 | 1-00313515 Rev. #4 | Non-recallable | FIO BEAU P33C | 0 0 0
2026-05-29 13:00 | 2026-08-18 12:00 | 80 | GARDINER TS | 1A-X2H, 1A-X4H | 1-00310861 Rev. #3 | Immediate | No Impact | #N/A
2026-06-08 08:00 | 2026-09-02 16:00 | 86 | DOBBIN TS | T2-K, T7-K | 1-00307293 Rev. #3 | 135 Min(s) | No Impact | #N/A
2026-07-05 08:00 | 2026-08-28 16:00 | 54 | L5C MSO JCT, ST. LAWRENCE TS | L5C.NYXLA, 49-L5C | 1-00312220 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2026-07-19 07:00 | 2026-08-28 09:00 | 40 | LENNOX TS | PL521, X4L521, 12-X521B | 1-00307924 Rev. #8 | 8 Hour(s) | No Impact | #N/A
2026-08-31 11:30 | 2026-09-10 17:00 | 10 | LENNOX TS, GRETNA JCT, NAPANEE TS, PICTON TS | X22.GRXLE, X22.GRXNA, X22.GRXPI, 12-X22, T2-X22 | 1-00297891 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2026-09-04 08:00 | 2027-03-23 17:00 | 200 | LENNOX TS | KL526 | 1-00285554 Rev. #9 | Non-recallable | No Impact | #N/A
2026-09-08 08:00 | 2026-09-14 16:00 | 6 | BOWMANVILLE SS | EL527, EL542, H1E, H3E, E1_BUS, E2_BUS, E1-E2 | 1-00295505 Rev. #6 | 4 Hour(s) | No Impact | #N/A
2026-09-29 05:30 | 2026-11-11 11:30 | 43 | LENNOX TS, GRETNA JCT, NAPANEE TS, PICTON TS | X22.GRXLE, X22.GRXNA, X22.GRXPI, 12-X22, T2-X22 | 1-00292505 Rev. #8 | 6 Hour(s) | No Impact | #N/A
2026-09-30 08:00 | 2026-11-30 16:00 | 61 | DOBBIN TS | T2-K, T7-K | 1-00290614 Rev. #4 | 4 Hour(s) | No Impact | #N/A
2026-10-18 06:00 | 2026-10-23 16:00 | 5 | ST. LAWRENCE TS, R. H. SAUNDERS GS | S30L.SAXLA, 49-S30L, S30L-D | 1-00298374 Rev. #6 | 4 Hour(s) | No Impact | #N/A
2026-09-28 08:00 | 2026-10-09 16:00 | 11 | ST. LAWRENCE TS, MASSENA JCT | L33P.ROXLA, 49-L33P | 1-00275118 Rev. #9 | 4 Hour(s) | No Impact | #N/A
2026-10-29 08:00 | 2026-11-13 16:00 | 15 | ST. LAWRENCE TS, MASSENA JCT | L34P.ROXLA, 49-L34P | 1-00275119 Rev. #10 | 4 Hour(s) | No Impact | #N/A
2027-05-31 03:30 | 2027-06-11 16:00 | 11 | HAWTHORNE TS, MASSON GS, IPB MASSON JCT, ST. ISIDORE TS, ORLEANS JCT 2, ORLEANS TS, CUMBERLAND JCT, LONGUEUIL JCT, LONGUEUIL TS | D5A.CUXGA, D5A.CUXIS, D5A.CUXO2, D5A.HAXO2, D5A.IPXMA, D5A.LOXIS, D5A.LOXLO, D5A.O2XOR, A1A2, HT5L5, KL5, 325T2-D5A, 48-D5A, 62D5A-26, T3-D5A, T1-A1, 62D5A-625 | 1-00296584 Rev. #3 | 6 Hour(s) | D5A | 250
Back to main menu

## Table 4.6
Back to main menu
Table 4.6: Essa Zone Transmission Outages
Planned Start | Planned End | Duration (Days) | Station | Equipment Name | Outage ID | Max Recall | Major Transmission Interface Impacted | Reduction in Limit (MW)
2026-09-15 08:00 | 2026-09-26 16:01 | 11 | WOODBRIDGE JCT, CLAIREVILLE TS, VAUGHAN 4 JCT, VAUGHAN MTS #4, HOLLAND TS, HOLLAND JCT | 51-H82V, 153-H82V, H82V.WJXCL, H82V.4JXV4, H82V.4JXWJ, H82V.HJX4J, H82V.HOXHJ | 1-00296672 Rev. #8 | 4 Hour(s) | No Impact | #N/A
2027-04-01 08:00 | 2027-06-04 16:00 | 64 | WOODBRIDGE JCT, CLAIREVILLE TS, VAUGHAN 4 JCT, VAUGHAN MTS #4, HOLLAND TS, HOLLAND JCT | 51-H82V, 153-H82V, H82V.WJXCL, H82V.4JXV4, H82V.4JXWJ, H82V.HJX4J, H82V.HOXHJ | 1-00308207 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2026-09-15 08:00 | 2026-09-26 16:01 | 11 | WOODBRIDGE JCT, CLAIREVILLE TS, VAUGHAN 4 JCT, VAUGHAN MTS #4, HOLLAND TS, HOLLAND JCT | 51-H82V, 153-H82V, H82V.WJXCL, H82V.4JXV4, H82V.4JXWJ, H82V.HJX4J, H82V.HOXHJ | 1-00296672 Rev. #8 | 4 Hour(s) | No Impact | #N/A
2027-04-01 08:00 | 2027-06-04 16:00 | 64 | WOODBRIDGE JCT, CLAIREVILLE TS, VAUGHAN 4 JCT, VAUGHAN MTS #4, HOLLAND TS, HOLLAND JCT | 51-H82V, 153-H82V, H82V.WJXCL, H82V.4JXV4, H82V.4JXWJ, H82V.HJX4J, H82V.HOXHJ | 1-00308207 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2026-07-06 08:00 | 2026-08-28 16:00 | 53 | BEAVER JCT, BROWN HILL TS, BEAVERTON JCT, LINDSAY TS, MINDEN TS, BEAVERTON TS | M80B.BEXBE, M80B.BEXBV, M80B.BSXBE, M80B.BVXLI, M80B.BVXMI, L80L88, 4T2-M80B, 87-M80B, T3-M80B | 1-00307491 Rev. #5 | 4 Hour(s) | No Impact | #N/A
2026-07-06 08:00 | 2026-08-28 16:00 | 53 | BEAVER JCT, BROWN HILL TS, BEAVERTON JCT, LINDSAY TS, MINDEN TS, BEAVERTON TS | M80B.BEXBE, M80B.BEXBV, M80B.BSXBE, M80B.BVXLI, M80B.BVXMI, L80L88, 4T2-M80B, 87-M80B, T3-M80B | 1-00307491 Rev. #5 | 4 Hour(s) | No Impact | #N/A
2026-08-10 06:15 | 2026-08-21 15:00 | 11 | EVERETT TS, ESSA TS, ALLISTON JCT, ALLISTON TS, EVERETT JCT, ORANGEVILLE TS | E9V.ALXAL, E9V.ALXES, E9V.ALXEV, E9V.EVXOR, 138E9V-MSO, 138T1-E9V, 18-E9V, 1807E9V-BO, 22-E9V, T2-E8V, T2-E9V, 9T4-E9V | 1-00298264 Rev. #17 | 4 Hour(s) | No Impact | #N/A
2026-08-31 07:15 | 2026-09-11 16:00 | 11 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, 18-E510V, 51-E510V | 1-00308103 Rev. #5 | 4 Hour(s) | FS FN P502X CLAN | -100 0 -100 700
2026-09-27 08:00 | 2026-10-28 16:00 | 31 | ESSA TS, CLAIREVILLE TS | E511V.CLXES, 18-E511V, 51-E511V | 1-00287147 Rev. #10 | 48 Hour(s) | FS FN P502X CLAN | -100 0 -100 700
2026-10-29 06:15 | 2026-11-04 07:15 | 6 | ESSA TS, CLAIREVILLE TS, MIDDLEPORT TS | E510V.CLXES, V586M.MDXCL, AL510, L552L586, PL586, W3L510, 18-E510V, 25-V586M, 51-E510V, 51-V586M | 1-00313522 Rev. #1 | 48 Hour(s) | FS FN P502X CLAN | -100 0 -100 700
2026-11-01 07:00 | 2026-12-04 17:00 | 33 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, 18-E510V, 51-E510V | 1-00296677 Rev. #8 | 48 Hour(s) | FS FN P502X CLAN | -100 0 -100 700
2026-11-01 08:00 | 2027-03-19 16:00 | 138 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, AL510, W3L510, 18-E510V, 51-E510V | 1-00296678 Rev. #3 | Non-recallable | FS FN P502X CLAN | -100 0 -100 700
2027-02-19 08:00 | 2027-02-26 16:00 | 7 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, 18-E510V, 51-E510V | 1-00308208 Rev. #1 | 8 Hour(s) | FS FN P502X CLAN | -100 0 -100 700
2026-07-06 08:00 | 2026-08-28 16:00 | 53 | BEAVER JCT, BROWN HILL TS, BEAVERTON JCT, LINDSAY TS, MINDEN TS, BEAVERTON TS | M80B.BEXBE, M80B.BEXBV, M80B.BSXBE, M80B.BVXLI, M80B.BVXMI, L80L88, 4T2-M80B, 87-M80B, T3-M80B | 1-00307491 Rev. #5 | 4 Hour(s) | No Impact | #N/A
2026-08-31 07:15 | 2026-09-11 16:00 | 11 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, 18-E510V, 51-E510V | 1-00308103 Rev. #5 | 4 Hour(s) | FS FN P502X CLAN | -100 0 -100 700
2026-09-27 08:00 | 2026-10-28 16:00 | 31 | ESSA TS, CLAIREVILLE TS | E511V.CLXES, 18-E511V, 51-E511V | 1-00287147 Rev. #10 | 48 Hour(s) | FS FN P502X CLAN | -100 0 -100 700
2026-10-29 06:15 | 2026-11-04 07:15 | 6 | ESSA TS, CLAIREVILLE TS, MIDDLEPORT TS | E510V.CLXES, V586M.MDXCL, AL510, L552L586, PL586, W3L510, 18-E510V, 25-V586M, 51-E510V, 51-V586M | 1-00313522 Rev. #1 | 48 Hour(s) | FS FN P502X CLAN | -100 0 -100 700
2026-11-01 07:00 | 2026-12-04 17:00 | 33 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, 18-E510V, 51-E510V | 1-00296677 Rev. #8 | 48 Hour(s) | FS FN P502X CLAN | -100 0 -100 700
2026-11-01 08:00 | 2027-03-19 16:00 | 138 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, AL510, W3L510, 18-E510V, 51-E510V | 1-00296678 Rev. #3 | Non-recallable | FS FN P502X CLAN | -100 0 -100 700
2027-02-19 08:00 | 2027-02-26 16:00 | 7 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, 18-E510V, 51-E510V | 1-00308208 Rev. #1 | 8 Hour(s) | FS FN P502X CLAN | -100 0 -100 700
2026-06-14 08:00 | 2026-07-05 16:00 | 21 | HANMER TS, ESSA TS | X504E.ESXHA, 18-X504E, 33-X504E | 1-00295049 Rev. #7 | 5 Hour(s) | FS FN P502X CLAN | 990 900 250 0
2026-08-31 07:15 | 2026-09-11 16:00 | 11 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, 18-E510V, 51-E510V | 1-00308103 Rev. #5 | 4 Hour(s) | FS FN P502X CLAN | -100 0 -100 700
2026-09-27 08:00 | 2026-10-28 16:00 | 31 | ESSA TS, CLAIREVILLE TS | E511V.CLXES, 18-E511V, 51-E511V | 1-00287147 Rev. #10 | 48 Hour(s) | FS FN P502X CLAN | -100 0 -100 700
2026-10-29 06:15 | 2026-11-04 07:15 | 6 | ESSA TS, CLAIREVILLE TS, MIDDLEPORT TS | E510V.CLXES, V586M.MDXCL, AL510, L552L586, PL586, W3L510, 18-E510V, 25-V586M, 51-E510V, 51-V586M | 1-00313522 Rev. #1 | 48 Hour(s) | FS FN P502X CLAN | -100 0 -100 700
2026-11-01 07:00 | 2026-12-04 17:00 | 33 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, 18-E510V, 51-E510V | 1-00296677 Rev. #8 | 48 Hour(s) | FS FN P502X CLAN | -100 0 -100 700
2026-11-01 08:00 | 2027-03-19 16:00 | 138 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, AL510, W3L510, 18-E510V, 51-E510V | 1-00296678 Rev. #3 | Non-recallable | FS FN P502X CLAN | -100 0 -100 700
2027-02-19 08:00 | 2027-02-26 16:00 | 7 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, 18-E510V, 51-E510V | 1-00308208 Rev. #1 | 8 Hour(s) | FS FN P502X CLAN | -100 0 -100 700
2027-11-01 12:00 | 2027-11-19 09:30 | 17 | DES JOACHIMS TS, OTTO HOLDEN TS | D5H.DEXHO, AL5, L1L5, L5L24 | 1-00300283 Rev. #1 | 8 Hour(s) | FS FN P502X CLAN | 25 0 25 0
2026-06-14 08:00 | 2026-07-05 16:00 | 21 | HANMER TS, ESSA TS | X504E.ESXHA, 18-X504E, 33-X504E | 1-00295049 Rev. #7 | 5 Hour(s) | FS FN P502X CLAN | 990 900 250 0
2026-08-31 07:15 | 2026-09-11 16:00 | 11 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, 18-E510V, 51-E510V | 1-00308103 Rev. #5 | 4 Hour(s) | FS FN P502X CLAN | -100 0 -100 700
2026-09-27 08:00 | 2026-10-28 16:00 | 31 | ESSA TS, CLAIREVILLE TS | E511V.CLXES, 18-E511V, 51-E511V | 1-00287147 Rev. #10 | 48 Hour(s) | FS FN P502X CLAN | -100 0 -100 700
2026-10-29 06:15 | 2026-11-04 07:15 | 6 | ESSA TS, CLAIREVILLE TS, MIDDLEPORT TS | E510V.CLXES, V586M.MDXCL, AL510, L552L586, PL586, W3L510, 18-E510V, 25-V586M, 51-E510V, 51-V586M | 1-00313522 Rev. #1 | 48 Hour(s) | FS FN P502X CLAN | -100 0 -100 700
2026-11-01 07:00 | 2026-12-04 17:00 | 33 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, 18-E510V, 51-E510V | 1-00296677 Rev. #8 | 48 Hour(s) | FS FN P502X CLAN | -100 0 -100 700
2026-11-01 08:00 | 2027-03-19 16:00 | 138 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, AL510, W3L510, 18-E510V, 51-E510V | 1-00296678 Rev. #3 | Non-recallable | FS FN P502X CLAN | -100 0 -100 700
2027-02-19 08:00 | 2027-02-26 16:00 | 7 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, 18-E510V, 51-E510V | 1-00308208 Rev. #1 | 8 Hour(s) | FS FN P502X CLAN | -100 0 -100 700
2027-11-01 12:00 | 2027-11-19 09:30 | 17 | DES JOACHIMS TS, OTTO HOLDEN TS | D5H.DEXHO, AL5, L1L5, L5L24 | 1-00300283 Rev. #1 | 8 Hour(s) | FS FN P502X CLAN | 25 0 25 0
2027-11-01 12:00 | 2027-11-19 09:30 | 17 | DES JOACHIMS TS, OTTO HOLDEN TS | D5H.DEXHO, AL5, L1L5, L5L24 | 1-00300283 Rev. #1 | 8 Hour(s) | FS FN P502X CLAN | 25 0 25 0
2026-06-18 14:01 | 2026-07-22 14:01 | 34 | DES JOACHIMS TS | T7-5D6, T6-P, T7-P | 1-00288711 Rev. #10 | 3 Hour(s) | No Impact | #N/A
2026-07-06 06:15 | 2026-07-30 16:00 | 24 | DES JOACHIMS TS, MINDEN TS | D1M.MIXDE, 5-D1M, 87-D1M | 1-00312237 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2026-08-03 06:15 | 2026-10-01 16:00 | 59 | OTTER CREEK JCT, DES JOACHIMS TS, MINDEN TS | D4M.OTXDE, D4M.OTXMI, 5-D4M, 87-D4M, B9D4M-B8 | 1-00295116 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2026-10-13 06:15 | 2026-11-06 16:00 | 24 | DES JOACHIMS TS, MINDEN TS | D1M.MIXDE, 5-D1M, 87-D1M | 1-00295094 Rev. #8 | 4 Hour(s) | No Impact | #N/A
2026-11-09 06:15 | 2026-11-27 16:00 | 18 | OTTER CREEK JCT, DES JOACHIMS TS, MINDEN TS | D2M.OTXDE, D2M.OTXMI, 5-D2M, 87-D2M, B9D2M-B8, B9D4M-B8 | 1-00299045 Rev. #4 | 4 Hour(s) | No Impact | #N/A
2026-11-30 07:15 | 2026-12-15 16:00 | 15 | DES JOACHIMS TS, MINDEN TS | D3M.MIXDE, 5-D3M, 87-D3M | 1-00295024 Rev. #6 | 4 Hour(s) | No Impact | #N/A
Back to main menu

## Table 4.7
Back to main menu
Table 4.7: Niagara Zone Transmission Outages
Planned Start | Planned End | Duration (Days) | Station | Equipment Name | Outage ID | Max Recall | Major Transmission Interface Impacted | Reduction in Limit (MW)
2026-07-20 06:15 | 2026-07-31 16:00 | 11.4062 | BURLINGTON TS, BURLINGTON DESN TS, BURLINGTON JCT, BECK 2 TS, NIAGARA WEST JCT, MIDDLEPORT TS, NEALE JCT, CARLUKE JCT | Q25BM.BEXNI, Q25BM.BUXBD, Q25BM.BUXBU, Q25BM.MIXCA, Q25BM.NEXBU, 25-Q25BM, 28-Q25BM, 39-Q25BM, T15-Q25BM | 1-00289213 Rev. #7 | 4 Hour(s) | No Impact | #N/A
2026-09-08 06:15 | 2026-09-15 16:00 | 7.4062 | BURLINGTON TS, BURLINGTON DESN TS, BURLINGTON JCT, BECK 2 TS, NIAGARA WEST JCT, MIDDLEPORT TS, NEALE JCT, CARLUKE JCT | Q25BM.BEXNI, Q25BM.BUXBD, Q25BM.BUXBU, Q25BM.MIXCA, Q25BM.NEXBU, 25-Q25BM, 28-Q25BM, 39-Q25BM, T15-Q25BM | 1-00313527 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2026-09-15 08:00 | 2026-11-17 16:00 | 63.3333 | BECK 2 TS, NY NIAGARA 345 KV | PA27.NIXBE, 28R27-PA27, R27-S | 1-00308330 Rev. #3 | Non-recallable | NY-W-EXP NY-W-IMP NY-S-EXP NY-S-IMP | 150 0 100 0
2026-07-20 06:15 | 2026-07-31 16:00 | 11.4062 | BURLINGTON TS, BURLINGTON DESN TS, BURLINGTON JCT, BECK 2 TS, NIAGARA WEST JCT, MIDDLEPORT TS, NEALE JCT, CARLUKE JCT | Q25BM.BEXNI, Q25BM.BUXBD, Q25BM.BUXBU, Q25BM.MIXCA, Q25BM.NEXBU, 25-Q25BM, 28-Q25BM, 39-Q25BM, T15-Q25BM | 1-00289213 Rev. #7 | 4 Hour(s) | No Impact | #N/A
2026-09-08 06:15 | 2026-09-15 16:00 | 7.4062 | BURLINGTON TS, BURLINGTON DESN TS, BURLINGTON JCT, BECK 2 TS, NIAGARA WEST JCT, MIDDLEPORT TS, NEALE JCT, CARLUKE JCT | Q25BM.BEXNI, Q25BM.BUXBD, Q25BM.BUXBU, Q25BM.MIXCA, Q25BM.NEXBU, 25-Q25BM, 28-Q25BM, 39-Q25BM, T15-Q25BM | 1-00313527 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2026-09-15 08:00 | 2026-11-17 16:00 | 63.3333 | BECK 2 TS, NY NIAGARA 345 KV | PA27.NIXBE, 28R27-PA27, R27-S | 1-00308330 Rev. #3 | Non-recallable | NY-W-EXP NY-W-IMP NY-S-EXP NY-S-IMP | 150 0 100 0
2026-09-15 08:00 | 2026-11-17 16:00 | 63.3333 | BECK 2 TS, NY NIAGARA 345 KV | PA27.NIXBE, 28R27-PA27, R27-S | 1-00308330 Rev. #3 | Non-recallable | NY-W-EXP NY-W-IMP NY-S-EXP NY-S-IMP | 150 0 100 0
2026-01-23 08:00 | 2026-09-03 17:00 | 223.375 | BECK 1 SS | 6E-7, E3_BUS, E4_BUS, E5_BUS, E6_BUS, E7_BUS, E5-E15, E6-E16, E8-E18, E9-E19, E8_BUS, E5-E6, E4-E5, E3-E4, E8-E9, AQ11S-A11, E9_BUS, A1-A11, E7-E8, A11_BUSNORTH, A11_BUSSOUTH, E3-E13, E4-E14 | 1-00305350 Rev. #28 | Non-recallable | No Impact | #N/A
2026-06-01 04:00 | 2026-07-10 14:30 | 39.4375 | NY NIAGARA 230 KV | 2508, 2522 | 1-00312891 Rev. #2 | Non-recallable | No Impact | #N/A
2026-06-21 05:30 | 2026-07-03 16:00 | 12.4375 | BECK 2 TS | K1L25 | 1-00259343 Rev. #6 | 3 Day(s) | No Impact | #N/A
2026-06-21 06:15 | 2026-07-06 16:00 | 15.4062 | BEAMSVILLE TS, WINONA TS, WINONA JCT | Q2AH.WIXBE, 115Q2AH-18, 18Q2AH-17 | 1-00298777 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2026-07-05 05:30 | 2026-07-17 15:00 | 12.3958 | BECK 2 TS | K1TL26 | 1-00259344 Rev. #9 | 3 Day(s) | No Impact | #N/A
2026-07-19 05:30 | 2026-07-31 15:00 | 12.3958 | BECK 2 TS | D1L302 | 1-00259309 Rev. #9 | 3 Day(s) | No Impact | #N/A
2026-08-09 05:30 | 2026-08-21 15:00 | 12.3958 | BECK 2 TS | TL21L24 | 1-00259321 Rev. #12 | 3 Day(s) | No Impact | #N/A
2026-08-23 05:30 | 2026-09-04 15:00 | 12.3958 | BECK 2 TS | K1K2 | 1-00259341 Rev. #12 | 3 Day(s) | No Impact | #N/A
2026-09-13 05:30 | 2026-09-25 15:00 | 12.3958 | BECK 2 TS | D1D2 | 1-00259300 Rev. #12 | 3 Day(s) | No Impact | #N/A
2026-09-16 04:00 | 2026-11-06 19:00 | 51.625 | NY NIAGARA 230 KV | 2102, 2002, 2202, 2322, 2302 | 1-00286541 Rev. #3 | Non-recallable | No Impact | #N/A
2026-10-01 08:15 | 2026-10-30 16:00 | 29.3229 | ALLANBURG TS, ALLANBURG WEST JCT, MIDDLEPORT TS, ABITIBI CONSOLIDATED NAN91 JCT, BECK 2 TS | Q26M.MIXAW, Q28A.ALXAB, 25-Q26M, 28-Q28A, 45-Q28A, 64Q26M-25, Q26M-Q10P, Q28A-Q10P | 1-00289214 Rev. #3 | 60 Hour(s) | No Impact | #N/A
2026-10-02 07:00 | 2026-10-15 16:00 | 13.375 | WINONA TS, WINONA JCT, SALTFLEET JCT, BEACH TS | Q2AH.HAXSA, Q2AH.SAXWI, Q2AH.WI2XWI2, 115Q2AH-17, 17-Q2AH | 1-00310812 Rev. #2 | 0 Hour(s) | No Impact | #N/A
2026-10-02 15:00 | 2026-10-18 05:30 | 15.6042 | BECK 2 TS | K2L29, K2-BO4, K1K2 | 1-00268449 Rev. #5 | Non-recallable | NY-W-EXP NY-W-IMP NY-S-EXP NY-S-IMP | 500 650 600 500
2026-11-15 06:30 | 2026-11-27 16:00 | 12.3958 | BECK 2 TS | D1L27 | 1-00259303 Rev. #9 | 3 Day(s) | No Impact | #N/A
Back to main menu

## Table 4.8
Back to main menu
Table 4.8: Northeast Zone Transmission Outages
Planned Start | Planned End | Duration (Days) | Station | Equipment Name | Outage ID | Max Recall | Major Transmission Interface Impacted | Reduction in Limit (MW)
2026-10-13 07:00 | 2026-11-06 16:00 | 24.375 | HUNTA SS | L2L9 | 1-00287779 Rev. #4 | 8 Hour(s) | No Impact | #N/A
2026-07-13 08:00 | 2026-07-30 16:00 | 17.3333 | LOWER NOTCH JCT, WIDDIFIELD TS | W71D.WIXLO, 38-W71D, W71D-38 | 1-00298159 Rev. #5 | 5 Hour(s) | No Impact | #N/A
2026-08-04 08:00 | 2026-08-21 16:00 | 17.3333 | LOWER NOTCH JCT, DYMOND TS | T1-L71, T2-L71, W71D-32, W71D.LOXDY | 1-00313264 Rev. #1 | 5 Hour(s) | No Impact | #N/A
2026-10-18 08:00 | 2026-11-08 07:00 | 20.9583 | RAMORE TS | 120A9K-16 | 1-00302108 Rev. #2 | 2 Hour(s) | No Impact | #N/A
2026-10-19 06:00 | 2026-11-08 07:00 | 20.0417 | KIRKLAND LAKE TS | D4D9, D8D9, SC11D9, SC11SC, 16-A9K, D9_BUS, SC11, SC11D9-D9 | 1-00299098 Rev. #4 | 6 Hour(s) | No Impact | #N/A
2026-11-16 08:00 | 2026-12-03 16:00 | 17.3333 | KIRKLAND LAKE TS, DYMOND TS, DANE JCT, GULL LAKE SOUTH JCT, NINE MILE JCT, NORTHLAND KIRKLAND LAKE CGS | D3K.DAXGU, D3K.DYXNI, D3K.GUXKI, D3K.GUXNP, D3K.NIXDA, 16-D3K, 32-D3K, 59D3K-16, 59D3K-68, 68D3K-32, 68D3K-16 | 1-00299028 Rev. #2 | 5 Hour(s) | No Impact | #N/A
2026-09-01 07:00 | 2026-09-22 16:30 | 21.3958 | TRAFALGAR TS, PALERMO TS, BURLINGTON TS, GLENORCHY JCT, PALERMO TXB JCT, LANTZ JCT, GLENORCHY MTS1 | T37B.GJXGL, T37B.GJXLA, T37B.PAXBU, T37B.PAXTR, T37B.PJXGJ, 31-T37B, 31SC21L-T37B, 39-T37B, T4-T37B | 1-00296683 Rev. #6 | 12 Hour(s) | No Impact | #N/A
2026-09-23 07:00 | 2026-10-20 16:00 | 27.375 | PALERMO TS, TRAFALGAR TS, BURLINGTON TS, PALERMO TXB JCT, GLENORCHY JCT, LANTZ JCT, GLENORCHY MTS1 | T36B.GJXGL, T36B.GJXLA, T36B.PAXBU, T36B.PAXTR, T36B.PJXGJ, 31-T36B, 31SC21L-T36B, 39-T36B, T3-T36B | 1-00310816 Rev. #2 | 8 Hour(s) | No Impact | #N/A
2026-10-21 07:00 | 2026-11-20 10:00 | 30.125 | TRAFALGAR TS, PALERMO TS, BURLINGTON TS, GLENORCHY JCT, PALERMO TXB JCT, LANTZ JCT, GLENORCHY MTS1 | T37B.GJXGL, T37B.GJXLA, T37B.PAXBU, T37B.PAXTR, T37B.PJXGJ, 31-T37B, 31SC21L-T37B, 39-T37B, T4-T37B | 1-00309267 Rev. #6 | 12 Hour(s) | No Impact | #N/A
2026-06-14 08:00 | 2026-07-05 16:00 | 21.3333 | HANMER TS, ESSA TS | X504E.ESXHA, 18-X504E, 33-X504E | 1-00295049 Rev. #7 | 5 Hour(s) | FS FN P502X CLAN | 990 900 250 0
2027-11-01 12:00 | 2027-11-19 09:30 | 17.8958 | DES JOACHIMS TS, OTTO HOLDEN TS | D5H.DEXHO, AL5, L1L5, L5L24 | 1-00300283 Rev. #1 | 8 Hour(s) | FS FN P502X CLAN | 25 0 25 0
2026-06-14 08:00 | 2026-07-05 16:00 | 21.3333 | HANMER TS, ESSA TS | X504E.ESXHA, 18-X504E, 33-X504E | 1-00295049 Rev. #7 | 5 Hour(s) | FS FN P502X CLAN | 990 900 250 0
2027-11-01 12:00 | 2027-11-19 09:30 | 17.8958 | DES JOACHIMS TS, OTTO HOLDEN TS | D5H.DEXHO, AL5, L1L5, L5L24 | 1-00300283 Rev. #1 | 8 Hour(s) | FS FN P502X CLAN | 25 0 25 0
2026-08-09 08:00 | 2026-08-27 16:00 | 18.3333 | HANMER TS, MARTINDALE TS | X26S.MAXHA, 33-X26S, 9-X26S | 1-00295122 Rev. #3 | 5 Hour(s) | No Impact | #N/A
2026-11-08 09:00 | 2026-11-24 17:00 | 16.3333 | HANMER TS, MARTINDALE TS, HANMER PARALLEL B JCT, MARTINDALE PARALLEL B JCT | X25S.MAXHA, 33-X25S, 9-X25S, X29S.HAXHB, X29S.HBXMB, X29S.MBXMA | 1-00299046 Rev. #3 | 5 Hour(s) | No Impact | #N/A
2026-07-13 08:00 | 2026-07-30 16:00 | 17.3333 | LOWER NOTCH JCT, WIDDIFIELD TS | W71D.WIXLO, 38-W71D, W71D-38 | 1-00298159 Rev. #5 | 5 Hour(s) | No Impact | #N/A
2026-09-02 08:00 | 2026-10-03 16:00 | 31.3333 | OTTO HOLDEN TS, WIDDIFIELD TS | H24S.WIXHO, 6-H24S, H24S-6 | 1-00294340 Rev. #4 | 5 Hour(s) | No Impact | #N/A
2026-10-06 08:00 | 2026-10-29 16:00 | 23.3333 | CRYSTAL FALLS TS, MARTINDALE TS, PEDLEY JCT, WIDDIFIELD TS | H23S.PEXCR, H23S.PEXMA, H23S.PEXWI, 7T5-H23S, 9-H23S, H23S-9 | 1-00299061 Rev. #3 | 5 Hour(s) | No Impact | #N/A
2026-10-18 08:00 | 2026-11-08 07:00 | 20.9583 | RAMORE TS | 120A9K-16 | 1-00302108 Rev. #2 | 2 Hour(s) | No Impact | #N/A
2026-10-19 06:00 | 2026-11-08 07:00 | 20.0417 | KIRKLAND LAKE TS | D4D9, D8D9, SC11D9, SC11SC, 16-A9K, D9_BUS, SC11, SC11D9-D9 | 1-00299098 Rev. #4 | 6 Hour(s) | No Impact | #N/A
2026-11-16 08:00 | 2026-12-03 16:00 | 17.3333 | KIRKLAND LAKE TS, DYMOND TS, DANE JCT, GULL LAKE SOUTH JCT, NINE MILE JCT, NORTHLAND KIRKLAND LAKE CGS | D3K.DAXGU, D3K.DYXNI, D3K.GUXKI, D3K.GUXNP, D3K.NIXDA, 16-D3K, 32-D3K, 59D3K-16, 59D3K-68, 68D3K-32, 68D3K-16 | 1-00299028 Rev. #2 | 5 Hour(s) | No Impact | #N/A
2027-11-01 12:00 | 2027-11-19 09:30 | 17.8958 | DES JOACHIMS TS, OTTO HOLDEN TS | D5H.DEXHO, AL5, L1L5, L5L24 | 1-00300283 Rev. #1 | 8 Hour(s) | FS FN P502X CLAN | 25 0 25 0
2026-07-13 08:00 | 2026-07-30 16:00 | 17.3333 | LOWER NOTCH JCT, WIDDIFIELD TS | W71D.WIXLO, 38-W71D, W71D-38 | 1-00298159 Rev. #5 | 5 Hour(s) | No Impact | #N/A
2026-08-04 08:00 | 2026-08-21 16:00 | 17.3333 | LOWER NOTCH JCT, DYMOND TS | T1-L71, T2-L71, W71D-32, W71D.LOXDY | 1-00313264 Rev. #1 | 5 Hour(s) | No Impact | #N/A
2026-08-23 21:00 | 2026-08-30 16:00 | 6.7917 | KAPUSKASING TS, CARMICHAEL FALLS JCT | L1L9, 3021-27 | 1-00313102 Rev. #1 | 5 Hour(s) | No Impact | #N/A
2026-09-23 06:00 | 2026-09-29 17:00 | 6.4583 | PINARD TS, PORCUPINE TS | D501P.POXPI, 30-D501P, T1-D501P, T2-D501P | 1-00294189 Rev. #8 | 4 Hour(s) | No Impact | #N/A
2026-09-23 07:00 | 2026-09-29 16:00 | 6.375 | PINARD TS, PORCUPINE TS | D501P.POXPI, KL21, KL22, 30-D501P, 31T1-K, 31T2-K, K_BUS, T1-D501P, T2-D501P | 1-00313210 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2026-09-23 07:00 | 2026-09-29 16:00 | 6.375 | PORCUPINE TS, PINARD TS | D501P.POXPI, H1L501, H2L501, 30-D501P, T1-D501P, T2-D501P | 1-00313113 Rev. #1 | 5 Hour(s) | No Impact | #N/A
2026-10-05 16:00 | 2026-11-09 07:00 | 34.625 | PINARD TS | L20L21, PL20, 31-L20D | 1-00304043 Rev. #2 | 6 Hour(s) | No Impact | #N/A
2026-10-05 16:00 | 2026-11-09 07:00 | 34.625 | PINARD TS | 31-L20D | 1-00302163 Rev. #4 | 5 Hour(s) | No Impact | #N/A
2026-10-13 07:00 | 2026-11-06 16:00 | 24.375 | HUNTA SS | L2L9 | 1-00287779 Rev. #4 | 8 Hour(s) | No Impact | #N/A
2026-10-18 08:00 | 2026-11-08 07:00 | 20.9583 | RAMORE TS | 120A9K-16 | 1-00302108 Rev. #2 | 2 Hour(s) | No Impact | #N/A
2026-10-19 06:00 | 2026-11-08 07:00 | 20.0417 | KIRKLAND LAKE TS | D4D9, D8D9, SC11D9, SC11SC, 16-A9K, D9_BUS, SC11, SC11D9-D9 | 1-00299098 Rev. #4 | 6 Hour(s) | No Impact | #N/A
2026-11-16 08:00 | 2026-12-03 16:00 | 17.3333 | KIRKLAND LAKE TS, DYMOND TS, DANE JCT, GULL LAKE SOUTH JCT, NINE MILE JCT, NORTHLAND KIRKLAND LAKE CGS | D3K.DAXGU, D3K.DYXNI, D3K.GUXKI, D3K.GUXNP, D3K.NIXDA, 16-D3K, 32-D3K, 59D3K-16, 59D3K-68, 68D3K-32, 68D3K-16 | 1-00299028 Rev. #2 | 5 Hour(s) | No Impact | #N/A
2026-07-13 08:00 | 2026-07-30 16:00 | 17.3333 | LOWER NOTCH JCT, WIDDIFIELD TS | W71D.WIXLO, 38-W71D, W71D-38 | 1-00298159 Rev. #5 | 5 Hour(s) | No Impact | #N/A
2026-08-04 08:00 | 2026-08-21 16:00 | 17.3333 | LOWER NOTCH JCT, DYMOND TS | T1-L71, T2-L71, W71D-32, W71D.LOXDY | 1-00313264 Rev. #1 | 5 Hour(s) | No Impact | #N/A
2026-07-13 08:00 | 2026-07-30 16:00 | 17.3333 | LOWER NOTCH JCT, WIDDIFIELD TS | W71D.WIXLO, 38-W71D, W71D-38 | 1-00298159 Rev. #5 | 5 Hour(s) | No Impact | #N/A
2026-08-04 08:00 | 2026-08-21 16:00 | 17.3333 | LOWER NOTCH JCT, DYMOND TS | T1-L71, T2-L71, W71D-32, W71D.LOXDY | 1-00313264 Rev. #1 | 5 Hour(s) | No Impact | #N/A
2026-08-23 08:00 | 2026-09-24 16:00 | 32.3333 | AUBREY FALLS JCT, WAWA TS, MISSISSAGI TS | P25W.AUXMI, P25W.AUXWA, 14-P25W, 34-P25W | 1-00294347 Rev. #7 | 5 Hour(s) | EWTE EWTW | 280 200
2026-10-25 08:00 | 2026-11-19 16:00 | 25.3333 | AUBREY FALLS JCT, WAWA TS, MISSISSAGI TS | P26W.AUXMI, P26W.AUXWA, 34-P26W, 14-P26W | 1-00302105 Rev. #2 | 5 Hour(s) | EWTE EWTW | 280 200
2026-12-06 08:00 | 2026-12-17 16:00 | 11.3333 | MISSISSAGI TS, ALGOMA TS | A23P.MIXAL, 26-A23P, 34-A23P | 1-00298969 Rev. #2 | 5 Hour(s) | EWTE EWTW | 175 150
2024-06-20 18:00 | 2027-12-31 16:00 | 1288.9167 | PATRICK ST TS | 1900-07-23 | 1-00257104 Rev. #19 | Non-recallable | No Impact | #N/A
2026-03-12 16:30 | 2026-09-30 16:00 | 201.9792 | BFN JCT | 653W4H-9989 | 1-00309134 Rev. #11 | Non-recallable | No Impact | #N/A
2026-04-27 07:00 | 2027-12-16 16:00 | 598.375 | PORCUPINE TS | T1-D1, SVC1 | 1-00312403 Rev. #6 | Non-recallable | No Impact | #N/A
2026-05-26 08:00 | 2026-07-08 16:00 | 43.3333 | MARTINDALE TS, ETHEL LAKE JCT, CREIGHTON JCT, ESPANOLA TS | 52S2B-32, 66S2B-52, 9-S2B, S2B-9 | 1-00295068 Rev. #19 | 6 Hour(s) | No Impact | #N/A
2026-05-26 08:00 | 2026-07-09 16:00 | 44.3333 | CLARABELLE JCT, VALE FROOD STOBIE 2 JCT, HANMER TS, VALE COPPER 4 CTS, CLARABELLE TS | X23N.CLXCL, X23N.CLXFR, X23N.CLXIN, X23N.FRXHA, 33-X23N, 28T1-X23N | 1-00295078 Rev. #9 | 5 Hour(s) | No Impact | #N/A
2026-06-01 17:00 | 2026-09-21 08:00 | 111.625 | PORCUPINE TS | T8, T8-HT8, 30T8-H2, TEMPH2-BO1 | 1-00305822 Rev. #13 | 46 Day(s) | No Impact | #N/A
2026-06-02 08:00 | 2026-07-14 16:00 | 42.3333 | BLIND RIVER TS, ELLIOTT LAKE TS | B4E.ELXBL, 19-B4E, 23-B4E | 1-00312168 Rev. #1 | 5 Hour(s) | No Impact | #N/A
2026-08-04 08:00 | 2026-08-14 16:00 | 10.3333 | PINARD TS, PINARD JCT, OTTER RAPIDS SS, ABITIBI CANYON SS | R21D.PIXCA, R21D.PIXOT, R21D.PIXPI, 31-R21D | 1-00295120 Rev. #5 | 5 Hour(s) | No Impact | #N/A
2026-08-10 13:00 | 2026-08-17 12:00 | 6.9583 | MACKAY TS, MILE HILL JCT | 678, 682, 680, L24_BUS, 539K24G-MSO | 1-00290726 Rev. #5 | 8 Hour(s) | EWTE EWTW | 175 150
2026-08-22 08:00 | 2026-09-01 16:00 | 10.3333 | MATTAWA JCT, NORTH BAY TS | 15L5A-A3, 583L5A-387 | 1-00300376 Rev. #3 | 5 Hour(s) | No Impact | #N/A
2026-09-13 12:00 | 2026-09-25 09:00 | 11.875 | THIRD LINE TS | 408, DL21, DL22, AL25, DL26, L25L26, 1709-G25, 1709-G26 | 1-00291016 Rev. #9 | 8 Hour(s) | No Impact | #N/A
2026-09-28 07:00 | 2026-10-08 09:00 | 10.0833 | THIRD LINE TS | 405, 412, 545, K24G-BO, AWT3, AL25, DL26, L25L26, 1709-G25, 1709-G26 | 1-00292533 Rev. #9 | 8 Hour(s) | EWTE EWTW | 175 150
2026-10-14 07:00 | 2026-10-23 17:00 | 9.4167 | THIRD LINE TS | 412, 415, 1657, 549, T2, T2H_BUS | 1-00289949 Rev. #2 | 4 Hour(s) | No Impact | #N/A
2026-12-07 08:00 | 2026-12-17 16:00 | 10.3333 | MATTAWA JCT, NORTH BAY TS | 15L5A-A3, 583L5A-387 | 1-00298970 Rev. #2 | 5 Hour(s) | No Impact | #N/A
2026-12-06 08:00 | 2026-12-17 16:00 | 11.3333 | MISSISSAGI TS, ALGOMA TS | A23P.MIXAL, 26-A23P, 34-A23P | 1-00298969 Rev. #2 | 5 Hour(s) | EWTE EWTW | 175 150
Back to main menu

## Table 4.9
Back to main menu
Table 4.9: Northwest Zone Transmission Outages
Planned Start | Planned End | Duration (Days) | Station | Equipment Name | Outage ID | Max Recall | Major Transmission Interface Impacted | Reduction in Limit (MW)
2026-09-11 07:00 | 2026-10-15 16:00 | 34.375 | MOOSE LAKE TS | T2B, T3B, TL2, TL6, AT-MSO, ATPT-AT, T2, T3, TSS2, T2-AT, T3-AT | 1-00295125 Rev. #7 | 8 Hour(s) | No Impact | #N/A
2026-09-18 08:00 | 2026-10-20 16:00 | 32.3333 | MARGACH DS, RABBIT LAKE SS | 15-K6F, 24T2-L, K6FT1-T2 | 1-00304036 Rev. #5 | 5 Hour(s) | EWTE EWTW | 175 125
2026-11-23 08:00 | 2026-12-16 16:00 | 23.3333 | RABBIT LAKE SS | L2L4 | 1-00298951 Rev. #3 | 8 Hour(s) | No Impact | #N/A
2024-05-14 13:00 | 2026-12-31 16:00 | 961.125 | KENORA TS, WHITESHELL TS | K21W.WHXKE, 34-K21W | 1-00254393 Rev. #21 | 6 Hour(s) | EWTE EWTW | 25 25
2024-05-14 15:54 | 2026-12-31 23:59 | 961.3368 | WHITESHELL TS | R4, R70, PS7 | 1-00254335 Rev. #14 | Non-recallable | No Impact | #N/A
2025-11-18 08:00 | 2026-12-31 16:00 | 408.3333 | KENORA TS, WHITESHELL TS | K21W.WHXKE, 34-K21W | 1-00299527 Rev. #10 | 2 Hour(s) | EWTE EWTW | 25 25
2026-06-29 07:00 | 2026-07-10 16:00 | 11.375 | MACKENZIE TS, LAKEHEAD TS | A21L.MKXLA, HL21, L21L25, 12-A21L, 20-A21L | 1-00285118 Rev. #27 | 1 Day(s) | EWTE EWTW | 230 150
2026-06-29 08:00 | 2026-07-05 16:00 | 6.3333 | LAKEHEAD TS, MACKENZIE TS | A21L.MKXLA, 12-A21L, 20-A21L | 1-00295092 Rev. #11 | 6 Min(s) | EWTE EWTW | 230 150
2026-06-29 08:00 | 2026-07-10 16:00 | 11.3333 | MACKENZIE TS, LAKEHEAD TS | A21L: MACKENZIE TS x LAKEHEAD TS, 20-A21L | 1-00304070 Rev. #7 | 24 Hour(s) | EWTE EWTW | 230 150
2026-06-29 09:16 | 2026-07-10 16:00 | 11.2806 | LAKEHEAD TS, MACKENZIE TS | A21L.MKXLA, 12-A21L, 20-A21L | 1-00287610 Rev. #10 | 5 Hour(s) | EWTE EWTW | 230 150
2026-07-12 07:00 | 2026-07-24 16:00 | 12.375 | MACKENZIE TS, FORT FRANCES TS | F25A.FOXMK, L21L25, PL25, 20-F25A, 22-F25A | 1-00288965 Rev. #12 | 2 Day(s) | EWTE EWTW | 175 125
2026-07-12 08:00 | 2026-07-24 16:00 | 12.3333 | FORT FRANCES TS, MACKENZIE TS | F25A.FOXMK, 20-F25A, 22-F25A | 1-00295104 Rev. #4 | 5 Hour(s) | EWTE EWTW | 175 125
2026-07-27 08:00 | 2026-08-14 11:00 | 18.125 | LAKEHEAD TS, MACKENZIE TS | A22L.MKXLA, L22L93, PL22, 12-A22L, 20-A22L | 1-00285119 Rev. #16 | 1 Day(s) | EWTE EWTW | 230 150
2026-07-27 08:00 | 2026-08-14 11:00 | 18.125 | LAKEHEAD TS, MACKENZIE TS | A22L.MKXLA, 12-A22L, 20-A22L | 1-00287611 Rev. #11 | 6 Hour(s) | EWTE EWTW | 230 150
2026-07-27 09:16 | 2026-08-14 11:00 | 18.0722 | LAKEHEAD TS, MACKENZIE TS | A22L.MKXLA, 12-A22L, 20-A22L | 1-00295111 Rev. #8 | 5 Hour(s) | EWTE EWTW | 230 150
2026-08-21 08:00 | 2026-09-03 16:00 | 13.3333 | MARATHON DS, MARATHON TS, TERRACE BAY SS, PIC JCT, MARATHON DS JCT | T1M.PIXMA, T1M.PIXMD, 77T1M, 15-T1M, 2735T1-L | 1-00300375 Rev. #7 | 5 Hour(s) | EWTE EWTW | 175 125
2026-09-13 07:00 | 2026-09-27 16:00 | 14.375 | MACKENZIE TS | HL93 | 1-00288959 Rev. #11 | 5 Day(s) | EWTE EWTW | 175 125
2026-09-18 08:00 | 2026-10-20 16:00 | 32.3333 | MARGACH DS, RABBIT LAKE SS | 15-K6F, 24T2-L, K6FT1-T2 | 1-00304036 Rev. #5 | 5 Hour(s) | EWTE EWTW | 175 125
2026-10-06 07:00 | 2026-10-21 17:00 | 15.4167 | MACKENZIE TS | PL25 | 1-00288960 Rev. #10 | 5 Day(s) | EWTE EWTW | 175 125
2026-10-06 08:00 | 2026-10-29 16:00 | 23.3333 | LAKEHEAD TS, BIRCH TS, PINE PORTAGE SS | R2LB.BIXLA, R2LB.LAXPI, 12-R2LB, 17-R2LB, 26-R2LB | 1-00295286 Rev. #2 | 5 Hour(s) | No Impact | #N/A
2026-10-22 07:00 | 2026-11-05 16:00 | 14.375 | MOOSE LAKE TS | L1L3, L3L6, 3-A3M | 1-00299139 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2026-10-22 08:00 | 2026-11-06 16:00 | 15.3333 | MACKENZIE TS, MOOSE LAKE TS | A3M.MAXMO, 20-A3M, 3-A3M | 1-00287613 Rev. #2 | 5 Hour(s) | EWTE EWTW | 175 125
2026-11-22 08:00 | 2026-12-06 16:00 | 14.3333 | ALEXANDER SS, MINNOVA JCT | 4-A5A, A5A-5 | 1-00299012 Rev. #2 | 6 Hour(s) | EWTE EWTW | 175 125
2026-11-23 08:00 | 2026-12-05 16:00 | 12.3333 | FORT FRANCES TS, MACKENZIE TS | F25A.FOXMK, 20-F25A, 22-F25A | 1-00287614 Rev. #2 | 2 Day(s) | EWTE EWTW | 175 125
2027-03-30 08:00 | 2027-07-08 16:00 | 100.3333 | LAKEHEAD TS, MACKENZIE TS | A22L.MKXLA, L22L93, L22L23, PL22, L22_BUS | 1-00299000 Rev. #1 | 8 Hour(s) | EWTE EWTW | 230 150
2019-05-29 08:00 | 2026-12-31 16:00 | 2773.3333 | FORT FRANCES TS | SC1.2, SC1, SC1.2-1 | 1-00117652 Rev. #14 | Non-recallable | No Impact | #N/A
2026-06-29 08:00 | 2026-07-24 16:00 | 25.3333 | MACKENZIE TS | L21L25 | 1-00287615 Rev. #9 | Non-recallable | No Impact | #N/A
2026-07-06 11:00 | 2026-07-27 16:00 | 21.2083 | FORGIE JCT, KEEWATIN JCT | 299SK1-90, FORGIE-2 | 1-00300324 Rev. #4 | 5 Hour(s) | No Impact | #N/A
2026-07-09 08:00 | 2026-07-26 16:00 | 17.3333 | LAKEHEAD TS | PL37 | 1-00295102 Rev. #6 | 6 Hour(s) | No Impact | #N/A
2026-07-13 08:00 | 2026-12-27 16:00 | 167.3333 | BIRCH TS | SC11R11 | 1-00312184 Rev. #1 | 2 Hour(s) | No Impact | #N/A
2026-07-27 08:00 | 2026-09-13 16:00 | 48.3333 | RABBIT LAKE SS | HL7 | 1-00295115 Rev. #8 | 5 Day(s) | No Impact | #N/A
2026-08-04 08:00 | 2026-08-14 11:00 | 10.125 | MACKENZIE TS | PL22 | 1-00313040 Rev. #3 | 6 Day(s) | No Impact | #N/A
2026-08-11 17:00 | 2026-08-19 17:00 | 8 | MARATHON TS | T12, SC21T12-T, T12-H, T12-K, T12-SS | 1-00299165 Rev. #6 | 2 Hour(s) | No Impact | #N/A
2026-08-19 07:00 | 2026-09-07 17:00 | 19.4167 | MACKENZIE TS | HL21 | 1-00288970 Rev. #4 | 5 Day(s) | No Impact | #N/A
2026-08-25 08:00 | 2026-09-26 16:00 | 32.3333 | BIRCH TS, PORT ARTHUR TS 1 | P7B.BIXPO, 2P7B, 17-P7B | 1-00295071 Rev. #8 | 5 Hour(s) | No Impact | #N/A
2026-10-09 07:00 | 2026-10-22 19:00 | 13.5 | DRYDEN TS | HL26, HL23, T22R22, H_BUS, T22, R22, T22-H, T22-P, T22-T22R22, TSS22-T | 1-00288972 Rev. #3 | 3 Day(s) | No Impact | #N/A
2026-10-09 08:00 | 2026-10-22 16:00 | 13.3333 | DRYDEN TS | HL23, PL2, PL3, T22R22, 25-D5D, P_BUS, T22, TSS22, R22, T22-H, T22-P, T22-T22R22, TSS22-T | 1-00299072 Rev. #2 | 4 Hour(s) | No Impact | #N/A
2026-10-29 08:00 | 2026-11-20 16:00 | 22.3333 | RABBIT LAKE SS | L2L7 | 1-00298950 Rev. #4 | 8 Hour(s) | No Impact | #N/A
2026-11-05 07:00 | 2026-11-15 16:00 | 10.375 | LAKEHEAD TS, MARATHON TS | PL37, W1L37, 12-M37L, L37_BUS, 15-M37L | 1-00288977 Rev. #13 | 8 Hour(s) | EWTE EWTW | 175 125
2026-11-16 08:00 | 2026-11-22 16:00 | 6.3333 | SAPAWE JCT, KASHABOWIE JCT | FR67-3, SPWE-17 | 1-00299031 Rev. #2 | 8 Hour(s) | No Impact | #N/A
2027-06-23 07:00 | 2027-09-04 17:00 | 73.4167 | MARATHON TS | KL1 | 1-00297200 Rev. #4 | Non-recallable | No Impact | #N/A
Back to main menu

## Table 4.10
Back to main menu
Table 4.10: Ottawa Zone Transmission Outages
Planned Start | Planned End | Duration (Days) | Station | Equipment Name | Outage ID | Max Recall | Major Transmission Interface Impacted | Reduction in Limit (MW)
2026-07-20 08:00 | 2026-07-31 16:00 | 11.3333 | ST. ISIDORE TS, LONGUEUIL TS | A1A2, T3J, T1Q | 1-00311452 Rev. #3 | 2 Hour(s) | FIO BEAU P33C | 250 690 0
2026-09-17 08:00 | 2026-09-23 16:00 | 6.3333 | HAWTHORNE TS | HT5L31 | 1-00297864 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2026-11-30 08:00 | 2026-12-11 16:00 | 11.3333 | HAWTHORNE TS | HT5L5, KL5 | 1-00297876 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2027-05-31 03:30 | 2027-06-11 16:00 | 11.5208 | HAWTHORNE TS, MASSON GS, IPB MASSON JCT, ST. ISIDORE TS, ORLEANS JCT 2, ORLEANS TS, CUMBERLAND JCT, LONGUEUIL JCT, LONGUEUIL TS | D5A.CUXGA, D5A.CUXIS, D5A.CUXO2, D5A.HAXO2, D5A.IPXMA, D5A.LOXIS, D5A.LOXLO, D5A.O2XOR, A1A2, HT5L5, KL5, 325T2-D5A, 48-D5A, 62D5A-26, T3-D5A, T1-A1, 62D5A-625 | 1-00296584 Rev. #3 | 6 Hour(s) | FIO BEAU P33C | 250 690 0
2026-11-16 06:30 | 2026-11-27 16:30 | 11.4167 | CHATS FALLS TS, SOUTH MARCH TS | C3S.CFXSO, A1A2, 2-C3S, A9-C3S, A2_BUS, T2-A | 1-00196163 Rev. #50 | 6 Hour(s) | FIO BEAU P33C | 500 0 150
2026-11-16 06:30 | 2026-11-27 16:30 | 11.4167 | CHATS FALLS TS, SOUTH MARCH TS | C3S.CFXSO, 2-C3S, A9-C3S | 1-00299033 Rev. #3 | 4 Hour(s) | FIO BEAU P33C | 500 0 150
2026-11-16 06:30 | 2026-11-27 16:30 | 11.4167 | CHATS FALLS TS, SOUTH MARCH TS | C3S.CFXSO, DL3, HL3, 2-C3S, A9-C3S | 1-00299036 Rev. #3 | 8 Hour(s) | FIO BEAU P33C | 500 0 150
2026-07-20 08:00 | 2026-07-31 16:00 | 11.3333 | ST. ISIDORE TS, LONGUEUIL TS | A1A2, T3J, T1Q | 1-00311452 Rev. #3 | 2 Hour(s) | FIO BEAU P33C | 250 690 0
2026-09-14 06:30 | 2026-09-25 16:00 | 11.3958 | MERIVALE TS, TERRY FOX JCT | 319E34M-6, 6-E34M | 1-00295134 Rev. #3 | 6 Hour(s) | No Impact | #N/A
2026-09-27 14:30 | 2026-10-16 15:30 | 19.0417 | ALBION TS, ALBION JCT, MERIVALE TS, ELLWOOD MTS JCT, HAWTHORNE TS | M30A.AJXEJ, M30A.ALXME, M30A.EJXHA, 48-M30A, 6-M30A, 84T2-M30A | 1-00313177 Rev. #1 | 4 Hour(s) | FIO BEAU P33C | 0 0 0
2026-11-16 06:30 | 2026-11-27 16:30 | 11.4167 | CHATS FALLS TS, SOUTH MARCH TS | C3S.CFXSO, A1A2, 2-C3S, A9-C3S, A2_BUS, T2-A | 1-00196163 Rev. #50 | 6 Hour(s) | FIO BEAU P33C | 500 0 150
2026-11-16 06:30 | 2026-11-27 16:30 | 11.4167 | CHATS FALLS TS, SOUTH MARCH TS | C3S.CFXSO, 2-C3S, A9-C3S | 1-00299033 Rev. #3 | 4 Hour(s) | FIO BEAU P33C | 500 0 150
2026-11-16 06:30 | 2026-11-27 16:30 | 11.4167 | CHATS FALLS TS, SOUTH MARCH TS | C3S.CFXSO, DL3, HL3, 2-C3S, A9-C3S | 1-00299036 Rev. #3 | 8 Hour(s) | FIO BEAU P33C | 500 0 150
2027-05-31 03:30 | 2027-06-11 16:00 | 11.5208 | HAWTHORNE TS, MASSON GS, IPB MASSON JCT, ST. ISIDORE TS, ORLEANS JCT 2, ORLEANS TS, CUMBERLAND JCT, LONGUEUIL JCT, LONGUEUIL TS | D5A.CUXGA, D5A.CUXIS, D5A.CUXO2, D5A.HAXO2, D5A.IPXMA, D5A.LOXIS, D5A.LOXLO, D5A.O2XOR, A1A2, HT5L5, KL5, 325T2-D5A, 48-D5A, 62D5A-26, T3-D5A, T1-A1, 62D5A-625 | 1-00296584 Rev. #3 | 6 Hour(s) | FIO BEAU P33C | 250 690 0
2026-11-30 08:00 | 2026-12-11 16:00 | 11.3333 | HAWTHORNE TS | HT5L5, KL5 | 1-00297876 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2027-05-31 03:30 | 2027-06-11 16:00 | 11.5208 | HAWTHORNE TS, MASSON GS, IPB MASSON JCT, ST. ISIDORE TS, ORLEANS JCT 2, ORLEANS TS, CUMBERLAND JCT, LONGUEUIL JCT, LONGUEUIL TS | D5A.CUXGA, D5A.CUXIS, D5A.CUXO2, D5A.HAXO2, D5A.IPXMA, D5A.LOXIS, D5A.LOXLO, D5A.O2XOR, A1A2, HT5L5, KL5, 325T2-D5A, 48-D5A, 62D5A-26, T3-D5A, T1-A1, 62D5A-625 | 1-00296584 Rev. #3 | 6 Hour(s) | FIO BEAU P33C | 250 690 0
2026-07-05 08:00 | 2026-07-24 16:00 | 19.3333 | ARNPRIOR TS, ARNPRIOR JCT, MARCHWOOD JCT, MISSISSIPPI JCT, CHATS FALLS TS, STEWARTVILLE TS | W6CS.ARXAR, W6CS.ARXMI, W6CS.ARXST, W6CS.CHXMI, W6CS.MIXMA, 10-W6CS, 59W6CS-58, 61W6CS-ILS2, 61W6CS-LC2, 2W6CS-L | 1-00312236 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2025-11-27 08:00 | 2026-10-14 08:00 | 321 | RUSSELL TS | 36T2-A5RK, A5RK-TEMPNEWT2 | 1-00296803 Rev. #11 | Immediate | No Impact | #N/A
2025-11-27 08:00 | 2027-04-04 07:00 | 492.9583 | RUSSELL TS | 36T1-A6R, A6R-TEMPNEWT1 | 1-00296798 Rev. #9 | Immediate | No Impact | #N/A
2026-09-09 08:00 | 2026-09-15 16:00 | 6.3333 | HAWTHORNE TS | KL41 | 1-00297862 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2026-09-24 08:00 | 2026-09-30 16:00 | 6.3333 | HAWTHORNE TS | LT1L41 | 1-00297867 Rev. #3 | 4 Hour(s) | FIO BEAU P33C | 0 0 0
2026-09-25 11:30 | 2026-12-01 09:30 | 66.9167 | MERIVALE TS | T23-WT23 | 1-00313130 Rev. #1 | Non-recallable | No Impact | #N/A
2026-09-26 12:00 | 2026-10-10 08:00 | 13.8333 | CUMBERLAND JCT | 625D5A-BO | 1-00308402 Rev. #2 | 8 Hour(s) | FIO BEAU P33C | 0 0 0
2026-10-08 08:00 | 2026-10-15 16:00 | 7.3333 | HAWTHORNE TS | DLT1 | 1-00297871 Rev. #3 | 4 Hour(s) | FIO BEAU P33C | 0 0 0
2026-10-25 08:00 | 2026-11-06 16:00 | 12.3333 | HAWTHORNE TS, KING EDWARD TS, OVERBROOK TS, CYRVILLE JCT, BLACKBURN JCT, MOULTON JCT | A4K.BLXCY, A4K.HAXBL, A4K.KIXOV, 48-A4K, 63-A4K, 8A4K-48, A4K-63, A4K-48 | 1-00302104 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2027-05-04 08:00 | 2027-05-18 16:00 | 14.3333 | BORROMEE JCT, ORLEANS TS, HAWTHORNE TS | 325T1-H9A, 48-H9A, 64H9A-BO | 1-00295131 Rev. #6 | 4 Hour(s) | FIO BEAU P33C | 0 0 0
2027-05-31 07:00 | 2027-06-07 17:00 | 7.4167 | HAWTHORNE TS | KL42 | 1-00298961 Rev. #2 | 4 Hour(s) | No Impact | #N/A
2027-06-19 16:00 | 2027-09-20 07:00 | 92.625 | HAWTHORNE TS | KL42 | 1-00298958 Rev. #2 | Non-recallable | No Impact | #N/A
2026-07-20 08:00 | 2026-07-31 16:00 | 11.3333 | ST. ISIDORE TS, LONGUEUIL TS | A1A2, T3J, T1Q | 1-00311452 Rev. #3 | 2 Hour(s) | FIO BEAU P33C | 250 690 0
2026-09-17 08:00 | 2026-09-23 16:00 | 6.3333 | HAWTHORNE TS | HT5L31 | 1-00297864 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2026-11-30 08:00 | 2026-12-11 16:00 | 11.3333 | HAWTHORNE TS | HT5L5, KL5 | 1-00297876 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2027-05-31 03:30 | 2027-06-11 16:00 | 11.5208 | HAWTHORNE TS, MASSON GS, IPB MASSON JCT, ST. ISIDORE TS, ORLEANS JCT 2, ORLEANS TS, CUMBERLAND JCT, LONGUEUIL JCT, LONGUEUIL TS | D5A.CUXGA, D5A.CUXIS, D5A.CUXO2, D5A.HAXO2, D5A.IPXMA, D5A.LOXIS, D5A.LOXLO, D5A.O2XOR, A1A2, HT5L5, KL5, 325T2-D5A, 48-D5A, 62D5A-26, T3-D5A, T1-A1, 62D5A-625 | 1-00296584 Rev. #3 | 6 Hour(s) | FIO BEAU P33C | 250 690 0
Back to main menu

## Table 4.11
Back to main menu
Table 4.11: Southwest Zone Transmission Outages
Planned Start | Planned End | Duration (Days) | Station | Equipment Name | Outage ID | Max Recall | Major Transmission Interface Impacted | Reduction in Limit (MW)
2026-04-09 14:07 | 2026-08-30 16:00 | 143.0785 | MIDDLEPORT TS | T3, T3-L580, T3-HT3 | 1-00312084 Rev. #3 | Non-recallable | No Impact | #N/A
2026-05-04 07:00 | 2026-08-28 16:00 | 116.375 | MIDDLEPORT TS | T3, T3-L580, T3-HT3 | 1-00313634 Rev. #17 | Non-recallable | No Impact | #N/A
2026-06-09 07:00 | 2026-08-01 12:00 | 53.2083 | NANTICOKE TS, MIDDLEPORT TS, CLAIREVILLE TS | N580M.MDXNA, V586M.MDXCL, DL580, L580WT11, 25-N580M, 25-V586M, 51-V586M, 59-N580M | 1-00287149 Rev. #10 | 7 Day(s) | FABCW NBLIP BLIP | 550 0 0
2026-06-09 07:15 | 2026-07-18 16:00 | 39.3646 | MIDDLEPORT TS, CLAIREVILLE TS | V586M.MDXCL, 25-V586M, 51-V586M | 1-00308128 Rev. #6 | 4 Hour(s) | FABCW NBLIP BLIP | 300 0 0
2026-07-03 14:00 | 2026-08-14 16:00 | 42.0833 | MIDDLEPORT TS, HANNON JCT | 25-M34H, 61M34H-TEMP1 | 1-00287126 Rev. #13 | 4 Hour(s) |  | #N/A
2026-07-07 07:15 | 2026-07-18 16:00 | 11.3646 | MIDDLEPORT TS, CLAIREVILLE TS | V586M.MDXCL, 25-V586M, 51-V586M | 1-00306897 Rev. #6 | 4 Hour(s) | FABCW NBLIP BLIP | 300 0 0
2026-07-13 06:15 | 2026-07-24 16:00 | 11.4062 | BURLINGTON TS, HORNING JCT, MIDDLEPORT TS, HORNING TS | M27B.HOXBU, M27B.HOXHO, M27B.HOXMI, 25-M27B, 39-M27B, 4T4-M27B | 1-00296668 Rev. #5 | 6 Hour(s) | No Impact | #N/A
2026-07-20 06:15 | 2026-07-31 16:00 | 11.4062 | BURLINGTON TS, BURLINGTON DESN TS, BURLINGTON JCT, BECK 2 TS, NIAGARA WEST JCT, MIDDLEPORT TS, NEALE JCT, CARLUKE JCT | Q25BM.BEXNI, Q25BM.BUXBD, Q25BM.BUXBU, Q25BM.MIXCA, Q25BM.NEXBU, 25-Q25BM, 28-Q25BM, 39-Q25BM, T15-Q25BM | 1-00289213 Rev. #7 | 4 Hour(s) | No Impact | #N/A
2026-07-27 06:15 | 2026-08-12 16:00 | 16.4062 | BURLINGTON TS, HORNING TS, HORNING JCT, MIDDLEPORT TS | M28B.HOXBU, M28B.HOXHO, M28B.HOXMI, 25-M28B, 39-M28B, 4T3-M28B | 1-00296669 Rev. #5 | 6 Hour(s) | No Impact | #N/A
2026-08-04 07:00 | 2026-08-20 16:00 | 16.375 | CLAIREVILLE TS, MIDDLEPORT TS | V586M.MDXCL, L552L586, PL586, 25-V586M, 51-V586M | 1-00308169 Rev. #3 | 4 Hour(s) | FABCW NBLIP BLIP | 300 0 0
2026-08-10 06:15 | 2026-08-21 15:00 | 11.3646 | EVERETT TS, ESSA TS, ALLISTON JCT, ALLISTON TS, EVERETT JCT, ORANGEVILLE TS | E9V.ALXAL, E9V.ALXES, E9V.ALXEV, E9V.EVXOR, 138E9V-MSO, 138T1-E9V, 18-E9V, 1807E9V-BO, 22-E9V, T2-E8V, T2-E9V, 9T4-E9V | 1-00298264 Rev. #17 | 4 Hour(s) | FABCW NBLIP BLIP | 200 0 0
2026-08-31 08:00 | 2026-09-11 16:00 | 11.3333 | DETWEILER TS | AL4, AL6, AL7, ASC21, HT1A, SC21AT, 26-M21D, A_BUS, SC21, SVC1 | 1-00296349 Rev. #9 | 4 Hour(s) | FABCW NBLIP BLIP | 100 0 0
2026-09-08 06:15 | 2026-09-15 16:00 | 7.4062 | BURLINGTON TS, BURLINGTON DESN TS, BURLINGTON JCT, BECK 2 TS, NIAGARA WEST JCT, MIDDLEPORT TS, NEALE JCT, CARLUKE JCT | Q25BM.BEXNI, Q25BM.BUXBD, Q25BM.BUXBU, Q25BM.MIXCA, Q25BM.NEXBU, 25-Q25BM, 28-Q25BM, 39-Q25BM, T15-Q25BM | 1-00313527 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2026-09-13 06:00 | 2026-10-16 16:00 | 33.4167 | NANTICOKE TS, LONGWOOD TS | N582L.LOXNA, AWT13, DL582, HT8L582, L582WT13, 59-N582L, HT13_BUS, HT8_BUS, T13-WT13, W52-N582L | 1-00293595 Rev. #8 | 16 Hour(s) | FABCW NBLIP BLIP | 1100 300 800
2026-09-13 08:00 | 2026-09-18 16:00 | 5.3333 | LONGWOOD TS, NANTICOKE TS | N582L.LOXNA, HL582, KL582, 59-N582L, W52-N582L | 1-00295560 Rev. #9 | 4 Hour(s) | FABCW NBLIP BLIP | 1100 300 800
2026-09-14 06:15 | 2026-10-02 16:00 | 18.4062 | MEAFORD TS, OWEN SOUND TS | S2S.MEXOW, A1-OS, C2-S2S | 1-00312938 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2026-09-20 06:15 | 2026-09-27 16:00 | 7.4062 | PRESTON JCT, GALT JCT, GALT TS, GALT SOUTH JCT, DETWEILER TS, TRINITY JCT, DETWEILER JCT, KITCHENER MTS 6, PRESTON TS, MIDDLEPORT TS | M20D.DEXDE, M20D.DEXGA, M20D.DEXWI, M20D.GAXMI, M20D.GAXPR, M20D.PRXGA, M20D.PRXPR, 21-M20D, 25-M20D, 26-M20D, 65-M20D, M20D.GSXGJ, M20D.TRXGS, 429M20D-41 | 1-00295586 Rev. #4 | 4 Hour(s) | FABCW NBLIP BLIP | 100 0 0
2026-09-29 06:15 | 2026-10-09 15:00 | 10.3646 | SCHEIFELE JCT, GUELPH NORTH JCT, WATERLOO NORTH 3 JCT, WATERLOO MTS 3, DETWEILER TS | D6V.DEXWA, D6V.SCXGU, D6V.WAXSC, D6V.WAXWA, 26-D6V, 2613D6V-2602 | 1-00295582 Rev. #4 | 4 Hour(s) | FABCW NBLIP BLIP | 100 0 0
2026-10-14 06:15 | 2026-10-30 16:00 | 16.4062 | SCHEIFELE JCT, GUELPH NORTH JCT, WATERLOO NORTH 3 JCT, WATERLOO MTS 3, DETWEILER TS | D6V.DEXWA, D6V.SCXGU, D6V.WAXSC, D6V.WAXWA, 26-D6V, 2613D6V-2602 | 1-00295599 Rev. #3 | 4 Hour(s) | FABCW NBLIP BLIP | 100 0 0
2026-10-19 06:15 | 2026-10-29 06:15 | 10 | MIDDLEPORT TS, CLAIREVILLE TS | V586M.MDXCL, L552L586, PL586, 25-V586M, 51-V586M | 1-00313524 Rev. #1 | 48 Hour(s) | FABCW NBLIP BLIP | 300 0 0
2026-10-19 07:30 | 2026-12-11 16:00 | 53.3542 | MIDDLEPORT TS, CLAIREVILLE TS | V586M.MDXCL, L80L86, 25-V586M, 51-V586M | 1-00288368 Rev. #5 | Non-recallable | FABCW NBLIP BLIP | 300 0 0
2026-10-29 06:15 | 2026-11-04 07:15 | 6.0417 | ESSA TS, CLAIREVILLE TS, MIDDLEPORT TS | E510V.CLXES, V586M.MDXCL, AL510, L552L586, PL586, W3L510, 18-E510V, 25-V586M, 51-E510V, 51-V586M | 1-00313522 Rev. #1 | 48 Hour(s) | FABCW NBLIP BLIP | 300 0 0
2026-11-01 08:00 | 2027-03-19 16:00 | 138.3333 | CLAIREVILLE TS, MIDDLEPORT TS | V586M.MDXCL, AL510, W3L510, 25-V586M, 51-E510V, 51-V586M | 1-00311616 Rev. #1 | Non-recallable | FABCW NBLIP BLIP | 300 0 0
2026-11-03 06:15 | 2026-12-03 16:00 | 30.4062 | CAMPBELL TS, SPEED RIVER JCT, CEDAR TS, WATERLOO NORTH 3 JCT, SCHEIFELE JCT, WATERLOO MTS 3, GUELPH NORTH JCT, DETWEILER TS | D7V.CAXCJ, D7V.DEXWA, D7V.GUXCA, D7V.WAXSC, D7V.WAXWA, 26-D7V, 2613D7V-2608, 5T4-D7V, T2-D7V, T4-D7V | 1-00295584 Rev. #2 | 4 Hour(s) | FABCW NBLIP BLIP | 100 0 0
2027-02-22 08:00 | 2027-04-02 16:00 | 39.3333 | NANTICOKE TS, LONGWOOD TS | N582L.LOXNA, AWT13, DL582, HT8L582, L582WT13, 59-N582L, HT13_BUS, T13-WT13, W52-N582L | 1-00308115 Rev. #2 | Non-recallable | FABCW NBLIP BLIP | 1100 300 800
2026-07-03 14:00 | 2026-08-14 16:00 | 42.0833 | MIDDLEPORT TS, HANNON JCT | 25-M34H, 61M34H-TEMP1 | 1-00287126 Rev. #13 | 4 Hour(s) | No Impact | #N/A
2026-07-13 06:15 | 2026-07-24 16:00 | 11.4062 | BURLINGTON TS, HORNING JCT, MIDDLEPORT TS, HORNING TS | M27B.HOXBU, M27B.HOXHO, M27B.HOXMI, 25-M27B, 39-M27B, 4T4-M27B | 1-00296668 Rev. #5 | 6 Hour(s) | No Impact | #N/A
2026-07-20 06:15 | 2026-07-31 16:00 | 11.4062 | BURLINGTON TS, BURLINGTON DESN TS, BURLINGTON JCT, BECK 2 TS, NIAGARA WEST JCT, MIDDLEPORT TS, NEALE JCT, CARLUKE JCT | Q25BM.BEXNI, Q25BM.BUXBD, Q25BM.BUXBU, Q25BM.MIXCA, Q25BM.NEXBU, 25-Q25BM, 28-Q25BM, 39-Q25BM, T15-Q25BM | 1-00289213 Rev. #7 | 4 Hour(s) | No Impact | #N/A
2026-07-27 06:15 | 2026-08-12 16:00 | 16.4062 | BURLINGTON TS, HORNING TS, HORNING JCT, MIDDLEPORT TS | M28B.HOXBU, M28B.HOXHO, M28B.HOXMI, 25-M28B, 39-M28B, 4T3-M28B | 1-00296669 Rev. #5 | 6 Hour(s) | No Impact | #N/A
2026-09-08 06:15 | 2026-09-15 16:00 | 7.4062 | BURLINGTON TS, BURLINGTON DESN TS, BURLINGTON JCT, BECK 2 TS, NIAGARA WEST JCT, MIDDLEPORT TS, NEALE JCT, CARLUKE JCT | Q25BM.BEXNI, Q25BM.BUXBD, Q25BM.BUXBU, Q25BM.MIXCA, Q25BM.NEXBU, 25-Q25BM, 28-Q25BM, 39-Q25BM, T15-Q25BM | 1-00313527 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2026-06-09 07:00 | 2026-08-01 12:00 | 53.2083 | NANTICOKE TS, MIDDLEPORT TS, CLAIREVILLE TS | N580M.MDXNA, V586M.MDXCL, DL580, L580WT11, 25-N580M, 25-V586M, 51-V586M, 59-N580M | 1-00287149 Rev. #10 | 7 Day(s) | FABCW NBLIP BLIP | 550 0 0
2026-06-09 07:15 | 2026-07-18 16:00 | 39.3646 | MIDDLEPORT TS, CLAIREVILLE TS | V586M.MDXCL, 25-V586M, 51-V586M | 1-00308128 Rev. #6 | 4 Hour(s) | FABCW NBLIP BLIP | 300 0 0
2026-07-07 07:15 | 2026-07-18 16:00 | 11.3646 | MIDDLEPORT TS, CLAIREVILLE TS | V586M.MDXCL, 25-V586M, 51-V586M | 1-00306897 Rev. #6 | 4 Hour(s) | FABCW NBLIP BLIP | 300 0 0
2026-08-04 07:00 | 2026-08-20 16:00 | 16.375 | CLAIREVILLE TS, MIDDLEPORT TS | V586M.MDXCL, L552L586, PL586, 25-V586M, 51-V586M | 1-00308169 Rev. #3 | 4 Hour(s) | FABCW NBLIP BLIP | 300 0 0
2026-09-01 07:00 | 2026-09-22 16:30 | 21.3958 | TRAFALGAR TS, PALERMO TS, BURLINGTON TS, GLENORCHY JCT, PALERMO TXB JCT, LANTZ JCT, GLENORCHY MTS1 | T37B.GJXGL, T37B.GJXLA, T37B.PAXBU, T37B.PAXTR, T37B.PJXGJ, 31-T37B, 31SC21L-T37B, 39-T37B, T4-T37B | 1-00296683 Rev. #6 | 12 Hour(s) | No Impact | #N/A
2026-09-13 06:00 | 2026-10-16 16:00 | 33.4167 | NANTICOKE TS, LONGWOOD TS | N582L.LOXNA, AWT13, DL582, HT8L582, L582WT13, 59-N582L, HT13_BUS, HT8_BUS, T13-WT13, W52-N582L | 1-00293595 Rev. #8 | 16 Hour(s) | FABCW NBLIP BLIP | 1100 300 800
2026-09-13 08:00 | 2026-09-18 16:00 | 5.3333 | LONGWOOD TS, NANTICOKE TS | N582L.LOXNA, HL582, KL582, 59-N582L, W52-N582L | 1-00295560 Rev. #9 | 4 Hour(s) | FABCW NBLIP BLIP | 1100 300 800
2026-09-23 07:00 | 2026-10-20 16:00 | 27.375 | PALERMO TS, TRAFALGAR TS, BURLINGTON TS, PALERMO TXB JCT, GLENORCHY JCT, LANTZ JCT, GLENORCHY MTS1 | T36B.GJXGL, T36B.GJXLA, T36B.PAXBU, T36B.PAXTR, T36B.PJXGJ, 31-T36B, 31SC21L-T36B, 39-T36B, T3-T36B | 1-00310816 Rev. #2 | 8 Hour(s) | No Impact | #N/A
2026-10-19 06:15 | 2026-10-29 06:15 | 10 | MIDDLEPORT TS, CLAIREVILLE TS | V586M.MDXCL, L552L586, PL586, 25-V586M, 51-V586M | 1-00313524 Rev. #1 | 48 Hour(s) | FABCW NBLIP BLIP | 300 0 0
2026-10-19 07:30 | 2026-12-11 16:00 | 53.3542 | MIDDLEPORT TS, CLAIREVILLE TS | V586M.MDXCL, L80L86, 25-V586M, 51-V586M | 1-00288368 Rev. #5 | Non-recallable | FABCW NBLIP BLIP | 300 0 0
2026-10-21 07:00 | 2026-11-20 10:00 | 30.125 | TRAFALGAR TS, PALERMO TS, BURLINGTON TS, GLENORCHY JCT, PALERMO TXB JCT, LANTZ JCT, GLENORCHY MTS1 | T37B.GJXGL, T37B.GJXLA, T37B.PAXBU, T37B.PAXTR, T37B.PJXGJ, 31-T37B, 31SC21L-T37B, 39-T37B, T4-T37B | 1-00309267 Rev. #6 | 12 Hour(s) | No Impact | #N/A
2026-10-29 06:15 | 2026-11-04 07:15 | 6.0417 | ESSA TS, CLAIREVILLE TS, MIDDLEPORT TS | E510V.CLXES, V586M.MDXCL, AL510, L552L586, PL586, W3L510, 18-E510V, 25-V586M, 51-E510V, 51-V586M | 1-00313522 Rev. #1 | 48 Hour(s) | FABCW NBLIP BLIP | 300 0 0
2026-11-01 08:00 | 2027-03-19 16:00 | 138.3333 | CLAIREVILLE TS, MIDDLEPORT TS | V586M.MDXCL, AL510, W3L510, 25-V586M, 51-E510V, 51-V586M | 1-00311616 Rev. #1 | Non-recallable | FABCW NBLIP BLIP | 300 0 0
2027-02-22 08:00 | 2027-04-02 16:00 | 39.3333 | NANTICOKE TS, LONGWOOD TS | N582L.LOXNA, AWT13, DL582, HT8L582, L582WT13, 59-N582L, HT13_BUS, T13-WT13, W52-N582L | 1-00308115 Rev. #2 | Non-recallable | FABCW NBLIP BLIP | 1100 300 800
2026-10-29 06:15 | 2026-11-04 07:15 | 6.0417 | ESSA TS, CLAIREVILLE TS, MIDDLEPORT TS | E510V.CLXES, V586M.MDXCL, AL510, L552L586, PL586, W3L510, 18-E510V, 25-V586M, 51-E510V, 51-V586M | 1-00313522 Rev. #1 | 48 Hour(s) | FABCW NBLIP BLIP | 300 0 0
2026-11-01 08:00 | 2027-03-19 16:00 | 138.3333 | CLAIREVILLE TS, MIDDLEPORT TS | V586M.MDXCL, AL510, W3L510, 25-V586M, 51-E510V, 51-V586M | 1-00311616 Rev. #1 | Non-recallable | FABCW NBLIP BLIP | 300 0 0
2026-10-29 06:15 | 2026-11-04 07:15 | 6.0417 | ESSA TS, CLAIREVILLE TS, MIDDLEPORT TS | E510V.CLXES, V586M.MDXCL, AL510, L552L586, PL586, W3L510, 18-E510V, 25-V586M, 51-E510V, 51-V586M | 1-00313522 Rev. #1 | 48 Hour(s) | FABCW NBLIP BLIP | 300 0 0
2026-11-01 08:00 | 2027-03-19 16:00 | 138.3333 | CLAIREVILLE TS, MIDDLEPORT TS | V586M.MDXCL, AL510, W3L510, 25-V586M, 51-E510V, 51-V586M | 1-00311616 Rev. #1 | Non-recallable | FABCW NBLIP BLIP | 300 0 0
2026-10-22 07:00 | 2026-10-30 16:00 | 8.375 | NANTICOKE TS | SC22K1, SC22SC, SC22 | 1-00298903 Rev. #2 | 6 Hour(s) | No Impact | #N/A
2024-08-22 14:20 | 2026-12-31 16:00 | 861.0694 | NANTICOKE TS | SVC1 | 1-00263077 Rev. #8 | Non-recallable | No Impact | #N/A
2024-10-27 08:00 | 2026-12-31 16:00 | 795.3333 | NANTICOKE TS | T13, SVC1, T13-WT13 | 1-00269611 Rev. #4 | Non-recallable | No Impact | #N/A
2026-06-15 08:00 | 2026-12-25 16:00 | 193.3333 | MIDDLEPORT TS | SS3, SS3-K | 1-00308162 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2026-06-21 06:15 | 2026-07-06 16:00 | 15.4062 | BEAMSVILLE TS, WINONA TS, WINONA JCT | Q2AH.WIXBE, 115Q2AH-18, 18Q2AH-17 | 1-00298777 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2026-08-16 06:15 | 2026-10-16 16:00 | 61.4062 | BRONTE TS, BURLINGTON TS, PALERMO JCT | B8.BRXBR, B8.BRXBU, 39-B8, T2-B8, T2-B7, T4, 13T4-B8 | 1-00298822 Rev. #7 | 6 Hour(s) | No Impact | #N/A
2026-08-24 07:00 | 2026-09-11 16:00 | 18.375 | GLANFORD JCT, HORNING MOUNTAIN JCT, MOHAWK TS | B3.GLXHO, B3.MOXGL, 76B3-1, 20T2-B3 | 1-00298826 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2026-08-31 08:00 | 2026-09-11 16:00 | 11.3333 | DETWEILER TS | T1, T1-HT1, SVC1 | 1-00295860 Rev. #15 | 6 Hour(s) | No Impact | #N/A
2026-09-13 08:00 | 2026-10-16 16:00 | 33.3333 | NANTICOKE TS | HT8L582 | 1-00309262 Rev. #2 | 4 Hour(s) | No Impact | #N/A
2026-09-14 07:00 | 2026-10-02 16:00 | 18.375 | MOHAWK TS, GLANFORD JCT, HORNING MOUNTAIN JCT | 76B4-1, 20T1-B4, B4.GLXHO, B4.MOXGL | 1-00298849 Rev. #6 | 4 Hour(s) | No Impact | #N/A
2026-09-22 08:00 | 2026-09-30 16:00 | 8.3333 | BURLINGTON TS | L23L37 | 1-00298863 Rev. #4 | 6 Hour(s) | No Impact | #N/A
2026-10-01 08:15 | 2026-10-30 16:00 | 29.3229 | ALLANBURG TS, ALLANBURG WEST JCT, MIDDLEPORT TS, ABITIBI CONSOLIDATED NAN91 JCT, BECK 2 TS | Q26M.MIXAW, Q28A.ALXAB, 25-Q26M, 28-Q28A, 45-Q28A, 64Q26M-25, Q26M-Q10P, Q28A-Q10P | 1-00289214 Rev. #3 | 60 Hour(s) | No Impact | #N/A
2026-10-02 07:00 | 2026-10-15 16:00 | 13.375 | WINONA TS, WINONA JCT, SALTFLEET JCT, BEACH TS | Q2AH.HAXSA, Q2AH.SAXWI, Q2AH.WI2XWI2, 115Q2AH-17, 17-Q2AH | 1-00310812 Rev. #2 | 0 Hour(s) | No Impact | #N/A
2026-10-05 06:15 | 2026-10-30 17:00 | 25.4479 | BRANT TS, POWERLINE JCT, BURLINGTON TS, DUNDAS 2 JCT, DUNDAS 2 TS, HORNING MOUNTAIN JCT, ALFORD JCT, NEWTON TS | 117T5-B12BL, 12-B12BL, 26-B12BL, 26-B13BL, 39-B12BL, B12BL.BRXPO, B12BL.DUXDU, B12BL.HOXAL, B12BL.HOXDU, B12BL.ALXBR, B12BL.BUXDU, B12BL.NEXHO | 1-00296675 Rev. #2 | 4 Hour(s) | No Impact | #N/A
2026-10-08 07:15 | 2026-10-14 16:00 | 6.3646 | SUMMERHAVEN SS, MIDDLEPORT TS, CALEDONIA JCT, CALEDONIA TS | S39M.CAXCA, S39M.CAXMI, S39M.SUXCA, 25-S39M, 262-S39M, N27T1-S39M | 1-00296671 Rev. #6 | 4 Hour(s) | No Impact | #N/A
2026-10-16 16:00 | 2027-02-22 08:00 | 128.6667 | NANTICOKE TS | AWT13, HT8L582, L582WT13, HT13_BUS, HT8_BUS, T13-WT13 | 1-00298901 Rev. #2 | Non-recallable | No Impact | #N/A
2026-10-18 08:00 | 2026-10-23 16:00 | 5.3333 | BEACH TS | 17-H36D | 1-00298902 Rev. #2 | 4 Hour(s) | No Impact | #N/A
2026-11-02 06:15 | 2026-11-27 17:00 | 25.4479 | DUNDAS JCT, MCMASTER JCT, BURLINGTON TS, GLANFORD JCT, HORNING MOUNTAIN JCT, MOHAWK TS, NEWTON TS, DUNDAS TS | B3.DUXBU, B3.GLXHO, B3.HOXNE, B3.MCXDU, B3.MOXGL, 26B3-39, 26B4-39, 39-B3, 76B3-1, T2, T2-B3, 20T2-B3, B3.MCXHO | 1-00298907 Rev. #2 | 4 Hour(s) | No Impact | #N/A
2026-11-16 07:15 | 2026-12-03 16:00 | 17.3646 | BURLINGTON TS, GAGE TS, GAGE JCT, BIRMINGHAM TS | B10.BIXGA, B10.BUXGA, B10.GAXGA, B11.BIXGA, B11.BUXGA, B11.GAXGA, 24-B11, 24-K2G, 24-B10, 24-K1G, 39-B11, 39-B10, 50-B11, 50-B10 | 1-00298916 Rev. #2 | 4 Hour(s) | No Impact | #N/A
2026-07-16 07:00 | 2026-08-04 16:00 | 19.375 | BEACH TS | D1L24, D1L29, D1TL34, D1_BUS, T7-D1 | 1-00309214 Rev. #4 | 4 Hour(s) | No Impact | #N/A
2026-08-04 06:15 | 2026-08-28 16:00 | 24.4062 | FREEPORT SS, KITCHENER MTS 7 JCT, DETWEILER JCT, KITCHENER MTS 6 JCT, SIEBERT JCT, DETWEILER TS | D7F.DEXDE, D7F.DEXK6, D7F.FRXK7, D7F.SIXK6, 26-D7F, 59D7F-D1W, 59D9F-D1W, 60L7L12-7 | 1-00295715 Rev. #9 | 4 Hour(s) | No Impact | #N/A
2026-08-30 12:30 | 2026-09-10 16:30 | 11.1667 | SEAFORTH TS, SEAFORTH LSO JCT, ST. MARYS TS | BY, DTL18, KL6, KTL18, KTL7, 61-61M18, K_BUS, TL18_BUS, L7S-M18, T2-TL18, T5-K, DBUS-TEMP1 | 1-00296308 Rev. #5 | 8 Hour(s) | No Impact | #N/A
2026-09-15 07:30 | 2026-09-21 16:30 | 6.375 | SEAFORTH TS, SEAFORTH LSO JCT, ST. MARYS TS | BY, DL6, DTL18, DTL7, KTL7, 61-L7S, D_BUS, L7S-M18, T1-TL7, T6-D | 1-00296312 Rev. #5 | 12 Hour(s) | No Impact | #N/A
2026-09-20 06:15 | 2026-09-27 16:00 | 7.4062 | PRESTON JCT, GALT JCT, GALT TS, GALT SOUTH JCT, DETWEILER TS, TRINITY JCT, DETWEILER JCT, KITCHENER MTS 6, PRESTON TS, MIDDLEPORT TS | M20D.DEXDE, M20D.DEXGA, M20D.DEXWI, M20D.GAXMI, M20D.GAXPR, M20D.PRXGA, M20D.PRXPR, 21-M20D, 25-M20D, 26-M20D, 65-M20D, M20D.GSXGJ, M20D.TRXGS, 429M20D-41 | 1-00295586 Rev. #4 | 4 Hour(s) | FABCW NBLIP BLIP | 100 0 0
2026-09-22 07:30 | 2026-09-29 07:30 | 7 | SEAFORTH TS, SEAFORTH LSO JCT, ST. MARYS TS | BY, DTL7, KL6, KTL18, KTL7, 61-L7S, K_BUS, L7S-M18, T1-TL7, T5-K, DBUS-TEMP2 | 1-00296313 Rev. #5 | 6 Hour(s) | No Impact | #N/A
2026-09-29 07:30 | 2026-10-13 07:30 | 14 | SEAFORTH TS, ST. MARYS TS | BY, DL6, DTL18, DTL7, D_BUS, T6-D | 1-00296314 Rev. #8 | 4 Hour(s) | No Impact | #N/A
2026-09-29 07:30 | 2026-10-13 16:30 | 14.375 | SEAFORTH TS, SEAFORTH LSO JCT | DTL7, KTL7, 61-L7S, L7S-M18, T1-TL7 | 1-00296315 Rev. #5 | 6 Hour(s) | No Impact | #N/A
2026-10-15 08:30 | 2026-10-20 16:00 | 5.3125 | BUCHANAN TS, INGERSOLL TS | W12.BUXIN, L12K, L9L12, 19-W12, 38W7-19, 38W12-19 | 1-00295725 Rev. #4 | 4 Hour(s) | No Impact | #N/A
2026-10-22 07:00 | 2026-11-13 16:00 | 22.375 | BEACH TS | H3H5, H3L9, H4H8, H5H7, H6H7, H8L9, 17-HL3, H7_BUS, H8_BUS, T7-H7, T8-H8, H3_BUS | 1-00313526 Rev. #1 | 0 Hour(s) | No Impact | #N/A
Back to main menu

## Table 4.12
Back to main menu
Table 4.12: Toronto Zone Transmission Outages
Planned Start | Planned End | Duration (Days) | Station | Equipment Name | Outage ID | Max Recall | Major Transmission Interface Impacted | Reduction in Limit (MW)
2026-07-27 07:00 | 2026-08-14 16:00 | 18.375 | CLAIREVILLE TS, CHERRYWOOD TS, PARKWAY JCT, PARKWAY TS | C553VP.CHXPJ, C553VP.PJXCL, C553VP.PJXPR, A2L553, L553L560, 51-C553VP, 52-C553VP, 81-C553VP | 1-00295576 Rev. #8 | 4 Hour(s) | FABCW | 200
2026-08-21 07:00 | 2026-08-31 16:00 | 10.375 | GERRARD JCT, HEARN SS, DON FLEET JCT, LEASIDE TS, CECIL TS, BLOOR STREET JCT | H6LC.BLXLE, H6LC.CEXGE, H6LC.DOXHE, H6LC.GEXBL, H6LC.GEXDO, H1L6, L5L6, L6L13, PL6, 22-H6LC-L6-G, 34-H6LC, 49-H6LC, 80H6LC-34, 80H6LC-22, 80H6LC-49 | 1-00266296 Rev. #11 | 24 Hour(s) | No Impact | #N/A
2026-09-15 07:00 | 2026-09-23 16:00 | 8.375 | CLAIREVILLE TS | H1L82, L76L82, 51-H82V | 1-00293913 Rev. #19 | 4 Hour(s) | No Impact | #N/A
2026-09-15 08:00 | 2026-09-26 16:01 | 11.334 | WOODBRIDGE JCT, CLAIREVILLE TS, VAUGHAN 4 JCT, VAUGHAN MTS #4, HOLLAND TS, HOLLAND JCT | 51-H82V, 153-H82V, H82V.WJXCL, H82V.4JXV4, H82V.4JXWJ, H82V.HJX4J, H82V.HOXHJ | 1-00296672 Rev. #8 | 4 Hour(s) | No Impact | #N/A
2026-09-23 08:45 | 2026-10-02 16:00 | 9.3021 | HEARN SS, BASIN TS, BASIN JCT, GERRARD TS, CARLAW TS, LEASIDE TS, BLOOR STREET JCT, MILL STREET JCT | H3L.BAXBA, H3L.BAXHE, H3L.BAXMI, H3L.BLXLE, H3L.CAXGE, H3L.GEXBL, H3L.MIXGE, H2L3, LT2L3, LT2L11, 22-H3L-L3-G, 34-H3L, 4-H3L, 87-H3L, H3L-34, H3L-22, H3L-87, 4H3LR1, H3L-CA | 1-00239128 Rev. #33 | 6 Hour(s) | No Impact | #N/A
2026-11-03 08:00 | 2026-11-10 16:00 | 7.3333 | HEARN SS, DON FLEET JCT, ESPLANADE TS, COPELAND SS, LOWER SIMCOE ST JCT | K1L9, L7L9, L9L13, 22-H9DE, T13-D, H9DE.DOXES, H9DE.ESXLS, H9DE.HEXDO, H9DE.LSXCP, K2L9 | 1-00296049 Rev. #5 | 4 Hour(s) | No Impact | #N/A
2027-04-01 08:00 | 2027-06-04 16:00 | 64.3333 | WOODBRIDGE JCT, CLAIREVILLE TS, VAUGHAN 4 JCT, VAUGHAN MTS #4, HOLLAND TS, HOLLAND JCT | 51-H82V, 153-H82V, H82V.WJXCL, H82V.4JXV4, H82V.4JXWJ, H82V.HJX4J, H82V.HOXHJ | 1-00308207 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2026-10-13 08:00 | 2026-11-04 16:00 | 22.3333 | CLARINGTON TS, HAVELOCK TS, MARINE JCT, OTONABEE TS, DUFFIN JCT, OSHAWA WILSON TS, CHERRYWOOD TS, WHITBY TS, WILSON JCT, WHITBY JCT, B23C H26C TIE JCT | 81-T23C, 81-T28C, 128T1-T31H, 54T2-T23C, 40T3-T23C, 54T4-T23C, K2L28, L23L28, L23L31, P2L31, 296-T23C, 296-T28C, 296-T31H, L28_BUS, L31_BUS, T28C.CLXDJ, T31H.HAXMJ, T31H.MJXCL, T31H.MJXOT, T23C.BJXCH, T23C.CLXWJ, T23C.WJXBJ, T23C.WJXWH, T23C.WJXWI, T23C.WJXWY, 57-T31H, 54T7-T23C, L23_BUS | 1-00295709 Rev. #4 | 12 Hour(s) | No Impact | #N/A
2027-05-12 06:00 | 2027-05-19 16:30 | 7.4375 | CHERRYWOOD TS, CLARINGTON TS, DUFFIN JCT | 81-T28C, K2L28, L23L28, 296-T28C, T28C.CLXDJ | 1-00297185 Rev. #2 | 4 Hour(s) | No Impact | #N/A
2026-09-15 07:00 | 2026-09-23 16:00 | 8.375 | CLAIREVILLE TS | H1L82, L76L82, 51-H82V | 1-00293913 Rev. #19 | 4 Hour(s) | No Impact | #N/A
2026-09-15 08:00 | 2026-09-26 16:01 | 11.334 | WOODBRIDGE JCT, CLAIREVILLE TS, VAUGHAN 4 JCT, VAUGHAN MTS #4, HOLLAND TS, HOLLAND JCT | 51-H82V, 153-H82V, H82V.WJXCL, H82V.4JXV4, H82V.4JXWJ, H82V.HJX4J, H82V.HOXHJ | 1-00296672 Rev. #8 | 4 Hour(s) | No Impact | #N/A
2027-03-28 08:00 | 2027-04-23 16:00 | 26.3333 | WOODBRIDGE JCT, VAUGHAN 3 JCT, WOODBRIDGE TS, KLEINBURG TS, CLAIREVILLE TS | V44.CLXWJ, V44.KLXV3, V44.V3XWJ, V44.WJXWO, 45T1-V44, 51-V44, D6T5-V44 | 1-00308228 Rev. #1 | 8 Hour(s) | No Impact | #N/A
2027-04-01 08:00 | 2027-06-04 16:00 | 64.3333 | WOODBRIDGE JCT, CLAIREVILLE TS, VAUGHAN 4 JCT, VAUGHAN MTS #4, HOLLAND TS, HOLLAND JCT | 51-H82V, 153-H82V, H82V.WJXCL, H82V.4JXV4, H82V.4JXWJ, H82V.HJX4J, H82V.HOXHJ | 1-00308207 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2026-06-09 07:00 | 2026-08-01 12:00 | 53.2083 | NANTICOKE TS, MIDDLEPORT TS, CLAIREVILLE TS | N580M.MDXNA, V586M.MDXCL, DL580, L580WT11, 25-N580M, 25-V586M, 51-V586M, 59-N580M | 1-00287149 Rev. #10 | 7 Day(s) | FABCW | 550
2026-06-09 07:15 | 2026-07-18 16:00 | 39.3646 | MIDDLEPORT TS, CLAIREVILLE TS | V586M.MDXCL, 25-V586M, 51-V586M | 1-00308128 Rev. #6 | 4 Hour(s) | FABCW | 300
2026-07-07 07:15 | 2026-07-18 16:00 | 11.3646 | MIDDLEPORT TS, CLAIREVILLE TS | V586M.MDXCL, 25-V586M, 51-V586M | 1-00306897 Rev. #6 | 4 Hour(s) | FABCW | 300
2026-07-20 06:15 | 2026-08-28 16:00 | 39.4062 | BRUCE B SS, MILTON SS, BRUCE JCT, WILLOW CREEK JCT | B561M.BBXBR, B561M.BRXWI, B561M.WIXMI, 40-B561M, L501L563, 29-B561M | 1-00293589 Rev. #9 | 4 Hour(s) | FABCW | 1750
2026-07-27 07:00 | 2026-08-14 16:00 | 18.375 | CLAIREVILLE TS, CHERRYWOOD TS, PARKWAY JCT, PARKWAY TS | C553VP.CHXPJ, C553VP.PJXCL, C553VP.PJXPR, A2L553, L553L560, 51-C553VP, 52-C553VP, 81-C553VP | 1-00295576 Rev. #8 | 4 Hour(s) | FABCW | 200
2026-08-04 07:00 | 2026-08-20 16:00 | 16.375 | CLAIREVILLE TS, MIDDLEPORT TS | V586M.MDXCL, L552L586, PL586, 25-V586M, 51-V586M | 1-00308169 Rev. #3 | 4 Hour(s) | FABCW | 300
2026-08-30 08:00 | 2026-09-11 16:00 | 12.3333 | WILLOW CREEK JCT, MILTON SS, BRUCE B SS, BRUCE JCT | B501M.BBXBJ, B501M.BJXWJ, B501M.WJXMI, 40-B501M, 29-B501M | 1-00293593 Rev. #9 | 4 Hour(s) | FABCW | 1750
2026-08-30 08:00 | 2026-09-11 16:00 | 12.3333 | WILLOW CREEK JCT, MILTON SS, BRUCE B SS, BRUCE JCT | B501M.BBXBJ, B501M.BJXWJ, B501M.WJXMI, HL501, L501L570, 40-B501M, 29-B501M | 1-00295573 Rev. #10 | 4 Hour(s) | FABCW | 1750
2026-08-31 07:15 | 2026-09-11 16:00 | 11.3646 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, 18-E510V, 51-E510V | 1-00308103 Rev. #5 | 4 Hour(s) | No Impact | #N/A
2026-09-27 08:00 | 2026-10-28 16:00 | 31.3333 | ESSA TS, CLAIREVILLE TS | E511V.CLXES, 18-E511V, 51-E511V | 1-00287147 Rev. #10 | 48 Hour(s) | No Impact | #N/A
2026-09-28 07:00 | 2026-10-09 16:00 | 11.375 | CLAIREVILLE TS | HT16L75, HT16L72, HT16_BUS, T16, T16-W4, T16-HT16 | 1-00295577 Rev. #5 | 4 Hour(s) | FABCW | 250
2026-10-19 06:15 | 2026-10-29 06:15 | 10 | MIDDLEPORT TS, CLAIREVILLE TS | V586M.MDXCL, L552L586, PL586, 25-V586M, 51-V586M | 1-00313524 Rev. #1 | 48 Hour(s) | FABCW | 300
2026-10-19 07:30 | 2026-12-11 16:00 | 53.3542 | MIDDLEPORT TS, CLAIREVILLE TS | V586M.MDXCL, L80L86, 25-V586M, 51-V586M | 1-00288368 Rev. #5 | Non-recallable | FABCW | 300
2026-10-26 08:00 | 2026-12-25 16:00 | 60.3333 | CLAIREVILLE TS, RICHVIEW JCT, RICHVIEW DESN TS, RICHVIEW TS, WESTMORE JCT, REXDALE TS | V74R.RIXRD, V74R.RIXRI, V74R.RIXWE, V74R.WEXCL, V74R.WEXRE, H2L74, HT13L74, 51-V74R, 88-V74R, T1-V74R, T5-V74R, 51V74R-BO | 1-00308160 Rev. #3 | 36 Hour(s) | FABCW | 250
2026-10-29 06:15 | 2026-11-04 07:15 | 6.0417 | ESSA TS, CLAIREVILLE TS, MIDDLEPORT TS | E510V.CLXES, V586M.MDXCL, AL510, L552L586, PL586, W3L510, 18-E510V, 25-V586M, 51-E510V, 51-V586M | 1-00313522 Rev. #1 | 48 Hour(s) | FABCW | 300
2026-11-01 07:00 | 2026-12-04 17:00 | 33.4167 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, 18-E510V, 51-E510V | 1-00296677 Rev. #8 | 48 Hour(s) | No Impact | #N/A
2026-11-01 08:00 | 2027-03-19 16:00 | 138.3333 | CLAIREVILLE TS, MIDDLEPORT TS | V586M.MDXCL, AL510, W3L510, 25-V586M, 51-E510V, 51-V586M | 1-00311616 Rev. #1 | Non-recallable | FABCW | 300
2026-11-01 08:00 | 2027-03-19 16:00 | 138.3333 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, AL510, W3L510, 18-E510V, 51-E510V | 1-00296678 Rev. #3 | Non-recallable | No Impact | #N/A
2027-02-19 08:00 | 2027-02-26 16:00 | 7.3333 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, 18-E510V, 51-E510V | 1-00308208 Rev. #1 | 8 Hour(s) | No Impact | #N/A
2026-07-17 08:00 | 2026-07-30 17:01 | 13.3757 | CLAIREVILLE TS, RICHVIEW JCT, RICHVIEW DESN TS, RICHVIEW TS, WESTMORE JCT, REXDALE TS | V74R.RIXRD, V74R.RIXRI, V74R.RIXWE, V74R.WEXCL, V74R.WEXRE, 51-V74R, 88-V74R, T1-V74R, T5-V74R | 1-00308229 Rev. #6 | 4 Hour(s) | No Impact | #N/A
2026-07-27 07:00 | 2026-08-14 16:00 | 18.375 | CLAIREVILLE TS, CHERRYWOOD TS, PARKWAY JCT, PARKWAY TS | C553VP.CHXPJ, C553VP.PJXCL, C553VP.PJXPR, A2L553, L553L560, 51-C553VP, 52-C553VP, 81-C553VP | 1-00295576 Rev. #8 | 4 Hour(s) | FABCW | 200
2026-09-13 07:00 | 2026-09-18 16:00 | 5.375 | CLAIREVILLE TS, RICHVIEW TS | V73R.CLXRI, H1L73, HT15L73, 51-V73R, 88-V73R | 1-00296670 Rev. #6 | 4 Hour(s) | FABCW | 0
2026-10-26 08:00 | 2026-12-25 16:00 | 60.3333 | CLAIREVILLE TS, RICHVIEW JCT, RICHVIEW DESN TS, RICHVIEW TS, WESTMORE JCT, REXDALE TS | V74R.RIXRD, V74R.RIXRI, V74R.RIXWE, V74R.WEXCL, V74R.WEXRE, H2L74, HT13L74, 51-V74R, 88-V74R, T1-V74R, T5-V74R, 51V74R-BO | 1-00308160 Rev. #3 | 36 Hour(s) | FABCW | 0
2026-08-30 08:00 | 2026-09-11 16:00 | 12.3333 | WILLOW CREEK JCT, MILTON SS, BRUCE B SS, BRUCE JCT | B501M.BBXBJ, B501M.BJXWJ, B501M.WJXMI, 40-B501M, 29-B501M | 1-00293593 Rev. #9 | 4 Hour(s) | FABCW | 1750
2026-08-30 08:00 | 2026-09-11 16:00 | 12.3333 | WILLOW CREEK JCT, MILTON SS, BRUCE B SS, BRUCE JCT | B501M.BBXBJ, B501M.BJXWJ, B501M.WJXMI, HL501, L501L570, 40-B501M, 29-B501M | 1-00295573 Rev. #10 | 4 Hour(s) | FABCW | 1750
2026-06-09 07:00 | 2026-08-01 12:00 | 53.2083 | NANTICOKE TS, MIDDLEPORT TS, CLAIREVILLE TS | N580M.MDXNA, V586M.MDXCL, DL580, L580WT11, 25-N580M, 25-V586M, 51-V586M, 59-N580M | 1-00287149 Rev. #10 | 7 Day(s) | FABCW | 550
2026-06-09 07:15 | 2026-07-18 16:00 | 39.3646 | MIDDLEPORT TS, CLAIREVILLE TS | V586M.MDXCL, 25-V586M, 51-V586M | 1-00308128 Rev. #6 | 4 Hour(s) | FABCW | 300
2026-07-07 07:15 | 2026-07-18 16:00 | 11.3646 | MIDDLEPORT TS, CLAIREVILLE TS | V586M.MDXCL, 25-V586M, 51-V586M | 1-00306897 Rev. #6 | 4 Hour(s) | FABCW | 300
2026-07-20 06:15 | 2026-08-28 16:00 | 39.4062 | BRUCE B SS, MILTON SS, BRUCE JCT, WILLOW CREEK JCT | B561M.BBXBR, B561M.BRXWI, B561M.WIXMI, 40-B561M, L501L563, 29-B561M | 1-00293589 Rev. #9 | 4 Hour(s) | FABCW | 1750
2026-07-27 07:00 | 2026-08-07 16:00 | 11.375 | CLAIREVILLE TS, RICHVIEW TS, CLAIREVILLE JCT | V79R.CLXCL, V79R.CLXRI, HT14L79, K2L79, 51-V79R, 88-V79R | 1-00298812 Rev. #3 | 4 Hour(s) | FABCW | 0
2026-07-27 07:00 | 2026-08-14 16:00 | 18.375 | CLAIREVILLE TS, CHERRYWOOD TS, PARKWAY JCT, PARKWAY TS | C553VP.CHXPJ, C553VP.PJXCL, C553VP.PJXPR, A2L553, L553L560, 51-C553VP, 52-C553VP, 81-C553VP | 1-00295576 Rev. #8 | 4 Hour(s) | FABCW | 200
2026-08-04 07:00 | 2026-08-20 16:00 | 16.375 | CLAIREVILLE TS, MIDDLEPORT TS | V586M.MDXCL, L552L586, PL586, 25-V586M, 51-V586M | 1-00308169 Rev. #3 | 4 Hour(s) | FABCW | 300
2026-08-31 07:15 | 2026-09-11 16:00 | 11.3646 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, 18-E510V, 51-E510V | 1-00308103 Rev. #5 | 4 Hour(s) | No Impact | #N/A
2026-09-01 07:00 | 2026-09-22 16:30 | 21.3958 | TRAFALGAR TS, PALERMO TS, BURLINGTON TS, GLENORCHY JCT, PALERMO TXB JCT, LANTZ JCT, GLENORCHY MTS1 | T37B.GJXGL, T37B.GJXLA, T37B.PAXBU, T37B.PAXTR, T37B.PJXGJ, 31-T37B, 31SC21L-T37B, 39-T37B, T4-T37B | 1-00296683 Rev. #6 | 12 Hour(s) | No Impact | #N/A
2026-09-08 07:00 | 2026-10-16 17:00 | 38.4167 | GOREWAY PH JCT, GOREWAY TS, CLAIREVILLE TS, GOREWAY JCT, WOODBRIDGE JCT, KLEINBURG TS, VAUGHAN 3 JCT, WOODBRIDGE TS | V43.CLXGJ, V43.CLXWJ, V43.GJXGO, V43.GOXGO, V43.KLXV3, V43.V3XWJ, V43.WJXWO, H2L43, HT14L43, 136T2-V43, 136T4-V43, 136T6-V43, 45T2-V43, 51-V43, D6T3-V43 | 1-00287122 Rev. #17 | 48 Hour(s) | FABCW | 0
2026-09-13 07:00 | 2026-09-18 16:00 | 5.375 | CLAIREVILLE TS, RICHVIEW TS | V73R.CLXRI, H1L73, HT15L73, 51-V73R, 88-V73R | 1-00296670 Rev. #6 | 4 Hour(s) | FABCW | 0
2026-09-23 07:00 | 2026-10-20 16:00 | 27.375 | PALERMO TS, TRAFALGAR TS, BURLINGTON TS, PALERMO TXB JCT, GLENORCHY JCT, LANTZ JCT, GLENORCHY MTS1 | T36B.GJXGL, T36B.GJXLA, T36B.PAXBU, T36B.PAXTR, T36B.PJXGJ, 31-T36B, 31SC21L-T36B, 39-T36B, T3-T36B | 1-00310816 Rev. #2 | 8 Hour(s) | No Impact | #N/A
2026-09-27 08:00 | 2026-10-28 16:00 | 31.3333 | ESSA TS, CLAIREVILLE TS | E511V.CLXES, 18-E511V, 51-E511V | 1-00287147 Rev. #10 | 48 Hour(s) | No Impact | #N/A
2026-09-28 07:00 | 2026-10-09 16:00 | 11.375 | CLAIREVILLE TS | HT16L75, HT16L72, HT16_BUS, T16, T16-W4, T16-HT16 | 1-00295577 Rev. #5 | 4 Hour(s) | FABCW | 250
2026-10-19 06:15 | 2026-10-29 06:15 | 10 | MIDDLEPORT TS, CLAIREVILLE TS | V586M.MDXCL, L552L586, PL586, 25-V586M, 51-V586M | 1-00313524 Rev. #1 | 48 Hour(s) | FABCW | 300
2026-10-19 07:30 | 2026-12-11 16:00 | 53.3542 | MIDDLEPORT TS, CLAIREVILLE TS | V586M.MDXCL, L80L86, 25-V586M, 51-V586M | 1-00288368 Rev. #5 | Non-recallable | FABCW | 300
2026-10-21 07:00 | 2026-11-20 10:00 | 30.125 | TRAFALGAR TS, PALERMO TS, BURLINGTON TS, GLENORCHY JCT, PALERMO TXB JCT, LANTZ JCT, GLENORCHY MTS1 | T37B.GJXGL, T37B.GJXLA, T37B.PAXBU, T37B.PAXTR, T37B.PJXGJ, 31-T37B, 31SC21L-T37B, 39-T37B, T4-T37B | 1-00309267 Rev. #6 | 12 Hour(s) | No Impact | #N/A
2026-10-26 07:00 | 2026-11-20 16:00 | 25.375 | CLAIREVILLE TS, RICHVIEW TS | V77R.CLXCL, L41L77, L71L77, 51-V77R, 88-V77R | 1-00296680 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2026-10-29 06:15 | 2026-11-04 07:15 | 6.0417 | ESSA TS, CLAIREVILLE TS, MIDDLEPORT TS | E510V.CLXES, V586M.MDXCL, AL510, L552L586, PL586, W3L510, 18-E510V, 25-V586M, 51-E510V, 51-V586M | 1-00313522 Rev. #1 | 48 Hour(s) | FABCW | 300
2026-11-01 07:00 | 2026-12-04 17:00 | 33.4167 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, 18-E510V, 51-E510V | 1-00296677 Rev. #8 | 48 Hour(s) | No Impact | #N/A
2026-11-01 08:00 | 2027-03-19 16:00 | 138.3333 | CLAIREVILLE TS, MIDDLEPORT TS | V586M.MDXCL, AL510, W3L510, 25-V586M, 51-E510V, 51-V586M | 1-00311616 Rev. #1 | Non-recallable | FABCW | 300
2026-11-01 08:00 | 2027-03-19 16:00 | 138.3333 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, AL510, W3L510, 18-E510V, 51-E510V | 1-00296678 Rev. #3 | Non-recallable | No Impact | #N/A
2026-11-04 08:00 | 2026-11-10 16:00 | 6.3333 | RICHVIEW TS, CLAIREVILLE TS | V77R.CLXCL, A1L77, L21L77, 51-V77R, 88-V77R | 1-00295786 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2027-02-19 08:00 | 2027-02-26 16:00 | 7.3333 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, 18-E510V, 51-E510V | 1-00308208 Rev. #1 | 8 Hour(s) | No Impact | #N/A
2026-07-17 06:00 | 2026-07-28 16:00 | 11.4167 | CLARINGTON TS, HAVELOCK TS, MARINE JCT, OTONABEE TS | 128T1-T31H, L23L31, P2L31, 296-T31H, L31_BUS, T31H.HAXMJ, T31H.MJXCL, T31H.MJXOT, 57-T31H | 1-00289102 Rev. #31 | 34 Hour(s) | No Impact | #N/A
2026-10-13 08:00 | 2026-11-04 16:00 | 22.3333 | CLARINGTON TS, HAVELOCK TS, MARINE JCT, OTONABEE TS, DUFFIN JCT, OSHAWA WILSON TS, CHERRYWOOD TS, WHITBY TS, WILSON JCT, WHITBY JCT, B23C H26C TIE JCT | 81-T23C, 81-T28C, 128T1-T31H, 54T2-T23C, 40T3-T23C, 54T4-T23C, K2L28, L23L28, L23L31, P2L31, 296-T23C, 296-T28C, 296-T31H, L28_BUS, L31_BUS, T28C.CLXDJ, T31H.HAXMJ, T31H.MJXCL, T31H.MJXOT, T23C.BJXCH, T23C.CLXWJ, T23C.WJXBJ, T23C.WJXWH, T23C.WJXWI, T23C.WJXWY, 57-T31H, 54T7-T23C, L23_BUS | 1-00295709 Rev. #4 | 12 Hour(s) | No Impact | #N/A
2027-05-12 06:00 | 2027-05-19 16:30 | 7.4375 | CHERRYWOOD TS, CLARINGTON TS, DUFFIN JCT | 81-T28C, K2L28, L23L28, 296-T28C, T28C.CLXDJ | 1-00297185 Rev. #2 | 4 Hour(s) | No Impact | #N/A
2026-08-31 07:15 | 2026-09-11 16:00 | 11.3646 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, 18-E510V, 51-E510V | 1-00308103 Rev. #5 | 4 Hour(s) | No Impact | #N/A
2026-09-27 08:00 | 2026-10-28 16:00 | 31.3333 | ESSA TS, CLAIREVILLE TS | E511V.CLXES, 18-E511V, 51-E511V | 1-00287147 Rev. #10 | 48 Hour(s) | No Impact | #N/A
2026-10-29 06:15 | 2026-11-04 07:15 | 6.0417 | ESSA TS, CLAIREVILLE TS, MIDDLEPORT TS | E510V.CLXES, V586M.MDXCL, AL510, L552L586, PL586, W3L510, 18-E510V, 25-V586M, 51-E510V, 51-V586M | 1-00313522 Rev. #1 | 48 Hour(s) | FABCW | 300
2026-11-01 07:00 | 2026-12-04 17:00 | 33.4167 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, 18-E510V, 51-E510V | 1-00296677 Rev. #8 | 48 Hour(s) | No Impact | #N/A
2026-11-01 08:00 | 2027-03-19 16:00 | 138.3333 | CLAIREVILLE TS, MIDDLEPORT TS | V586M.MDXCL, AL510, W3L510, 25-V586M, 51-E510V, 51-V586M | 1-00311616 Rev. #1 | Non-recallable | FABCW | 300
2026-11-01 08:00 | 2027-03-19 16:00 | 138.3333 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, AL510, W3L510, 18-E510V, 51-E510V | 1-00296678 Rev. #3 | Non-recallable | No Impact | #N/A
2027-02-19 08:00 | 2027-02-26 16:00 | 7.3333 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, 18-E510V, 51-E510V | 1-00308208 Rev. #1 | 8 Hour(s) | No Impact | #N/A
2026-08-31 07:15 | 2026-09-11 16:00 | 11.3646 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, 18-E510V, 51-E510V | 1-00308103 Rev. #5 | 4 Hour(s) | No Impact | #N/A
2026-09-27 08:00 | 2026-10-28 16:00 | 31.3333 | ESSA TS, CLAIREVILLE TS | E511V.CLXES, 18-E511V, 51-E511V | 1-00287147 Rev. #10 | 48 Hour(s) | No Impact | #N/A
2026-10-29 06:15 | 2026-11-04 07:15 | 6.0417 | ESSA TS, CLAIREVILLE TS, MIDDLEPORT TS | E510V.CLXES, V586M.MDXCL, AL510, L552L586, PL586, W3L510, 18-E510V, 25-V586M, 51-E510V, 51-V586M | 1-00313522 Rev. #1 | 48 Hour(s) | FABCW | 300
2026-11-01 07:00 | 2026-12-04 17:00 | 33.4167 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, 18-E510V, 51-E510V | 1-00296677 Rev. #8 | 48 Hour(s) | No Impact | #N/A
2026-11-01 08:00 | 2027-03-19 16:00 | 138.3333 | CLAIREVILLE TS, MIDDLEPORT TS | V586M.MDXCL, AL510, W3L510, 25-V586M, 51-E510V, 51-V586M | 1-00311616 Rev. #1 | Non-recallable | FABCW | 300
2026-11-01 08:00 | 2027-03-19 16:00 | 138.3333 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, AL510, W3L510, 18-E510V, 51-E510V | 1-00296678 Rev. #3 | Non-recallable | No Impact | #N/A
2027-02-19 08:00 | 2027-02-26 16:00 | 7.3333 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, 18-E510V, 51-E510V | 1-00308208 Rev. #1 | 8 Hour(s) | No Impact | #N/A
2022-06-22 16:50 | 2026-12-31 16:00 | 1652.9653 | CLARINGTON TS | K1K2, P1P2 | 1-00202079 Rev. #19 | Non-recallable | No Impact | #N/A
2026-06-11 08:30 | 2026-06-30 16:00 | 19.3125 | HEARN SS | K1K2, K2L1, K2L11, K2L14, SC12K2, SC12SC, SS2, SC12, SC12CA-SS2, SC12SC-SC12CA, K2_BUS | 1-00266206 Rev. #40 | 6 Hour(s) | No Impact | #N/A
2026-06-11 08:30 | 2026-06-30 17:00 | 19.3542 | HEARN SS | SC12SC, SC12, SC12SC-SC12CA | 1-00295894 Rev. #10 | 6 Hour(s) | No Impact | #N/A
2026-06-15 09:00 | 2026-07-01 16:00 | 16.2917 | CLAIREVILLE TS | A1P, A2L553, AL510, AL550, AL571, A1_BUS, A2_BUS, A1-A2 | 1-00238547 Rev. #38 | 1 Day(s) | No Impact | #N/A
2026-08-09 07:00 | 2026-08-28 16:00 | 19.375 | WILTSHIRE TS, RUNNYMEDE TS, MANBY EAST TS | K11W.MAXRU, K11W.RUXWI, H2K11W, H2K12W, H1H2, H2H3, H2L18W, H2L13W, H2L14W, 38-K11W, H2_BUS, 11T1-K11W | 1-00308747 Rev. #7 | 6 Hour(s) | No Impact | #N/A
2026-08-09 17:00 | 2026-11-22 17:00 | 105 | CHARLES TS | H2-T4, H2BUS-TEMP | 1-00313374 Rev. #2 | Non-recallable | No Impact | #N/A
2026-08-12 05:45 | 2026-08-28 16:00 | 16.4271 | CLARINGTON TS | SC22P2, SC22SC, SC22 | 1-00298953 Rev. #8 | 8 Hour(s) | No Impact | #N/A
2026-08-16 06:15 | 2026-10-16 16:00 | 61.4062 | BRONTE TS, BURLINGTON TS, PALERMO JCT | B8.BRXBR, B8.BRXBU, 39-B8, T2-B8, T2-B7, T4, 13T4-B8 | 1-00298822 Rev. #7 | 6 Hour(s) | No Impact | #N/A
2026-09-13 08:00 | 2026-09-25 16:00 | 12.3333 | CLAIREVILLE TS | D1L552, DL511, DL560, DL551, DL570, D1_BUS, D2_BUS, D1-D2 | 1-00298848 Rev. #6 | 4 Hour(s) | No Impact | #N/A
2026-09-13 08:00 | 2026-10-02 08:00 | 19 | CLAIREVILLE TS | D1L552, DL511, DL560, DL551, DL570, D1_BUS, D2_BUS, D1-D2 | 1-00238542 Rev. #19 | 1 Day(s) | No Impact | #N/A
2026-09-15 07:00 | 2026-09-22 16:00 | 7.375 | LEASIDE TS | T17, T17-K, T17-L17 | 1-00295733 Rev. #3 | 6 Hour(s) | No Impact | #N/A
2026-09-26 08:00 | 2026-10-08 16:00 | 12.3333 | FAIRCHILD TS, FINCH JCT, FINCH TS, AGINCOURT JCT, CAVANAGH TS, RICHVIEW TS, CHERRYWOOD TS | C20R.AGXCA, C20R.AGXCH, C20R.FAXAG, C20R.FIXFA, C20R.FIXFI, C20R.FIXRI, 81-C20R, 88-C20R, T1-C20R, T2-C20R, T4-C20R | 1-00292313 Rev. #3 | 12 Hour(s) | No Impact | #N/A
2026-09-29 07:30 | 2026-10-16 16:00 | 17.3542 | MANBY EAST TS | H2H3, H2L23, H2_BUS, SC22H2-H2, T5-H2, T7-H2 | 1-00295671 Rev. #4 | 6 Hour(s) | No Impact | #N/A
2026-10-05 08:00 | 2026-10-29 16:00 | 24.3333 | PICKERING A SS | L6K, L8D, T1D, D_BUS, K_BUS, KBUS-TEMP, L8K | 1-00297696 Rev. #16 | 4 Hour(s) | No Impact | #N/A
2026-10-09 08:00 | 2026-10-23 16:00 | 14.3333 | PARKWAY TS, CHERRYWOOD TS | 52-C36P, 81-C36P | 1-00292312 Rev. #5 | 12 Hour(s) | No Impact | #N/A
2026-10-13 07:00 | 2026-10-27 16:00 | 14.375 | RUNNYMEDE TS, WILTSHIRE TS, MANBY EAST TS | K12W.RUXMA, K12W.RUXWI, H2K11W, H2K12W, H1H2, H2H3, H2L18W, H2L13W, H2L14W, 38-K12W, H2_BUS, 11T2-K12W, 11T5-K12W | 1-00308748 Rev. #6 | 6 Hour(s) | No Impact | #N/A
2026-10-19 08:00 | 2026-10-30 16:00 | 11.3333 | RICHVIEW TS | H1H2, H2L20, H2L18, H2L22, H2L72, H2L76, 88-R13K, H2_BUS, SC21H-H2, T7-H2 | 1-00295740 Rev. #4 | 4 Hour(s) | No Impact | #N/A
2026-11-03 08:00 | 2026-11-12 16:00 | 9.3333 | CHERRYWOOD TS | K1K2, KL18, K1L2, KL35, KL8, K1_BUS, SS1 | 1-00296246 Rev. #4 | 4 Hour(s) | No Impact | #N/A
2026-11-15 08:00 | 2026-12-11 16:00 | 26.3333 | BATHURST JCT, FAIRCHILD TS, BATHURST TS, RICHVIEW TS, CHERRYWOOD TS | C18R.BAXBA, C18R.BAXFA, C18R.BAXRI, C18R.FAXCH, 81-C18R, 88-C18R, T1-C18R, T2-C18R, T3-C18R, T4-C18R | 1-00295785 Rev. #4 | 12 Hour(s) | No Impact | #N/A
2026-12-08 08:00 | 2026-12-15 16:00 | 7.3333 | LEASIDE TS, SCARBORO TS, BERMONDSEY TS, SCARBORO JCT, CHERRYWOOD TS, WARDEN TS | C14L.BEXLE, C14L.BEXSC, C14L.SCXCH, C14L.SCXSC, C14L.SCXWA, HL14HL16, 34-C14L, 81-C14L, T14, T14-CA, T14-HL14, T2-C14L, T21-C14L, T3-C14L, T4-C14L, SS14-X, T14R-SS14 | 1-00265999 Rev. #20 | 4 Hour(s) | No Impact | #N/A
2027-03-14 08:00 | 2027-03-28 08:00 | 14 | GOREWAY PH JCT, GOREWAY TS, CLAIREVILLE TS, GOREWAY JCT, WOODBRIDGE JCT, KLEINBURG TS, VAUGHAN 3 JCT, WOODBRIDGE TS | V43.CLXGJ, V43.CLXWJ, V43.GJXGO, V43.GOXGO, V43.KLXV3, V43.V3XWJ, V43.WJXWO, 136T2-V43, 136T4-V43, 136T6-V43, 45T2-V43, 51-V43, D6T3-V43 | 1-00308101 Rev. #1 | 8 Hour(s) | No Impact | #N/A
2027-04-25 08:00 | 2027-05-07 16:00 | 12.3333 | GOREWAY PH JCT, GOREWAY TS, CLAIREVILLE TS, GOREWAY JCT, WOODBRIDGE JCT, KLEINBURG TS, VAUGHAN 3 JCT, WOODBRIDGE TS | V43.CLXGJ, V43.CLXWJ, V43.GJXGO, V43.GOXGO, V43.KLXV3, V43.V3XWJ, V43.WJXWO, 136T2-V43, 136T4-V43, 136T6-V43, 45T2-V43, 51-V43, D6T3-V43 | 1-00308225 Rev. #1 | 8 Hour(s) | No Impact | #N/A
2027-10-16 06:30 | 2028-05-12 11:30 | 209.2083 | CLARINGTON TS | SC21K1-K1, SC21 | 1-00294515 Rev. #2 | 200 Day(s) | No Impact | #N/A
Back to main menu

## Table 4.13
Back to main menu
Table 4.13: West Zone Transmission Outages
Planned Start | Planned End | Duration (Days) | Station | Equipment Name | Outage ID | Max Recall | Major Transmission Interface Impacted | Reduction in Limit (MW)
2027-03-02 06:45 | 2027-03-09 16:00 | 7.3854 | KEITH TS | AL20, AL5, T11, T23, T11-A, T23-A, AL25 | 1-00310054 Rev. #1 | 6 Hour(s) | No Impact | #N/A
2026-09-06 08:45 | 2026-09-25 15:00 | 19.2604 | CHATHAM SS | DL28, DL31, DL44, D_BUS, SC22D-D, SC23D-D, DL42, DL64, KL43, KL65, DL88 | 1-00285801 Rev. #6 | 6 Hour(s) | No Impact | #N/A
2026-11-29 09:00 | 2026-12-18 09:30 | 19.0208 | CHATHAM SS | DL28, DL31, DL44, D_BUS, SC22D-D, SC23D-D, DL42, DL64, DL88 | 1-00295731 Rev. #2 | 6 Hour(s) | No Impact | #N/A
2026-09-13 06:00 | 2026-10-16 16:00 | 33.4167 | NANTICOKE TS, LONGWOOD TS | N582L.LOXNA, AWT13, DL582, HT8L582, L582WT13, 59-N582L, HT13_BUS, HT8_BUS, T13-WT13, W52-N582L | 1-00293595 Rev. #8 | 16 Hour(s) | No Impact | #N/A
2026-09-13 08:00 | 2026-09-18 16:00 | 5.3333 | LONGWOOD TS, NANTICOKE TS | N582L.LOXNA, HL582, KL582, 59-N582L, W52-N582L | 1-00295560 Rev. #9 | 4 Hour(s) | No Impact | #N/A
2026-09-20 15:15 | 2027-02-12 08:30 | 144.7188 | BUCHANAN TS | 19-M31W, 19-M31WTEMP1 | 1-00297259 Rev. #9 | 90 Day(s) | No Impact | #N/A
2027-02-22 08:00 | 2027-04-02 16:00 | 39.3333 | NANTICOKE TS, LONGWOOD TS | N582L.LOXNA, AWT13, DL582, HT8L582, L582WT13, 59-N582L, HT13_BUS, T13-WT13, W52-N582L | 1-00308115 Rev. #2 | Non-recallable | No Impact | #N/A
2026-09-20 15:15 | 2027-02-12 08:30 | 144.7188 | BUCHANAN TS | 19-M31W, 19-M31WTEMP1 | 1-00297259 Rev. #9 | 90 Day(s) | No Impact | #N/A
2026-09-13 06:00 | 2026-10-16 16:00 | 33.4167 | NANTICOKE TS, LONGWOOD TS | N582L.LOXNA, AWT13, DL582, HT8L582, L582WT13, 59-N582L, HT13_BUS, HT8_BUS, T13-WT13, W52-N582L | 1-00293595 Rev. #8 | 16 Hour(s) | No Impact | #N/A
2026-09-13 08:00 | 2026-09-18 16:00 | 5.3333 | LONGWOOD TS, NANTICOKE TS | N582L.LOXNA, HL582, KL582, 59-N582L, W52-N582L | 1-00295560 Rev. #9 | 4 Hour(s) | No Impact | #N/A
2027-02-22 08:00 | 2027-04-02 16:00 | 39.3333 | NANTICOKE TS, LONGWOOD TS | N582L.LOXNA, AWT13, DL582, HT8L582, L582WT13, 59-N582L, HT13_BUS, T13-WT13, W52-N582L | 1-00308115 Rev. #2 | Non-recallable | No Impact | #N/A
2026-09-13 08:00 | 2026-09-27 08:00 | 14 | LAMBTON TS, LAMBTON TS 2 | P1P2, PL23, PL24, P1_BUS, JQ, T2-P1, T2 | 1-00293702 Rev. #6 | 6 Hour(s) | MICH-W-EXP MICH-W-IMP MICH-S-EXP MICH-S-IMP | 300 350 300 200
2026-09-27 08:45 | 2026-10-09 15:00 | 12.2604 | LAMBTON TS 2, LAMBTON TS | K1K2, KL25, KL37, K1L51, K1_BUS, T1-K1, T1, JQ | 1-00294547 Rev. #6 | 6 Hour(s) | No Impact | #N/A
2026-10-18 08:00 | 2026-11-01 08:45 | 14.0312 | LAMBTON TS 2 | P1P2, P2L27, PL38, PL4 | 1-00292251 Rev. #5 | 6 Hour(s) | No Impact | #N/A
2026-11-01 09:00 | 2026-11-13 15:00 | 12.25 | LAMBTON TS 2 | K1K2, KL26, K2L28, KL4, SS5.6-K2 | 1-00293517 Rev. #4 | 6 Hour(s) | No Impact | #N/A
2027-03-02 06:45 | 2027-03-09 16:00 | 7.3854 | KEITH TS | AL20, AL5, T11, T23, T11-A, T23-A, AL25 | 1-00310054 Rev. #1 | 6 Hour(s) | No Impact | #N/A
2025-09-29 12:00 | 2026-12-31 16:00 | 458.1667 | LAKESHORE TS | 530-H76 | 1-00295205 Rev. #20 | 4 Hour(s) | No Impact | #N/A
2025-12-04 07:00 | 2026-08-31 17:30 | 270.4375 | KENT TS, WALLACEBURG TS, BORALEX TILBURY JCT | N5K.KEXWA, L2L5, 5-N5K, 647K2Z-54 | 1-00266753 Rev. #34 | Non-recallable | No Impact | #N/A
2025-12-11 10:39 | 2026-12-31 16:00 | 385.2229 | LONGWOOD TS | SC22D, SC22 | 1-00303087 Rev. #7 | Non-recallable | No Impact | #N/A
2025-12-18 17:30 | 2026-12-31 17:30 | 378 | SCOTT TS, KIMBALL JCT, WALLACEBURG TS | N5K.KIXSC, N5K.WAXKI, 1N5K-A1, 40-N5K | 1-00267335 Rev. #27 | Non-recallable | No Impact | #N/A
2026-06-22 06:15 | 2026-08-06 16:00 | 45.4062 | BORALEX TILBURY JCT, KENT TS, KENT JCT, TILBURY JCT | K2Z.KEXKE, K2Z.TIXKE, L2L5, 5-K2Z, 647K2Z-54 | 1-00307640 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2026-07-27 07:00 | 2026-08-07 16:00 | 11.375 | SCOTT TS | L5L7 | 1-00307250 Rev. #5 | 2 Hour(s) | No Impact | #N/A
2026-08-16 08:00 | 2026-09-04 15:45 | 19.3229 | CHATHAM SS | KL29, KL47, SC21K, K_BUS, SC21, SC21K-K, SS1-K, KL43, KL65, KL87, KL88 | 1-00295732 Rev. #7 | 6 Hour(s) | No Impact | #N/A
2026-09-08 08:00 | 2026-10-20 16:00 | 42.3333 | LANXESS INC JCT | 103N7S-TEMP1 | 1-00291878 Rev. #8 | Non-recallable | No Impact | #N/A
2026-11-01 08:00 | 2026-11-06 16:00 | 5.3333 | CLARKE TS, TALBOT TS, BUCHANAN TS, OXFORD STREET JCT | W36.OXXBU, W36.OXXCL, W36.OXXTA, 19-W36, 26-W36, T3-W36 | 1-00295612 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2026-11-01 08:45 | 2026-11-20 09:30 | 19.0312 | CHATHAM SS, LAKESHORE TS | KL29, KL47, SC21K, K_BUS, SC21, SC21K-K, SS1-K, 530-C88H, KL43, KL65, C88H.CHXLA, DL88, KL87, KL88, 86-C88H | 1-00295669 Rev. #4 | 6 Hour(s) | No Impact | #N/A
2026-11-15 08:00 | 2026-11-20 16:00 | 5.3333 | ESSEX TS, CHRYSLER WINDSOR ASS. PLANT CTS | E8F.ESXCH, 15-E8F | 1-00295751 Rev. #2 | 4 Hour(s) | No Impact | #N/A
2026-11-22 08:00 | 2026-11-27 16:00 | 5.3333 | ESSEX TS, CHRYSLER WINDSOR ASS. PLANT CTS | E9F.ESXCH, 15-E9F | 1-00295752 Rev. #2 | 4 Hour(s) | No Impact | #N/A
2026-10-15 08:30 | 2026-10-20 16:00 | 5.3125 | BUCHANAN TS, INGERSOLL TS | W12.BUXIN, L12K, L9L12, 19-W12, 38W7-19, 38W12-19 | 1-00295725 Rev. #4 | 4 Hour(s) | No Impact | #N/A
2026-09-17 07:00 | 2026-10-08 17:00 | 21.4167 | WINDSOR LAUZON TS | A_BUS, T1-A, T5-A, T8-A, 56-H54Z | 1-00293516 Rev. #8 | 6 Hour(s) | No Impact | #N/A
2026-09-20 08:00 | 2026-10-02 16:00 | 12.3333 | WINDSOR LAUZON TS | SS1, T1, T1-A, T1-P | 1-00300160 Rev. #4 | 6 Hour(s) | No Impact | #N/A
2026-10-25 12:30 | 2026-12-16 12:30 | 52 | ESSEX TS | L3L4, L4L8, 15-J4E, L4_BUS | 1-00306028 Rev. #3 | 6 Hour(s) | No Impact | #N/A
2027-03-02 06:45 | 2027-03-09 16:00 | 7.3854 | KEITH TS | AL20, AL5, T11, T23, T11-A, T23-A, AL25 | 1-00310054 Rev. #1 | 6 Hour(s) | No Impact | #N/A
Back to main menu

## Table 4.14
Back to main menu
Table 4.14: External Interties Transmission Outages
Planned Start | Planned End | Duration (Days) | Station | Equipment Name | Outage ID | Max Recall | Major Transmission Interface Impacted | Reduction in Limit (MW)
2026-09-28 08:00 | 2026-10-09 16:00 | 11.3333 | ST. LAWRENCE TS, MASSENA JCT | L33P.ROXLA, 49-L33P | 1-00275118 Rev. #9 | 4 Hour(s) | No Impact | #N/A
2026-09-15 08:00 | 2026-11-17 16:00 | 63.3333 | BECK 2 TS, NY NIAGARA 345 KV | PA27.NIXBE, 28R27-PA27, R27-S | 1-00308330 Rev. #3 | Non-recallable | NY-W-EXP NY-W-IMP NY-S-EXP NY-S-IMP | 150 0 100 0
2024-05-14 13:00 | 2026-12-31 16:00 | 961.125 | KENORA TS, WHITESHELL TS | K21W.WHXKE, 34-K21W | 1-00254393 Rev. #21 | 6 Hour(s) | EWTE EWTW | 25 25
2027-05-31 03:30 | 2027-06-11 16:00 | 11.5208 | HAWTHORNE TS, MASSON GS, IPB MASSON JCT, ST. ISIDORE TS, ORLEANS JCT 2, ORLEANS TS, CUMBERLAND JCT, LONGUEUIL JCT, LONGUEUIL TS | D5A.CUXGA, D5A.CUXIS, D5A.CUXO2, D5A.HAXO2, D5A.IPXMA, D5A.LOXIS, D5A.LOXLO, D5A.O2XOR, A1A2, HT5L5, KL5, 325T2-D5A, 48-D5A, 62D5A-26, T3-D5A, T1-A1, 62D5A-625 | 1-00296584 Rev. #3 | 6 Hour(s) | FIO BEAU P33C | 250 690 0
2025-11-18 08:00 | 2026-12-31 16:00 | 408.3333 | KENORA TS, WHITESHELL TS | K21W.WHXKE, 34-K21W | 1-00299527 Rev. #10 | 2 Hour(s) | EWTE EWTW | 25 25
Back to main menu