## Summer Reference Net Forecast
The IRRP planning forecasts account for the median weather gross forecasts provided by the local distributors, savings from distributed generation and electricity Demand Side Management, as well as extreme weather adjustments. A power factor of 0.9 was assumed for the forecasts. Full details on the overall IRRP forecast methodology will be provided in the IRRP report, once finalized.
Transformer Station | SUMMER REFERENCE: Net Extreme Weather Station Peak Demand Forecast, Coincident to GTA East Region (MW)
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
CHERRYWOOD TS | 173.0138 | 175.861 | 178.788 | 182.06 | 182.9398 | 181.0968 | 179.2716 | 177.6243 | 176.1107 | 174.589 | 173.7893 | 173.2377 | 173.1856 | 173.1641 | 173.1117 | 173.009 | 172.981 | 172.9429 | 172.8612 | 172.8107
ENFIELD TS T5/T6 | 123.4524 | 125.5861 | 131.9632 | 136.2246 | 139.3289 | 142.9474 | 146.0915 | 148.8531 | 152.2102 | 155.9184 | 160.7838 | 166.2229 | 175.0456 | 182.7116 | 189.1649 | 195.1159 | 200.4807 | 205.867 | 211.173 | 216.4471
SEATON MTS | 16.9978 | 23.2873 | 30.359 | 38.788 | 47.2334 | 55.882 | 64.2342 | 72.8836 | 82.4632 | 92.7202 | 107.9303 | 122.5085 | 138.5685 | 156.058 | 174.077 | 192.5767 | 211.5529 | 231.1867 | 250.7932 | 270.3883
THORNTON TS | 168.0664 | 168.219 | 168.4027 | 169.2919 | 170.7626 | 173.2023 | 175.78 | 178.9312 | 183.0038 | 187.5544 | 193.7314 | 200.8142 | 208.6888 | 217.0663 | 225.449 | 232.7898 | 238.826 | 244.8289 | 250.6689 | 256.4075
WHITBY TS T1/T2 27.6 kV | 65.7251 | 66.5369 | 67.3303 | 68.2085 | 69.0811 | 70.1511 | 71.164 | 72.3579 | 78.6035 | 85.4362 | 96.1024 | 106.7497 | 118.3217 | 130.9413 | 143.9148 | 157.0746 | 170.2671 | 183.572 | 196.7207 | 209.7169
WHITBY TS T1/T2 44 kV | 77.6277 | 81.9844 | 86.4096 | 90.9449 | 95.5734 | 100.7349 | 105.6429 | 111.031 | 113.8628 | 116.8868 | 122.1837 | 127.419 | 133.4355 | 140.0043 | 146.7544 | 153.5799 | 160.4445 | 167.3632 | 174.191 | 180.9463
WHITBY TS T3/T4 | 190.2598 | 191.7034 | 193.0719 | 194.7839 | 196.5226 | 198.7205 | 200.761 | 203.2677 | 205.2217 | 207.4633 | 229.3068 | 234.4983 | 240.5811 | 247.2138 | 253.9702 | 260.7803 | 267.6796 | 274.6271 | 281.4532 | 288.2279
WILSON TS T7/T8 | 129.0127 | 130.4464 | 132.3895 | 137.6216 | 142.8726 | 147.2249 | 151.7647 | 156.9862 | 163.4796 | 170.6591 | 179.3958 | 189.2787 | 200.1069 | 211.5704 | 223.0842 | 233.1581 | 241.4003 | 249.5967 | 257.6046 | 265.4448
WILSON TS T3/T4 | 144.9367 | 158.6577 | 172.8371 | 188.0456 | 201.2391 | 224.3976 | 232.5881 | 243.9279 | 254.5917 | 264.973 | 277.1441 | 307.8919 | 321.9515 | 336.4756 | 351.125 | 365.5599 | 379.0249 | 392.6678 | 406.2281 | 419.9147
Total Region | 1089.0925 | 1122.2822 | 1161.5514 | 1205.969 | 1245.5535 | 1294.3574 | 1327.298 | 1365.8628 | 1409.5473 | 1456.2005 | 1540.3676 | 1628.6209 | 1709.8851 | 1795.2053 | 1880.6511 | 1963.6441 | 2042.657 | 2122.6522 | 2201.6939 | 2280.3042
This document and the information contained herein is provided for informational purposes only and is subject to redaction and/or aggregation to protect against identifying specific customer electricity usage. The IESO has prepared this document based on information currently available to the IESO and reasonable assumptions associated therewith, including relating to electricity supply and demand. The information, statements and conclusions contained herein are subject to risks, uncertainties and other factors, and actual results or circumstances may differ materially. The IESO provides no guarantee, representation, or warranty, express or implied, with respect to any statement or information contained herein and disclaims any liability in connection therewith. Readers are cautioned not to place undue reliance on forward-looking information contained in this document as actual results could differ materially from the plans, expectations, estimates, intentions and statements expressed herein. The IESO undertakes no obligation to revise or update any information contained in this document as a result of new information, future events or otherwise. In the event there is any conflict or inconsistency between this document and the IESO market rules, any IESO contract, any legislation or regulation, or any request for proposals or other procurement document, the terms in the market rules, or the subject contract, legislation, regulation, or procurement document, as applicable, govern.
DRAFT

## Winter Reference Net Forecast
The IRRP planning forecasts account for the median weather gross forecasts provided by the local distributors, savings from distributed generation and electricity Demand Side Management, as well as extreme weather adjustments. A power factor of 0.9 was assumed for the forecasts. Full details on the overall IRRP forecast methodology will be provided in the IRRP report, once finalized.
Transformer Station | WINTER REFERENCE: Net Extreme Weather Station Peak Demand Forecast, Coincident to GTA East Region (MW)
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
CHERRYWOOD TS | 131.3767 | 136.6377 | 142.2827 | 148.3487 | 154.2529 | 152.7446 | 151.2019 | 149.7966 | 148.5569 | 147.3631 | 146.8432 | 146.51 | 146.5153 | 146.4966 | 146.4535 | 146.4083 | 146.3412 | 146.2784 | 146.2289 | 146.1826
ENFIELD TS T5/T6 | 111.6447 | 114.1109 | 122.3393 | 127.1211 | 130.3817 | 134.2393 | 137.4547 | 140.341 | 143.8965 | 147.8769 | 153.1969 | 158.9282 | 170.4854 | 179.5381 | 186.2238 | 192.4944 | 197.982 | 203.4951 | 209.0193 | 214.5048
SEATON MTS | 16.5706 | 23.3498 | 31.4422 | 40.8808 | 50.3847 | 60.1958 | 69.233 | 78.7479 | 89.1307 | 100.1711 | 115.4776 | 130.4043 | 146.8975 | 164.6371 | 182.926 | 201.7707 | 220.589 | 240.1879 | 259.9533 | 279.8016
THORNTON TS | 117.9593 | 118.874 | 120.0189 | 121.801 | 123.9221 | 127.0051 | 130.0266 | 133.5956 | 138.048 | 142.9953 | 149.3301 | 156.3336 | 164.0167 | 172.1197 | 180.2315 | 187.4421 | 193.25 | 199.0136 | 204.6967 | 210.2493
WHITBY TS T1/T2 27.6 kV | 48.1992 | 49.8579 | 51.5594 | 53.3684 | 55.0488 | 56.9475 | 58.595 | 60.4219 | 68.6951 | 77.5956 | 90.151 | 102.5088 | 116.1547 | 130.8576 | 145.9154 | 161.3237 | 176.3466 | 191.5721 | 206.8011 | 221.9494
WHITBY TS T1/T2 44 kV | 59.1875 | 65.4038 | 71.7906 | 78.3703 | 84.8887 | 91.9482 | 98.1814 | 104.8815 | 108.2596 | 111.9833 | 117.7733 | 123.5402 | 130.0905 | 137.1478 | 144.3531 | 151.7274 | 158.9 | 166.1674 | 173.4484 | 180.6952
WHITBY TS T3/T4 | 152.7861 | 155.751 | 158.8622 | 162.3759 | 165.5414 | 169.2194 | 172.3095 | 175.8418 | 178.4609 | 181.4551 | 203.6388 | 209.1702 | 215.6703 | 222.6564 | 229.7739 | 237.0571 | 244.1276 | 251.2966 | 258.4866 | 265.6444
WILSON TS T7/T8 | 96.7919 | 98.3621 | 100.497 | 105.4519 | 110.595 | 114.6677 | 118.6707 | 123.2953 | 128.9285 | 135.1595 | 142.8463 | 151.2505 | 160.3854 | 170.0461 | 179.7076 | 188.3009 | 195.2185 | 202.0707 | 208.8319 | 215.4412
WILSON TS T3/T4 | 128.3148 | 141.0046 | 154.3684 | 168.7409 | 181.0773 | 202.3248 | 210.1075 | 220.631 | 230.5302 | 240.1095 | 251.3818 | 276.2457 | 289.0329 | 302.1406 | 315.4245 | 328.6587 | 340.7598 | 353.0771 | 365.4762 | 377.9222
Total Region | 862.8309 | 903.3517 | 953.1608 | 1006.4591 | 1056.0927 | 1109.2925 | 1145.7802 | 1187.5525 | 1234.5064 | 1284.7095 | 1370.639 | 1454.8915 | 1539.2486 | 1625.6399 | 1711.0092 | 1795.1833 | 1873.5147 | 1953.1589 | 2032.9424 | 2112.3907
This document and the information contained herein is provided for informational purposes only and is subject to redaction and/or aggregation to protect against identifying specific customer electricity usage. The IESO has prepared this document based on information currently available to the IESO and reasonable assumptions associated therewith, including relating to electricity supply and demand. The information, statements and conclusions contained herein are subject to risks, uncertainties and other factors, and actual results or circumstances may differ materially. The IESO provides no guarantee, representation, or warranty, express or implied, with respect to any statement or information contained herein and disclaims any liability in connection therewith. Readers are cautioned not to place undue reliance on forward-looking information contained in this document as actual results could differ materially from the plans, expectations, estimates, intentions and statements expressed herein. The IESO undertakes no obligation to revise or update any information contained in this document as a result of new information, future events or otherwise. In the event there is any conflict or inconsistency between this document and the IESO market rules, any IESO contract, any legislation or regulation, or any request for proposals or other procurement document, the terms in the market rules, or the subject contract, legislation, regulation, or procurement document, as applicable, govern.
DRAFT

## Summer DG
Peak demand contribution from contracted, existing distributed generation was estimated based on technology type and totalled for each station in the region. The resulting forecast savings were applied to gross demand to help determine the net peak demand for the IRRP planning forecast. Additional details on the overall IRRP forecast methodology will be provided in the final report.
Transformer Station | SUMMER: Total Contracted Distributed Generation (DG) Contribution to Peak (MW)
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
CHERRYWOOD TS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ENFIELD TS T5/T6 | 5.6575 | 5.6575 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 1.2625 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SEATON MTS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
THORNTON TS | 0.49747 | 0.49747 | 0.49747 | 0.49747 | 0.49747 | 0.49747 | 0.49747 | 0.47154 | 0.44045 | 0.40268 | 0.27322 | 0.095227 | 0.066992 | 0.033502 | 0 | 0 | 0 | 0 | 0 | 0
WHITBY TS T1/T2 27.6 kV | 0.45378 | 0.45378 | 0.45378 | 0.45378 | 0.45378 | 0.45378 | 0.45378 | 0.42475 | 0.39234 | 0.38038 | 0.37588 | 0.11449 | 0.067869 | 0.047069 | 0 | 0 | 0 | 0 | 0 | 0
WHITBY TS T1/T2 44 kV | 0.40416 | 0.40416 | 0.40416 | 0.40416 | 0.40416 | 0.40416 | 0.40416 | 0.29211 | 0.14606 | 0.13178 | 0.094799 | 0.069001 | 0.036271 | 0.026649 | 0 | 0 | 0 | 0 | 0 | 0
WHITBY TS T3/T4 | 17.7699 | 17.7699 | 17.7699 | 17.7699 | 17.7699 | 17.7699 | 17.7699 | 17.7069 | 17.5464 | 17.4246 | 0.39571 | 0.1338 | 0.051582 | 0.015261 | 0 | 0 | 0 | 0 | 0 | 0
WILSON TS T7/T8 | 2.8039 | 2.8039 | 2.8039 | 2.8039 | 0.64186 | 0.64186 | 0.64186 | 0.62196 | 0.51931 | 0.40966 | 0.37983 | 0.25012 | 0.14971 | 0.082698 | 0 | 0 | 0 | 0 | 0 | 0
WILSON TS T3/T4 | 19.0162 | 19.0162 | 19.0162 | 19.0162 | 19.0162 | 19.0162 | 19.0162 | 18.9348 | 18.7702 | 18.4712 | 18.348 | 0.21677 | 0.09746 | 0.048404 | 0 | 0 | 0 | 0 | 0 | 0
Total Region | 46.6028 | 46.6028 | 44.9853 | 44.9853 | 42.8233 | 42.8233 | 42.8233 | 42.492 | 41.8547 | 41.2602 | 23.9073 | 4.9194 | 1.7324 | 0.25358 | 0 | 0 | 0 | 0 | 0 | 0
DRAFT

## Winter DG
Peak demand contribution from contracted, existing distributed generation was estimated based on technology type and totalled for each station in the region. The resulting forecast savings were applied to gross demand to help determine the net peak demand for the IRRP planning forecast. Additional details on the overall IRRP forecast methodology will be provided in the final report.
Transformer Station | WINTER: Total Contracted Distributed Generation (DG) Contribution to Peak (MW)
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
CHERRYWOOD TS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ENFIELD TS T5/T6 | 10.6423 | 10.6423 | 7.5995 | 7.5995 | 7.5995 | 7.5995 | 7.5995 | 7.5995 | 7.5995 | 7.5995 | 7.5995 | 7.5995 | 2.3749 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SEATON MTS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
THORNTON TS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WHITBY TS T1/T2 27.6 kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WHITBY TS T1/T2 44 kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WHITBY TS T3/T4 | 16.7433 | 16.7433 | 16.7433 | 16.7433 | 16.7433 | 16.7433 | 16.7433 | 16.7433 | 16.7433 | 16.7433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WILSON TS T7/T8 | 2.162 | 2.162 | 2.162 | 2.162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WILSON TS T3/T4 | 13.066 | 13.066 | 13.066 | 13.066 | 13.066 | 13.066 | 13.066 | 13.066 | 13.066 | 13.066 | 13.066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Region | 42.6136 | 42.6136 | 39.5708 | 39.5708 | 37.4088 | 37.4088 | 37.4088 | 37.4088 | 37.4088 | 37.4088 | 20.6655 | 7.5995 | 2.3749 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DRAFT

## Summer eDSM
Peak demand savings from codes and standards, as well as the delivery of conservation programs, were estimated for each sector and totalled for each station in the region. The resulting forecast savings were applied to gross demand to help determine the net peak demand for the IRRP planning forecast. Additional details on the overall IRRP forecast methodology will be provided in the final report.
Transformer Station | SUMMER: Total electricity Demand Side Management (eDSM) Forecast (MW)
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
CHERRYWOOD TS | 2.1437 | 4.1904 | 6.5099 | 8.5784 | 10.6355 | 12.4785 | 14.3037 | 15.951 | 17.4646 | 18.9862 | 19.786 | 20.3375 | 20.3897 | 20.4111 | 20.4636 | 20.5662 | 20.5942 | 20.6323 | 20.714 | 20.7646
ENFIELD TS T5/T6 | 1.4404 | 2.7634 | 4.3259 | 5.833 | 7.4857 | 9.1314 | 10.7869 | 12.3205 | 13.8203 | 15.3606 | 16.5572 | 17.508 | 18.1791 | 18.8661 | 19.5873 | 20.3495 | 20.9628 | 21.6057 | 22.2958 | 22.958
SEATON MTS | 0.21061 | 0.55488 | 1.1054 | 1.8276 | 2.746 | 3.8506 | 5.1251 | 6.5451 | 8.1777 | 10.0831 | 12.2879 | 14.3821 | 16.3141 | 18.3948 | 20.5777 | 22.8923 | 25.1864 | 27.5809 | 30.0526 | 32.4893
THORNTON TS | 2.0873 | 4.0166 | 6.1383 | 7.9757 | 9.9123 | 11.9024 | 13.9718 | 15.9851 | 18.0244 | 20.2182 | 21.8144 | 23.256 | 24.1971 | 25.1555 | 26.1586 | 27.1303 | 27.8534 | 28.5923 | 29.3827 | 30.1204
WHITBY TS T1/T2 27.6 kV | 0.76678 | 1.4719 | 2.2624 | 2.9944 | 3.8003 | 4.5884 | 5.3837 | 6.1404 | 7.3238 | 8.6561 | 10.1793 | 11.5533 | 12.8313 | 14.2151 | 15.663 | 17.2135 | 18.7015 | 20.2279 | 21.8 | 23.3354
WHITBY TS T1/T2 44 kV | 0.89442 | 1.7976 | 2.8649 | 3.9125 | 5.1044 | 6.3856 | 7.7475 | 9.1343 | 10.2956 | 11.5265 | 12.6041 | 13.5113 | 14.1868 | 14.9002 | 15.6532 | 16.4788 | 17.2497 | 18.0451 | 18.8739 | 19.6768
WHITBY TS T3/T4 | 2.4727 | 4.7577 | 7.2825 | 9.5282 | 11.9154 | 14.2846 | 16.6887 | 18.968 | 21.0705 | 23.245 | 24.8483 | 26.1128 | 26.8559 | 27.6244 | 28.4545 | 29.3925 | 30.2255 | 31.0899 | 32.0174 | 32.8968
WILSON TS T7/T8 | 1.4927 | 2.8802 | 4.401 | 5.9 | 7.4285 | 9.079 | 10.8367 | 12.5985 | 14.448 | 16.4664 | 18.1177 | 19.6751 | 20.8553 | 22.0647 | 23.3071 | 24.4978 | 25.4152 | 26.3549 | 27.332 | 28.268
WILSON TS T3/T4 | 2.1581 | 4.5233 | 7.5621 | 10.6289 | 14.0256 | 18.42 | 22.058 | 25.9728 | 29.8641 | 34.0106 | 37.1118 | 39.8532 | 41.7428 | 43.6631 | 45.7064 | 47.8752 | 49.7121 | 51.5998 | 53.6405 | 55.5944
Total Region | 13.6667 | 26.9559 | 42.4525 | 57.1789 | 73.0537 | 90.1204 | 106.902 | 123.6156 | 140.489 | 158.5527 | 173.3067 | 186.1892 | 195.5521 | 205.295 | 215.5715 | 226.3961 | 235.9008 | 245.7289 | 256.109 | 266.1036
DRAFT

## Winter eDSM
Peak demand savings from codes and standards, as well as the delivery of conservation programs, were estimated for each sector and totalled for each station in the region. The resulting forecast savings were applied to gross demand to help determine the net peak demand for the IRRP planning forecast. Additional details on the overall IRRP forecast methodology will be provided in the final report.
Transformer Station | WINTER: Total electricity Demand Side Management (eDSM) Forecast (MW)
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
CHERRYWOOD TS | 1.4413 | 3.0348 | 4.736 | 6.2515 | 8.2184 | 9.7267 | 11.2694 | 12.6747 | 13.9144 | 15.1081 | 15.6281 | 15.9613 | 15.956 | 15.9747 | 16.0178 | 16.063 | 16.1301 | 16.1929 | 16.2424 | 16.2886
ENFIELD TS T5/T6 | 1.2878 | 2.5575 | 4.0003 | 5.3096 | 7.1437 | 8.9026 | 10.7062 | 12.3996 | 13.9921 | 15.5571 | 16.6033 | 17.5241 | 18.1739 | 18.8601 | 19.6294 | 20.3577 | 21.0779 | 21.822 | 22.5282 | 23.2194
SEATON MTS | 0.18206 | 0.51909 | 1.0481 | 1.726 | 2.6908 | 3.8429 | 5.1732 | 6.6802 | 8.3695 | 10.2959 | 12.3208 | 14.2407 | 16.0361 | 17.997 | 20.0568 | 22.1932 | 24.3761 | 26.6567 | 28.9487 | 31.2582
THORNTON TS | 1.292 | 2.64 | 3.9896 | 5.1182 | 6.5717 | 8.0438 | 9.6352 | 11.2345 | 12.8461 | 14.5572 | 15.7718 | 16.8968 | 17.7109 | 18.5956 | 19.5191 | 20.3532 | 21.0755 | 21.7956 | 22.4899 | 23.168
WHITBY TS T1/T2 27.6 kV | 0.51262 | 1.0364 | 1.6116 | 2.1364 | 2.886 | 3.6151 | 4.3717 | 5.1183 | 6.414 | 7.8572 | 9.4246 | 10.9208 | 12.3615 | 13.9178 | 15.5696 | 17.2697 | 18.9986 | 20.7792 | 22.5397 | 24.2921
WHITBY TS T1/T2 44 kV | 0.62444 | 1.3711 | 2.248 | 3.1144 | 4.3485 | 5.6728 | 7.1095 | 8.6201 | 9.8213 | 11.0477 | 12.0163 | 12.8795 | 13.5491 | 14.2729 | 15.0641 | 15.8773 | 16.7215 | 17.5925 | 18.4421 | 19.2834
WHITBY TS T3/T4 | 1.8221 | 3.7024 | 5.6456 | 7.3133 | 9.5424 | 11.6983 | 13.9453 | 16.1264 | 18.0595 | 19.9861 | 21.2643 | 22.3236 | 23.0006 | 23.7495 | 24.5811 | 25.4368 | 26.3356 | 27.2568 | 28.1492 | 29.0315
WILSON TS T7/T8 | 1.0404 | 2.1518 | 3.2565 | 4.2815 | 5.5369 | 6.8629 | 8.3271 | 9.8279 | 11.3818 | 13.0423 | 14.303 | 15.5328 | 16.4686 | 17.4601 | 18.5072 | 19.4485 | 20.2705 | 21.1027 | 21.9 | 22.6753
WILSON TS T3/T4 | 1.61 | 3.5606 | 5.8531 | 8.0994 | 10.9132 | 14.4585 | 17.5144 | 20.8335 | 24.0698 | 27.4707 | 29.8349 | 31.8757 | 33.3492 | 34.9668 | 36.6298 | 38.3123 | 39.9003 | 41.4876 | 43.0807 | 44.6909
Total Region | 9.8129 | 20.5737 | 32.3887 | 43.3503 | 57.8516 | 72.8237 | 88.052 | 103.5152 | 118.8685 | 134.9224 | 147.1671 | 158.1553 | 166.606 | 175.7945 | 185.5749 | 195.3116 | 204.886 | 214.686 | 224.3211 | 233.9077
DRAFT