## Summer Reference Net Forecast
The IRRP planning forecasts account for the median weather gross forecasts provided by the local distributors, savings from distributed generation and conservation and demand management, as well as extreme weather adjustments. A power factor of 0.9 was assumed for the forecasts. Full details on the overall IRRP forecast methodology will be provided in the IRRP report, once finalized.
Transformer Station | SUMMER REFERENCE: Net Extreme Weather Station Peak Demand Forecast, Coincident to GTA West Region (MW)
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
Bramalea TS | 289.0734 | 293.9531 | 302.5857 | 318.2031 | 334.6495 | 353.9036 | 359.3503 | 361.7557 | 365.331 | 371.2961 | 379.7909 | 389.4735 | 401.292 | 412.8132 | 423.7777 | 433.998 | 440.2021 | 446.7173 | 452.8998 | 459.1229
Cardiff TS | 121.9145 | 121.6135 | 119.0476 | 116.9474 | 114.7647 | 112.8309 | 110.9407 | 112.5753 | 114.3155 | 116.6636 | 121.1278 | 126.1525 | 129.0754 | 132.2714 | 134.9001 | 137.5044 | 140.2971 | 143.428 | 146.4419 | 149.1646
Churchill Meadows TS | 103.2434 | 102.6974 | 109.6396 | 116.6558 | 123.2583 | 129.8135 | 131.8692 | 129.8006 | 128.0188 | 126.8745 | 127.9632 | 129.6296 | 132.6412 | 135.5201 | 137.8404 | 140.1305 | 142.6131 | 145.3929 | 148.052 | 150.4684
Cooksville TS | 96.054 | 95.9113 | 94.0035 | 102.0362 | 124.2808 | 161.2749 | 193.4359 | 216.6881 | 229.8697 | 238.7514 | 244.7909 | 251.8851 | 257.6388 | 263.9285 | 269.1166 | 274.2618 | 279.7594 | 285.914 | 291.8524 | 297.2135
Erindale TS | 470.6621 | 453.8238 | 459.4725 | 460.8389 | 461.6019 | 465.8553 | 469.9243 | 480.747 | 492.2598 | 506.3394 | 522.7843 | 537.224 | 555.0898 | 568.7696 | 579.9663 | 591.0777 | 602.9291 | 616.1966 | 629.0124 | 640.5729
Glenorchy MTS | 89.6461 | 85.3883 | 96.7362 | 74.8775 | 76.7431 | 77.3892 | 79.9153 | 68.7159 | 71.3642 | 70.3656 | 72.2808 | 74.252 | 77.5809 | 81.1384 | 80.4425 | 83.0559 | 85.5719 | 87.6342 | 87.4604 | 89.4855
Goreway TS | 278.8143 | 287.9914 | 297.3155 | 308.6253 | 320.9667 | 329.3672 | 337.0697 | 345.8697 | 355.6125 | 366.0006 | 377.2103 | 389.0493 | 402.3904 | 414.9476 | 427.1873 | 439.5134 | 444.7797 | 450.0976 | 455.1473 | 460.5236
Halton TS | 147.6579 | 153.8243 | 154.3394 | 162.4165 | 180.9595 | 187.1453 | 193.6734 | 212.9594 | 213.0194 | 211.5279 | 214.2665 | 213.8817 | 221.3517 | 230.3007 | 236.6208 | 248.784 | 254.2136 | 259.9497 | 265.715 | 275.135
Halton Hills MTS | 9.0111 | 8.9049 | 8.7874 | 8.5227 | 9.7938 | 10.9276 | 13.4043 | 13.3487 | 13.331 | 12.5799 | 13.6193 | 12.996 | 12.9811 | 13.684 | 13.1252 | 13.2665 | 13.1486 | 13.1039 | 12.9898 | 13.4826
Jim Yarrow MTS | 140.9407 | 145.3922 | 149.9075 | 155.4087 | 161.4165 | 165.4986 | 169.2097 | 173.4453 | 178.1917 | 183.5515 | 188.805 | 194.4688 | 201.1152 | 207.2382 | 213.2416 | 219.2873 | 221.8711 | 224.4805 | 226.9568 | 229.5947
Kleinburg TS | 187.6703 | 214.4934 | 226.7697 | 271.1217 | 276.9101 | 294.7621 | 302.8746 | 310.4166 | 318.2328 | 317.1357 | 317.3804 | 317.8517 | 319.1462 | 320.6909 | 334.555 | 349.2256 | 365.4247 | 383.1005 | 402.2508 | 403.4798
Lorne Park TS | 85.4493 | 85.0876 | 86.4295 | 88.0016 | 89.3728 | 90.8323 | 92.2129 | 93.7228 | 95.2466 | 94.3114 | 95.1958 | 96.5496 | 98.79 | 101.2045 | 103.172 | 105.1141 | 107.2167 | 109.571 | 111.8235 | 113.8697
Meadowvale TS | 106.3497 | 105.9317 | 112.4223 | 118.9887 | 125.2906 | 134.8121 | 135.6804 | 136.6299 | 137.8652 | 139.9449 | 141.4319 | 143.4307 | 146.8243 | 150.3959 | 153.4136 | 156.5726 | 159.736 | 163.2687 | 166.7887 | 169.8681
Oakville TS | 126.6961 | 130.2326 | 131.3156 | 132.4945 | 130.4595 | 131.8925 | 131.7877 | 133.9177 | 134.3614 | 134.698 | 136.1267 | 138.3063 | 141.2636 | 144.2482 | 147.0128 | 149.7442 | 152.5938 | 155.2449 | 157.7969 | 160.3421
Palermo TS | 100.4102 | 115.0277 | 113.6276 | 147.7534 | 159.5068 | 165.969 | 171.3255 | 168.2971 | 167.7465 | 167.6529 | 169.4718 | 170.1513 | 171.5767 | 173.0249 | 177.7696 | 179.5737 | 181.1529 | 182.6371 | 186.1957 | 187.8993
Pleasant TS | 413.7957 | 431.5149 | 453.4143 | 476.1908 | 495.1691 | 508.2745 | 519.3005 | 532.6479 | 547.1326 | 566.8609 | 606.8912 | 641.3126 | 679.6708 | 720.1983 | 755.1877 | 791.3063 | 818.2852 | 845.5254 | 872.046 | 896.8477
Tomken TS | 200.7669 | 200.4791 | 196.4698 | 193.188 | 189.7775 | 186.7557 | 184.0582 | 181.4107 | 179.3243 | 178.3707 | 180.963 | 183.8016 | 188.2075 | 192.8369 | 202.7025 | 212.6447 | 222.9714 | 227.8769 | 232.611 | 242.9388
Trafalgar TS | 57.3844 | 57.6407 | 57.7313 | 58.1011 | 58.3772 | 58.7047 | 59.0438 | 59.2507 | 59.6478 | 60.3376 | 61.9755 | 63.6032 | 65.4953 | 67.5867 | 70.5193 | 73.5868 | 76.6455 | 79.5237 | 82.4734 | 85.5129
Tremaine TS | 100.622 | 102.6195 | 104.4306 | 106.0822 | 107.0886 | 108.7965 | 110.4135 | 113.8366 | 117.4389 | 120.7692 | 125.1107 | 129.9224 | 134.5881 | 138.1645 | 141.9712 | 145.7191 | 149.1338 | 151.2153 | 153.2849 | 154.5772
Total Region | 3126.162 | 3192.5272 | 3274.4455 | 3416.454 | 3540.3869 | 3674.8056 | 3765.4897 | 3846.0358 | 3918.3096 | 3984.032 | 4097.186 | 4203.9419 | 4336.7189 | 4468.9626 | 4602.5223 | 4744.3665 | 4858.5457 | 4970.8779 | 5081.7985 | 5180.0992
This document and the information contained herein is provided for informational purposes only and is subject to redaction and/or aggregation to protect against identifying specific customer electricity usage. The IESO has prepared this document based on information currently available to the IESO and reasonable assumptions associated therewith, including relating to electricity supply and demand. The information, statements and conclusions contained herein are subject to risks, uncertainties and other factors, and actual results or circumstances may differ materially. The IESO provides no guarantee, representation, or warranty, express or implied, with respect to any statement or information contained herein and disclaims any liability in connection therewith. Readers are cautioned not to place undue reliance on forward-looking information contained in this document as actual results could differ materially from the plans, expectations, estimates, intentions and statements expressed herein. The IESO undertakes no obligation to revise or update any information contained in this document as a result of new information, future events or otherwise. In the event there is any conflict or inconsistency between this document and the IESO market rules, any IESO contract, any legislation or regulation, or any request for proposals or other procurement document, the terms in the market rules, or the subject contract, legislation, regulation, or procurement document, as applicable, govern.
DRAFT

## Winter Reference Net Forecast
The IRRP planning forecasts account for the median weather gross forecasts provided by the local distributors, savings from distributed generation and conservation and demand management, as well as extreme weather adjustments. A power factor of 0.9 was assumed for the forecasts. Full details on the overall IRRP forecast methodology will be provided in the IRRP report, once finalized.
Transformer Station | WINTER REFERENCE: Net Extreme Weather Station Peak Demand Forecast, Coincident to GTA West Region (MW)
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
Bramalea TS | 219.6563 | 228.2223 | 237.8767 | 258.2166 | 282.0848 | 326.33 | 354.9327 | 382.3454 | 410.8913 | 442.4807 | 468.6993 | 497.5867 | 526.813 | 556.7546 | 588.8775 | 613.1577 | 625.221 | 637.4902 | 649.6115 | 661.6018
Cardiff TS | 63.071 | 63.9785 | 64.5312 | 65.9419 | 68.3157 | 70.3634 | 74.0955 | 77.3097 | 80.7256 | 83.9991 | 88.4493 | 93.5144 | 99.1 | 104.8747 | 111.0499 | 113.1362 | 115.3037 | 117.5773 | 119.8676 | 122.1838
Churchill Meadows TS | 60.448 | 61.3352 | 73.2067 | 83.1642 | 93.7199 | 103.1534 | 102.5669 | 101.6358 | 101.0187 | 101.0541 | 105.73 | 111.1004 | 117.0469 | 123.1824 | 129.7501 | 131.9618 | 134.2632 | 136.6824 | 139.1176 | 141.5791
Cooksville TS | 61.448 | 62.4983 | 63.232 | 71.8494 | 94.4867 | 122.5731 | 194.5187 | 236.264 | 270.2931 | 329.33 | 347.2051 | 367.2647 | 389.22 | 412.0255 | 436.3723 | 444.6695 | 453.2585 | 462.2198 | 471.2685 | 480.4348
Erindale TS | 309.9074 | 318.5925 | 331.3009 | 344.1983 | 353.7267 | 367.3021 | 385.2469 | 402.8294 | 419.0746 | 451.5197 | 476.1118 | 503.6539 | 533.7662 | 565.066 | 598.4731 | 609.8719 | 621.6657 | 633.9613 | 646.3811 | 658.9651
Glenorchy MTS | 41.2487 | 36.1138 | 42.6253 | 46.2515 | 46.853 | 47.3335 | 50.0823 | 52.091 | 55.044 | 57.8187 | 60.0819 | 62.6536 | 66.2873 | 70.153 | 70.9898 | 74.7934 | 78.4513 | 81.2153 | 81.9744 | 84.7077
Goreway TS | 201.7157 | 213.6626 | 227.9926 | 250.777 | 277.7324 | 305.3337 | 333.0658 | 354.5408 | 376.8373 | 402.178 | 428.527 | 456.8009 | 483.605 | 510.9077 | 540.3134 | 571.7539 | 583.4262 | 595.0485 | 606.3547 | 617.3559
Halton TS | 113.6953 | 118.7822 | 119.5577 | 126.6605 | 141.0366 | 145.858 | 150.5957 | 165.6851 | 165.5354 | 166.3677 | 166.1232 | 166.8282 | 172.7031 | 178.6331 | 184.4276 | 193.8484 | 198.265 | 202.878 | 207.6491 | 214.2878
Halton Hills MTS | 6.5021 | 6.4512 | 6.4103 | 6.3565 | 7.1028 | 7.8626 | 9.4157 | 9.3423 | 9.2809 | 9.6378 | 9.2449 | 9.2283 | 9.2554 | 9.2821 | 9.2591 | 9.3039 | 9.2914 | 9.3112 | 9.3218 | 9.3339
Jim Yarrow MTS | 94.5282 | 99.8835 | 106.3059 | 116.5771 | 128.7175 | 141.1504 | 153.6295 | 163.2635 | 173.2718 | 184.6457 | 196.5308 | 209.3166 | 221.4552 | 233.8071 | 247.1154 | 261.3429 | 266.6204 | 271.8805 | 276.9952 | 281.9699
Kleinburg TS | 163.8536 | 192.6433 | 206.5458 | 244.1759 | 248.5349 | 263.1171 | 268.9322 | 276.7392 | 285.5544 | 294.5113 | 306.7422 | 313.7906 | 315.6385 | 317.6547 | 319.2443 | 320.6408 | 322.013 | 335.6412 | 352.0182 | 353.2931
Lorne Park TS | 56.059 | 56.9213 | 59.9627 | 63.8335 | 68.738 | 74.4515 | 82.1003 | 89.286 | 94.6816 | 95.6549 | 100.7689 | 106.5587 | 112.9255 | 119.5193 | 126.5662 | 128.9547 | 131.4328 | 134.027 | 136.6427 | 139.2895
Meadowvale TS | 75.0471 | 76.2197 | 83.8244 | 85.7759 | 96.0458 | 106.0787 | 111.8749 | 116.1364 | 121.4176 | 125.7516 | 132.5397 | 140.2994 | 148.6033 | 157.4096 | 166.7375 | 170.039 | 173.3804 | 176.7953 | 180.2031 | 183.7334
Oakville TS | 82.9772 | 88.0064 | 91.5946 | 95.3451 | 96.3961 | 100.7561 | 104.2288 | 109.7788 | 114.341 | 119.0727 | 123.0919 | 127.995 | 133.2794 | 138.6669 | 144.2905 | 148.3766 | 152.399 | 155.3675 | 158.3506 | 161.352
Palermo TS | 67.8291 | 85.0957 | 85.5635 | 117.4304 | 130.3678 | 138.1853 | 144.9195 | 143.6495 | 145.1022 | 147.1096 | 151.1642 | 153.7878 | 157.01 | 160.3523 | 165.26 | 169.0159 | 172.5003 | 175.2372 | 180.3146 | 183.3372
Pleasant TS | 320.6109 | 343.2347 | 372.8698 | 412.4014 | 449.3232 | 486.8279 | 522.4577 | 552.1153 | 582.891 | 626.577 | 680.0423 | 737.4504 | 793.4744 | 850.0835 | 908.9217 | 968.863 | 1004.1572 | 1039.4417 | 1074.3115 | 1104.322
Tomken TS | 166.7647 | 168.1628 | 170.423 | 176.1839 | 185.3108 | 193.9444 | 202.9953 | 209.8767 | 216.5042 | 221.2491 | 233.2114 | 246.6659 | 261.4097 | 276.7129 | 293.0547 | 298.616 | 304.3764 | 310.3915 | 316.4631 | 322.6119
Trafalgar TS | 50.8635 | 52.6444 | 54.4941 | 56.5292 | 58.4431 | 60.2799 | 62.2225 | 63.9628 | 65.9245 | 68.2461 | 71.5961 | 74.9909 | 78.4531 | 82.2072 | 87.8683 | 92.8318 | 98.1577 | 102.51 | 106.9341 | 111.4871
Tremaine TS | 71.2816 | 74.646 | 77.7146 | 80.7485 | 83.552 | 86.8079 | 90.065 | 95.1105 | 100.4228 | 105.5958 | 112.2207 | 119.3556 | 125.5739 | 131.2402 | 136.9967 | 142.9867 | 148.806 | 153.4126 | 157.9743 | 161.86
Total Region | 2227.5076 | 2347.0943 | 2476.0319 | 2702.417 | 2910.4879 | 3147.709 | 3397.9459 | 3601.9621 | 3788.8119 | 4032.7997 | 4258.0809 | 4498.8421 | 4745.6198 | 4998.5328 | 5265.5679 | 5464.1642 | 5592.9892 | 5731.0884 | 5871.7535 | 5993.7061
This document and the information contained herein is provided for informational purposes only and is subject to redaction and/or aggregation to protect against identifying specific customer electricity usage. The IESO has prepared this document based on information currently available to the IESO and reasonable assumptions associated therewith, including relating to electricity supply and demand. The information, statements and conclusions contained herein are subject to risks, uncertainties and other factors, and actual results or circumstances may differ materially. The IESO provides no guarantee, representation, or warranty, express or implied, with respect to any statement or information contained herein and disclaims any liability in connection therewith. Readers are cautioned not to place undue reliance on forward-looking information contained in this document as actual results could differ materially from the plans, expectations, estimates, intentions and statements expressed herein. The IESO undertakes no obligation to revise or update any information contained in this document as a result of new information, future events or otherwise. In the event there is any conflict or inconsistency between this document and the IESO market rules, any IESO contract, any legislation or regulation, or any request for proposals or other procurement document, the terms in the market rules, or the subject contract, legislation, regulation, or procurement document, as applicable, govern.
DRAFT

## Summer DG
Peak demand contribution from contracted, existing distributed generation was estimated based on technology type and totalled for each station in the region. The resulting forecast savings were applied to gross demand to help determine the net peak demand for the IRRP planning forecast. Additional details on the overall IRRP forecast methodology will be provided in the final report.
Transformer Station | SUMMER: Total Contracted Distributed Generation (DG) Contribution to Peak (MW)
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
Bramalea TS | 16.7123 | 16.7123 | 16.7123 | 16.7123 | 16.7123 | 2.7523 | 2.0634 | 2.0282 | 1.666 | 1.3117 | 0.86275 | 0.53324 | 0.013323 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff TS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Churchill Meadows TS | 0.71601 | 0.71601 | 0.71601 | 0.71601 | 0.71601 | 0.71601 | 0.71601 | 0.69729 | 0.65111 | 0.63369 | 0.55501 | 0.45227 | 0.04171 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cooksville TS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Erindale TS | 8.0036 | 8.0036 | 2.3786 | 2.3723 | 2.3723 | 2.3723 | 2.3682 | 2.3384 | 2.0891 | 1.7951 | 1.6155 | 1.2403 | 0.11962 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Glenorchy MTS | 0.32119 | 0.32119 | 0.32119 | 0.32119 | 0.32119 | 0.32119 | 0.32119 | 0.32119 | 0.31842 | 0.3174 | 0.074588 | 0.023005 | 0.014653 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Goreway TS | 3.333 | 3.333 | 3.333 | 3.333 | 3.333 | 3.333 | 3.27 | 3.0641 | 2.8769 | 2.5505 | 1.7371 | 1.1561 | 0.21352 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Halton TS | 0.98295 | 0.98295 | 0.98295 | 0.98295 | 0.98073 | 0.98073 | 0.97004 | 0.79125 | 0.53306 | 0.3613 | 0.21206 | 0.14817 | 0.012161 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Halton Hills MTS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Jim Yarrow MTS | 1.5385 | 1.5385 | 1.5385 | 1.5385 | 1.5385 | 1.5385 | 1.5385 | 1.4861 | 1.398 | 0.94482 | 0.77866 | 0.63047 | 0.067302 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kleinburg TS | 0.79284 | 0.79284 | 0.79284 | 0.79284 | 0.79184 | 0.79184 | 0.78001 | 0.74305 | 0.54043 | 0.52857 | 0.38008 | 0.17046 | 0.14766 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lorne Park TS | 0.17319 | 0.17319 | 0.17319 | 0.17319 | 0.17319 | 0.17319 | 0.17319 | 0.074757 | 0.068644 | 0.068644 | 0.063641 | 0.046683 | 0.010126 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Meadowvale TS | 0.59371 | 0.59371 | 0.59371 | 0.59371 | 0.59371 | 0.59371 | 0.59371 | 0.57935 | 0.50576 | 0.31219 | 0.2209 | 0.15389 | 0.01964 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Oakville TS | 0.41774 | 0.41774 | 0.41774 | 0.41774 | 0.41774 | 0.41774 | 0.38584 | 0.2693 | 0.25931 | 0.25931 | 0.15933 | 0.15459 | 0.011481 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Palermo TS | 0.0075532 | 0.0075532 | 0.0075532 | 0.0075532 | 0.0075532 | 0.0075532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pleasant TS | 3.9179 | 3.9179 | 3.9179 | 3.9179 | 3.9127 | 3.9127 | 3.7676 | 3.4329 | 3.248 | 2.8641 | 1.9545 | 1.0602 | 0.21709 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tomken TS | 1.9192 | 1.9192 | 1.9192 | 1.9192 | 1.9192 | 1.9192 | 1.6631 | 1.5977 | 1.3394 | 1.0364 | 0.37819 | 0.23544 | 0.033524 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Trafalgar TS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tremaine TS | 0.35237 | 0.35237 | 0.35237 | 0.35237 | 0.35237 | 0.35237 | 0.35237 | 0.35237 | 0.35147 | 0.33416 | 0.28249 | 0.1872 | 0.0071 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Region | 39.782 | 39.782 | 34.157 | 34.1507 | 34.1423 | 20.1823 | 18.9633 | 17.7761 | 15.8456 | 13.3179 | 9.2747 | 6.192 | 0.92891 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DRAFT

## Winter DG
Peak demand contribution from contracted, existing distributed generation was estimated based on technology type and totalled for each station in the region. The resulting forecast savings were applied to gross demand to help determine the net peak demand for the IRRP planning forecast. Additional details on the overall IRRP forecast methodology will be provided in the final report.
Transformer Station | WINTER: Total Contracted Distributed Generation (DG) Contribution to Peak (MW)
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
Bramalea TS | 14.63 | 14.63 | 14.63 | 14.63 | 14.63 | 0.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cardiff TS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Churchill Meadows TS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cooksville TS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Erindale TS | 5.625 | 5.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Glenorchy MTS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Goreway TS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Halton TS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Halton Hills MTS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Jim Yarrow MTS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kleinburg TS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lorne Park TS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Meadowvale TS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Oakville TS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Palermo TS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pleasant TS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tomken TS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Trafalgar TS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tremaine TS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Region | 20.255 | 20.255 | 14.63 | 14.63 | 14.63 | 0.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DRAFT

## Summer CDM
Peak demand savings from codes and standards, as well as the delivery of conservation programs, were estimated for each sector and totalled for each station in the region. The resulting forecast savings were applied to gross demand to help determine the net peak demand for the IRRP planning forecast. Additional details on the overall IRRP forecast methodology will be provided in the final report.
Transformer Station | SUMMER: Total Conservation and Demand Management (CDM) Forecast (MW)
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
Bramalea TS | 5.7729 | 11.442 | 18.8801 | 26.2472 | 34.8869 | 42.2508 | 49.7935 | 56.7511 | 63.5813 | 71.2515 | 76.2973 | 80.1368 | 82.5376 | 85.1022 | 87.9186 | 90.8638 | 92.2997 | 93.8191 | 95.7481 | 97.3126
Cardiff TS | 2.2649 | 4.4263 | 6.9922 | 9.0924 | 11.2751 | 13.2089 | 15.0991 | 17.3549 | 19.5898 | 22.1071 | 24.0556 | 25.705 | 26.3231 | 27.0393 | 27.76 | 28.5525 | 29.1692 | 29.8576 | 30.6813 | 31.3187
Churchill Meadows TS | 1.9416 | 3.7843 | 6.5176 | 9.1769 | 12.2499 | 15.3703 | 18.1524 | 20.2396 | 22.1851 | 24.3127 | 25.6837 | 26.6729 | 27.2296 | 27.8784 | 28.5444 | 29.282 | 29.8385 | 30.4584 | 31.2153 | 31.7929
Cooksville TS | 1.684 | 3.291 | 5.1988 | 7.462 | 11.472 | 17.7206 | 24.6841 | 31.29 | 36.8628 | 42.2952 | 45.4256 | 47.944 | 49.0806 | 50.3976 | 51.7261 | 53.1876 | 54.3215 | 55.5856 | 57.1012 | 58.2733
Erindale TS | 8.1988 | 15.4764 | 24.9334 | 33.0542 | 41.772 | 50.1596 | 58.7357 | 67.9578 | 77.2021 | 87.6292 | 94.7133 | 99.7435 | 102.9319 | 105.694 | 108.4802 | 111.5451 | 113.9232 | 116.5741 | 119.7526 | 122.2109
Glenorchy MTS | 1.5567 | 2.8775 | 5.2099 | 5.3571 | 6.945 | 8.3536 | 10.0177 | 9.7493 | 11.2056 | 12.1465 | 12.9943 | 13.6836 | 14.3139 | 15.0095 | 14.9265 | 15.4115 | 15.8864 | 16.2848 | 16.2846 | 16.6921
Goreway TS | 4.5888 | 9.2191 | 15.2257 | 20.8863 | 27.4355 | 33.4966 | 39.7485 | 46.0302 | 52.3949 | 59.3069 | 63.8397 | 67.3395 | 69.5442 | 71.8387 | 74.4149 | 77.2446 | 78.284 | 79.3474 | 80.7555 | 81.9146
Halton TS | 1.4888 | 2.8927 | 4.4489 | 6.2057 | 9.3492 | 11.5937 | 13.8968 | 17.1202 | 18.6576 | 19.9057 | 20.9554 | 21.1678 | 21.916 | 22.8135 | 23.4813 | 24.7012 | 25.2938 | 25.9563 | 26.6648 | 27.7182
Halton Hills MTS | 0.091974 | 0.16651 | 0.25579 | 0.30953 | 0.41215 | 0.51985 | 0.73348 | 0.82001 | 0.90616 | 0.93917 | 1.0618 | 1.052 | 1.0554 | 1.1143 | 1.0705 | 1.0821 | 1.0726 | 1.0692 | 1.0607 | 1.1017
Jim Yarrow MTS | 2.2992 | 4.6137 | 7.6109 | 10.4258 | 13.675 | 16.6795 | 19.7756 | 22.882 | 26.0252 | 29.4361 | 31.6645 | 33.3806 | 34.4535 | 35.5709 | 36.8277 | 38.2089 | 38.715 | 39.2327 | 39.9209 | 40.4855
Kleinburg TS | 2.0728 | 4.5754 | 7.2438 | 10.9868 | 13.4897 | 16.9367 | 20.1514 | 23.2631 | 26.3897 | 28.9731 | 30.3703 | 31.6215 | 31.8821 | 32.0376 | 33.4589 | 35.0247 | 36.6863 | 38.5168 | 40.54 | 40.7373
Lorne Park TS | 1.7508 | 3.4216 | 5.6209 | 7.5898 | 9.7598 | 11.8415 | 14.0021 | 16.1318 | 18.2536 | 20.0229 | 21.1997 | 22.0677 | 22.5908 | 23.1971 | 23.8085 | 24.4812 | 25.0031 | 25.585 | 26.2826 | 26.8221
Meadowvale TS | 2.1634 | 4.2159 | 7.2215 | 10.1512 | 13.3454 | 17.1185 | 20.0486 | 22.9119 | 25.6919 | 28.8091 | 30.4522 | 31.7786 | 32.5493 | 33.4463 | 34.24 | 34.9451 | 35.6604 | 36.4667 | 37.3063 | 38.048
Oakville TS | 2.2035 | 4.4079 | 7.1158 | 9.4915 | 11.8206 | 14.221 | 16.4866 | 18.9021 | 21.0155 | 23.2084 | 24.548 | 25.5531 | 26.0997 | 26.7134 | 27.396 | 28.1571 | 28.7362 | 29.2883 | 29.9691 | 30.5324
Palermo TS | 1.5252 | 3.4504 | 5.3729 | 8.6176 | 12.0527 | 14.9609 | 17.8205 | 19.6531 | 21.5496 | 23.437 | 24.8042 | 25.3704 | 25.6408 | 25.9446 | 26.9112 | 27.2373 | 27.5623 | 27.8887 | 28.6705 | 29.0613
Pleasant TS | 6.5095 | 13.1129 | 21.7185 | 29.8819 | 39.0893 | 47.6562 | 56.4018 | 65.1892 | 74.0366 | 83.9036 | 92.6292 | 99.1905 | 104.1393 | 109.538 | 114.6323 | 120.3241 | 123.7091 | 127.1902 | 131.112 | 134.5701
Tomken TS | 3.5391 | 6.9164 | 10.9258 | 14.2075 | 17.6181 | 20.6398 | 23.5934 | 26.3063 | 28.8382 | 31.6335 | 33.4927 | 34.8639 | 35.6905 | 36.6482 | 38.7762 | 41.0424 | 43.0893 | 44.0919 | 45.2941 | 47.4054
Trafalgar TS | 1.0978 | 2.1432 | 3.4393 | 4.6021 | 5.8609 | 7.0431 | 8.2424 | 9.3716 | 10.4602 | 11.6508 | 12.5167 | 13.1837 | 13.5938 | 14.0682 | 14.7246 | 15.3651 | 16.0121 | 16.6296 | 17.2811 | 17.9513
Tremaine TS | 1.0916 | 2.0731 | 3.2148 | 4.363 | 6.0997 | 7.4762 | 8.8023 | 10.1586 | 11.4122 | 12.5643 | 13.5443 | 14.1678 | 14.6573 | 15.0496 | 15.4689 | 15.8742 | 16.2748 | 16.563 | 16.8771 | 17.0966
Total Region | 51.8414 | 102.5064 | 167.1467 | 228.1086 | 298.609 | 367.2474 | 436.1861 | 502.083 | 566.2581 | 633.5327 | 680.2487 | 714.6229 | 736.2294 | 759.1014 | 784.567 | 812.5305 | 831.5376 | 850.4053 | 872.5177 | 891.045
DRAFT

## Winter CDM
Peak demand savings from codes and standards, as well as the delivery of conservation programs, were estimated for each sector and totalled for each station in the region. The resulting forecast savings were applied to gross demand to help determine the net peak demand for the IRRP planning forecast. Additional details on the overall IRRP forecast methodology will be provided in the final report.
Transformer Station | WINTER: Total Conservation and Demand Management (CDM) Forecast (MW)
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
Bramalea TS | 3.7242 | 7.6569 | 12.509 | 17.8095 | 25.0582 | 33.2603 | 42.3411 | 52.0769 | 62.2363 | 74.0324 | 81.7393 | 88.1853 | 93.4757 | 99.6548 | 106.0697 | 111.2166 | 114.0412 | 116.5988 | 119.2464 | 121.9696
Cardiff TS | 1.0399 | 2.1109 | 3.361 | 4.5305 | 6.0222 | 7.4451 | 9.1833 | 10.946 | 12.7349 | 14.6996 | 16.1713 | 17.3834 | 18.4517 | 19.7301 | 21.0312 | 21.5865 | 22.1135 | 22.5883 | 23.1013 | 23.6444
Churchill Meadows TS | 0.97916 | 1.9876 | 3.7437 | 5.6085 | 8.1067 | 10.7068 | 12.466 | 14.1075 | 15.6187 | 17.3267 | 18.9375 | 20.2312 | 21.3486 | 22.7008 | 24.0701 | 24.6628 | 25.2219 | 25.7203 | 26.2612 | 26.8353
Cooksville TS | 0.84687 | 1.7191 | 2.7371 | 4.0918 | 6.8827 | 10.6871 | 19.8085 | 27.4088 | 34.8481 | 46.9723 | 51.6753 | 55.5486 | 58.9621 | 63.0475 | 67.205 | 68.9794 | 70.6634 | 72.1806 | 73.8198 | 75.5553
Erindale TS | 4.2215 | 8.6539 | 13.9099 | 19.0052 | 24.9707 | 31.0226 | 37.9874 | 45.2319 | 52.2765 | 62.2855 | 68.5217 | 73.6577 | 78.1841 | 83.6013 | 89.1142 | 91.4671 | 93.7001 | 95.7118 | 97.8855 | 100.1868
Glenorchy MTS | 0.58719 | 1.0529 | 1.8935 | 2.7222 | 3.5491 | 4.423 | 5.4718 | 6.4958 | 7.6283 | 8.8485 | 9.5628 | 10.0684 | 10.7047 | 11.3794 | 11.5828 | 12.2262 | 12.8635 | 13.3562 | 13.5524 | 14.0491
Goreway TS | 2.6775 | 5.6084 | 9.3748 | 13.553 | 19.3694 | 25.5807 | 32.6378 | 39.5604 | 46.6438 | 54.8414 | 60.8347 | 65.8689 | 69.8132 | 74.3789 | 79.1415 | 84.3155 | 86.5078 | 88.4706 | 90.4708 | 92.4979
Halton TS | 0.92089 | 1.8333 | 2.8112 | 3.9098 | 5.9057 | 7.592 | 9.2211 | 11.4841 | 12.5864 | 13.6306 | 13.8917 | 14.0476 | 14.5499 | 15.0558 | 15.6757 | 16.5207 | 16.9842 | 17.4871 | 17.9962 | 18.6432
Halton Hills MTS | 0.062403 | 0.12209 | 0.18459 | 0.2414 | 0.35699 | 0.48897 | 0.68627 | 0.77393 | 0.84763 | 0.95788 | 0.94642 | 0.95246 | 0.95821 | 0.96367 | 0.96861 | 0.97612 | 0.9791 | 0.98594 | 0.99257 | 0.99771
Jim Yarrow MTS | 1.2996 | 2.7178 | 4.5342 | 6.5384 | 9.318 | 12.2791 | 15.6386 | 18.9333 | 22.3008 | 26.196 | 29.0355 | 31.414 | 33.2743 | 35.4312 | 37.6789 | 40.1209 | 41.1556 | 42.0804 | 43.0238 | 43.9805
Kleinburg TS | 1.7274 | 4.1565 | 6.4555 | 9.4034 | 11.6333 | 14.5082 | 17.2884 | 20.1422 | 23.0634 | 26.2339 | 28.4103 | 30.0048 | 30.2978 | 30.5045 | 30.8517 | 31.0268 | 31.2467 | 32.6743 | 34.3485 | 34.5166
Lorne Park TS | 0.86856 | 1.7631 | 2.9286 | 4.1086 | 5.67 | 7.3638 | 9.5015 | 11.7921 | 13.9195 | 15.5837 | 17.144 | 18.429 | 19.5615 | 20.9169 | 22.2963 | 22.8849 | 23.4436 | 23.947 | 24.4908 | 25.0666
Meadowvale TS | 1.0628 | 2.239 | 3.7469 | 5.0801 | 7.2249 | 9.8082 | 12.0566 | 14.2797 | 16.6155 | 19.0824 | 20.9843 | 22.436 | 23.8963 | 25.4399 | 27.0831 | 27.6579 | 28.2705 | 28.8886 | 29.5944 | 30.2601
Oakville TS | 1.2352 | 2.5911 | 4.2282 | 5.7915 | 7.5811 | 9.5389 | 11.5692 | 13.9018 | 16.0951 | 18.5071 | 19.9379 | 21.0716 | 21.9753 | 23.0695 | 24.1649 | 25.0155 | 25.8323 | 26.4086 | 27.013 | 27.6428
Palermo TS | 0.66613 | 1.7242 | 2.6375 | 4.4174 | 6.4207 | 8.3709 | 10.2556 | 11.531 | 12.8665 | 14.2213 | 15.1193 | 15.5337 | 15.943 | 16.3649 | 17.0678 | 17.5523 | 18.0329 | 18.4264 | 19.1377 | 19.5483
Pleasant TS | 4.0079 | 8.411 | 14.162 | 20.4692 | 29.0049 | 37.9147 | 47.7592 | 57.4914 | 67.3038 | 79.2944 | 89.0096 | 97.6806 | 104.7577 | 112.5668 | 120.6783 | 129.1529 | 134.1187 | 138.8638 | 143.6062 | 147.9047
Tomken TS | 2.3729 | 4.7776 | 7.6235 | 10.3734 | 13.9628 | 17.4993 | 21.4023 | 25.2196 | 28.9249 | 32.7148 | 35.9903 | 38.6879 | 41.0654 | 43.9107 | 46.8063 | 48.0422 | 49.215 | 50.2717 | 51.4133 | 52.6221
Trafalgar TS | 0.61936 | 1.3101 | 2.0618 | 2.828 | 3.7539 | 4.7645 | 5.7375 | 6.7171 | 7.679 | 8.7606 | 9.5503 | 10.0976 | 10.6145 | 11.1708 | 12.0087 | 12.7101 | 13.4796 | 14.1181 | 14.8036 | 15.4821
Tremaine TS | 0.55948 | 1.0976 | 1.7455 | 2.3884 | 3.4294 | 4.4537 | 5.4611 | 6.5488 | 7.5731 | 8.5317 | 9.2334 | 9.8872 | 10.4109 | 10.8881 | 11.4838 | 12.0393 | 12.6096 | 13.1009 | 13.5765 | 13.9827
Total Region | 29.4788 | 61.5331 | 100.6485 | 142.8702 | 198.2206 | 257.7079 | 326.4732 | 394.6422 | 461.762 | 542.7207 | 596.696 | 641.1861 | 678.2449 | 720.7757 | 764.9786 | 798.1537 | 820.479 | 841.8795 | 864.3343 | 885.3858
DRAFT